## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_223-12_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_223-12_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_223-12_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_223-12_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_223-12_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_223-12_0_4_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_223-12_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_223-12_0_4_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_223-12_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_223-12_0_4_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_223-12_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_223-12_0_4_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_223-12_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_223-12_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_223-12_0_4_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_223-12_0_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_223-12_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_223-12_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_223-12_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_223-12_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_223-12_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_223-12_0_4_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_223-12_0_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_223-12_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_223-12_0_4_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_223-12_0_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_223-12_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_223-12_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_223-12_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_223-12_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_223-12_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_223-12_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_223-12_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_223-12_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_223-12_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_MV_371_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_223-12_0_4_load_0 | 0 | 0.0046442 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_223-12_0_4_load_26 | 5 | 0.0021256 | 0.00053273 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_223-12_0_4_load_27 | 6 | 0.029219 | 0.0073229 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_223-12_0_4_load_24 | 7 | 0.0025198 | 0.00063152 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_223-12_0_4_load_32 | 10 | 0.054112 | 0.013562 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_223-12_0_4_load_25 | 11 | 0.0059076 | 0.0014806 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_223-12_0_4_load_35 | 14 | 0.043776 | 0.010971 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_223-12_0_4_load_18 | 15 | 0.041464 | 0.010392 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_223-12_0_4_load_13 | 18 | 0.038283 | 0.0095947 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_223-12_0_4_load_21 | 20 | 0.044015 | 0.011031 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_223-12_0_4_load_28 | 21 | 0.0088118 | 0.0022085 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_223-12_0_4_load_33 | 22 | 0.031252 | 0.0078324 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_223-12_0_4_load_17 | 23 | 0.043773 | 0.01097 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_223-12_0_4_load_36 | 24 | 0.0032365 | 0.00081115 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_223-12_0_4_load_37 | 25 | 0.0078629 | 0.0019706 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_223-12_0_4_load_19 | 26 | 0.030448 | 0.0076311 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_223-12_0_4_load_22 | 28 | 0.0044253 | 0.0011091 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_223-12_0_4_load_31 | 30 | 0.0077887 | 0.001952 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_223-12_0_4_load_16 | 31 | 0.099663 | 0.024978 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_223-12_0_4_load_20 | 34 | 0.017429 | 0.0043681 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_223-12_0_4_line_0 |  | 0 | 1 | 0.0097863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_223-12_0_4_line_1 |  | 0 | 2 | 0.029965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_223-12_0_4_line_2 |  | 1 | 3 | 0.009115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_223-12_0_4_line_3 |  | 2 | 4 | 0.003967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_223-12_0_4_line_4 |  | 3 | 5 | 0.021246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_223-12_0_4_line_5 |  | 3 | 6 | 0.018908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_223-12_0_4_line_6 |  | 3 | 7 | 0.009942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_223-12_0_4_line_7 |  | 4 | 11 | 0.028393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_223-12_0_4_line_8 |  | 5 | 21 | 0.0081695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_223-12_0_4_line_9 |  | 6 | 22 | 0.017669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_223-12_0_4_line_10 |  | 8 | 9 | 0.002994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_223-12_0_4_line_11 |  | 8 | 10 | 0.028105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_223-12_0_4_line_12 |  | 9 | 23 | 0.014592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_223-12_0_4_line_13 |  | 9 | 12 | 0.004645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_223-12_0_4_line_14 |  | 10 | 22 | 0.026193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_223-12_0_4_line_15 |  | 12 | 13 | 0.009614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_223-12_0_4_line_16 |  | 12 | 14 | 0.0060687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_223-12_0_4_line_17 |  | 13 | 15 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_223-12_0_4_line_18 |  | 15 | 26 | 0.013152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_223-12_0_4_line_19 |  | 16 | 17 | 0.020172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_223-12_0_4_line_20 |  | 16 | 18 | 0.014944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_223-12_0_4_line_21 |  | 17 | 19 | 0.033822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_223-12_0_4_line_22 |  | 17 | 20 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_223-12_0_4_line_23 |  | 18 | 27 | 0.0012665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_223-12_0_4_line_24 |  | 19 | 24 | 0.017048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_223-12_0_4_line_25 |  | 20 | 28 | 0.0043485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_223-12_0_4_line_26 |  | 21 | 33 | 0.00027573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_223-12_0_4_line_27 |  | 24 | 25 | 0.0118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_223-12_0_4_line_28 |  | 26 | 34 | 0.00024299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_223-12_0_4_line_29 |  | 27 | 29 | 0.015348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_223-12_0_4_line_30 |  | 29 | 30 | 0.010791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_223-12_0_4_line_31 |  | 30 | 33 | 0.019586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_223-12_0_4_line_32 |  | 31 | 32 | 0.029823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_223-12_0_4_line_33 |  | 32 | 33 | 0.013046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_223-12_0_4_trafo_17 | 0.63 MVA 20/0.4 kV | 35 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2692503.4781 | 1264891.0236 | 2692505.1338 | 1264883.41 | 2692505.8338 | 1264881.5422
1 | 2692509.2248 | 1264852.5378 | 2692510.1764 | 1264855.7442 | 2692510.6238 | 1264859.8768 | 2692510.9984 | 1264863.3744 | 2692509.0245 | 1264873.0291 | 2692505.8338 | 1264881.5422
2 | 2692503.4781 | 1264891.0236 | 2692504.4864 | 1264894.9314 | 2692509.3807 | 1264893.5736
3 | 2692509.2248 | 1264852.5378 | 2692512.6385 | 1264850.5007
4 | 2692509.3807 | 1264893.5736 | 2692525.6445 | 1264888.5796 | 2692529.4502 | 1264890.4324
5 | 2692509.3807 | 1264893.5736 | 2692510.8627 | 1264899.9353 | 2692513.2787 | 1264907.2568 | 2692515.3046 | 1264911.4602
6 | 2692509.3807 | 1264893.5736 | 2692508.6435 | 1264890.1482 | 2692508.2985 | 1264886.6844 | 2692508.77 | 1264885.4352 | 2692509.9474 | 1264884.3194
7 | 2692512.6385 | 1264850.5007 | 2692524.5751 | 1264843.3595 | 2692537.115 | 1264850.606
8 | 2692529.4502 | 1264890.4324 | 2692536.7955 | 1264894.0084
9 | 2692515.3046 | 1264911.4602 | 2692518.2901 | 1264917.6547 | 2692522.9762 | 1264927.3765
10 | 2692555.2692 | 1264968.2189 | 2692553.1201 | 1264970.3092
11 | 2692553.1201 | 1264970.3092 | 2692546.5379 | 1264967.882 | 2692542.0983 | 1264964.254 | 2692534.7098 | 1264950.7923
12 | 2692555.2692 | 1264968.2189 | 2692559.703 | 1264963.5623 | 2692565.1782 | 1264957.5093
13 | 2692558.7763 | 1264971.2763 | 2692555.2692 | 1264968.2189
14 | 2692534.7098 | 1264950.7923 | 2692534.6 | 1264950.5922 | 2692527.5689 | 1264936.9044 | 2692522.9762 | 1264927.3765
15 | 2692558.7763 | 1264971.2763 | 2692565.2595 | 1264964.1609
16 | 2692558.7763 | 1264971.2763 | 2692561.6679 | 1264973.7125 | 2692560.241 | 1264975.5007
17 | 2692565.2595 | 1264964.1609 | 2692568.6001 | 1264966.782 | 2692576.0869 | 1264972.6301
18 | 2692586.4518 | 1264980.7264 | 2692576.0869 | 1264972.6301
19 | 2692593.3663 | 1264918.5751 | 2692597.8176 | 1264920.969 | 2692594.9036 | 1264928.1292 | 2692601.8066 | 1264930.7616
20 | 2692593.3663 | 1264918.5751 | 2692589.2062 | 1264916.3415 | 2692587.0998 | 1264915.2187 | 2692580.1276 | 1264911.6441
21 | 2692633.4831 | 1264942.8676 | 2692601.8066 | 1264930.7616
22 | 2692601.8066 | 1264930.7616 | 2692606.0446 | 1264948.5412
23 | 2692579.0006 | 1264911.0663 | 2692580.1276 | 1264911.6441
24 | 2692633.4831 | 1264942.8676 | 2692640.8411 | 1264958.2456
25 | 2692607.0529 | 1264952.7712 | 2692606.0446 | 1264948.5412
26 | 2692537.0434 | 1264894.1291 | 2692536.7955 | 1264894.0084
27 | 2692640.8411 | 1264958.2456 | 2692641.4977 | 1264959.6179 | 2692649.4541 | 1264966.125
28 | 2692586.6433 | 1264980.876 | 2692586.4518 | 1264980.7264
29 | 2692579.0006 | 1264911.0663 | 2692565.4213 | 1264903.8367
30 | 2692565.4213 | 1264903.8367 | 2692555.8979 | 1264898.7613
31 | 2692537.0434 | 1264894.1291 | 2692541.9767 | 1264896.5305 | 2692555.8979 | 1264898.7613
32 | 2692545.9651 | 1264903.4763 | 2692545.5407 | 1264904.1258 | 2692540.7248 | 1264912.0235 | 2692540.1069 | 1264913.0035 | 2692541.4455 | 1264918.4177 | 2692552.6393 | 1264925.1487
33 | 2692545.9651 | 1264903.4763 | 2692543.2348 | 1264901.7989 | 2692542.0034 | 1264900.1116 | 2692537.0434 | 1264894.1291

## bus_geodata
| x | y | coords
0 | 2692505.8338 | 1264881.5422
1 | 2692503.4781 | 1264891.0236
2 | 2692509.2248 | 1264852.5378
3 | 2692509.3807 | 1264893.5736
4 | 2692512.6385 | 1264850.5007
5 | 2692529.4502 | 1264890.4324
6 | 2692515.3046 | 1264911.4602
7 | 2692509.9474 | 1264884.3194
8 | 2692553.1201 | 1264970.3092
9 | 2692555.2692 | 1264968.2189
10 | 2692534.7098 | 1264950.7923
11 | 2692537.115 | 1264850.606
12 | 2692558.7763 | 1264971.2763
13 | 2692565.2595 | 1264964.1609
14 | 2692560.241 | 1264975.5007
15 | 2692576.0869 | 1264972.6301
16 | 2692593.3663 | 1264918.5751
17 | 2692601.8066 | 1264930.7616
18 | 2692580.1276 | 1264911.6441
19 | 2692633.4831 | 1264942.8676
20 | 2692606.0446 | 1264948.5412
21 | 2692536.7955 | 1264894.0084
22 | 2692522.9762 | 1264927.3765
23 | 2692565.1782 | 1264957.5093
24 | 2692640.8411 | 1264958.2456
25 | 2692649.4541 | 1264966.125
26 | 2692586.4518 | 1264980.7264
27 | 2692579.0006 | 1264911.0663
28 | 2692607.0529 | 1264952.7712
29 | 2692565.4213 | 1264903.8367
30 | 2692555.8979 | 1264898.7613
31 | 2692552.6393 | 1264925.1487
32 | 2692545.9651 | 1264903.4763
33 | 2692537.0434 | 1264894.1291
34 | 2692586.6433 | 1264980.876
35 | 2692555.2692 | 1264968.2189

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99198 | -0.1535 | 0.0046442 | 0.0011639
1 | 0.99208 | -0.15167 | 0 | 0
2 | 0.99182 | -0.15664 | 0 | 0
3 | 0.99217 | -0.14997 | 0 | 0
4 | 0.9918 | -0.15706 | 0 | 0
5 | 0.99111 | -0.17033 | 0.0021256 | 0.00053273
6 | 0.99316 | -0.1308 | 0.029219 | 0.0073229
7 | 0.99214 | -0.15041 | 0.0025198 | 0.00063152
8 | 0.99817 | -0.034879 | 0 | 0
9 | 0.99841 | -0.030377 | 0 | 0
10 | 0.99595 | -0.077242 | 0.054112 | 0.013562
11 | 0.99165 | -0.16003 | 0.0059076 | 0.0014806
12 | 0.99784 | -0.041195 | 0 | 0
13 | 0.99706 | -0.056243 | 0 | 0
14 | 0.9976 | -0.045847 | 0.043776 | 0.010971
15 | 0.99594 | -0.077799 | 0.041464 | 0.010392
16 | 0.98549 | -0.27927 | 0 | 0
17 | 0.98438 | -0.30085 | 0 | 0
18 | 0.98631 | -0.26331 | 0.038283 | 0.0095947
19 | 0.98403 | -0.3076 | 0 | 0
20 | 0.98356 | -0.31679 | 0.044015 | 0.011031
21 | 0.99071 | -0.17809 | 0.0088118 | 0.0022085
22 | 0.99421 | -0.11064 | 0.031252 | 0.0078324
23 | 1 | 0 | -0.48253 | -0.12203
24 | 0.98386 | -0.31101 | 0.0032365 | 0.00081115
25 | 0.98377 | -0.31268 | 0.0078629 | 0.0019706
26 | 0.99537 | -0.08887 | 0.030448 | 0.0076311
27 | 0.98642 | -0.26109 | 0 | 0
28 | 0.98355 | -0.31713 | 0.0044253 | 0.0011091
29 | 0.9878 | -0.23424 | 0 | 0
30 | 0.98878 | -0.2154 | 0.0077887 | 0.001952
31 | 0.98676 | -0.25477 | 0.099663 | 0.024978
32 | 0.98949 | -0.20171 | 0 | 0
33 | 0.99068 | -0.17859 | 0 | 0
34 | 0.99537 | -0.088944 | 0.017429 | 0.0043681
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010554 | -0.0026449 | 0.010555 | 0.0026454 | 9.1972e-07 | 4.6227e-07 | 0.015831 | 0.015831 | 0.015831 | 0.99198 | -0.1535 | 0.99208 | -0.15167 | 4.3491
1 | 0.0059095 | 0.001481 | -0.0059086 | -0.0014808 | 8.8297e-07 | 1.7833e-07 | 0.0088644 | 0.0088645 | 0.0088645 | 0.99198 | -0.1535 | 0.99182 | -0.15664 | 2.4353
2 | -0.010555 | -0.0026454 | 0.010555 | 0.0026458 | 8.5663e-07 | 4.3054e-07 | 0.015831 | 0.015831 | 0.015831 | 0.99208 | -0.15167 | 0.99217 | -0.14997 | 4.3491
3 | 0.0059086 | 0.0014808 | -0.0059085 | -0.0014808 | 1.169e-07 | 2.3619e-08 | 0.0088645 | 0.0088646 | 0.0088646 | 0.99182 | -0.15664 | 0.9918 | -0.15706 | 2.4353
4 | 0.21743 | 0.054965 | -0.21722 | -0.054831 | 0.00021203 | 0.0001346 | 0.32627 | 0.32627 | 0.32627 | 0.99217 | -0.14997 | 0.99111 | -0.17033 | 22.4084
5 | -0.23051 | -0.058243 | 0.23072 | 0.058377 | 0.00021206 | 0.00013474 | 0.34588 | 0.34588 | 0.34588 | 0.99217 | -0.14997 | 0.99316 | -0.1308 | 23.7553
6 | 0.0025199 | 0.00063143 | -0.0025198 | -0.00063152 | 5.3248e-08 | -9.4315e-08 | 0.0037792 | 0.0037792 | 0.0037792 | 0.99217 | -0.14997 | 0.99214 | -0.15041 | 1.0382
7 | 0.0059085 | 0.0014808 | -0.0059076 | -0.0014806 | 8.3668e-07 | 1.6912e-07 | 0.0088646 | 0.0088647 | 0.0088647 | 0.9918 | -0.15706 | 0.99165 | -0.16003 | 2.4354
8 | 0.2151 | 0.054298 | -0.21502 | -0.054247 | 7.9942e-05 | 5.0742e-05 | 0.32308 | 0.32308 | 0.32308 | 0.99111 | -0.17033 | 0.99071 | -0.17809 | 22.1893
9 | -0.25994 | -0.0657 | 0.26019 | 0.06586 | 0.0002515 | 0.00016004 | 0.38965 | 0.38965 | 0.38965 | 0.99316 | -0.1308 | 0.99421 | -0.11064 | 26.7619
10 | -0.34673 | -0.088002 | 0.3468 | 0.08805 | 7.5104e-05 | 4.791e-05 | 0.51727 | 0.51727 | 0.51727 | 0.99817 | -0.034879 | 0.99841 | -0.030377 | 35.5269
11 | 0.34673 | 0.088002 | -0.34602 | -0.087552 | 0.00070501 | 0.00044974 | 0.51727 | 0.51727 | 0.51727 | 0.99817 | -0.034879 | 0.99595 | -0.077242 | 35.527
12 | -0.48018 | -0.12158 | 0.48088 | 0.12203 | 0.00070148 | 0.00044818 | 0.71609 | 0.71609 | 0.71609 | 0.99841 | -0.030377 | 1 | 0 | 49.1821
13 | 0.13338 | 0.033528 | -0.13331 | -0.033484 | 6.8855e-05 | 4.4007e-05 | 0.19882 | 0.19882 | 0.19882 | 0.99841 | -0.030377 | 0.99784 | -0.041195 | 54.621
14 | 0.29191 | 0.073991 | -0.29144 | -0.073693 | 0.00046772 | 0.00029798 | 0.43643 | 0.43643 | 0.43643 | 0.99595 | -0.077242 | 0.99421 | -0.11064 | 29.9743
15 | 0.089523 | 0.022507 | -0.089459 | -0.022466 | 6.4277e-05 | 4.1012e-05 | 0.13352 | 0.13352 | 0.13352 | 0.99784 | -0.041195 | 0.99706 | -0.056243 | 36.6825
16 | 0.043786 | 0.010977 | -0.043776 | -0.010971 | 9.7029e-06 | 6.1306e-06 | 0.065296 | 0.065296 | 0.065296 | 0.99784 | -0.041195 | 0.9976 | -0.045847 | 17.9384
17 | 0.089459 | 0.022466 | -0.089367 | -0.022407 | 9.1905e-05 | 5.864e-05 | 0.13352 | 0.13352 | 0.13352 | 0.99706 | -0.056243 | 0.99594 | -0.077799 | 36.6826
18 | 0.047903 | 0.012015 | -0.047877 | -0.011999 | 2.5266e-05 | 1.5999e-05 | 0.071573 | 0.071574 | 0.071574 | 0.99594 | -0.077799 | 0.99537 | -0.08887 | 19.6631
19 | 0.059644 | 0.014987 | -0.059583 | -0.014948 | 6.1372e-05 | 3.9022e-05 | 0.090072 | 0.090072 | 0.090072 | 0.98549 | -0.27927 | 0.98438 | -0.30085 | 24.7451
20 | -0.059644 | -0.014987 | 0.059689 | 0.015016 | 4.5465e-05 | 2.8907e-05 | 0.090072 | 0.090072 | 0.090072 | 0.98549 | -0.27927 | 0.98631 | -0.26331 | 24.7451
21 | 0.011105 | 0.0027848 | -0.011102 | -0.002783 | 3.5746e-06 | 1.8579e-06 | 0.016788 | 0.016788 | 0.016788 | 0.98438 | -0.30085 | 0.98403 | -0.3076 | 4.6121
22 | 0.048477 | 0.012164 | -0.04844 | -0.01214 | 3.6811e-05 | 2.3327e-05 | 0.073284 | 0.073284 | 0.073284 | 0.98438 | -0.30085 | 0.98356 | -0.31679 | 20.1331
23 | -0.097973 | -0.024611 | 0.097983 | 0.024618 | 1.0379e-05 | 6.6263e-06 | 0.14783 | 0.14783 | 0.14783 | 0.98631 | -0.26331 | 0.98642 | -0.26109 | 40.6124
24 | 0.011102 | 0.002783 | -0.0111 | -0.002782 | 1.8018e-06 | 9.366e-07 | 0.016788 | 0.016788 | 0.016788 | 0.98403 | -0.3076 | 0.98386 | -0.31101 | 4.6121
25 | 0.0044254 | 0.0011091 | -0.0044253 | -0.0011091 | 7.3093e-08 | -8.4081e-09 | 0.0066951 | 0.0066951 | 0.0066951 | 0.98356 | -0.31679 | 0.98355 | -0.31713 | 1.8393
26 | 0.2062 | 0.052039 | -0.2062 | -0.052036 | 4.9633e-06 | 3.1694e-06 | 0.30984 | 0.30984 | 0.30984 | 0.99071 | -0.17809 | 0.99068 | -0.17859 | 42.5605
27 | 0.0078636 | 0.0019709 | -0.0078629 | -0.0019706 | 6.2588e-07 | 2.5073e-07 | 0.011893 | 0.011893 | 0.011893 | 0.98386 | -0.31101 | 0.98377 | -0.31268 | 3.2673
28 | 0.017429 | 0.0043681 | -0.017429 | -0.0043681 | 6.186e-08 | 3.6432e-08 | 0.026055 | 0.026055 | 0.026055 | 0.99537 | -0.08887 | 0.99537 | -0.088944 | 7.158
29 | -0.097983 | -0.024618 | 0.098109 | 0.024698 | 0.00012578 | 8.0301e-05 | 0.14783 | 0.14783 | 0.14783 | 0.98642 | -0.26109 | 0.9878 | -0.23424 | 40.6124
30 | -0.098109 | -0.024698 | 0.098197 | 0.024754 | 8.8436e-05 | 5.6461e-05 | 0.14783 | 0.14783 | 0.14783 | 0.9878 | -0.23424 | 0.98878 | -0.2154 | 40.6123
31 | -0.10599 | -0.026706 | 0.10617 | 0.026826 | 0.00018697 | 0.00011941 | 0.15955 | 0.15955 | 0.15955 | 0.98878 | -0.2154 | 0.99068 | -0.17859 | 43.8325
32 | -0.099663 | -0.024978 | 0.099916 | 0.025139 | 0.00025261 | 0.00016129 | 0.15029 | 0.15029 | 0.15029 | 0.98676 | -0.25477 | 0.98949 | -0.20171 | 41.2887
33 | -0.099916 | -0.025139 | 0.10003 | 0.02521 | 0.0001105 | 7.0554e-05 | 0.15029 | 0.15029 | 0.15029 | 0.98949 | -0.20171 | 0.99068 | -0.17859 | 41.2886

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5263 | 0.133

## res_load
| p_mw | q_mvar
0 | 0.0046442 | 0.0011639
1 | 0.0021256 | 0.00053273
2 | 0.029219 | 0.0073229
3 | 0.0025198 | 0.00063152
4 | 0.054112 | 0.013562
5 | 0.0059076 | 0.0014806
6 | 0.043776 | 0.010971
7 | 0.041464 | 0.010392
8 | 0.038283 | 0.0095947
9 | 0.044015 | 0.011031
10 | 0.0088118 | 0.0022085
11 | 0.031252 | 0.0078324
12 | 0.043773 | 0.01097
13 | 0.0032365 | 0.00081115
14 | 0.0078629 | 0.0019706
15 | 0.030448 | 0.0076311
16 | 0.0044253 | 0.0011091
17 | 0.0077887 | 0.001952
18 | 0.099663 | 0.024978
19 | 0.017429 | 0.0043681

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1