## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_223-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_223-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_223-15_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_223-15_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_223-15_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_223-15_0_2_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_223-15_0_2_node_117 | 0.4 | n |  | TRUE
7 | bus_LV_223-15_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_223-15_0_2_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_223-15_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_223-15_0_2_node_54 | 0.4 | n |  | TRUE
11 | bus_LV_223-15_0_2_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_223-15_0_2_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_223-15_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_223-15_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_223-15_0_2_node_69 | 0.4 | n |  | TRUE
16 | bus_LV_223-15_0_2_node_50 | 0.4 | n |  | TRUE
17 | bus_LV_223-15_0_2_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_223-15_0_2_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_223-15_0_2_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_223-15_0_2_node_58 | 0.4 | n |  | TRUE
21 | bus_LV_223-15_0_2_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_223-15_0_2_node_135 | 0.4 | n |  | TRUE
23 | bus_LV_223-15_0_2_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_223-15_0_2_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_223-15_0_2_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_223-15_0_2_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_223-15_0_2_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_223-15_0_2_node_123 | 0.4 | n |  | TRUE
29 | bus_LV_223-15_0_2_node_122 | 0.4 | n |  | TRUE
30 | bus_LV_223-15_0_2_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_223-15_0_2_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_223-15_0_2_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_223-15_0_2_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_223-15_0_2_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_223-15_0_2_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_223-15_0_2_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_223-15_0_2_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_223-15_0_2_node_132 | 0.4 | n |  | TRUE
39 | bus_LV_223-15_0_2_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_223-15_0_2_node_103 | 0.4 | n |  | TRUE
41 | bus_LV_223-15_0_2_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_223-15_0_2_node_116 | 0.4 | n |  | TRUE
43 | bus_LV_223-15_0_2_node_125 | 0.4 | n |  | TRUE
44 | bus_LV_223-15_0_2_node_124 | 0.4 | n |  | TRUE
45 | bus_LV_223-15_0_2_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_223-15_0_2_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_223-15_0_2_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_223-15_0_2_node_131 | 0.4 | n |  | TRUE
49 | bus_LV_223-15_0_2_node_80 | 0.4 | n |  | TRUE
50 | bus_LV_223-15_0_2_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_223-15_0_2_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_223-15_0_2_node_126 | 0.4 | n |  | TRUE
53 | bus_LV_223-15_0_2_node_134 | 0.4 | n |  | TRUE
54 | bus_LV_223-15_0_2_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_223-15_0_2_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_223-15_0_2_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_223-15_0_2_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_223-15_0_2_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_223-15_0_2_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_223-15_0_2_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_223-15_0_2_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_223-15_0_2_node_26 | 0.4 | n |  | TRUE
63 | bus_LV_223-15_0_2_node_28 | 0.4 | n |  | TRUE
64 | bus_LV_223-15_0_2_node_133 | 0.4 | n |  | TRUE
65 | bus_LV_223-15_0_2_node_129 | 0.4 | n |  | TRUE
66 | bus_LV_223-15_0_2_node_32 | 0.4 | n |  | TRUE
67 | bus_LV_223-15_0_2_node_33 | 0.4 | n |  | TRUE
68 | bus_LV_223-15_0_2_node_31 | 0.4 | n |  | TRUE
69 | bus_LV_223-15_0_2_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_223-15_0_2_node_101 | 0.4 | n |  | TRUE
71 | bus_LV_223-15_0_2_node_25 | 0.4 | n |  | TRUE
72 | bus_LV_223-15_0_2_node_105 | 0.4 | n |  | TRUE
73 | bus_LV_223-15_0_2_node_106 | 0.4 | n |  | TRUE
74 | bus_LV_223-15_0_2_node_35 | 0.4 | n |  | TRUE
75 | bus_LV_223-15_0_2_node_37 | 0.4 | n |  | TRUE
76 | bus_LV_223-15_0_2_node_45 | 0.4 | n |  | TRUE
77 | bus_LV_223-15_0_2_node_104 | 0.4 | n |  | TRUE
78 | bus_LV_223-15_0_2_node_99 | 0.4 | n |  | TRUE
79 | bus_LV_223-15_0_2_node_130 | 0.4 | n |  | TRUE
80 | bus_LV_223-15_0_2_node_97 | 0.4 | n |  | TRUE
81 | bus_LV_223-15_0_2_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_223-15_0_2_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_223-15_0_2_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_223-15_0_2_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_223-15_0_2_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_223-15_0_2_node_62 | 0.4 | n |  | TRUE
87 | bus_LV_223-15_0_2_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_223-15_0_2_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_223-15_0_2_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_223-15_0_2_node_67 | 0.4 | n |  | TRUE
91 | bus_LV_223-15_0_2_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_223-15_0_2_node_128 | 0.4 | n |  | TRUE
93 | bus_LV_223-15_0_2_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_223-15_0_2_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_223-15_0_2_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_223-15_0_2_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_223-15_0_2_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_223-15_0_2_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_223-15_0_2_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_223-15_0_2_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_223-15_0_2_node_75 | 0.4 | n |  | TRUE
102 | bus_LV_223-15_0_2_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_223-15_0_2_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_223-15_0_2_node_127 | 0.4 | n |  | TRUE
105 | bus_LV_223-15_0_2_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_223-15_0_2_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_223-15_0_2_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_223-15_0_2_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_223-15_0_2_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_223-15_0_2_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_223-15_0_2_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_223-15_0_2_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_223-15_0_2_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_223-15_0_2_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_223-15_0_2_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_223-15_0_2_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_223-15_0_2_node_98 | 0.4 | n |  | TRUE
118 | bus_LV_223-15_0_2_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_223-15_0_2_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_223-15_0_2_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_223-15_0_2_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_223-15_0_2_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_223-15_0_2_node_110 | 0.4 | n |  | TRUE
124 | bus_LV_223-15_0_2_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_223-15_0_2_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_223-15_0_2_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_223-15_0_2_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_223-15_0_2_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_223-15_0_2_node_113 | 0.4 | n |  | TRUE
130 | bus_LV_223-15_0_2_node_114 | 0.4 | n |  | TRUE
131 | bus_MV_371_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_223-15_0_2_load_0 | 0 | 0.0034897 | 0.00087459 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_223-15_0_2_load_1 | 1 | 0.00063471 | 0.00015907 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_223-15_0_2_load_3 | 3 | 0.00056962 | 0.00014276 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_223-15_0_2_load_117 | 6 | 0.001177 | 0.000295 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_223-15_0_2_load_54 | 10 | 0.0015607 | 0.00039115 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_223-15_0_2_load_22 | 12 | 0.0070049 | 0.0017556 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_223-15_0_2_load_69 | 15 | 0.00081787 | 0.00020498 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_223-15_0_2_load_50 | 16 | 0.004278 | 0.0010722 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_223-15_0_2_load_49 | 17 | 0.0016012 | 0.00040129 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_223-15_0_2_load_61 | 19 | 0.0017731 | 0.00044439 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_223-15_0_2_load_58 | 20 | 0.00094537 | 0.00023693 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_223-15_0_2_load_135 | 22 | 0.0020759 | 0.00052027 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_223-15_0_2_load_34 | 24 | 0.00043206 | 0.00010828 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_223-15_0_2_load_123 | 28 | 0.0024296 | 0.00060891 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_223-15_0_2_load_122 | 29 | 0.00087991 | 0.00022053 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_223-15_0_2_load_30 | 30 | 0.005626 | 0.00141 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_223-15_0_2_load_29 | 31 | 0.0028431 | 0.00071256 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_223-15_0_2_load_60 | 33 | 0.0024197 | 0.00060644 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_223-15_0_2_load_56 | 36 | 0.00081826 | 0.00020507 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_223-15_0_2_load_132 | 38 | 0.00011252 | 2.82e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_223-15_0_2_load_24 | 41 | 0.010087 | 0.0025279 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_223-15_0_2_load_116 | 42 | 0.0012229 | 0.0003065 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_223-15_0_2_load_125 | 43 | 0.012922 | 0.0032386 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_223-15_0_2_load_124 | 44 | 0.00082019 | 0.00020556 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_223-15_0_2_load_55 | 45 | 0.00097209 | 0.00024363 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_223-15_0_2_load_23 | 46 | 0.0008075 | 0.00020238 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_223-15_0_2_load_131 | 48 | 0.001384 | 0.00034687 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_223-15_0_2_load_80 | 49 | 0.0014006 | 0.00035102 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_223-15_0_2_load_52 | 51 | 0.0015269 | 0.00038267 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_223-15_0_2_load_126 | 52 | 0.00058004 | 0.00014537 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_223-15_0_2_load_134 | 53 | 0.0029311 | 0.0007346 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_223-15_0_2_load_53 | 55 | 0.0037252 | 0.00093363 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_223-15_0_2_load_51 | 56 | 0.003269 | 0.0008193 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_223-15_0_2_load_68 | 57 | 0.0011751 | 0.00029452 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_223-15_0_2_load_48 | 58 | 0.00065414 | 0.00016394 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_223-15_0_2_load_46 | 59 | 0.00095112 | 0.00023837 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_223-15_0_2_load_47 | 60 | 0.0014989 | 0.00037567 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_223-15_0_2_load_59 | 61 | 0.0006177 | 0.00015481 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_223-15_0_2_load_28 | 63 | 0.0038861 | 0.00097395 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_223-15_0_2_load_133 | 64 | 0.000132 | 3.3083e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_223-15_0_2_load_129 | 65 | 0.00040827 | 0.00010232 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_223-15_0_2_load_33 | 67 | 0.0010469 | 0.00026239 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_223-15_0_2_load_31 | 68 | 0.0066057 | 0.0016556 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_223-15_0_2_load_44 | 69 | 0.0023111 | 0.00057921 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_223-15_0_2_load_105 | 72 | 0.001128 | 0.0002827 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_223-15_0_2_load_106 | 73 | 0.0011407 | 0.00028588 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_223-15_0_2_load_35 | 74 | 0.002023 | 0.00050702 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_223-15_0_2_load_45 | 76 | 0.010981 | 0.0027521 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_223-15_0_2_load_99 | 78 | 0.00079353 | 0.00019888 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_223-15_0_2_load_130 | 79 | 0.0019705 | 0.00049384 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_223-15_0_2_load_65 | 81 | 0.0013808 | 0.00034605 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_223-15_0_2_load_78 | 82 | 0.0010127 | 0.00025382 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_223-15_0_2_load_76 | 83 | 0.00088341 | 0.0002214 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_223-15_0_2_load_71 | 85 | 0.0007205 | 0.00018057 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_223-15_0_2_load_62 | 86 | 0.0012477 | 0.00031269 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_223-15_0_2_load_63 | 87 | 0.00090808 | 0.00022759 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_223-15_0_2_load_70 | 91 | 0.0013896 | 0.00034827 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_223-15_0_2_load_128 | 92 | 0.0047565 | 0.0011921 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_223-15_0_2_load_89 | 93 | 0.00075232 | 0.00018855 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_223-15_0_2_load_88 | 95 | 0.0017094 | 0.00042843 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_223-15_0_2_load_73 | 96 | 0.0012062 | 0.00030231 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_223-15_0_2_load_81 | 97 | 0.0034186 | 0.00085679 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_223-15_0_2_load_85 | 98 | 0.0010836 | 0.00027159 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_223-15_0_2_load_84 | 100 | 0.001224 | 0.00030676 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_223-15_0_2_load_75 | 101 | 0.00080033 | 0.00020058 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_223-15_0_2_load_79 | 103 | 0.0010399 | 0.00026062 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_223-15_0_2_load_127 | 104 | 0.0016046 | 0.00040215 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_223-15_0_2_load_92 | 105 | 0.0009971 | 0.0002499 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_223-15_0_2_load_86 | 106 | 0.0015752 | 0.00039478 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_223-15_0_2_load_87 | 107 | 0.0011568 | 0.00028992 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_223-15_0_2_load_83 | 108 | 0.0011282 | 0.00028274 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_223-15_0_2_load_91 | 109 | 0.0011771 | 0.00029501 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_223-15_0_2_load_90 | 110 | 0.0011903 | 0.00029832 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_223-15_0_2_load_93 | 111 | 0.00012744 | 3.1939e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_223-15_0_2_load_94 | 112 | 0.00014084 | 3.5298e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_223-15_0_2_load_95 | 113 | 0.00013177 | 3.3025e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_223-15_0_2_load_96 | 114 | 0.0007748 | 0.00019418 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_223-15_0_2_load_102 | 115 | 0.0006493 | 0.00016273 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_223-15_0_2_load_100 | 116 | 0.00070127 | 0.00017576 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_223-15_0_2_load_98 | 117 | 0.00088008 | 0.00022057 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_223-15_0_2_load_107 | 118 | 0.0011851 | 0.00029701 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_223-15_0_2_load_121 | 119 | 0.0012447 | 0.00031195 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_223-15_0_2_load_120 | 120 | 0.0011114 | 0.00027855 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_223-15_0_2_load_108 | 121 | 0.0011868 | 0.00029744 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_223-15_0_2_load_109 | 122 | 0.0010666 | 0.00026731 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_223-15_0_2_load_110 | 123 | 0.0011333 | 0.00028403 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_223-15_0_2_load_111 | 124 | 0.0011108 | 0.0002784 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_223-15_0_2_load_112 | 125 | 0.00053784 | 0.00013479 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_223-15_0_2_load_119 | 126 | 0.0009773 | 0.00024493 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_223-15_0_2_load_115 | 127 | 0.00047683 | 0.0001195 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_223-15_0_2_load_118 | 128 | 0.0013334 | 0.00033417 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_223-15_0_2_load_113 | 129 | 0.0012296 | 0.00030818 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_223-15_0_2_load_114 | 130 | 0.001126 | 0.0002822 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_223-15_0_2_line_0 |  | 0 | 1 | 0.030924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_223-15_0_2_line_1 |  | 0 | 2 | 0.028101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_223-15_0_2_line_2 |  | 1 | 3 | 0.0075734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_223-15_0_2_line_3 |  | 2 | 4 | 0.034293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_223-15_0_2_line_4 |  | 4 | 5 | 0.01051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_223-15_0_2_line_5 |  | 4 | 6 | 0.010386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_223-15_0_2_line_6 |  | 5 | 12 | 0.025432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_223-15_0_2_line_7 |  | 6 | 42 | 0.006419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_223-15_0_2_line_8 |  | 7 | 8 | 0.014906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_223-15_0_2_line_9 |  | 7 | 9 | 0.017386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_223-15_0_2_line_10 |  | 7 | 10 | 0.029945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_223-15_0_2_line_11 |  | 8 | 43 | 0.017261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_223-15_0_2_line_12 |  | 8 | 44 | 0.037696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_223-15_0_2_line_13 |  | 9 | 11 | 0.048896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_223-15_0_2_line_14 |  | 10 | 45 | 0.014065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_223-15_0_2_line_15 |  | 11 | 41 | 0.014446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_223-15_0_2_line_16 |  | 12 | 46 | 0.030276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_223-15_0_2_line_17 |  | 13 | 14 | 0.09872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_223-15_0_2_line_18 |  | 13 | 15 | 0.213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_223-15_0_2_line_19 |  | 14 | 16 | 0.01954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_223-15_0_2_line_20 |  | 14 | 17 | 0.0044474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_223-15_0_2_line_21 |  | 15 | 57 | 0.034357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_223-15_0_2_line_22 |  | 17 | 60 | 0.050141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_223-15_0_2_line_23 |  | 18 | 19 | 0.014394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_223-15_0_2_line_24 |  | 18 | 20 | 0.0086516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_223-15_0_2_line_25 |  | 19 | 32 | 0.013284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_223-15_0_2_line_26 |  | 20 | 61 | 0.037511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_223-15_0_2_line_27 |  | 21 | 22 | 0.011879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_223-15_0_2_line_28 |  | 21 | 23 | 0.024558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_223-15_0_2_line_29 |  | 23 | 24 | 0.014874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_223-15_0_2_line_30 |  | 24 | 25 | 0.084855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_223-15_0_2_line_31 |  | 25 | 26 | 0.045807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_223-15_0_2_line_32 |  | 26 | 30 | 0.044493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_223-15_0_2_line_33 |  | 26 | 31 | 0.013265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_223-15_0_2_line_34 |  | 27 | 28 | 0.021077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_223-15_0_2_line_35 |  | 27 | 29 | 0.016057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_223-15_0_2_line_36 |  | 29 | 39 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_223-15_0_2_line_37 |  | 30 | 62 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_223-15_0_2_line_38 |  | 31 | 63 | 0.010407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_223-15_0_2_line_39 |  | 32 | 33 | 0.009588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_223-15_0_2_line_40 |  | 32 | 34 | 0.036313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_223-15_0_2_line_41 |  | 34 | 35 | 0.032056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_223-15_0_2_line_42 |  | 34 | 36 | 0.006322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_223-15_0_2_line_43 |  | 35 | 37 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_223-15_0_2_line_44 |  | 35 | 38 | 0.040008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_223-15_0_2_line_45 |  | 36 | 45 | 0.02986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_223-15_0_2_line_46 |  | 36 | 50 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_223-15_0_2_line_47 |  | 37 | 53 | 0.020942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_223-15_0_2_line_48 |  | 38 | 64 | 0.003767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_223-15_0_2_line_49 |  | 38 | 65 | 0.0062617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_223-15_0_2_line_50 |  | 39 | 40 | 0.067858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_223-15_0_2_line_51 |  | 40 | 69 | 0.030223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_223-15_0_2_line_52 |  | 40 | 70 | 0.003758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_223-15_0_2_line_53 |  | 41 | 71 | 0.019757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_223-15_0_2_line_54 |  | 42 | 130 | 0.01054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_223-15_0_2_line_55 |  | 44 | 85 | 0.00029355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_223-15_0_2_line_56 |  | 47 | 48 | 0.026603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_223-15_0_2_line_57 |  | 47 | 49 | 0.018204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_223-15_0_2_line_58 |  | 48 | 84 | 0.022028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_223-15_0_2_line_59 |  | 50 | 51 | 0.043325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_223-15_0_2_line_60 |  | 50 | 52 | 0.010795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_223-15_0_2_line_61 |  | 51 | 56 | 0.017201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_223-15_0_2_line_62 |  | 52 | 81 | 0.010628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_223-15_0_2_line_63 |  | 54 | 55 | 0.043244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_223-15_0_2_line_64 |  | 54 | 56 | 0.031221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_223-15_0_2_line_65 |  | 57 | 89 | 0.021072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_223-15_0_2_line_66 |  | 58 | 59 | 0.029358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_223-15_0_2_line_67 |  | 59 | 60 | 0.036583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_223-15_0_2_line_68 |  | 62 | 68 | 0.013937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_223-15_0_2_line_69 |  | 62 | 71 | 0.008306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_223-15_0_2_line_70 |  | 65 | 80 | 0.020581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_223-15_0_2_line_71 |  | 66 | 67 | 0.010105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_223-15_0_2_line_72 |  | 66 | 68 | 0.00922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_223-15_0_2_line_73 |  | 67 | 72 | 0.027585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_223-15_0_2_line_74 |  | 70 | 77 | 0.050686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_223-15_0_2_line_75 |  | 70 | 78 | 0.030653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_223-15_0_2_line_76 |  | 72 | 73 | 0.00024949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_223-15_0_2_line_77 |  | 73 | 118 | 0.00019764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_223-15_0_2_line_78 |  | 74 | 75 | 0.019588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_223-15_0_2_line_79 |  | 75 | 76 | 0.04053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_223-15_0_2_line_80 |  | 76 | 77 | 0.021709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_223-15_0_2_line_81 |  | 78 | 117 | 0.0057536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_223-15_0_2_line_82 |  | 79 | 80 | 0.012063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_223-15_0_2_line_83 |  | 80 | 113 | 0.024838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_223-15_0_2_line_84 |  | 81 | 87 | 0.0078991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_223-15_0_2_line_85 |  | 82 | 83 | 0.008031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_223-15_0_2_line_86 |  | 83 | 101 | 0.0087785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_223-15_0_2_line_87 |  | 84 | 98 | 0.014527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_223-15_0_2_line_88 |  | 86 | 87 | 0.0039132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_223-15_0_2_line_89 |  | 86 | 88 | 0.0032921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_223-15_0_2_line_90 |  | 88 | 89 | 0.033111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_223-15_0_2_line_91 |  | 88 | 90 | 0.019276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_223-15_0_2_line_92 |  | 89 | 91 | 0.040356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_223-15_0_2_line_93 |  | 90 | 92 | 0.041419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_223-15_0_2_line_94 |  | 90 | 93 | 0.012248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_223-15_0_2_line_95 |  | 91 | 94 | 0.0065021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_223-15_0_2_line_96 |  | 93 | 95 | 0.0091213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_223-15_0_2_line_97 |  | 94 | 96 | 0.017926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_223-15_0_2_line_98 |  | 95 | 110 | 0.0067783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_223-15_0_2_line_99 |  | 96 | 97 | 0.028634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_223-15_0_2_line_100 |  | 97 | 99 | 0.01664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_223-15_0_2_line_101 |  | 98 | 100 | 9.2287e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_223-15_0_2_line_102 |  | 99 | 106 | 0.05332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_223-15_0_2_line_103 |  | 99 | 107 | 0.02138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_223-15_0_2_line_104 |  | 99 | 108 | 0.016395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_223-15_0_2_line_105 |  | 100 | 108 | 0.012684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_223-15_0_2_line_106 |  | 101 | 102 | 0.024068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_223-15_0_2_line_107 |  | 102 | 103 | 0.015636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_223-15_0_2_line_108 |  | 103 | 104 | 0.0032076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_223-15_0_2_line_109 |  | 104 | 105 | 0.00018404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_223-15_0_2_line_110 |  | 105 | 109 | 0.0067878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_223-15_0_2_line_111 |  | 107 | 109 | 0.0070335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_223-15_0_2_line_112 |  | 111 | 112 | 0.00014529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_223-15_0_2_line_113 |  | 111 | 113 | 8.5094e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_223-15_0_2_line_114 |  | 112 | 114 | 0.00062613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_223-15_0_2_line_115 |  | 114 | 115 | 0.021979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_223-15_0_2_line_116 |  | 115 | 116 | 0.0046465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_223-15_0_2_line_117 |  | 116 | 117 | 0.0054377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_223-15_0_2_line_118 |  | 118 | 119 | 0.00025313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_223-15_0_2_line_119 |  | 119 | 120 | 0.025022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_223-15_0_2_line_120 |  | 120 | 128 | 0.00044687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_223-15_0_2_line_121 |  | 121 | 122 | 0.024888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_223-15_0_2_line_122 |  | 121 | 123 | 0.00052282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_223-15_0_2_line_123 |  | 122 | 124 | 0.00026809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_223-15_0_2_line_124 |  | 123 | 125 | 0.0049826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_223-15_0_2_line_125 |  | 124 | 126 | 0.00016304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_223-15_0_2_line_126 |  | 125 | 127 | 0.0037632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_223-15_0_2_line_127 |  | 126 | 128 | 0.00046817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_223-15_0_2_line_128 |  | 127 | 129 | 0.010757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_223-15_0_2_line_129 |  | 129 | 130 | 0.0065922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_223-15_0_2_trafo_55 | 0.63 MVA 20/0.4 kV | 131 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2693779.8232 | 1265808.6575 | 2693775.9864 | 1265824.9858 | 2693769.3855 | 1265837.5029
1 | 2693786.2512 | 1265781.3018 | 2693779.8232 | 1265808.6575
2 | 2693769.3855 | 1265837.5029 | 2693767.1118 | 1265841.8143 | 2693765.7159 | 1265844.1245
3 | 2693786.2512 | 1265781.3018 | 2693792.0815 | 1265782.6287 | 2693819.7842 | 1265788.9401
4 | 2693819.7842 | 1265788.9401 | 2693825.727 | 1265790.2911 | 2693830.1133 | 1265791.0168
5 | 2693819.7842 | 1265788.9401 | 2693817.2724 | 1265799.018
6 | 2693830.1133 | 1265791.0168 | 2693838.27 | 1265792.3696 | 2693854.0603 | 1265796.2456 | 2693854.9342 | 1265796.4787
7 | 2693815.7201 | 1265805.2465 | 2693817.2724 | 1265799.018
8 | 2693977.2239 | 1265820.333 | 2693987.3686 | 1265809.3853
9 | 2693965.3867 | 1265833.0664 | 2693971.5926 | 1265826.3929 | 2693977.2239 | 1265820.333
10 | 2693977.2239 | 1265820.333 | 2694006.1586 | 1265828.0443
11 | 2693977.6555 | 1265795.097 | 2693987.3686 | 1265809.3853
12 | 2693987.3686 | 1265809.3853 | 2693993.5673 | 1265802.6895 | 2694002.5429 | 1265803.2215 | 2694018.6841 | 1265792.1383
13 | 2693965.3867 | 1265833.0664 | 2693965.7436 | 1265836.6639 | 2693964.6895 | 1265840.9173 | 2693956.7232 | 1265858.3716 | 2693946.2167 | 1265877.398
14 | 2694006.1586 | 1265828.0443 | 2694019.7496 | 1265831.6664
15 | 2693946.2167 | 1265877.398 | 2693936.9952 | 1265874.349 | 2693932.2922 | 1265873.8099
16 | 2693854.9342 | 1265796.4787 | 2693884.1878 | 1265804.2794
17 | 2694004.5343 | 1265520.4886 | 2694007.2751 | 1265488.8063 | 2694072.1251 | 1265505.3179
18 | 2694072.1251 | 1265505.3179 | 2694060.0162 | 1265598.4347 | 2694049.0724 | 1265667.1168 | 2694046.646 | 1265682.3462 | 2694041.4264 | 1265712.1987 | 2694041.3794 | 1265716.0234
19 | 2694004.5343 | 1265520.4886 | 2694002.8463 | 1265539.9555
20 | 2694004.5343 | 1265520.4886 | 2694004.1501 | 1265524.9194
21 | 2694044.1175 | 1265750.0892 | 2694041.1466 | 1265734.9796 | 2694041.3794 | 1265716.0234
22 | 2694015.7755 | 1265567.0113 | 2694016.6949 | 1265554.6766 | 2694014.7269 | 1265545.3599 | 2694010.9574 | 1265542.7756 | 2694002.8463 | 1265539.9555 | 2694004.1501 | 1265524.9194
23 | 2694016.5802 | 1265886.9466 | 2694018.5855 | 1265872.6925
24 | 2694016.5802 | 1265886.9466 | 2694019.2599 | 1265893.1721 | 2694020.4712 | 1265894.6018
25 | 2694029.8939 | 1265868.5099 | 2694022.6453 | 1265868.3055 | 2694018.6266 | 1265872.4005 | 2694018.5855 | 1265872.6925
26 | 2694020.4712 | 1265894.6018 | 2694029.9555 | 1265905.7969 | 2694043.8852 | 1265909.2102 | 2694045.8878 | 1265900.953
27 | 2694028.3376 | 1266013.1146 | 2694039.752 | 1266016.5212
28 | 2694028.3376 | 1266013.1146 | 2694017.2807 | 1266012.3159 | 2694010.8755 | 1266015.9059 | 2694006.4689 | 1266020.2505
29 | 2694006.4689 | 1266020.2505 | 2693994.2895 | 1266011.7132
30 | 2693926.1047 | 1265961.5806 | 2693929.8479 | 1265966.2773 | 2693979.279 | 1266001.1915 | 2693994.2895 | 1266011.7132
31 | 2693900.4573 | 1265930.2476 | 2693899.6787 | 1265944.647 | 2693907.7072 | 1265949.7898 | 2693914.1621 | 1265953.9625 | 2693926.1047 | 1265961.5806
32 | 2693900.4573 | 1265930.2476 | 2693903.3829 | 1265885.8507
33 | 2693900.4573 | 1265930.2476 | 2693887.7311 | 1265926.506
34 | 2694201.5171 | 1266021.3117 | 2694212.5022 | 1266003.3238
35 | 2694201.5171 | 1266021.3117 | 2694187.7014 | 1266013.1293
36 | 2694173.7454 | 1266009.971 | 2694187.7014 | 1266013.1293
37 | 2693904.3874 | 1265870.6056 | 2693903.3829 | 1265885.8507
38 | 2693877.7463 | 1265923.5703 | 2693877.7463 | 1265923.5703 | 2693887.7311 | 1265926.506
39 | 2694029.8939 | 1265868.5099 | 2694039.0311 | 1265871.4152
40 | 2694047.5751 | 1265843.9377 | 2694039.8803 | 1265841.9581 | 2694037.5515 | 1265848.2262 | 2694029.8939 | 1265868.5099
41 | 2694047.5751 | 1265843.9377 | 2694045.9814 | 1265850.8624 | 2694070.2262 | 1265856.753
42 | 2694047.5751 | 1265843.9377 | 2694048.9461 | 1265837.7656
43 | 2694086.452 | 1265860.6922 | 2694070.2262 | 1265856.753
44 | 2694076.5729 | 1265896.0973 | 2694073.4472 | 1265881.4689 | 2694071.8461 | 1265861.427 | 2694070.2262 | 1265856.753
45 | 2694048.9461 | 1265837.7656 | 2694042.3038 | 1265836.3699 | 2694030.6075 | 1265834.5601 | 2694019.7496 | 1265831.6664
46 | 2694065.6655 | 1265836.7196 | 2694061.3026 | 1265835.4714 | 2694060.9514 | 1265837.1894 | 2694059.0565 | 1265838.9051 | 2694056.1403 | 1265839.4925 | 2694048.9461 | 1265837.7656
47 | 2694100.7806 | 1265872.63 | 2694088.668 | 1265868.6006 | 2694086.452 | 1265860.6922
48 | 2694072.8724 | 1265895.3378 | 2694076.5729 | 1265896.0973
49 | 2694076.5729 | 1265896.0973 | 2694082.7044 | 1265897.3675
50 | 2694146.8308 | 1265947.6802 | 2694148.0121 | 1265950.5792 | 2694157.2499 | 1265971.4879 | 2694166.4199 | 1265992.8737 | 2694173.7454 | 1266009.971
51 | 2694146.8308 | 1265947.6802 | 2694176.9839 | 1265949.7321
52 | 2694145.4103 | 1265944.1992 | 2694146.8308 | 1265947.6802
53 | 2693912.6633 | 1265871.5601 | 2693932.2922 | 1265873.8099
54 | 2693815.7201 | 1265805.2465 | 2693813.1711 | 1265815.4738
55 | 2694018.6841 | 1265792.1383 | 2694018.9261 | 1265791.9722
56 | 2694181.1079 | 1265721.5188 | 2694161.2323 | 1265725.9058 | 2694155.2134 | 1265727.5856
57 | 2694181.1079 | 1265721.5188 | 2694183.3087 | 1265739.5893
58 | 2694134.7657 | 1265735.5922 | 2694137.8271 | 1265733.9285 | 2694148.1913 | 1265729.5455 | 2694155.2134 | 1265727.5856
59 | 2694065.6655 | 1265836.7196 | 2694087.9948 | 1265845.1485 | 2694106.5423 | 1265851.0304
60 | 2694065.6655 | 1265836.7196 | 2694065.9796 | 1265825.929
61 | 2694123.0509 | 1265855.8331 | 2694116.4969 | 1265854.1873 | 2694106.5423 | 1265851.0304
62 | 2694065.9796 | 1265825.929 | 2694066.2889 | 1265815.306
63 | 2694153.3319 | 1265863.437 | 2694161.4846 | 1265858.4183 | 2694164.0415 | 1265853.9109 | 2694164.8126 | 1265848.5298 | 2694164.0516 | 1265843.3579 | 2694161.6048 | 1265838.5928 | 2694157.1414 | 1265834.6741 | 2694150.9588 | 1265832.5782
64 | 2694153.3319 | 1265863.437 | 2694123.0509 | 1265855.8331
65 | 2694051.1038 | 1265769.8777 | 2694045.2569 | 1265755.8843 | 2694044.1175 | 1265750.0892
66 | 2693986.636 | 1265581.0553 | 2693979.861 | 1265582.1468 | 2693971.4085 | 1265581.3784 | 2693968.3126 | 1265576.6921 | 2693969.3978 | 1265568.3712
67 | 2693986.636 | 1265581.0553 | 2694010.832 | 1265577.1573 | 2694015.3447 | 1265572.7921 | 2694015.7755 | 1265567.0113
68 | 2693904.3874 | 1265870.6056 | 2693890.524 | 1265869.1732
69 | 2693912.6633 | 1265871.5601 | 2693904.3874 | 1265870.6056
70 | 2694102.8578 | 1265901.5423 | 2694082.7044 | 1265897.3675
71 | 2693881.6866 | 1265871.8016 | 2693873.2273 | 1265866.2739
72 | 2693881.6866 | 1265871.8016 | 2693890.524 | 1265869.1732
73 | 2693864.2104 | 1265848.188 | 2693875.749 | 1265850.7012 | 2693873.2273 | 1265866.2739
74 | 2694174.2003 | 1265921.4502 | 2694162.7886 | 1265920.7011 | 2694154.2251 | 1265924.5679 | 2694140.0259 | 1265930.9804 | 2694145.4103 | 1265944.1992
75 | 2694145.4103 | 1265944.1992 | 2694132.3946 | 1265941.0894 | 2694131.3256 | 1265944.8532 | 2694118.3949 | 1265941.5006
76 | 2693864.2104 | 1265848.188 | 2693863.9666 | 1265848.1349
77 | 2693863.9666 | 1265848.1349 | 2693863.7735 | 1265848.0929
78 | 2694236.3164 | 1265920.6616 | 2694240.6838 | 1265901.567
79 | 2694236.3164 | 1265920.6616 | 2694197.7533 | 1265923.0045 | 2694195.8618 | 1265922.8797
80 | 2694174.2003 | 1265921.4502 | 2694195.8618 | 1265922.8797
81 | 2694112.8255 | 1265940.0566 | 2694118.3949 | 1265941.5006
82 | 2694102.8578 | 1265901.5423 | 2694114.5403 | 1265904.5469
83 | 2694102.8578 | 1265901.5423 | 2694100.7631 | 1265909.1819 | 2694097.3114 | 1265911.2509 | 2694094.2996 | 1265923.7861
84 | 2694065.3759 | 1265807.5347 | 2694066.3968 | 1265811.5995 | 2694066.2889 | 1265815.306
85 | 2694189.1999 | 1265810.8691 | 2694188.8195 | 1265818.8912
86 | 2694189.0075 | 1265802.0989 | 2694189.2939 | 1265808.8874 | 2694189.1999 | 1265810.8691
87 | 2694134.7657 | 1265735.5922 | 2694138.8654 | 1265749.5285
88 | 2694064.4227 | 1265803.7393 | 2694065.3759 | 1265807.5347
89 | 2694063.6208 | 1265800.5463 | 2694064.4227 | 1265803.7393
90 | 2694063.6208 | 1265800.5463 | 2694051.1038 | 1265769.8777
91 | 2694082.7481 | 1265797.7373 | 2694063.6208 | 1265800.5463
92 | 2694051.1038 | 1265769.8777 | 2694064.8241 | 1265762.8124 | 2694079.4319 | 1265757.2403 | 2694088.3043 | 1265754.4903
93 | 2694076.6179 | 1265775.0545 | 2694080.9945 | 1265771.6658 | 2694085.9081 | 1265771.9109 | 2694088.4264 | 1265774.5531 | 2694091.9903 | 1265785.3075 | 2694091.0802 | 1265789.0183 | 2694083.9307 | 1265795.3541 | 2694082.7481 | 1265797.7373
94 | 2694082.7481 | 1265797.7373 | 2694094.9156 | 1265799.1408
95 | 2694094.515 | 1265752.5654 | 2694088.3043 | 1265754.4903
96 | 2694103.9769 | 1265800.186 | 2694094.9156 | 1265799.1408
97 | 2694094.515 | 1265752.5654 | 2694095.7252 | 1265765.94 | 2694097.1523 | 1265770.2045
98 | 2694110.7105 | 1265800.9627 | 2694103.9769 | 1265800.186
99 | 2694097.1523 | 1265770.2045 | 2694100.484 | 1265780.1607 | 2694106.1059 | 1265782.7412 | 2694117.7847 | 1265780.2131
100 | 2694134.0795 | 1265777.2376 | 2694132.3276 | 1265777.0651 | 2694117.7847 | 1265780.2131
101 | 2694138.8654 | 1265749.5285 | 2694138.8914 | 1265749.617
102 | 2694134.0795 | 1265777.2376 | 2694131.8992 | 1265784.0974 | 2694127.5254 | 1265817.0881 | 2694139.9655 | 1265820.4222
103 | 2694134.0795 | 1265777.2376 | 2694155.3514 | 1265779.38
104 | 2694134.0795 | 1265777.2376 | 2694139.3689 | 1265761.7193
105 | 2694139.3689 | 1265761.7193 | 2694141.0235 | 1265756.8648 | 2694138.8914 | 1265749.617
106 | 2694187.9932 | 1265778.0525 | 2694189.0075 | 1265802.0989
107 | 2694187.9932 | 1265778.0525 | 2694172.4668 | 1265779.9025
108 | 2694169.2818 | 1265780.282 | 2694172.4668 | 1265779.9025
109 | 2694169.2818 | 1265780.282 | 2694169.099 | 1265780.3038
110 | 2694169.099 | 1265780.3038 | 2694167.0032 | 1265780.5535 | 2694162.3496 | 1265780.0848
111 | 2694155.3514 | 1265779.38 | 2694162.3496 | 1265780.0848
112 | 2694094.2458 | 1265924.0101 | 2694094.2798 | 1265923.8688
113 | 2694094.2798 | 1265923.8688 | 2694094.2996 | 1265923.7861
114 | 2694094.0995 | 1265924.6189 | 2694094.2458 | 1265924.0101
115 | 2694103.0641 | 1265937.5256 | 2694091.7061 | 1265934.5808 | 2694094.0995 | 1265924.6189
116 | 2694107.5619 | 1265938.6918 | 2694103.0641 | 1265937.5256
117 | 2694112.8255 | 1265940.0566 | 2694107.5619 | 1265938.6918
118 | 2693863.7735 | 1265848.0929 | 2693863.5262 | 1265848.039
119 | 2693863.5262 | 1265848.039 | 2693839.0775 | 1265842.7139
120 | 2693839.0775 | 1265842.7139 | 2693838.6409 | 1265842.6188
121 | 2693813.4447 | 1265837.1309 | 2693837.7622 | 1265842.4274
122 | 2693813.4447 | 1265837.1309 | 2693812.9339 | 1265837.0196
123 | 2693838.0241 | 1265842.4845 | 2693837.7622 | 1265842.4274
124 | 2693808.0654 | 1265835.9592 | 2693812.9339 | 1265837.0196
125 | 2693838.1834 | 1265842.5192 | 2693838.0241 | 1265842.4845
126 | 2693808.0654 | 1265835.9592 | 2693808.0654 | 1265835.9592 | 2693808.9755 | 1265832.3078
127 | 2693838.6409 | 1265842.6188 | 2693838.1834 | 1265842.5192
128 | 2693811.5769 | 1265821.8703 | 2693808.9755 | 1265832.3078
129 | 2693811.5769 | 1265821.8703 | 2693813.1711 | 1265815.4738

## bus_geodata
| x | y | coords
0 | 2693779.8232 | 1265808.6575
1 | 2693769.3855 | 1265837.5029
2 | 2693786.2512 | 1265781.3018
3 | 2693765.7159 | 1265844.1245
4 | 2693819.7842 | 1265788.9401
5 | 2693830.1133 | 1265791.0168
6 | 2693817.2724 | 1265799.018
7 | 2693977.2239 | 1265820.333
8 | 2693987.3686 | 1265809.3853
9 | 2693965.3867 | 1265833.0664
10 | 2694006.1586 | 1265828.0443
11 | 2693946.2167 | 1265877.398
12 | 2693854.9342 | 1265796.4787
13 | 2694072.1251 | 1265505.3179
14 | 2694004.5343 | 1265520.4886
15 | 2694041.3794 | 1265716.0234
16 | 2694002.8463 | 1265539.9555
17 | 2694004.1501 | 1265524.9194
18 | 2694016.5802 | 1265886.9466
19 | 2694018.5855 | 1265872.6925
20 | 2694020.4712 | 1265894.6018
21 | 2694028.3376 | 1266013.1146
22 | 2694039.752 | 1266016.5212
23 | 2694006.4689 | 1266020.2505
24 | 2693994.2895 | 1266011.7132
25 | 2693926.1047 | 1265961.5806
26 | 2693900.4573 | 1265930.2476
27 | 2694201.5171 | 1266021.3117
28 | 2694212.5022 | 1266003.3238
29 | 2694187.7014 | 1266013.1293
30 | 2693903.3829 | 1265885.8507
31 | 2693887.7311 | 1265926.506
32 | 2694029.8939 | 1265868.5099
33 | 2694039.0311 | 1265871.4152
34 | 2694047.5751 | 1265843.9377
35 | 2694070.2262 | 1265856.753
36 | 2694048.9461 | 1265837.7656
37 | 2694086.452 | 1265860.6922
38 | 2694076.5729 | 1265896.0973
39 | 2694173.7454 | 1266009.971
40 | 2694146.8308 | 1265947.6802
41 | 2693932.2922 | 1265873.8099
42 | 2693815.7201 | 1265805.2465
43 | 2693977.6555 | 1265795.097
44 | 2694018.6841 | 1265792.1383
45 | 2694019.7496 | 1265831.6664
46 | 2693884.1878 | 1265804.2794
47 | 2694181.1079 | 1265721.5188
48 | 2694155.2134 | 1265727.5856
49 | 2694183.3087 | 1265739.5893
50 | 2694065.6655 | 1265836.7196
51 | 2694106.5423 | 1265851.0304
52 | 2694065.9796 | 1265825.929
53 | 2694100.7806 | 1265872.63
54 | 2694153.3319 | 1265863.437
55 | 2694150.9588 | 1265832.5782
56 | 2694123.0509 | 1265855.8331
57 | 2694044.1175 | 1265750.0892
58 | 2693969.3978 | 1265568.3712
59 | 2693986.636 | 1265581.0553
60 | 2694015.7755 | 1265567.0113
61 | 2694045.8878 | 1265900.953
62 | 2693904.3874 | 1265870.6056
63 | 2693877.7463 | 1265923.5703
64 | 2694072.8724 | 1265895.3378
65 | 2694082.7044 | 1265897.3675
66 | 2693881.6866 | 1265871.8016
67 | 2693873.2273 | 1265866.2739
68 | 2693890.524 | 1265869.1732
69 | 2694176.9839 | 1265949.7321
70 | 2694145.4103 | 1265944.1992
71 | 2693912.6633 | 1265871.5601
72 | 2693864.2104 | 1265848.188
73 | 2693863.9666 | 1265848.1349
74 | 2694240.6838 | 1265901.567
75 | 2694236.3164 | 1265920.6616
76 | 2694195.8618 | 1265922.8797
77 | 2694174.2003 | 1265921.4502
78 | 2694118.3949 | 1265941.5006
79 | 2694114.5403 | 1265904.5469
80 | 2694102.8578 | 1265901.5423
81 | 2694066.2889 | 1265815.306
82 | 2694188.8195 | 1265818.8912
83 | 2694189.1999 | 1265810.8691
84 | 2694134.7657 | 1265735.5922
85 | 2694018.9261 | 1265791.9722
86 | 2694064.4227 | 1265803.7393
87 | 2694065.3759 | 1265807.5347
88 | 2694063.6208 | 1265800.5463
89 | 2694051.1038 | 1265769.8777
90 | 2694082.7481 | 1265797.7373
91 | 2694088.3043 | 1265754.4903
92 | 2694076.6179 | 1265775.0545
93 | 2694094.9156 | 1265799.1408
94 | 2694094.515 | 1265752.5654
95 | 2694103.9769 | 1265800.186
96 | 2694097.1523 | 1265770.2045
97 | 2694117.7847 | 1265780.2131
98 | 2694138.8654 | 1265749.5285
99 | 2694134.0794 | 1265777.2376
100 | 2694138.8914 | 1265749.617
101 | 2694189.0075 | 1265802.0989
102 | 2694187.9932 | 1265778.0525
103 | 2694172.4668 | 1265779.9025
104 | 2694169.2818 | 1265780.282
105 | 2694169.099 | 1265780.3038
106 | 2694139.9655 | 1265820.4222
107 | 2694155.3514 | 1265779.38
108 | 2694139.3689 | 1265761.7193
109 | 2694162.3496 | 1265780.0848
110 | 2694110.7105 | 1265800.9627
111 | 2694094.2798 | 1265923.8688
112 | 2694094.2458 | 1265924.0101
113 | 2694094.2996 | 1265923.7861
114 | 2694094.0995 | 1265924.6189
115 | 2694103.0641 | 1265937.5256
116 | 2694107.5619 | 1265938.6918
117 | 2694112.8255 | 1265940.0566
118 | 2693863.7735 | 1265848.0929
119 | 2693863.5262 | 1265848.039
120 | 2693839.0775 | 1265842.7139
121 | 2693813.4447 | 1265837.1309
122 | 2693837.7622 | 1265842.4274
123 | 2693812.9339 | 1265837.0196
124 | 2693838.0241 | 1265842.4845
125 | 2693808.0654 | 1265835.9592
126 | 2693838.1834 | 1265842.5192
127 | 2693808.9755 | 1265832.3078
128 | 2693838.6409 | 1265842.6188
129 | 2693811.5769 | 1265821.8703
130 | 2693813.1711 | 1265815.4738
131 | 2694048.9461 | 1265837.7656

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98676 | -0.25499 | 0.0034897 | 0.00087459
1 | 0.98673 | -0.25566 | 0.00063471 | 0.00015907
2 | 0.98689 | -0.25263 | 0 | 0
3 | 0.98673 | -0.25574 | 0.00056962 | 0.00014276
4 | 0.98703 | -0.24975 | 0 | 0
5 | 0.98696 | -0.25122 | 0 | 0
6 | 0.98715 | -0.24743 | 0.001177 | 0.000295
7 | 0.99684 | -0.060395 | 0 | 0
8 | 0.99664 | -0.064177 | 0 | 0
9 | 0.99583 | -0.079785 | 0 | 0
10 | 0.99898 | -0.019521 | 0.0015607 | 0.00039115
11 | 0.99298 | -0.13453 | 0 | 0
12 | 0.98678 | -0.25478 | 0.0070049 | 0.0017556
13 | 0.99183 | -0.15722 | 0 | 0
14 | 0.99102 | -0.17296 | 0 | 0
15 | 0.99358 | -0.12334 | 0.00081787 | 0.00020498
16 | 0.99095 | -0.17444 | 0.004278 | 0.0010722
17 | 0.991 | -0.17333 | 0.0016012 | 0.00040129
18 | 0.99711 | -0.055323 | 0 | 0
19 | 0.99713 | -0.054928 | 0.0017731 | 0.00044439
20 | 0.9971 | -0.05556 | 0.00094537 | 0.00023693
21 | 0.9898 | -0.19599 | 0 | 0
22 | 0.98978 | -0.19643 | 0.0020759 | 0.00052027
23 | 0.98985 | -0.19508 | 0 | 0
24 | 0.98988 | -0.19453 | 0.00043206 | 0.00010828
25 | 0.99007 | -0.19074 | 0 | 0
26 | 0.99018 | -0.18869 | 0 | 0
27 | 0.99291 | -0.13643 | 0 | 0
28 | 0.99286 | -0.13734 | 0.0024296 | 0.00060891
29 | 0.99294 | -0.13574 | 0.00087991 | 0.00022053
30 | 0.99055 | -0.18139 | 0.005626 | 0.00141
31 | 0.9901 | -0.19028 | 0.0028431 | 0.00071256
32 | 0.99717 | -0.054151 | 0 | 0
33 | 0.99715 | -0.054557 | 0.0024197 | 0.00060644
34 | 0.99736 | -0.050485 | 0 | 0
35 | 0.99653 | -0.066448 | 0 | 0
36 | 0.99756 | -0.046703 | 0.00081826 | 0.00020507
37 | 0.99649 | -0.067304 | 0 | 0
38 | 0.9956 | -0.084343 | 0.00011252 | 2.82e-05
39 | 0.99299 | -0.1349 | 0 | 0
40 | 0.99319 | -0.13093 | 0 | 0
41 | 0.99214 | -0.15076 | 0.010087 | 0.0025279
42 | 0.98723 | -0.24586 | 0.0012229 | 0.0003065
43 | 0.99644 | -0.068092 | 0.012922 | 0.0032386
44 | 0.99659 | -0.065197 | 0.00082019 | 0.00020556
45 | 1 | 0 | -0.17184 | -0.043091
46 | 0.98675 | -0.25521 | 0.0008075 | 0.00020238
47 | 0.99175 | -0.15879 | 0 | 0
48 | 0.99179 | -0.15813 | 0.001384 | 0.00034687
49 | 0.99173 | -0.15924 | 0.0014006 | 0.00035102
50 | 0.99661 | -0.065037 | 0 | 0
51 | 0.99627 | -0.071521 | 0.0015269 | 0.00038267
52 | 0.99615 | -0.073759 | 0.00058004 | 0.00014537
53 | 0.99643 | -0.068382 | 0.0029311 | 0.0007346
54 | 0.99606 | -0.075679 | 0 | 0
55 | 0.99591 | -0.07851 | 0.0037252 | 0.00093363
56 | 0.99616 | -0.073635 | 0.003269 | 0.0008193
57 | 0.99389 | -0.11738 | 0.0011751 | 0.00029452
58 | 0.99079 | -0.17748 | 0.00065414 | 0.00016394
59 | 0.99081 | -0.17714 | 0.00095112 | 0.00023837
60 | 0.99086 | -0.1761 | 0.0014989 | 0.00037567
61 | 0.99708 | -0.055967 | 0.0006177 | 0.00015481
62 | 0.99076 | -0.17735 | 0 | 0
63 | 0.99006 | -0.191 | 0.0038861 | 0.00097395
64 | 0.9956 | -0.084352 | 0.000132 | 3.3083e-05
65 | 0.99546 | -0.08712 | 0.00040827 | 0.00010232
66 | 0.99 | -0.19213 | 0 | 0
67 | 0.9897 | -0.19788 | 0.0010469 | 0.00026239
68 | 0.99027 | -0.1869 | 0.0066057 | 0.0016556
69 | 0.99313 | -0.13217 | 0.0023111 | 0.00057921
70 | 0.99321 | -0.13056 | 0 | 0
71 | 0.99117 | -0.16947 | 0 | 0
72 | 0.98892 | -0.21306 | 0.001128 | 0.0002827
73 | 0.98891 | -0.21319 | 0.0011407 | 0.00028588
74 | 0.99224 | -0.14936 | 0.002023 | 0.00050702
75 | 0.99228 | -0.14866 | 0 | 0
76 | 0.99235 | -0.14721 | 0.010981 | 0.0027521
77 | 0.99261 | -0.14221 | 0 | 0
78 | 0.99373 | -0.12047 | 0.00079353 | 0.00019888
79 | 0.99497 | -0.096523 | 0.0019705 | 0.00049384
80 | 0.99499 | -0.096104 | 0 | 0
81 | 0.99571 | -0.082244 | 0.0013808 | 0.00034605
82 | 0.99164 | -0.16092 | 0.0010127 | 0.00025382
83 | 0.99165 | -0.16077 | 0.00088341 | 0.0002214
84 | 0.99184 | -0.15704 | 0 | 0
85 | 0.99659 | -0.065201 | 0.0007205 | 0.00018057
86 | 0.99524 | -0.091335 | 0.0012477 | 0.00031269
87 | 0.9954 | -0.088364 | 0.00090808 | 0.00022759
88 | 0.99512 | -0.093762 | 0 | 0
89 | 0.9941 | -0.1133 | 0 | 0
90 | 0.99497 | -0.096616 | 0 | 0
91 | 0.99327 | -0.12932 | 0.0013896 | 0.00034827
92 | 0.99479 | -0.10009 | 0.0047565 | 0.0011921
93 | 0.99493 | -0.097404 | 0.00075232 | 0.00018855
94 | 0.99315 | -0.13175 | 0 | 0
95 | 0.9949 | -0.09787 | 0.0017094 | 0.00042843
96 | 0.9928 | -0.13843 | 0.0012062 | 0.00030231
97 | 0.99228 | -0.14851 | 0.0034186 | 0.00085679
98 | 0.99188 | -0.15633 | 0.0010836 | 0.00027159
99 | 0.99203 | -0.15337 | 0 | 0
100 | 0.99188 | -0.15632 | 0.001224 | 0.00030676
101 | 0.99167 | -0.16048 | 0.00080033 | 0.00020058
102 | 0.99172 | -0.15933 | 0 | 0
103 | 0.99176 | -0.15858 | 0.0010399 | 0.00026062
104 | 0.99177 | -0.15837 | 0.0016046 | 0.00040215
105 | 0.99177 | -0.15835 | 0.0009971 | 0.0002499
106 | 0.99196 | -0.15486 | 0.0015752 | 0.00039478
107 | 0.99186 | -0.15665 | 0.0011568 | 0.00028992
108 | 0.99194 | -0.15517 | 0.0011282 | 0.00028274
109 | 0.99181 | -0.15759 | 0.0011771 | 0.00029501
110 | 0.9949 | -0.098012 | 0.0011903 | 0.00029832
111 | 0.99448 | -0.10613 | 0.00012744 | 3.1939e-05
112 | 0.99447 | -0.10619 | 0.00014084 | 3.5298e-05
113 | 0.99448 | -0.10609 | 0.00013177 | 3.3025e-05
114 | 0.99446 | -0.10643 | 0.0007748 | 0.00019418
115 | 0.99402 | -0.11483 | 0.0006493 | 0.00016273
116 | 0.99394 | -0.11655 | 0.00070127 | 0.00017576
117 | 0.99384 | -0.1185 | 0.00088008 | 0.00022057
118 | 0.98891 | -0.21329 | 0.0011851 | 0.00029701
119 | 0.9889 | -0.21342 | 0.0012447 | 0.00031195
120 | 0.9883 | -0.22511 | 0.0011114 | 0.00027855
121 | 0.9878 | -0.23483 | 0.0011868 | 0.00029744
122 | 0.98827 | -0.22568 | 0.0010666 | 0.00026731
123 | 0.98779 | -0.23501 | 0.0011333 | 0.00028403
124 | 0.98828 | -0.22557 | 0.0011108 | 0.0002784
125 | 0.98771 | -0.23664 | 0.00053784 | 0.00013479
126 | 0.98828 | -0.22551 | 0.0009773 | 0.00024493
127 | 0.98765 | -0.23784 | 0.00047683 | 0.0001195
128 | 0.98829 | -0.22531 | 0.0013334 | 0.00033417
129 | 0.98748 | -0.24115 | 0.0012296 | 0.00030818
130 | 0.98738 | -0.24304 | 0.001126 | 0.0002822
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0012044 | 0.00030137 | -0.0012043 | -0.00030174 | 3.8246e-08 | -3.7054e-07 | 0.001816 | 0.0018161 | 0.0018161 | 0.98676 | -0.25499 | 0.98673 | -0.25566 | 0.49893
1 | -0.004694 | -0.001176 | 0.0046945 | 0.0011759 | 5.2796e-07 | -2.112e-08 | 0.0070783 | 0.0070782 | 0.0070783 | 0.98676 | -0.25499 | 0.98689 | -0.25263 | 1.9446
2 | 0.00056962 | 0.00014266 | -0.00056962 | -0.00014276 | 2.0955e-09 | -9.5396e-08 | 0.00085897 | 0.000859 | 0.000859 | 0.98673 | -0.25566 | 0.98673 | -0.25574 | 0.23599
3 | -0.0046945 | -0.0011759 | 0.0046952 | 0.0011759 | 6.4427e-07 | -2.591e-08 | 0.0070782 | 0.007078 | 0.0070782 | 0.98689 | -0.25263 | 0.98703 | -0.24975 | 1.9446
4 | 0.0078142 | 0.0019583 | -0.0078137 | -0.0019581 | 5.4696e-07 | 2.1574e-07 | 0.01178 | 0.01178 | 0.01178 | 0.98703 | -0.24975 | 0.98696 | -0.25122 | 3.2364
5 | -0.012509 | -0.0031342 | 0.012511 | 0.003135 | 1.3852e-06 | 7.5374e-07 | 0.018858 | 0.018858 | 0.018858 | 0.98703 | -0.24975 | 0.98715 | -0.24743 | 5.1809
6 | 0.0078137 | 0.0019581 | -0.0078124 | -0.0019576 | 1.3235e-06 | 5.2212e-07 | 0.01178 | 0.011781 | 0.011781 | 0.98696 | -0.25122 | 0.98678 | -0.25478 | 3.2364
7 | -0.013688 | -0.00343 | 0.013689 | 0.0034306 | 1.0247e-06 | 5.7376e-07 | 0.020633 | 0.020633 | 0.020633 | 0.98715 | -0.24743 | 0.98723 | -0.24586 | 5.6683
8 | 0.014468 | 0.0036271 | -0.014465 | -0.0036256 | 2.6073e-06 | 1.4744e-06 | 0.021597 | 0.021597 | 0.021597 | 0.99684 | -0.060395 | 0.99664 | -0.064177 | 5.9334
9 | 0.063945 | 0.016191 | -0.063885 | -0.016153 | 5.9474e-05 | 3.7837e-05 | 0.095511 | 0.095511 | 0.095511 | 0.99684 | -0.060395 | 0.99583 | -0.079785 | 26.2393
10 | -0.078413 | -0.019818 | 0.078567 | 0.019917 | 0.000154 | 9.817e-05 | 0.11711 | 0.11711 | 0.11711 | 0.99684 | -0.060395 | 0.99898 | -0.019521 | 32.1727
11 | 0.012925 | 0.0032399 | -0.012922 | -0.0032386 | 2.4104e-06 | 1.3178e-06 | 0.019297 | 0.019297 | 0.019297 | 0.99664 | -0.064177 | 0.99644 | -0.068092 | 5.3015
12 | 0.0015408 | 0.00038569 | -0.0015407 | -0.00038613 | 7.48e-08 | -4.4333e-07 | 0.0023002 | 0.0023004 | 0.0023004 | 0.99664 | -0.064177 | 0.99659 | -0.065197 | 0.63198
13 | 0.063885 | 0.016153 | -0.063718 | -0.016047 | 0.00016727 | 0.00010642 | 0.095511 | 0.095511 | 0.095511 | 0.99583 | -0.079785 | 0.99298 | -0.13453 | 26.2394
14 | -0.080128 | -0.020308 | 0.080203 | 0.020356 | 7.5237e-05 | 4.7967e-05 | 0.11943 | 0.11943 | 0.11943 | 0.99898 | -0.019521 | 1 | 0 | 32.8113
15 | 0.063718 | 0.016047 | -0.063669 | -0.016016 | 4.942e-05 | 3.1442e-05 | 0.095511 | 0.095512 | 0.095512 | 0.99298 | -0.13453 | 0.99214 | -0.15076 | 26.2394
16 | 0.00080751 | 0.000202 | -0.0008075 | -0.00020238 | 1.6833e-08 | -3.7598e-07 | 0.0012176 | 0.0012177 | 0.0012177 | 0.98678 | -0.25478 | 0.98675 | -0.25521 | 0.33453
17 | 0.008991 | 0.0022532 | -0.0089842 | -0.0022502 | 6.7359e-06 | 3.038e-06 | 0.013489 | 0.013489 | 0.013489 | 0.99183 | -0.15722 | 0.99102 | -0.17296 | 3.7058
18 | -0.008991 | -0.0022532 | 0.0090055 | 0.0022598 | 1.4532e-05 | 6.5468e-06 | 0.013489 | 0.013488 | 0.013489 | 0.99183 | -0.15722 | 0.99358 | -0.12334 | 3.7057
19 | 0.0042783 | 0.0010721 | -0.004278 | -0.0010722 | 3.0237e-07 | -5.8229e-08 | 0.0064238 | 0.0064239 | 0.0064239 | 0.99102 | -0.17296 | 0.99095 | -0.17444 | 1.7648
20 | 0.0047059 | 0.0011781 | -0.0047058 | -0.0011781 | 8.3258e-08 | -4.0181e-09 | 0.0070655 | 0.0070655 | 0.0070655 | 0.99102 | -0.17296 | 0.991 | -0.17333 | 1.9411
21 | -0.0098234 | -0.0024648 | 0.0098262 | 0.0024661 | 2.7888e-06 | 1.3397e-06 | 0.014713 | 0.014713 | 0.014713 | 0.99358 | -0.12334 | 0.99389 | -0.11738 | 4.042
22 | 0.0031047 | 0.00077681 | -0.0031043 | -0.00077719 | 4.0857e-07 | -3.8446e-07 | 0.0046613 | 0.0046615 | 0.0046615 | 0.991 | -0.17333 | 0.99086 | -0.1761 | 1.2806
23 | -0.0015631 | -0.00039116 | 0.0015631 | 0.00039099 | 2.9366e-08 | -1.6897e-07 | 0.0023325 | 0.0023324 | 0.0023325 | 0.99711 | -0.055323 | 0.99713 | -0.054928 | 0.64078
24 | 0.0015631 | 0.00039116 | -0.0015631 | -0.00039126 | 1.7651e-08 | -1.0155e-07 | 0.0023325 | 0.0023325 | 0.0023325 | 0.99711 | -0.055323 | 0.9971 | -0.05556 | 0.64079
25 | -0.0033363 | -0.00083538 | 0.0033364 | 0.00083529 | 1.2346e-07 | -9.4268e-08 | 0.0049784 | 0.0049784 | 0.0049784 | 0.99713 | -0.054928 | 0.99717 | -0.054151 | 1.3677
26 | 0.00061771 | 0.00015433 | -0.0006177 | -0.00015481 | 1.1951e-08 | -4.8161e-07 | 0.00092167 | 0.00092184 | 0.00092184 | 0.9971 | -0.05556 | 0.99708 | -0.055967 | 0.25325
27 | 0.0020759 | 0.00052014 | -0.0020759 | -0.00052027 | 4.3386e-08 | -1.2491e-07 | 0.0031208 | 0.0031209 | 0.0031209 | 0.9898 | -0.19599 | 0.98978 | -0.19643 | 0.85738
28 | -0.0020759 | -0.00052014 | 0.002076 | 0.00051989 | 8.969e-08 | -2.5826e-07 | 0.0031208 | 0.0031207 | 0.0031208 | 0.9898 | -0.19599 | 0.98985 | -0.19508 | 0.85737
29 | -0.002076 | -0.00051989 | 0.0020761 | 0.00051973 | 5.4318e-08 | -1.5643e-07 | 0.0031207 | 0.0031206 | 0.0031207 | 0.98985 | -0.19508 | 0.98988 | -0.19453 | 0.85733
30 | -0.0025081 | -0.00062801 | 0.0025086 | 0.00062721 | 4.5224e-07 | -8.0159e-07 | 0.0037701 | 0.0037697 | 0.0037701 | 0.98988 | -0.19453 | 0.99007 | -0.19074 | 1.0357
31 | -0.0025086 | -0.00062721 | 0.0025088 | 0.00062678 | 2.4409e-07 | -4.3292e-07 | 0.0037697 | 0.0037695 | 0.0037697 | 0.99007 | -0.19074 | 0.99018 | -0.18869 | 1.0356
32 | -0.0092388 | -0.0023134 | 0.009242 | 0.0023149 | 3.2158e-06 | 1.4856e-06 | 0.013883 | 0.013883 | 0.013883 | 0.99018 | -0.18869 | 0.99055 | -0.18139 | 3.814
33 | 0.0067299 | 0.0016866 | -0.0067294 | -0.0016865 | 5.0879e-07 | 1.5502e-07 | 0.010114 | 0.010114 | 0.010114 | 0.99018 | -0.18869 | 0.9901 | -0.19028 | 2.7785
34 | 0.0024297 | 0.0006087 | -0.0024296 | -0.00060891 | 1.0479e-07 | -2.0553e-07 | 0.0036411 | 0.0036412 | 0.0036412 | 0.99291 | -0.13643 | 0.99286 | -0.13734 | 1.0003
35 | -0.0024297 | -0.0006087 | 0.0024297 | 0.00060854 | 7.9828e-08 | -1.566e-07 | 0.0036411 | 0.0036411 | 0.0036411 | 0.99291 | -0.13643 | 0.99294 | -0.13574 | 1.0003
36 | -0.0033097 | -0.00082907 | 0.0033098 | 0.00082897 | 1.3199e-07 | -1.0062e-07 | 0.0049597 | 0.0049596 | 0.0049597 | 0.99294 | -0.13574 | 0.99299 | -0.1349 | 1.3625
37 | -0.014868 | -0.0037249 | 0.014871 | 0.0037265 | 2.8578e-06 | 1.6323e-06 | 0.022334 | 0.022334 | 0.022334 | 0.99055 | -0.18139 | 0.99076 | -0.17735 | 6.1358
38 | 0.0038863 | 0.00097391 | -0.0038861 | -0.00097395 | 1.3314e-07 | -4.8635e-08 | 0.0058406 | 0.0058407 | 0.0058407 | 0.9901 | -0.19028 | 0.99006 | -0.191 | 1.6046
39 | 0.0024198 | 0.00060635 | -0.0024197 | -0.00060644 | 4.6879e-08 | -9.5073e-08 | 0.0036108 | 0.0036109 | 0.0036109 | 0.99717 | -0.054151 | 0.99715 | -0.054557 | 0.992
40 | -0.0057562 | -0.0014416 | 0.0057572 | 0.0014418 | 1.0046e-06 | 1.6914e-07 | 0.0085892 | 0.008589 | 0.0085892 | 0.99717 | -0.054151 | 0.99736 | -0.050485 | 2.3597
41 | 0.028482 | 0.0071718 | -0.02846 | -0.0071583 | 2.1719e-05 | 1.3482e-05 | 0.042505 | 0.042506 | 0.042506 | 0.99736 | -0.050485 | 0.99653 | -0.066448 | 11.6774
42 | -0.034239 | -0.0086136 | 0.034245 | 0.0086175 | 6.1892e-06 | 3.8786e-06 | 0.051094 | 0.051094 | 0.051094 | 0.99736 | -0.050485 | 0.99756 | -0.046703 | 14.0369
43 | 0.0029314 | 0.00073429 | -0.0029313 | -0.00073443 | 1.1961e-07 | -1.4035e-07 | 0.004377 | 0.004377 | 0.004377 | 0.99653 | -0.066448 | 0.99649 | -0.067304 | 1.2025
44 | 0.025529 | 0.006424 | -0.025507 | -0.0064106 | 2.1811e-05 | 1.3439e-05 | 0.038129 | 0.038129 | 0.038129 | 0.99653 | -0.066448 | 0.9956 | -0.084343 | 10.4749
45 | -0.089786 | -0.022607 | 0.089987 | 0.022735 | 0.00020096 | 0.00012822 | 0.13397 | 0.13397 | 0.13397 | 0.99756 | -0.046703 | 1 | 0 | 36.8038
46 | 0.054722 | 0.013784 | -0.054674 | -0.013754 | 4.7936e-05 | 3.0429e-05 | 0.081651 | 0.081651 | 0.081651 | 0.99756 | -0.046703 | 0.99661 | -0.065037 | 22.4316
47 | 0.0029313 | 0.00073443 | -0.0029311 | -0.0007346 | 1.5046e-07 | -1.7651e-07 | 0.004377 | 0.0043771 | 0.0043771 | 0.99649 | -0.067304 | 0.99643 | -0.068382 | 1.2025
48 | 0.000132 | 3.3034e-05 | -0.000132 | -3.3083e-05 | 5.4993e-11 | -4.8952e-08 | 0.00019727 | 0.00019729 | 0.00019729 | 0.9956 | -0.084343 | 0.9956 | -0.084352 | 0.054201
49 | 0.025263 | 0.0063494 | -0.025259 | -0.0063473 | 3.3486e-06 | 2.0617e-06 | 0.037763 | 0.037763 | 0.037763 | 0.9956 | -0.084343 | 0.99546 | -0.08712 | 10.3746
50 | -0.0033098 | -0.00082897 | 0.0033104 | 0.00082849 | 6.259e-07 | -4.7742e-07 | 0.0049596 | 0.0049593 | 0.0049596 | 0.99299 | -0.1349 | 0.99319 | -0.13093 | 1.3625
51 | 0.0023112 | 0.0005789 | -0.0023111 | -0.00057921 | 1.3589e-07 | -3.0413e-07 | 0.0034626 | 0.0034627 | 0.0034627 | 0.99319 | -0.13093 | 0.99313 | -0.13217 | 0.95129
52 | -0.0056216 | -0.0014074 | 0.0056217 | 0.0014074 | 9.9955e-08 | 1.5337e-08 | 0.0084219 | 0.0084218 | 0.0084219 | 0.99319 | -0.13093 | 0.99321 | -0.13056 | 2.3137
53 | 0.053582 | 0.013488 | -0.053534 | -0.013457 | 4.7873e-05 | 3.0384e-05 | 0.080384 | 0.080384 | 0.080384 | 0.99214 | -0.15076 | 0.99117 | -0.16947 | 22.0834
54 | -0.014912 | -0.0037371 | 0.014914 | 0.0037382 | 1.9967e-06 | 1.1431e-06 | 0.022476 | 0.022476 | 0.022476 | 0.98723 | -0.24586 | 0.98738 | -0.24304 | 6.1747
55 | 0.0007205 | 0.00018057 | -0.0007205 | -0.00018057 | 1.2758e-10 | -3.7434e-09 | 0.0010758 | 0.0010758 | 0.0010758 | 0.99659 | -0.065197 | 0.99659 | -0.065201 | 0.29555
56 | -0.0014006 | -0.00035081 | 0.0014007 | 0.00035049 | 4.4051e-08 | -3.151e-07 | 0.0021014 | 0.0021013 | 0.0021014 | 0.99175 | -0.15879 | 0.99179 | -0.15813 | 0.57731
57 | 0.0014006 | 0.00035081 | -0.0014006 | -0.00035102 | 3.0146e-08 | -2.156e-07 | 0.0021014 | 0.0021015 | 0.0021015 | 0.99175 | -0.15879 | 0.99173 | -0.15924 | 0.57733
58 | -0.0027847 | -0.00069736 | 0.0027848 | 0.00069717 | 1.4417e-07 | -1.92e-07 | 0.0041778 | 0.0041777 | 0.0041778 | 0.99179 | -0.15813 | 0.99184 | -0.15704 | 1.1477
59 | 0.0085253 | 0.0021365 | -0.0085227 | -0.0021354 | 2.6325e-06 | 1.1204e-06 | 0.012729 | 0.012729 | 0.012729 | 0.99661 | -0.065037 | 0.99627 | -0.071521 | 3.497
60 | 0.046149 | 0.011617 | -0.04613 | -0.011605 | 1.923e-05 | 1.2166e-05 | 0.068922 | 0.068922 | 0.068922 | 0.99661 | -0.065037 | 0.99615 | -0.073759 | 18.9346
61 | 0.0069958 | 0.0017527 | -0.0069951 | -0.0017525 | 7.0421e-07 | 2.2674e-07 | 0.010449 | 0.010449 | 0.010449 | 0.99627 | -0.071521 | 0.99616 | -0.073635 | 2.8705
62 | 0.04555 | 0.011459 | -0.045531 | -0.011448 | 1.8458e-05 | 1.1675e-05 | 0.068056 | 0.068056 | 0.068056 | 0.99615 | -0.073759 | 0.99571 | -0.082244 | 18.6966
63 | 0.0037257 | 0.00093339 | -0.0037252 | -0.00093363 | 5.0237e-07 | -2.4126e-07 | 0.0055658 | 0.005566 | 0.005566 | 0.99606 | -0.075679 | 0.99591 | -0.07851 | 1.5291
64 | -0.0037257 | -0.00093339 | 0.0037261 | 0.00093322 | 3.6268e-07 | -1.743e-07 | 0.0055658 | 0.0055656 | 0.0055658 | 0.99606 | -0.075679 | 0.99616 | -0.073635 | 1.5291
65 | -0.011001 | -0.0027606 | 0.011003 | 0.0027617 | 2.144e-06 | 1.099e-06 | 0.016472 | 0.016472 | 0.016472 | 0.99389 | -0.11738 | 0.9941 | -0.1133 | 4.5253
66 | -0.00065414 | -0.00016394 | 0.00065415 | 0.00016357 | 1.0624e-08 | -3.713e-07 | 0.00098241 | 0.00098228 | 0.00098241 | 0.99079 | -0.17748 | 0.99081 | -0.17714 | 0.26989
67 | -0.0016053 | -0.00040194 | 0.0016053 | 0.00040152 | 7.972e-08 | -4.2017e-07 | 0.0024107 | 0.0024105 | 0.0024107 | 0.99081 | -0.17714 | 0.99086 | -0.1761 | 0.66228
68 | 0.038643 | 0.0097179 | -0.038626 | -0.0097069 | 1.7612e-05 | 1.1092e-05 | 0.05805 | 0.05805 | 0.05805 | 0.99076 | -0.17735 | 0.99027 | -0.1869 | 15.9477
69 | -0.053514 | -0.013444 | 0.053534 | 0.013457 | 2.0126e-05 | 1.2774e-05 | 0.080384 | 0.080384 | 0.080384 | 0.99076 | -0.17735 | 0.99117 | -0.16947 | 22.0834
70 | 0.024851 | 0.006245 | -0.02484 | -0.0062384 | 1.0654e-05 | 6.5509e-06 | 0.037153 | 0.037153 | 0.037153 | 0.99546 | -0.08712 | 0.99499 | -0.096104 | 10.2069
71 | 0.032012 | 0.0080463 | -0.032003 | -0.0080408 | 8.7759e-06 | 5.4867e-06 | 0.048124 | 0.048124 | 0.048124 | 0.99 | -0.19213 | 0.9897 | -0.19788 | 13.2208
72 | -0.032012 | -0.0080463 | 0.03202 | 0.0080513 | 8.0071e-06 | 5.006e-06 | 0.048124 | 0.048124 | 0.048124 | 0.99 | -0.19213 | 0.99027 | -0.1869 | 13.2208
73 | 0.030956 | 0.0077784 | -0.030934 | -0.0077644 | 2.2415e-05 | 1.3991e-05 | 0.04655 | 0.04655 | 0.04655 | 0.9897 | -0.19788 | 0.98892 | -0.21306 | 12.7884
74 | 0.013015 | 0.0032642 | -0.013007 | -0.0032602 | 7.227e-06 | 3.9697e-06 | 0.019499 | 0.0195 | 0.0195 | 0.99321 | -0.13056 | 0.99261 | -0.14221 | 5.357
75 | -0.018636 | -0.0046716 | 0.018645 | 0.0046769 | 8.9612e-06 | 5.3383e-06 | 0.027921 | 0.027921 | 0.027921 | 0.99321 | -0.13056 | 0.99373 | -0.12047 | 7.6706
76 | 0.029806 | 0.0074817 | -0.029806 | -0.0074816 | 1.8821e-07 | 1.1726e-07 | 0.044852 | 0.044852 | 0.044852 | 0.98892 | -0.21306 | 0.98891 | -0.21319 | 12.3221
77 | 0.028665 | 0.0071957 | -0.028665 | -0.0071956 | 1.3791e-07 | 8.5724e-08 | 0.043136 | 0.043136 | 0.043136 | 0.98891 | -0.21319 | 0.98891 | -0.21329 | 11.8506
78 | -0.002023 | -0.00050702 | 0.0020231 | 0.00050681 | 6.7606e-08 | -2.0975e-07 | 0.0030338 | 0.0030337 | 0.0030338 | 0.99224 | -0.14936 | 0.99228 | -0.14866 | 0.83347
79 | -0.0020231 | -0.00050681 | 0.0020232 | 0.00050637 | 1.3987e-07 | -4.3406e-07 | 0.0030337 | 0.0030336 | 0.0030337 | 0.99228 | -0.14866 | 0.99235 | -0.14721 | 0.83345
80 | -0.013004 | -0.0032585 | 0.013007 | 0.0032602 | 3.0954e-06 | 1.7005e-06 | 0.0195 | 0.0195 | 0.0195 | 0.99235 | -0.14721 | 0.99261 | -0.14221 | 5.357
81 | -0.019439 | -0.0048758 | 0.019441 | 0.0048769 | 1.8282e-06 | 1.0955e-06 | 0.029109 | 0.029109 | 0.029109 | 0.99373 | -0.12047 | 0.99384 | -0.1185 | 7.997
82 | -0.0019705 | -0.00049384 | 0.0019705 | 0.00049371 | 3.9282e-08 | -1.3153e-07 | 0.0029469 | 0.0029468 | 0.0029469 | 0.99497 | -0.096523 | 0.99499 | -0.096104 | 0.80959
83 | 0.02287 | 0.0057447 | -0.022859 | -0.0057381 | 1.0898e-05 | 6.6525e-06 | 0.034206 | 0.034206 | 0.034206 | 0.99499 | -0.096104 | 0.99448 | -0.10609 | 9.3974
84 | 0.04415 | 0.011102 | -0.044137 | -0.011094 | 1.29e-05 | 8.1533e-06 | 0.065992 | 0.065992 | 0.065992 | 0.99571 | -0.082244 | 0.9954 | -0.088364 | 18.1297
85 | -0.0010127 | -0.00025382 | 0.0010128 | 0.00025372 | 6.955e-09 | -9.9157e-08 | 0.0015197 | 0.0015196 | 0.0015197 | 0.99164 | -0.16092 | 0.99165 | -0.16077 | 0.41749
86 | -0.0018962 | -0.00047512 | 0.0018962 | 0.00047503 | 2.6649e-08 | -9.6199e-08 | 0.0028452 | 0.0028452 | 0.0028452 | 0.99165 | -0.16077 | 0.99167 | -0.16048 | 0.78166
87 | -0.0027848 | -0.00069717 | 0.0027849 | 0.00069704 | 9.5075e-08 | -1.2664e-07 | 0.0041777 | 0.0041776 | 0.0041777 | 0.99184 | -0.15704 | 0.99188 | -0.15633 | 1.1477
88 | -0.043223 | -0.010862 | 0.043229 | 0.010866 | 6.1305e-06 | 3.8727e-06 | 0.064635 | 0.064635 | 0.064635 | 0.99524 | -0.091335 | 0.9954 | -0.088364 | 17.7568
89 | 0.041976 | 0.010549 | -0.041971 | -0.010546 | 4.8641e-06 | 3.0703e-06 | 0.062769 | 0.062769 | 0.062769 | 0.99524 | -0.091335 | 0.99512 | -0.093762 | 17.2443
90 | 0.03356 | 0.0084387 | -0.033529 | -0.0084192 | 3.1281e-05 | 1.959e-05 | 0.050193 | 0.050193 | 0.050193 | 0.99512 | -0.093762 | 0.9941 | -0.1133 | 13.7893
91 | 0.0084107 | 0.0021076 | -0.0084096 | -0.0021071 | 1.1433e-06 | 4.8135e-07 | 0.012577 | 0.012577 | 0.012577 | 0.99512 | -0.093762 | 0.99497 | -0.096616 | 3.4551
92 | 0.022525 | 0.0056574 | -0.022508 | -0.0056469 | 1.7209e-05 | 1.0491e-05 | 0.033721 | 0.033721 | 0.033721 | 0.9941 | -0.1133 | 0.99327 | -0.12932 | 9.2641
93 | 0.0047573 | 0.0011921 | -0.0047565 | -0.0011921 | 7.8622e-07 | -3.4655e-08 | 0.0071146 | 0.0071148 | 0.0071148 | 0.99497 | -0.096616 | 0.99479 | -0.10009 | 1.9546
94 | 0.0036523 | 0.00091506 | -0.0036521 | -0.00091514 | 1.3703e-07 | -7.1369e-08 | 0.005462 | 0.0054621 | 0.0054621 | 0.99497 | -0.096616 | 0.99493 | -0.097404 | 1.5006
95 | 0.021118 | 0.0052987 | -0.021116 | -0.0052972 | 2.4409e-06 | 1.478e-06 | 0.03164 | 0.03164 | 0.03164 | 0.99327 | -0.12932 | 0.99315 | -0.13175 | 8.6922
96 | 0.0028998 | 0.00072659 | -0.0028998 | -0.00072667 | 6.4337e-08 | -7.7276e-08 | 0.0043369 | 0.004337 | 0.004337 | 0.99493 | -0.097404 | 0.9949 | -0.09787 | 1.1915
97 | 0.021116 | 0.0052972 | -0.021109 | -0.0052931 | 6.7295e-06 | 4.075e-06 | 0.03164 | 0.03164 | 0.03164 | 0.99315 | -0.13175 | 0.9928 | -0.13843 | 8.6922
98 | 0.0011903 | 0.00029824 | -0.0011903 | -0.00029832 | 8.0561e-09 | -8.2865e-08 | 0.0017803 | 0.0017803 | 0.0017803 | 0.9949 | -0.09787 | 0.9949 | -0.098012 | 0.48909
99 | 0.019903 | 0.0049908 | -0.019894 | -0.0049851 | 9.5559e-06 | 5.7457e-06 | 0.029832 | 0.029832 | 0.029832 | 0.9928 | -0.13843 | 0.99228 | -0.14851 | 8.1956
100 | 0.016475 | 0.0041283 | -0.016471 | -0.0041261 | 3.8086e-06 | 2.2226e-06 | 0.024705 | 0.024705 | 0.024705 | 0.99228 | -0.14851 | 0.99203 | -0.15337 | 6.7872
101 | -0.0038686 | -0.00096863 | 0.0038686 | 0.00096863 | 1.1659e-09 | -4.4575e-10 | 0.0058033 | 0.0058033 | 0.0058033 | 0.99188 | -0.15633 | 0.99188 | -0.15632 | 1.5943
102 | 0.0015753 | 0.00039417 | -0.0015752 | -0.00039478 | 1.1163e-07 | -6.1692e-07 | 0.0023627 | 0.0023629 | 0.0023629 | 0.99203 | -0.15337 | 0.99196 | -0.15486 | 0.64916
103 | 0.0086742 | 0.0021736 | -0.0086729 | -0.002173 | 1.3572e-06 | 5.9264e-07 | 0.013011 | 0.013011 | 0.013011 | 0.99203 | -0.15337 | 0.99186 | -0.15665 | 3.5745
104 | 0.0062215 | 0.0015583 | -0.006221 | -0.0015581 | 5.3539e-07 | 1.3099e-07 | 0.0093317 | 0.0093318 | 0.0093318 | 0.99203 | -0.15337 | 0.99194 | -0.15517 | 2.5637
105 | -0.0050926 | -0.0012754 | 0.0050928 | 0.0012754 | 2.7759e-07 | 1.3939e-08 | 0.0076395 | 0.0076395 | 0.0076395 | 0.99188 | -0.15632 | 0.99194 | -0.15517 | 2.0988
106 | -0.0026965 | -0.00067561 | 0.0026967 | 0.00067539 | 1.4775e-07 | -2.1597e-07 | 0.0040461 | 0.004046 | 0.0040461 | 0.99167 | -0.16048 | 0.99172 | -0.15933 | 1.1116
107 | -0.0026967 | -0.00067539 | 0.0026968 | 0.00067525 | 9.5986e-08 | -1.4033e-07 | 0.004046 | 0.0040459 | 0.004046 | 0.99172 | -0.15933 | 0.99176 | -0.15858 | 1.1115
108 | -0.0037367 | -0.00093588 | 0.0037367 | 0.00093586 | 3.7804e-08 | -1.7196e-08 | 0.0056062 | 0.0056062 | 0.0056062 | 0.99176 | -0.15858 | 0.99177 | -0.15837 | 1.5402
109 | -0.0053413 | -0.001338 | 0.0053413 | 0.001338 | 4.4319e-09 | 4.6154e-10 | 0.0080137 | 0.0080137 | 0.0080137 | 0.99177 | -0.15837 | 0.99177 | -0.15835 | 2.2016
110 | -0.0063384 | -0.0015879 | 0.0063387 | 0.001588 | 2.3019e-07 | 5.9727e-08 | 0.0095097 | 0.0095096 | 0.0095097 | 0.99177 | -0.15835 | 0.99181 | -0.15759 | 2.6125
111 | 0.0075161 | 0.0018831 | -0.0075158 | -0.001883 | 3.3534e-07 | 1.2384e-07 | 0.011276 | 0.011276 | 0.011276 | 0.99186 | -0.15665 | 0.99181 | -0.15759 | 3.0977
112 | 0.0226 | 0.0056731 | -0.0226 | -0.005673 | 6.2312e-08 | 3.7995e-08 | 0.033819 | 0.033819 | 0.033819 | 0.99448 | -0.10613 | 0.99447 | -0.10619 | 9.2908
113 | -0.022727 | -0.005705 | 0.022727 | 0.005705 | 3.6906e-08 | 2.2517e-08 | 0.034009 | 0.034009 | 0.034009 | 0.99448 | -0.10613 | 0.99448 | -0.10609 | 9.3432
114 | 0.022459 | 0.0056377 | -0.022458 | -0.0056376 | 2.652e-07 | 1.6161e-07 | 0.033608 | 0.033608 | 0.033608 | 0.99447 | -0.10619 | 0.99446 | -0.10643 | 9.2329
115 | 0.021684 | 0.0054434 | -0.021675 | -0.0054381 | 8.6782e-06 | 5.269e-06 | 0.032449 | 0.032449 | 0.032449 | 0.99446 | -0.10643 | 0.99402 | -0.11483 | 8.9145
116 | 0.021026 | 0.0052754 | -0.021024 | -0.0052744 | 1.7264e-06 | 1.0447e-06 | 0.031477 | 0.031477 | 0.031477 | 0.99402 | -0.11483 | 0.99394 | -0.11655 | 8.6474
117 | 0.020323 | 0.0050986 | -0.020321 | -0.0050975 | 1.8878e-06 | 1.1377e-06 | 0.030427 | 0.030427 | 0.030427 | 0.99394 | -0.11655 | 0.99384 | -0.1185 | 8.359
118 | 0.02748 | 0.0068986 | -0.027479 | -0.0068985 | 1.6232e-07 | 1.0064e-07 | 0.041353 | 0.041353 | 0.041353 | 0.98891 | -0.21329 | 0.9889 | -0.21342 | 11.3607
119 | 0.026235 | 0.0065866 | -0.02622 | -0.0065775 | 1.4625e-05 | 9.0394e-06 | 0.03948 | 0.03948 | 0.03948 | 0.9889 | -0.21342 | 0.9883 | -0.22511 | 10.8462
120 | 0.025109 | 0.006299 | -0.025108 | -0.0062988 | 2.3953e-07 | 1.4757e-07 | 0.037807 | 0.037807 | 0.037807 | 0.9883 | -0.22511 | 0.98829 | -0.22531 | 10.3864
121 | -0.020611 | -0.0051683 | 0.02062 | 0.0051738 | 8.9974e-06 | 5.4396e-06 | 0.031049 | 0.031049 | 0.031049 | 0.9878 | -0.23483 | 0.98827 | -0.22568 | 8.53
122 | 0.019424 | 0.0048709 | -0.019424 | -0.0048708 | 1.6787e-07 | 1.0074e-07 | 0.029261 | 0.029261 | 0.029261 | 0.9878 | -0.23483 | 0.98779 | -0.23501 | 8.0389
123 | -0.021687 | -0.0054411 | 0.021687 | 0.0054412 | 1.072e-07 | 6.5175e-08 | 0.032655 | 0.032655 | 0.032655 | 0.98827 | -0.22568 | 0.98828 | -0.22557 | 8.9712
124 | 0.018291 | 0.0045868 | -0.018289 | -0.0045859 | 1.4186e-06 | 8.4413e-07 | 0.027554 | 0.027554 | 0.027554 | 0.98779 | -0.23501 | 0.98771 | -0.23664 | 7.5699
125 | -0.022798 | -0.0057196 | 0.022798 | 0.0057196 | 7.2048e-08 | 4.4021e-08 | 0.034328 | 0.034328 | 0.034328 | 0.98828 | -0.22557 | 0.98828 | -0.22551 | 9.4307
126 | 0.017751 | 0.0044511 | -0.01775 | -0.0044505 | 1.0093e-06 | 5.9782e-07 | 0.026744 | 0.026744 | 0.026744 | 0.98771 | -0.23664 | 0.98765 | -0.23784 | 7.3473
127 | -0.023775 | -0.0059645 | 0.023775 | 0.0059647 | 2.25e-07 | 1.38e-07 | 0.035799 | 0.035799 | 0.035799 | 0.98828 | -0.22551 | 0.98829 | -0.22531 | 9.8349
128 | 0.017274 | 0.004331 | -0.017271 | -0.0043294 | 2.7322e-06 | 1.611e-06 | 0.026026 | 0.026026 | 0.026026 | 0.98765 | -0.23784 | 0.98748 | -0.24115 | 7.1499
129 | 0.016041 | 0.0040212 | -0.01604 | -0.0040204 | 1.4445e-06 | 8.4015e-07 | 0.024173 | 0.024173 | 0.024173 | 0.98748 | -0.24115 | 0.98738 | -0.24304 | 6.6409

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.17281 | 0.043334

## res_load
| p_mw | q_mvar
0 | 0.0034897 | 0.00087459
1 | 0.00063471 | 0.00015907
2 | 0.00056962 | 0.00014276
3 | 0.001177 | 0.000295
4 | 0.0015607 | 0.00039115
5 | 0.0070049 | 0.0017556
6 | 0.00081787 | 0.00020498
7 | 0.004278 | 0.0010722
8 | 0.0016012 | 0.00040129
9 | 0.0017731 | 0.00044439
10 | 0.00094537 | 0.00023693
11 | 0.0020759 | 0.00052027
12 | 0.00043206 | 0.00010828
13 | 0.0024296 | 0.00060891
14 | 0.00087991 | 0.00022053
15 | 0.005626 | 0.00141
16 | 0.0028431 | 0.00071256
17 | 0.0024197 | 0.00060644
18 | 0.00081826 | 0.00020507
19 | 0.00011252 | 2.82e-05
20 | 0.010087 | 0.0025279
21 | 0.0012229 | 0.0003065
22 | 0.012922 | 0.0032386
23 | 0.00082019 | 0.00020556
24 | 0.00097209 | 0.00024363
25 | 0.0008075 | 0.00020238
26 | 0.001384 | 0.00034687
27 | 0.0014006 | 0.00035102
28 | 0.0015269 | 0.00038267
29 | 0.00058004 | 0.00014537
30 | 0.0029311 | 0.0007346
31 | 0.0037252 | 0.00093363
32 | 0.003269 | 0.0008193
33 | 0.0011751 | 0.00029452
34 | 0.00065414 | 0.00016394
35 | 0.00095112 | 0.00023837
36 | 0.0014989 | 0.00037567
37 | 0.0006177 | 0.00015481
38 | 0.0038861 | 0.00097395
39 | 0.000132 | 3.3083e-05
40 | 0.00040827 | 0.00010232
41 | 0.0010469 | 0.00026239
42 | 0.0066057 | 0.0016556
43 | 0.0023111 | 0.00057921
44 | 0.001128 | 0.0002827
45 | 0.0011407 | 0.00028588
46 | 0.002023 | 0.00050702
47 | 0.010981 | 0.0027521
48 | 0.00079353 | 0.00019888
49 | 0.0019705 | 0.00049384
50 | 0.0013808 | 0.00034605
51 | 0.0010127 | 0.00025382
52 | 0.00088341 | 0.0002214
53 | 0.0007205 | 0.00018057
54 | 0.0012477 | 0.00031269
55 | 0.00090808 | 0.00022759
56 | 0.0013896 | 0.00034827
57 | 0.0047565 | 0.0011921
58 | 0.00075232 | 0.00018855
59 | 0.0017094 | 0.00042843
60 | 0.0012062 | 0.00030231
61 | 0.0034186 | 0.00085679
62 | 0.0010836 | 0.00027159
63 | 0.001224 | 0.00030676
64 | 0.00080033 | 0.00020058
65 | 0.0010399 | 0.00026062
66 | 0.0016046 | 0.00040215
67 | 0.0009971 | 0.0002499
68 | 0.0015752 | 0.00039478
69 | 0.0011568 | 0.00028992
70 | 0.0011282 | 0.00028274
71 | 0.0011771 | 0.00029501
72 | 0.0011903 | 0.00029832
73 | 0.00012744 | 3.1939e-05
74 | 0.00014084 | 3.5298e-05
75 | 0.00013177 | 3.3025e-05
76 | 0.0007748 | 0.00019418
77 | 0.0006493 | 0.00016273
78 | 0.00070127 | 0.00017576
79 | 0.00088008 | 0.00022057
80 | 0.0011851 | 0.00029701
81 | 0.0012447 | 0.00031195
82 | 0.0011114 | 0.00027855
83 | 0.0011868 | 0.00029744
84 | 0.0010666 | 0.00026731
85 | 0.0011333 | 0.00028403
86 | 0.0011108 | 0.0002784
87 | 0.00053784 | 0.00013479
88 | 0.0009773 | 0.00024493
89 | 0.00047683 | 0.0001195
90 | 0.0013334 | 0.00033417
91 | 0.0012296 | 0.00030818
92 | 0.001126 | 0.0002822

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1