## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_223-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_223-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_223-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_223-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_223-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_223-4_0_4_node_97 | 0.4 | n |  | TRUE
6 | bus_LV_223-4_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_223-4_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_223-4_0_4_node_98 | 0.4 | n |  | TRUE
9 | bus_LV_223-4_0_4_node_105 | 0.4 | n |  | TRUE
10 | bus_LV_223-4_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_223-4_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_223-4_0_4_node_100 | 0.4 | n |  | TRUE
13 | bus_LV_223-4_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_223-4_0_4_node_95 | 0.4 | n |  | TRUE
15 | bus_LV_223-4_0_4_node_96 | 0.4 | n |  | TRUE
16 | bus_LV_223-4_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_223-4_0_4_node_106 | 0.4 | n |  | TRUE
18 | bus_LV_223-4_0_4_node_111 | 0.4 | n |  | TRUE
19 | bus_LV_223-4_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_223-4_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_223-4_0_4_node_107 | 0.4 | n |  | TRUE
22 | bus_LV_223-4_0_4_node_114 | 0.4 | n |  | TRUE
23 | bus_LV_223-4_0_4_node_113 | 0.4 | n |  | TRUE
24 | bus_LV_223-4_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_223-4_0_4_node_101 | 0.4 | n |  | TRUE
26 | bus_LV_223-4_0_4_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_223-4_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_223-4_0_4_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_223-4_0_4_node_11 | 0.4 | n |  | TRUE
30 | bus_LV_223-4_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_223-4_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_223-4_0_4_node_9 | 0.4 | n |  | TRUE
33 | bus_LV_223-4_0_4_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_223-4_0_4_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_223-4_0_4_node_53 | 0.4 | n |  | TRUE
36 | bus_LV_223-4_0_4_node_104 | 0.4 | n |  | TRUE
37 | bus_LV_223-4_0_4_node_99 | 0.4 | n |  | TRUE
38 | bus_LV_223-4_0_4_node_93 | 0.4 | n |  | TRUE
39 | bus_LV_223-4_0_4_node_90 | 0.4 | n |  | TRUE
40 | bus_LV_223-4_0_4_node_10 | 0.4 | n |  | TRUE
41 | bus_LV_223-4_0_4_node_108 | 0.4 | n |  | TRUE
42 | bus_LV_223-4_0_4_node_110 | 0.4 | n |  | TRUE
43 | bus_LV_223-4_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_223-4_0_4_node_112 | 0.4 | n |  | TRUE
45 | bus_LV_223-4_0_4_node_102 | 0.4 | n |  | TRUE
46 | bus_LV_223-4_0_4_node_82 | 0.4 | n |  | TRUE
47 | bus_LV_223-4_0_4_node_88 | 0.4 | n |  | TRUE
48 | bus_LV_223-4_0_4_node_89 | 0.4 | n |  | TRUE
49 | bus_LV_223-4_0_4_node_52 | 0.4 | n |  | TRUE
50 | bus_LV_223-4_0_4_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_223-4_0_4_node_22 | 0.4 | n |  | TRUE
52 | bus_LV_223-4_0_4_node_23 | 0.4 | n |  | TRUE
53 | bus_LV_223-4_0_4_node_24 | 0.4 | n |  | TRUE
54 | bus_LV_223-4_0_4_node_25 | 0.4 | n |  | TRUE
55 | bus_LV_223-4_0_4_node_26 | 0.4 | n |  | TRUE
56 | bus_LV_223-4_0_4_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_223-4_0_4_node_117 | 0.4 | n |  | TRUE
58 | bus_LV_223-4_0_4_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_223-4_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_223-4_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_223-4_0_4_node_29 | 0.4 | n |  | TRUE
62 | bus_LV_223-4_0_4_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_223-4_0_4_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_223-4_0_4_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_223-4_0_4_node_35 | 0.4 | n |  | TRUE
66 | bus_LV_223-4_0_4_node_36 | 0.4 | n |  | TRUE
67 | bus_LV_223-4_0_4_node_37 | 0.4 | n |  | TRUE
68 | bus_LV_223-4_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_223-4_0_4_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_223-4_0_4_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_223-4_0_4_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_223-4_0_4_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_223-4_0_4_node_43 | 0.4 | n |  | TRUE
74 | bus_LV_223-4_0_4_node_48 | 0.4 | n |  | TRUE
75 | bus_LV_223-4_0_4_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_223-4_0_4_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_223-4_0_4_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_223-4_0_4_node_115 | 0.4 | n |  | TRUE
79 | bus_LV_223-4_0_4_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_223-4_0_4_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_223-4_0_4_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_223-4_0_4_node_60 | 0.4 | n |  | TRUE
83 | bus_LV_223-4_0_4_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_223-4_0_4_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_223-4_0_4_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_223-4_0_4_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_223-4_0_4_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_223-4_0_4_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_223-4_0_4_node_63 | 0.4 | n |  | TRUE
90 | bus_LV_223-4_0_4_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_223-4_0_4_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_223-4_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_223-4_0_4_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_223-4_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_223-4_0_4_node_61 | 0.4 | n |  | TRUE
96 | bus_LV_223-4_0_4_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_223-4_0_4_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_223-4_0_4_node_118 | 0.4 | n |  | TRUE
99 | bus_LV_223-4_0_4_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_223-4_0_4_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_223-4_0_4_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_223-4_0_4_node_81 | 0.4 | n |  | TRUE
103 | bus_LV_223-4_0_4_node_55 | 0.4 | n |  | TRUE
104 | bus_LV_223-4_0_4_node_59 | 0.4 | n |  | TRUE
105 | bus_LV_223-4_0_4_node_56 | 0.4 | n |  | TRUE
106 | bus_LV_223-4_0_4_node_116 | 0.4 | n |  | TRUE
107 | bus_LV_223-4_0_4_node_57 | 0.4 | n |  | TRUE
108 | bus_LV_223-4_0_4_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_223-4_0_4_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_223-4_0_4_node_73 | 0.4 | n |  | TRUE
111 | bus_LV_223-4_0_4_node_77 | 0.4 | n |  | TRUE
112 | bus_LV_223-4_0_4_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_223-4_0_4_node_92 | 0.4 | n |  | TRUE
114 | bus_LV_223-4_0_4_node_109 | 0.4 | n |  | TRUE
115 | bus_MV_371_0_node_160 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_223-4_0_4_load_0 | 0 | 0.0008882 | 0.00022261 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_223-4_0_4_load_2 | 2 | 0.0019697 | 0.00049365 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_223-4_0_4_load_97 | 5 | 0.00071909 | 0.00018022 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_223-4_0_4_load_8 | 6 | 0.0011405 | 0.00028584 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_223-4_0_4_load_98 | 8 | 0.0030135 | 0.00075525 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_223-4_0_4_load_100 | 12 | 0.0012012 | 0.00030105 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_223-4_0_4_load_96 | 15 | 0.0013014 | 0.00032615 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_223-4_0_4_load_106 | 17 | 0.0023677 | 0.0005934 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_223-4_0_4_load_111 | 18 | 0.0014819 | 0.00037141 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_223-4_0_4_load_107 | 21 | 0.0041262 | 0.0010341 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_223-4_0_4_load_114 | 22 | 0.0014556 | 0.0003648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_223-4_0_4_load_113 | 23 | 0.00085734 | 0.00021487 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_223-4_0_4_load_103 | 26 | 0.0015414 | 0.00038632 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_223-4_0_4_load_32 | 28 | 0.00041735 | 0.0001046 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_223-4_0_4_load_9 | 32 | 0.0012267 | 0.00030744 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_223-4_0_4_load_83 | 33 | 0.00050018 | 0.00012536 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_223-4_0_4_load_53 | 35 | 0.00038075 | 9.5424e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_223-4_0_4_load_104 | 36 | 0.0013773 | 0.00034519 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_223-4_0_4_load_99 | 37 | 0.0008222 | 0.00020606 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_223-4_0_4_load_90 | 39 | 0.0035874 | 0.00089908 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_223-4_0_4_load_10 | 40 | 0.0031214 | 0.0007823 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_223-4_0_4_load_108 | 41 | 0.0095579 | 0.0023954 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_223-4_0_4_load_30 | 43 | 0.00094161 | 0.00023599 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_223-4_0_4_load_112 | 44 | 0.0033111 | 0.00082984 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_223-4_0_4_load_102 | 45 | 0.0036565 | 0.00091641 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_223-4_0_4_load_82 | 46 | 0.0019107 | 0.00047886 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_223-4_0_4_load_88 | 47 | 0.00060255 | 0.00015101 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_223-4_0_4_load_89 | 48 | 0.001062 | 0.00026617 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_223-4_0_4_load_52 | 49 | 0.00058875 | 0.00014755 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_223-4_0_4_load_22 | 51 | 0.0022881 | 0.00057346 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_223-4_0_4_load_23 | 52 | 0.00014896 | 3.7332e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_223-4_0_4_load_26 | 55 | 0.00073102 | 0.00018321 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_223-4_0_4_load_28 | 56 | 6.2889e-05 | 1.5761e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_223-4_0_4_load_117 | 57 | 0.00049275 | 0.0001235 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_223-4_0_4_load_45 | 60 | 0.0029474 | 0.00073869 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_223-4_0_4_load_29 | 61 | 0.0042121 | 0.0010557 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_223-4_0_4_load_33 | 63 | 0.00040011 | 0.00010028 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_223-4_0_4_load_34 | 64 | 0.0011247 | 0.00028187 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_223-4_0_4_load_35 | 65 | 0.00093928 | 0.00023541 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_223-4_0_4_load_42 | 69 | 0.0015144 | 0.00037955 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_223-4_0_4_load_38 | 70 | 0.0044803 | 0.0011229 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_223-4_0_4_load_39 | 71 | 0.0003364 | 8.4309e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_223-4_0_4_load_41 | 72 | 0.0019009 | 0.00047641 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_223-4_0_4_load_43 | 73 | 0.0010156 | 0.00025453 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_223-4_0_4_load_48 | 74 | 0.0010039 | 0.0002516 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_223-4_0_4_load_44 | 75 | 0.0024126 | 0.00060465 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_223-4_0_4_load_115 | 78 | 7.3432e-05 | 1.8404e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_223-4_0_4_load_72 | 80 | 0.00029172 | 7.3112e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_223-4_0_4_load_74 | 81 | 0.00068844 | 0.00017254 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_223-4_0_4_load_75 | 84 | 0.00016271 | 4.0779e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_223-4_0_4_load_78 | 88 | 0.00039289 | 9.8468e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_223-4_0_4_load_79 | 91 | 0.0010016 | 0.00025102 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_223-4_0_4_load_76 | 92 | 0.00027266 | 6.8335e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_223-4_0_4_load_86 | 94 | 0.0010576 | 0.00026505 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_223-4_0_4_load_84 | 96 | 0.00072856 | 0.00018259 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_223-4_0_4_load_85 | 97 | 0.00058163 | 0.00014577 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_223-4_0_4_load_118 | 98 | 0.0012265 | 0.00030739 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_223-4_0_4_load_80 | 101 | 0.0006292 | 0.00015769 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_223-4_0_4_load_81 | 102 | 0.0001465 | 3.6717e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_223-4_0_4_load_55 | 103 | 0.00064972 | 0.00016284 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_223-4_0_4_load_59 | 104 | 0.00072266 | 0.00018112 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_223-4_0_4_load_56 | 105 | 0.0008701 | 0.00021807 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_223-4_0_4_load_116 | 106 | 0.0005594 | 0.0001402 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_223-4_0_4_load_57 | 107 | 0.00057609 | 0.00014438 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_223-4_0_4_load_87 | 108 | 0.0039992 | 0.0010023 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_223-4_0_4_load_94 | 109 | 0.00030779 | 7.7139e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_223-4_0_4_load_73 | 110 | 0.00031938 | 8.0045e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_223-4_0_4_load_77 | 111 | 0.00085513 | 0.00021432 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_223-4_0_4_load_91 | 112 | 0.0003107 | 7.7869e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_223-4_0_4_load_92 | 113 | 0.00051598 | 0.00012932 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_223-4_0_4_load_109 | 114 | 0.00094208 | 0.00023611 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_223-4_0_4_line_0 |  | 0 | 1 | 0.018178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_223-4_0_4_line_1 |  | 0 | 2 | 0.0041098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_223-4_0_4_line_2 |  | 1 | 3 | 0.22768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_223-4_0_4_line_3 |  | 1 | 4 | 0.027623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_223-4_0_4_line_4 |  | 3 | 5 | 0.24163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_223-4_0_4_line_5 |  | 4 | 6 | 0.012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_223-4_0_4_line_6 |  | 5 | 8 | 0.028064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_223-4_0_4_line_7 |  | 7 | 8 | 0.014388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_223-4_0_4_line_8 |  | 7 | 9 | 0.007535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_223-4_0_4_line_9 |  | 9 | 17 | 0.012234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_223-4_0_4_line_10 |  | 9 | 36 | 0.018394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_223-4_0_4_line_11 |  | 10 | 11 | 0.20905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_223-4_0_4_line_12 |  | 10 | 12 | 0.076079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_223-4_0_4_line_13 |  | 11 | 33 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_223-4_0_4_line_14 |  | 12 | 37 | 0.0065284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_223-4_0_4_line_15 |  | 13 | 14 | 0.040714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_223-4_0_4_line_16 |  | 13 | 15 | 0.015308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_223-4_0_4_line_17 |  | 14 | 38 | 0.025428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_223-4_0_4_line_18 |  | 14 | 39 | 0.034169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_223-4_0_4_line_19 |  | 16 | 17 | 0.012885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_223-4_0_4_line_20 |  | 16 | 18 | 0.012322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_223-4_0_4_line_21 |  | 16 | 19 | 0.19312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_223-4_0_4_line_22 |  | 18 | 42 | 0.025465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_223-4_0_4_line_23 |  | 19 | 20 | 0.31161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_223-4_0_4_line_24 |  | 19 | 21 | 0.027079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_223-4_0_4_line_25 |  | 20 | 22 | 0.0246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_223-4_0_4_line_26 |  | 20 | 23 | 0.0010807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_223-4_0_4_line_27 |  | 21 | 41 | 0.011569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_223-4_0_4_line_28 |  | 22 | 30 | 0.030258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_223-4_0_4_line_29 |  | 24 | 25 | 0.010432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_223-4_0_4_line_30 |  | 24 | 26 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_223-4_0_4_line_31 |  | 25 | 45 | 0.021748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_223-4_0_4_line_32 |  | 25 | 37 | 0.0093116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_223-4_0_4_line_33 |  | 26 | 36 | 0.064913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_223-4_0_4_line_34 |  | 27 | 28 | 0.20666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_223-4_0_4_line_35 |  | 27 | 29 | 0.11972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_223-4_0_4_line_36 |  | 28 | 43 | 0.029074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_223-4_0_4_line_37 |  | 29 | 32 | 0.0093647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_223-4_0_4_line_38 |  | 30 | 31 | 0.37106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_223-4_0_4_line_39 |  | 31 | 34 | 0.016789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_223-4_0_4_line_40 |  | 31 | 35 | 0.010017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_223-4_0_4_line_41 |  | 32 | 40 | 0.044205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_223-4_0_4_line_42 |  | 33 | 46 | 0.023772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_223-4_0_4_line_43 |  | 34 | 49 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_223-4_0_4_line_44 |  | 35 | 50 | 0.099793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_223-4_0_4_line_45 |  | 38 | 112 | 0.021942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_223-4_0_4_line_46 |  | 38 | 83 | 0.009296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_223-4_0_4_line_47 |  | 39 | 48 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_223-4_0_4_line_48 |  | 42 | 44 | 0.020989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_223-4_0_4_line_49 |  | 42 | 114 | 0.017007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_223-4_0_4_line_50 |  | 43 | 61 | 0.019811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_223-4_0_4_line_51 |  | 46 | 95 | 0.021968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_223-4_0_4_line_52 |  | 47 | 48 | 0.005426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_223-4_0_4_line_53 |  | 49 | 67 | 0.077685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_223-4_0_4_line_54 |  | 50 | 103 | 0.0021542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_223-4_0_4_line_55 |  | 51 | 52 | 0.014122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_223-4_0_4_line_56 |  | 51 | 53 | 0.016821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_223-4_0_4_line_57 |  | 52 | 54 | 0.037248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_223-4_0_4_line_58 |  | 53 | 55 | 0.033268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_223-4_0_4_line_59 |  | 54 | 56 | 0.038207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_223-4_0_4_line_60 |  | 55 | 57 | 0.0077024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_223-4_0_4_line_61 |  | 57 | 58 | 0.019536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_223-4_0_4_line_62 |  | 58 | 59 | 0.097835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_223-4_0_4_line_63 |  | 59 | 60 | 0.04108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_223-4_0_4_line_64 |  | 60 | 76 | 0.1306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_223-4_0_4_line_65 |  | 61 | 62 | 0.04734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_223-4_0_4_line_66 |  | 62 | 63 | 0.013511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_223-4_0_4_line_67 |  | 62 | 64 | 0.11055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_223-4_0_4_line_68 |  | 63 | 65 | 0.0089868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_223-4_0_4_line_69 |  | 64 | 66 | 0.0048111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_223-4_0_4_line_70 |  | 66 | 67 | 0.20068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_223-4_0_4_line_71 |  | 67 | 68 | 0.15926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_223-4_0_4_line_72 |  | 68 | 69 | 0.0020536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_223-4_0_4_line_73 |  | 68 | 70 | 0.082622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_223-4_0_4_line_74 |  | 69 | 74 | 0.04296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_223-4_0_4_line_75 |  | 70 | 71 | 0.00045363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_223-4_0_4_line_76 |  | 71 | 72 | 0.069765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_223-4_0_4_line_77 |  | 72 | 73 | 0.0067904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_223-4_0_4_line_78 |  | 73 | 75 | 0.012125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_223-4_0_4_line_79 |  | 74 | 76 | 0.13376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_223-4_0_4_line_80 |  | 76 | 77 | 0.14503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_223-4_0_4_line_81 |  | 77 | 78 | 0.18396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_223-4_0_4_line_82 |  | 78 | 106 | 0.024767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_223-4_0_4_line_83 |  | 79 | 80 | 0.033453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_223-4_0_4_line_84 |  | 79 | 81 | 0.019205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_223-4_0_4_line_85 |  | 80 | 104 | 0.028138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_223-4_0_4_line_86 |  | 81 | 110 | 0.021267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_223-4_0_4_line_87 |  | 82 | 83 | 0.89709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_223-4_0_4_line_88 |  | 82 | 84 | 0.032984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_223-4_0_4_line_89 |  | 82 | 85 | 0.012305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_223-4_0_4_line_90 |  | 83 | 98 | 0.013278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_223-4_0_4_line_91 |  | 84 | 87 | 0.19637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_223-4_0_4_line_92 |  | 85 | 104 | 0.0029996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_223-4_0_4_line_93 |  | 85 | 105 | 0.020226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_223-4_0_4_line_94 |  | 86 | 87 | 0.025655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_223-4_0_4_line_95 |  | 86 | 88 | 0.05492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_223-4_0_4_line_96 |  | 87 | 92 | 0.039979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_223-4_0_4_line_97 |  | 88 | 90 | 0.017741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_223-4_0_4_line_98 |  | 89 | 90 | 0.035725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_223-4_0_4_line_99 |  | 89 | 91 | 0.024775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_223-4_0_4_line_100 |  | 91 | 101 | 0.00062201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_223-4_0_4_line_101 |  | 92 | 111 | 0.0080917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_223-4_0_4_line_102 |  | 93 | 94 | 0.021252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_223-4_0_4_line_103 |  | 93 | 95 | 0.066767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_223-4_0_4_line_104 |  | 95 | 96 | 0.013299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_223-4_0_4_line_105 |  | 95 | 97 | 0.011893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_223-4_0_4_line_106 |  | 96 | 108 | 0.014592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_223-4_0_4_line_107 |  | 97 | 109 | 0.0051728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_223-4_0_4_line_108 |  | 99 | 100 | 0.45576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_223-4_0_4_line_109 |  | 99 | 101 | 0.0258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_223-4_0_4_line_110 |  | 100 | 102 | 0.10051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_223-4_0_4_line_111 |  | 105 | 107 | 0.0036036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_223-4_0_4_line_112 |  | 109 | 113 | 0.0014245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_223-4_0_4_line_113 |  | 112 | 113 | 0.01119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_223-4_0_4_trafo_13 | 0.63 MVA 20/0.4 kV | 115 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44
0 | 2690242.8102 | 1265082.4329 | 2690235.2493 | 1265065.9015
1 | 2690233.5399 | 1265062.164 | 2690235.2493 | 1265065.9015
2 | 2690242.8102 | 1265082.4329 | 2690252.7709 | 1265076.7359 | 2690260.7452 | 1265070.4192 | 2690263.8435 | 1265063.8167 | 2690264.8435 | 1265058.5055 | 2690260.1558 | 1264982.7951 | 2690258.5851 | 1264955.9495 | 2690260.6925 | 1264935.8322 | 2690265.4256 | 1264917.3784 | 2690272.2937 | 1264905.0956 | 2690280.3855 | 1264897.513 | 2690288.8771 | 1264892.85 | 2690299.5455 | 1264890.1441 | 2690304.9361 | 1264889.2924
3 | 2690242.8102 | 1265082.4329 | 2690225.6908 | 1265093.3249 | 2690220.4461 | 1265098.449
4 | 2690304.9361 | 1264889.2924 | 2690361.7666 | 1264899.3354 | 2690401.166 | 1264916.4514 | 2690454.604 | 1264933.5713 | 2690466.1014 | 1264940.6752 | 2690470.1528 | 1264947.5983 | 2690478.5583 | 1264968.7217 | 2690488.58 | 1264990.0478 | 2690496.953 | 1265004.8595
5 | 2690220.4461 | 1265098.449 | 2690227.7704 | 1265108.6391
6 | 2690496.953 | 1265004.8595 | 2690503.2089 | 1265015.9259 | 2690510.2387 | 1265025.0742 | 2690513.0793 | 1265027.6203
7 | 2690525.7064 | 1265033.5512 | 2690521.6708 | 1265032.9778 | 2690517.2817 | 1265031.3871 | 2690513.0793 | 1265027.6203
8 | 2690533.2201 | 1265032.7433 | 2690525.7064 | 1265033.5512
9 | 2690533.2201 | 1265032.7433 | 2690542.7405 | 1265025.8169 | 2690543.0629 | 1265025.4879
10 | 2690533.2201 | 1265032.7433 | 2690532.8263 | 1265038.2862 | 2690537.1647 | 1265047.6046 | 2690539.2177 | 1265049.1311
11 | 2690745.9856 | 1265314.0098 | 2690745.2382 | 1265303.8346 | 2690742.4155 | 1265301.2892 | 2690736.5902 | 1265277.5028 | 2690734.4049 | 1265269.7408 | 2690722.7299 | 1265244.3522 | 2690719.9569 | 1265235.6248 | 2690713.0962 | 1265197.8446 | 2690707.7235 | 1265178.4132 | 2690702.9447 | 1265163.9615 | 2690696.0911 | 1265151.702 | 2690678.3776 | 1265130.6022 | 2690670.9419 | 1265123.8828
12 | 2690670.9419 | 1265123.8828 | 2690666.5093 | 1265114.8297 | 2690644.8463 | 1265088.5096 | 2690632.8173 | 1265075.8372 | 2690620.6595 | 1265068.0503
13 | 2690745.9856 | 1265314.0098 | 2690750.1571 | 1265326.3329
14 | 2690614.6109 | 1265065.713 | 2690619.2809 | 1265067.1672 | 2690620.6595 | 1265068.0503
15 | 2690708.8928 | 1265370.5641 | 2690728.7944 | 1265395.7565 | 2690735.7567 | 1265400.912
16 | 2690708.8928 | 1265370.5641 | 2690702.0976 | 1265375.6195 | 2690697.7746 | 1265380.9177
17 | 2690735.7567 | 1265400.912 | 2690746.9295 | 1265406.9995 | 2690759.1163 | 1265410.8118
18 | 2690735.7567 | 1265400.912 | 2690741.1532 | 1265393.7668 | 2690742.8464 | 1265386.9873 | 2690741.3238 | 1265377.7565 | 2690736.6727 | 1265370.2012 | 2690736.6727 | 1265370.2012
19 | 2690552.0824 | 1265016.2856 | 2690543.0629 | 1265025.4879
20 | 2690552.0824 | 1265016.2856 | 2690546.2028 | 1265005.4573
21 | 2690552.0824 | 1265016.2856 | 2690565.8595 | 1264999.4497 | 2690573.9725 | 1264990.5 | 2690583.8155 | 1264982.1886 | 2690639.771 | 1264941.6689 | 2690651.6051 | 1264935.1562 | 2690664.2527 | 1264930.1127 | 2690674.5815 | 1264927.4578 | 2690684.1767 | 1264924.0244 | 2690690.8236 | 1264923.2702 | 2690695.1089 | 1264922.7911 | 2690702.4315 | 1264919.2339 | 2690710.3774 | 1264912.8506
22 | 2690534.4948 | 1264982.9783 | 2690536.3341 | 1264988.7667 | 2690545.2265 | 1265003.6593 | 2690546.2028 | 1265005.4573
23 | 2690710.3774 | 1264912.8506 | 2690724.9118 | 1264901.1753 | 2690728.8127 | 1264893.3622 | 2690729.5439 | 1264877.1381 | 2690735.2582 | 1264868.9414 | 2690740.1993 | 1264872.3533 | 2690750.1383 | 1264876.4536 | 2690754.1736 | 1264880.9747 | 2690764.5797 | 1264887.0282 | 2690806.5172 | 1264905.5537 | 2690838.9208 | 1264915.1814 | 2690858.3447 | 1264923.9981 | 2690865.7792 | 1264926.392 | 2690871.3059 | 1264926.4881 | 2690884.1299 | 1264927.1302 | 2690906.4793 | 1264923.0038 | 2690922.1676 | 1264919.0863 | 2690928.4964 | 1264914.0462 | 2690932.9619 | 1264907.2427 | 2690938.8425 | 1264891.1979 | 2690939.93 | 1264881.2177 | 2690942.3002 | 1264873.5369 | 2690946.1235 | 1264869.3145
24 | 2690710.3774 | 1264912.8506 | 2690703.3741 | 1264898.5539 | 2690703.6642 | 1264892.8982 | 2690706.8362 | 1264888.4099
25 | 2690946.1235 | 1264869.3145 | 2690951.1938 | 1264875.5753 | 2690958.6329 | 1264883.0513 | 2690961.4242 | 1264888.3595
26 | 2690946.1235 | 1264869.3145 | 2690945.5378 | 1264868.4063
27 | 2690703.1786 | 1264877.4338 | 2690706.8362 | 1264888.4099
28 | 2690964.7062 | 1264918.0953 | 2690964.5756 | 1264904.0708 | 2690963.2429 | 1264891.8182 | 2690961.4242 | 1264888.3595
29 | 2690610.17 | 1265051.3148 | 2690607.3919 | 1265057.1436 | 2690607.0675 | 1265061.1085
30 | 2690610.17 | 1265051.3148 | 2690595.0114 | 1265043.9266
31 | 2690607.0675 | 1265061.1085 | 2690596.799 | 1265070.6477 | 2690592.944 | 1265072.0565 | 2690589.4358 | 1265070.9796
32 | 2690607.0675 | 1265061.1085 | 2690609.0644 | 1265063.9859 | 2690614.6109 | 1265065.713
33 | 2690595.0114 | 1265043.9266 | 2690587.108 | 1265040.0746 | 2690580.8617 | 1265038.7779 | 2690575.1941 | 1265041.4932 | 2690570.5501 | 1265048.183 | 2690563.2474 | 1265052.9195 | 2690553.5361 | 1265056.0844 | 2690547.4112 | 1265055.2232 | 2690539.2177 | 1265049.1311
34 | 2690615.3383 | 1264344.9915 | 2690626.4325 | 1264357.327 | 2690657.6121 | 1264388.5189 | 2690690.1801 | 1264415.6067 | 2690709.8505 | 1264429.0971 | 2690723.375 | 1264437.6559 | 2690755.4629 | 1264461.1449 | 2690767.6201 | 1264473.3858 | 2690771.5255 | 1264478.8691
35 | 2690555.7766 | 1264421.9076 | 2690555.8454 | 1264401.2031 | 2690561.1031 | 1264392.3432 | 2690573.5072 | 1264380.1567 | 2690579.9364 | 1264368.0899 | 2690582.3532 | 1264358.8195 | 2690585.8311 | 1264357.9721 | 2690589.5111 | 1264358.1842 | 2690592.6996 | 1264358.5222 | 2690591.7219 | 1264355.9718 | 2690591.3332 | 1264353.3193 | 2690591.5315 | 1264350.2087 | 2690592.3786 | 1264347.5306 | 2690593.9571 | 1264344.797 | 2690596.562 | 1264342.4239 | 2690600.1938 | 1264341.3565 | 2690603.8886 | 1264341.1018 | 2690615.3383 | 1264344.9915
36 | 2690771.5255 | 1264478.8691 | 2690780.1764 | 1264491.015 | 2690788.588 | 1264502.4089
37 | 2690555.7766 | 1264421.9076 | 2690546.4229 | 1264422.3605
38 | 2690964.7062 | 1264918.0953 | 2690969.7 | 1264911.2221 | 2690974.6582 | 1264906.1721 | 2690992.8508 | 1264889.3051 | 2690996.4778 | 1264884.6238 | 2690998.2136 | 1264878.5233 | 2691004.6197 | 1264878.7443 | 2691014.1545 | 1264876.8006 | 2691021.3103 | 1264873.3302 | 2691033.7135 | 1264863.6466 | 2691038.1593 | 1264861.5578 | 2691042.7272 | 1264861.3169 | 2691048.0747 | 1264864.7353 | 2691053.6776 | 1264873.5731 | 2691057.8514 | 1264881.3103 | 2691059.5454 | 1264882.8154 | 2691059.6155 | 1264888.0429 | 2691060.6049 | 1264893.2401 | 2691071.3898 | 1264924.5315 | 2691075.1356 | 1264929.2486 | 2691105.945 | 1264897.6532 | 2691132.3569 | 1264854.7812 | 2691135.2241 | 1264847.6084 | 2691149.3503 | 1264807.7829 | 2691152.8268 | 1264802.1319 | 2691166.4834 | 1264789.3433 | 2691185.1251 | 1264778.0772
39 | 2691185.1251 | 1264778.0772 | 2691183.8998 | 1264761.3336
40 | 2691185.1251 | 1264778.0772 | 2691193.6653 | 1264783.3126
41 | 2690546.4229 | 1264422.3605 | 2690542.5176 | 1264422.5496 | 2690521.5354 | 1264417.4687 | 2690504.658 | 1264409.4014
42 | 2690757.7792 | 1265348.8499 | 2690750.1571 | 1265326.3329
43 | 2691183.8998 | 1264761.3336 | 2691172.2752 | 1264754.9627
44 | 2691283.6853 | 1264823.946 | 2691279.9598 | 1264820.8416 | 2691267.9368 | 1264813.1942 | 2691257.3409 | 1264808.7271 | 2691243.7647 | 1264805.0813 | 2691229.0634 | 1264801.6295 | 2691216.6888 | 1264797.235 | 2691203.6214 | 1264789.416 | 2691193.6653 | 1264783.3126
45 | 2690759.1163 | 1265410.8118 | 2690759.7757 | 1265402.2039 | 2690755.0635 | 1265389.757
46 | 2690759.1163 | 1265410.8118 | 2690768.0128 | 1265413.5951
47 | 2690736.6727 | 1265370.2012 | 2690736.665 | 1265363.8404 | 2690737.8919 | 1265358.6389
48 | 2690534.4948 | 1264982.9783 | 2690533.5174 | 1264976.9696 | 2690533.4752 | 1264962.068
49 | 2690534.4948 | 1264982.9783 | 2690526.3093 | 1264978.9608 | 2690518.518 | 1264980.2005
50 | 2690804.3506 | 1264514.3705 | 2690800.6342 | 1264512.0572 | 2690788.588 | 1264502.4089 | 2690788.588 | 1264502.4089
51 | 2690769.5502 | 1265366.9588 | 2690764.6047 | 1265361.901 | 2690760.0769 | 1265355.6375 | 2690757.7792 | 1265348.8499
52 | 2690739.1376 | 1265353.3578 | 2690737.8919 | 1265358.6389
53 | 2691104.3893 | 1264717.1947 | 2691159.3055 | 1264747.8546 | 2691172.2752 | 1264754.9627
54 | 2691283.6853 | 1264823.946 | 2691285.5036 | 1264825.1012
55 | 2690932.4764 | 1264411.5308 | 2690930.2231 | 1264397.5895
56 | 2690920.4061 | 1264420.2679 | 2690931.906 | 1264415.9746 | 2690932.6645 | 1264412.6948 | 2690932.4764 | 1264411.5308
57 | 2690964.217 | 1264387.7488 | 2690959.515 | 1264386.8869 | 2690947.9395 | 1264388.2544 | 2690939.1725 | 1264396.0481 | 2690930.2231 | 1264397.5895
58 | 2690920.4061 | 1264420.2679 | 2690924.5554 | 1264425.7139 | 2690933.0588 | 1264434.0625 | 2690942.9533 | 1264438.6517 | 2690946.5351 | 1264438.9936
59 | 2690936.9548 | 1264361.9977 | 2690941.3658 | 1264363.6557 | 2690961.8621 | 1264382.6752 | 2690964.217 | 1264387.7488
60 | 2690954.2026 | 1264439.7256 | 2690946.5351 | 1264438.9936
61 | 2690973.5885 | 1264437.5554 | 2690963.5158 | 1264439.1684 | 2690954.6186 | 1264439.7653 | 2690954.2026 | 1264439.7256
62 | 2690973.5885 | 1264437.5554 | 2691070.5489 | 1264422.5135
63 | 2691070.5489 | 1264422.5135 | 2691111.1434 | 1264416.215
64 | 2691240.8492 | 1264412.4861 | 2691238.8417 | 1264412.2549 | 2691196.0366 | 1264407.3351 | 2691170.4722 | 1264407.8191 | 2691135.0888 | 1264412.4997 | 2691111.1434 | 1264416.215
65 | 2690845.5708 | 1264537.5234 | 2690827.1197 | 1264528.5439 | 2690804.3506 | 1264514.3705
66 | 2690845.5708 | 1264537.5234 | 2690837.3428 | 1264544.5805 | 2690835.8335 | 1264546.7839
67 | 2690845.5708 | 1264537.5234 | 2690862.6894 | 1264544.5032 | 2690885.7979 | 1264558.2027 | 2690936.5131 | 1264599.1849
68 | 2690830.755 | 1264554.1982 | 2690835.8335 | 1264546.7839
69 | 2690940.2551 | 1264602.2087 | 2690936.5131 | 1264599.1849
70 | 2690940.2551 | 1264602.2087 | 2690999.9673 | 1264649.7434 | 2691044.1316 | 1264683.1725 | 2691069.3347 | 1264700.1854 | 2691104.3893 | 1264717.1947
71 | 2691174.1058 | 1264576.5112 | 2691170.5335 | 1264584.4625 | 2691128.3465 | 1264692.3994 | 2691120.2936 | 1264703.7177 | 2691104.3893 | 1264717.1947
72 | 2691174.1058 | 1264576.5112 | 2691174.853 | 1264574.5983
73 | 2691174.1058 | 1264576.5112 | 2691145.8934 | 1264565.6008 | 2691129.332 | 1264554.759 | 2691114.9079 | 1264549.8884 | 2691097.8694 | 1264546.5908
74 | 2691190.3157 | 1264534.5217 | 2691189.0446 | 1264538.2662 | 2691174.853 | 1264574.5983
75 | 2691097.8694 | 1264546.5908 | 2691097.424 | 1264546.5046
76 | 2691046.4791 | 1264509.4859 | 2691046.5966 | 1264519.7786 | 2691049.527 | 1264525.6173 | 2691057.8164 | 1264532.684 | 2691089.9984 | 1264545.0674 | 2691097.424 | 1264546.5046
77 | 2691046.4791 | 1264509.4859 | 2691046.4017 | 1264502.6959
78 | 2691046.2633 | 1264490.5721 | 2691046.4017 | 1264502.6959
79 | 2691240.8492 | 1264412.4861 | 2691239.5189 | 1264420.105 | 2691220.4565 | 1264449.7571 | 2691204.3881 | 1264479.1774 | 2691201.8886 | 1264495.6966 | 2691196.825 | 1264515.3455 | 2691190.3157 | 1264534.5217
80 | 2691240.8492 | 1264412.4861 | 2691258.1681 | 1264416.2452 | 2691262.4446 | 1264391.002 | 2691269.2102 | 1264367.4874 | 2691281.9996 | 1264320.2245 | 2691289.781 | 1264303.1308 | 2691282.5162 | 1264297.0249
81 | 2691282.5162 | 1264297.0249 | 2691272.7337 | 1264297.3742 | 2691271.0327 | 1264296.803 | 2691174.2805 | 1264264.0063 | 2691163.7728 | 1264258.1507 | 2691153.0341 | 1264251.6355 | 2691131.2085 | 1264245.5498 | 2691109.7029 | 1264237.4676
82 | 2691088.6337 | 1264224.6325 | 2691105.5061 | 1264235.8904 | 2691109.7029 | 1264237.4676
83 | 2691198.04 | 1265646.1564 | 2691194.8998 | 1265652.9802 | 2691186.4066 | 1265677.4918
84 | 2691198.04 | 1265646.1564 | 2691215.7984 | 1265653.4699
85 | 2691177.1942 | 1265704.0791 | 2691186.4066 | 1265677.4918
86 | 2691232.0484 | 1265648.615 | 2691227.9225 | 1265655.8586 | 2691224.0736 | 1265656.8778 | 2691215.7984 | 1265653.4699
87 | 2690768.0128 | 1265413.5951 | 2690788.5486 | 1265420.0378 | 2690794.4689 | 1265427.3235 | 2690801.3842 | 1265434.5467 | 2690817.4671 | 1265448.4716 | 2690830.3972 | 1265459.7683 | 2690834.9629 | 1265469.4351 | 2690848.929 | 1265480.9368 | 2690842.0076 | 1265494.1967 | 2690815.5115 | 1265519.3434 | 2690785.9471 | 1265541.296 | 2690755.4093 | 1265560.4426 | 2690734.8482 | 1265575.7839 | 2690726.3091 | 1265590.9318 | 2690727.9697 | 1265604.9019 | 2690732.8282 | 1265617.5756 | 2690698.1072 | 1265637.9816 | 2690688.5692 | 1265648.0657 | 2690684.8948 | 1265658.818 | 2690682.0054 | 1265667.0025 | 2690685.3487 | 1265672.9141 | 2690697.4387 | 1265679.0712 | 2690709.9065 | 1265681.7091 | 2690716.711 | 1265681.9137 | 2690722.8943 | 1265688.247 | 2690737.4724 | 1265696.6553 | 2690747.2814 | 1265697.362 | 2690777.9393 | 1265686.0346 | 2690804.8341 | 1265684.8577 | 2690831.0177 | 1265675.5747 | 2690860.7863 | 1265676.0547 | 2690876.7756 | 1265681.8162 | 2690889.9814 | 1265689.8368 | 2690901.4935 | 1265696.8306 | 2690953.0893 | 1265714.1937 | 2690978.0166 | 1265719.0145 | 2691014.999 | 1265718.5389 | 2691034.4488 | 1265715.2245 | 2691081.5671 | 1265715.2614 | 2691121.3225 | 1265713.6949 | 2691128.1123 | 1265712.8989 | 2691141.9709 | 1265711.289 | 2691163.5208 | 1265711.944 | 2691173.8081 | 1265713.8598 | 2691172.4769 | 1265718.632
88 | 2691172.4769 | 1265718.632 | 2691190.4301 | 1265726.9045 | 2691200.82 | 1265735.0735
89 | 2691172.4769 | 1265718.632 | 2691173.8081 | 1265713.8598 | 2691176.2122 | 1265706.9134
90 | 2690768.0128 | 1265413.5951 | 2690768.4351 | 1265400.3242
91 | 2691319.469 | 1265888.4606 | 2691262.8097 | 1265838.8009 | 2691249.793 | 1265821.03 | 2691224.9508 | 1265776.1214 | 2691209.5148 | 1265748.2161 | 2691201.3077 | 1265735.457 | 2691200.82 | 1265735.0735
92 | 2691176.2122 | 1265706.9134 | 2691177.1942 | 1265704.0791
93 | 2691176.2122 | 1265706.9134 | 2691166.7637 | 1265698.4609 | 2691160.0319 | 1265695.0451
94 | 2691319.469 | 1265888.4606 | 2691328.2732 | 1265896.1806 | 2691341.8188 | 1265892.865
95 | 2691341.8188 | 1265892.865 | 2691346.1808 | 1265900.0493 | 2691354.4332 | 1265905.459 | 2691390.1871 | 1265913.5049
96 | 2691319.469 | 1265888.4606 | 2691302.7061 | 1265889.458 | 2691296.2352 | 1265888.6352 | 2691290.5097 | 1265885.8668 | 2691282.8839 | 1265878.9383
97 | 2691407.4955 | 1265917.4 | 2691390.1871 | 1265913.5049
98 | 2691407.4955 | 1265917.4 | 2691402.1945 | 1265938.3017 | 2691396.3247 | 1265951.1992
99 | 2691396.3247 | 1265951.1992 | 2691420.3142 | 1265957.3897
100 | 2691420.3142 | 1265957.3897 | 2691420.9165 | 1265957.5451
101 | 2691282.8839 | 1265878.9383 | 2691276.8949 | 1265873.497
102 | 2690820.2577 | 1265387.454 | 2690826.4386 | 1265383.1788 | 2690837.5391 | 1265375.0878
103 | 2690769.5502 | 1265366.9588 | 2690789.6872 | 1265387.1065 | 2690793.8821 | 1265395.9225 | 2690810.8191 | 1265393.9699 | 2690820.2577 | 1265387.454
104 | 2690769.5502 | 1265366.9588 | 2690782.3097 | 1265363.21
105 | 2690769.5502 | 1265366.9588 | 2690768.142 | 1265371.3629 | 2690762.1733 | 1265375.5122
106 | 2690796.1005 | 1265358.5996 | 2690794.0084 | 1265359.7729 | 2690782.3097 | 1265363.21
107 | 2690757.926 | 1265378.4648 | 2690762.1733 | 1265375.5122
108 | 2691369.1812 | 1266133.5499 | 2691394.2218 | 1266147.9487 | 2691458.8475 | 1266184.2332 | 2691470.8968 | 1266187.5556 | 2691511.3957 | 1266189.3283 | 2691513.5151 | 1266174.5268 | 2691512.9856 | 1266163.4986 | 2691508.255 | 1266149.514 | 2691497.4218 | 1266133.3109 | 2691475.8077 | 1266111.125 | 2691419.2916 | 1266055.8392 | 2691414.4713 | 1266047.6358 | 2691412.9478 | 1266039.5168 | 2691414.0297 | 1266030.9154 | 2691416.9418 | 1266021.8086 | 2691421.4666 | 1266013.1048 | 2691440.5104 | 1265987.8121 | 2691444.9881 | 1265982.6439 | 2691459.8848 | 1265959.1775 | 2691443.1309 | 1265954.7369
109 | 2691443.1309 | 1265954.7369 | 2691436.8489 | 1265961.6565 | 2691420.9165 | 1265957.5451
110 | 2691369.1812 | 1266133.5499 | 2691369.2396 | 1266141.9465 | 2691373.3478 | 1266163.572 | 2691379.9387 | 1266181.444 | 2691387.2692 | 1266193.367 | 2691405.1386 | 1266211.3245 | 2691413.2068 | 1266219.8289
111 | 2691156.8184 | 1265693.4145 | 2691160.0319 | 1265695.0451
112 | 2690756.7563 | 1265379.2779 | 2690757.926 | 1265378.4648
113 | 2690755.0635 | 1265389.757 | 2690754.7747 | 1265388.9942 | 2690754.2811 | 1265384.3607 | 2690756.3886 | 1265379.5336 | 2690756.7563 | 1265379.2779

## bus_geodata
| x | y | coords
0 | 2690235.2493 | 1265065.9015
1 | 2690242.8102 | 1265082.4329
2 | 2690233.5399 | 1265062.164
3 | 2690304.9361 | 1264889.2924
4 | 2690220.4461 | 1265098.449
5 | 2690496.953 | 1265004.8595
6 | 2690227.7704 | 1265108.6391
7 | 2690525.7064 | 1265033.5512
8 | 2690513.0793 | 1265027.6203
9 | 2690533.2201 | 1265032.7433
10 | 2690670.9419 | 1265123.8828
11 | 2690745.9856 | 1265314.0098
12 | 2690620.6595 | 1265068.0503
13 | 2690708.8928 | 1265370.5641
14 | 2690735.7567 | 1265400.912
15 | 2690697.7746 | 1265380.9177
16 | 2690552.0824 | 1265016.2856
17 | 2690543.0629 | 1265025.4879
18 | 2690546.2028 | 1265005.4573
19 | 2690710.3774 | 1264912.8506
20 | 2690946.1235 | 1264869.3145
21 | 2690706.8362 | 1264888.4099
22 | 2690961.4242 | 1264888.3595
23 | 2690945.5378 | 1264868.4063
24 | 2690610.17 | 1265051.3148
25 | 2690607.0675 | 1265061.1085
26 | 2690595.0114 | 1265043.9266
27 | 2690615.3383 | 1264344.9915
28 | 2690771.5255 | 1264478.8691
29 | 2690555.7766 | 1264421.9076
30 | 2690964.7062 | 1264918.0953
31 | 2691185.1251 | 1264778.0772
32 | 2690546.4229 | 1264422.3605
33 | 2690750.1571 | 1265326.3329
34 | 2691183.8998 | 1264761.3336
35 | 2691193.6654 | 1264783.3126
36 | 2690539.2177 | 1265049.1311
37 | 2690614.6109 | 1265065.713
38 | 2690759.1163 | 1265410.8118
39 | 2690736.6727 | 1265370.2012
40 | 2690504.658 | 1264409.4014
41 | 2690703.1786 | 1264877.4338
42 | 2690534.4948 | 1264982.9783
43 | 2690788.588 | 1264502.4089
44 | 2690533.4752 | 1264962.068
45 | 2690589.4358 | 1265070.9796
46 | 2690757.7792 | 1265348.8499
47 | 2690739.1376 | 1265353.3578
48 | 2690737.8919 | 1265358.6389
49 | 2691172.2752 | 1264754.9627
50 | 2691283.6853 | 1264823.946
51 | 2690932.4764 | 1264411.5308
52 | 2690930.2231 | 1264397.5895
53 | 2690920.4061 | 1264420.2679
54 | 2690964.217 | 1264387.7488
55 | 2690946.5351 | 1264438.9936
56 | 2690936.9548 | 1264361.9977
57 | 2690954.2026 | 1264439.7256
58 | 2690973.5885 | 1264437.5554
59 | 2691070.5489 | 1264422.5135
60 | 2691111.1434 | 1264416.215
61 | 2690804.3506 | 1264514.3705
62 | 2690845.5708 | 1264537.5234
63 | 2690835.8335 | 1264546.7839
64 | 2690936.5131 | 1264599.1849
65 | 2690830.755 | 1264554.1982
66 | 2690940.2551 | 1264602.2087
67 | 2691104.3893 | 1264717.1947
68 | 2691174.1058 | 1264576.5112
69 | 2691174.853 | 1264574.5983
70 | 2691097.8694 | 1264546.5908
71 | 2691097.424 | 1264546.5046
72 | 2691046.4791 | 1264509.4859
73 | 2691046.4017 | 1264502.6959
74 | 2691190.3157 | 1264534.5217
75 | 2691046.2633 | 1264490.5721
76 | 2691240.8492 | 1264412.4861
77 | 2691282.5162 | 1264297.0249
78 | 2691109.7029 | 1264237.4676
79 | 2691198.04 | 1265646.1564
80 | 2691186.4066 | 1265677.4918
81 | 2691215.7984 | 1265653.4699
82 | 2691172.4769 | 1265718.632
83 | 2690768.0128 | 1265413.5951
84 | 2691200.82 | 1265735.0735
85 | 2691176.2122 | 1265706.9134
86 | 2691341.8188 | 1265892.865
87 | 2691319.469 | 1265888.4606
88 | 2691390.1871 | 1265913.5049
89 | 2691396.3247 | 1265951.1992
90 | 2691407.4955 | 1265917.4
91 | 2691420.3142 | 1265957.3897
92 | 2691282.8839 | 1265878.9383
93 | 2690820.2577 | 1265387.454
94 | 2690837.5391 | 1265375.0878
95 | 2690769.5502 | 1265366.9588
96 | 2690782.3097 | 1265363.21
97 | 2690762.1733 | 1265375.5122
98 | 2690768.4351 | 1265400.3242
99 | 2691443.1309 | 1265954.7369
100 | 2691369.1812 | 1266133.5499
101 | 2691420.9165 | 1265957.5451
102 | 2691413.2068 | 1266219.8289
103 | 2691285.5036 | 1264825.1012
104 | 2691177.1942 | 1265704.0791
105 | 2691160.0319 | 1265695.0451
106 | 2691088.6337 | 1264224.6325
107 | 2691156.8184 | 1265693.4145
108 | 2690796.1005 | 1265358.5996
109 | 2690757.926 | 1265378.4648
110 | 2691232.0484 | 1265648.615
111 | 2691276.8949 | 1265873.497
112 | 2690755.0635 | 1265389.757
113 | 2690756.7563 | 1265379.2779
114 | 2690518.518 | 1264980.2005
115 | 2690703.1786 | 1264877.4338

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98823 | -0.22564 | 0.0008882 | 0.00022261
1 | 0.98828 | -0.22472 | 0 | 0
2 | 0.98822 | -0.22579 | 0.0019697 | 0.00049365
3 | 0.98911 | -0.20846 | 0 | 0
4 | 0.98825 | -0.22528 | 0 | 0
5 | 0.99 | -0.19121 | 0.00071909 | 0.00018022
6 | 0.98824 | -0.22554 | 0.0011405 | 0.00028584
7 | 0.99022 | -0.18686 | 0 | 0
8 | 0.99012 | -0.18884 | 0.0030135 | 0.00075525
9 | 0.99027 | -0.18582 | 0 | 0
10 | 0.9849 | -0.2897 | 0 | 0
11 | 0.98012 | -0.38294 | 0 | 0
12 | 0.98664 | -0.25599 | 0.0012012 | 0.00030105
13 | 0.9779 | -0.42658 | 0 | 0
14 | 0.97795 | -0.42562 | 0 | 0
15 | 0.97788 | -0.42695 | 0.0013014 | 0.00032615
16 | 0.99125 | -0.16697 | 0 | 0
17 | 0.99074 | -0.1769 | 0.0023677 | 0.0005934
18 | 0.99119 | -0.16822 | 0.0014819 | 0.00037141
19 | 1 | 0 | -0.10231 | -0.025773
20 | 0.99473 | -0.099323 | 0 | 0
21 | 0.99966 | -0.0064611 | 0.0041262 | 0.0010341
22 | 0.99392 | -0.11473 | 0.0014556 | 0.0003648
23 | 0.99473 | -0.09934 | 0.00085734 | 0.00021487
24 | 0.98732 | -0.24283 | 0 | 0
25 | 0.98703 | -0.2485 | 0 | 0
26 | 0.98779 | -0.23368 | 0.0015414 | 0.00038632
27 | 0.97292 | -0.52198 | 0 | 0
28 | 0.97376 | -0.50541 | 0.00041735 | 0.0001046
29 | 0.97243 | -0.53157 | 0 | 0
30 | 0.99296 | -0.13292 | 0 | 0
31 | 0.98122 | -0.35895 | 0 | 0
32 | 0.9724 | -0.53233 | 0.0012267 | 0.00030744
33 | 0.97983 | -0.38878 | 0.00050018 | 0.00012536
34 | 0.9807 | -0.36899 | 0 | 0
35 | 0.98121 | -0.35914 | 0.00038075 | 9.5424e-05
36 | 0.98971 | -0.19672 | 0.0013773 | 0.00034519
37 | 0.9868 | -0.25296 | 0.0008222 | 0.00020606
38 | 0.97811 | -0.42258 | 0 | 0
39 | 0.97778 | -0.42889 | 0.0035874 | 0.00089908
40 | 0.97227 | -0.53487 | 0.0031214 | 0.0007823
41 | 0.99956 | -0.00839 | 0.0095579 | 0.0023954
42 | 0.99109 | -0.17014 | 0 | 0
43 | 0.97389 | -0.50286 | 0.00094161 | 0.00023599
44 | 0.99103 | -0.17138 | 0.0033111 | 0.00082984
45 | 0.98695 | -0.24993 | 0.0036565 | 0.00091641
46 | 0.97929 | -0.39922 | 0.0019107 | 0.00047886
47 | 0.97776 | -0.4293 | 0.00060255 | 0.00015101
48 | 0.97777 | -0.42924 | 0.001062 | 0.00026617
49 | 0.9803 | -0.37692 | 0.00058875 | 0.00014755
50 | 0.98115 | -0.36032 | 0 | 0
51 | 0.97223 | -0.53563 | 0.0022881 | 0.00057346
52 | 0.97223 | -0.53568 | 0.00014896 | 3.7332e-05
53 | 0.97227 | -0.53485 | 0 | 0
54 | 0.97223 | -0.53573 | 0 | 0
55 | 0.97235 | -0.53331 | 0.00073102 | 0.00018321
56 | 0.97223 | -0.53577 | 6.2889e-05 | 1.5761e-05
57 | 0.97237 | -0.53285 | 0.00049275 | 0.0001235
58 | 0.97244 | -0.53151 | 0 | 0
59 | 0.97278 | -0.52479 | 0 | 0
60 | 0.97292 | -0.52196 | 0.0029474 | 0.00073869
61 | 0.97399 | -0.50078 | 0.0042121 | 0.0010557
62 | 0.97443 | -0.49214 | 0 | 0
63 | 0.97441 | -0.49247 | 0.00040011 | 0.00010028
64 | 0.97559 | -0.46928 | 0.0011247 | 0.00028187
65 | 0.9744 | -0.49263 | 0.00093928 | 0.00023541
66 | 0.97564 | -0.46819 | 0 | 0
67 | 0.97796 | -0.42271 | 0 | 0
68 | 0.975 | -0.48095 | 0 | 0
69 | 0.97498 | -0.48133 | 0.0015144 | 0.00037955
70 | 0.97422 | -0.49634 | 0.0044803 | 0.0011229
71 | 0.97421 | -0.49639 | 0.0003364 | 8.4309e-05
72 | 0.97387 | -0.50322 | 0.0019009 | 0.00047641
73 | 0.97385 | -0.50365 | 0.0010156 | 0.00025453
74 | 0.97465 | -0.4879 | 0.0010039 | 0.0002516
75 | 0.97382 | -0.50419 | 0.0024126 | 0.00060465
76 | 0.97374 | -0.5059 | 0 | 0
77 | 0.97365 | -0.50762 | 0 | 0
78 | 0.97354 | -0.50977 | 7.3432e-05 | 1.8404e-05
79 | 0.97213 | -0.54095 | 0 | 0
80 | 0.97216 | -0.54033 | 0.00029172 | 7.3112e-05
81 | 0.97211 | -0.54131 | 0.00068844 | 0.00017254
82 | 0.97224 | -0.53875 | 0 | 0
83 | 0.97804 | -0.42397 | 0 | 0
84 | 0.97214 | -0.54087 | 0.00016271 | 4.0779e-05
85 | 0.9722 | -0.53954 | 0 | 0
86 | 0.97148 | -0.55397 | 0 | 0
87 | 0.97153 | -0.55293 | 0 | 0
88 | 0.97137 | -0.55619 | 0.00039289 | 9.8468e-05
89 | 0.97128 | -0.55797 | 0 | 0
90 | 0.97134 | -0.55678 | 0 | 0
91 | 0.97124 | -0.55879 | 0.0010016 | 0.00025102
92 | 0.97149 | -0.55376 | 0.00027266 | 6.8335e-05
93 | 0.97877 | -0.40941 | 0 | 0
94 | 0.97875 | -0.40982 | 0.0010576 | 0.00026505
95 | 0.97884 | -0.40813 | 0 | 0
96 | 0.97878 | -0.40927 | 0.00072856 | 0.00018259
97 | 0.97866 | -0.4117 | 0.00058163 | 0.00014577
98 | 0.97802 | -0.42427 | 0.0012265 | 0.00030739
99 | 0.97124 | -0.55888 | 0 | 0
100 | 0.97118 | -0.5602 | 0 | 0
101 | 0.97124 | -0.5588 | 0.0006292 | 0.00015769
102 | 0.97116 | -0.56047 | 0.0001465 | 3.6717e-05
103 | 0.98115 | -0.36034 | 0.00064972 | 0.00016284
104 | 0.9722 | -0.53965 | 0.00072266 | 0.00018112
105 | 0.97218 | -0.54008 | 0.0008701 | 0.00021807
106 | 0.97353 | -0.51002 | 0.0005594 | 0.0001402
107 | 0.97217 | -0.54012 | 0.00057609 | 0.00014438
108 | 0.97873 | -0.41033 | 0.0039992 | 0.0010023
109 | 0.97858 | -0.41319 | 0.00030779 | 7.7139e-05
110 | 0.97211 | -0.54143 | 0.00031938 | 8.0045e-05
111 | 0.97149 | -0.55389 | 0.00085513 | 0.00021432
112 | 0.97841 | -0.41667 | 0.0003107 | 7.7869e-05
113 | 0.97856 | -0.4136 | 0.00051598 | 0.00012932
114 | 0.99108 | -0.17043 | 0.00094208 | 0.00023611
115 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0028579 | -0.00071621 | 0.002858 | 0.00071606 | 1.2623e-07 | -1.5213e-07 | 0.0043032 | 0.0043031 | 0.0043032 | 0.98823 | -0.22564 | 0.98828 | -0.22472 | 1.1822
1 | 0.0019697 | 0.0004936 | -0.0019697 | -0.00049365 | 1.3556e-08 | -4.398e-08 | 0.0029658 | 0.0029658 | 0.0029658 | 0.98823 | -0.22564 | 0.98822 | -0.22579 | 0.81479
2 | -0.0039986 | -0.0010014 | 0.0040017 | 0.0010005 | 3.094e-06 | -9.3973e-07 | 0.0060203 | 0.0060192 | 0.0060203 | 0.98828 | -0.22472 | 0.98911 | -0.20846 | 1.6539
3 | 0.0011406 | 0.00028536 | -0.0011405 | -0.00028569 | 3.0545e-08 | -3.3439e-07 | 0.0017171 | 0.0017173 | 0.0017173 | 0.98828 | -0.22472 | 0.98825 | -0.22528 | 0.47178
4 | -0.0040017 | -0.0010005 | 0.004005 | 0.00099947 | 3.2824e-06 | -1.0034e-06 | 0.0060192 | 0.0060181 | 0.0060192 | 0.98911 | -0.20846 | 0.99 | -0.19121 | 1.6536
5 | 0.0011405 | 0.00028569 | -0.0011405 | -0.00028584 | 1.3878e-08 | -1.5191e-07 | 0.0017173 | 0.0017173 | 0.0017173 | 0.98825 | -0.22528 | 0.98824 | -0.22554 | 0.47179
6 | -0.0047241 | -0.0011797 | 0.0047246 | 0.0011797 | 5.3036e-07 | -2.1471e-08 | 0.007099 | 0.0070988 | 0.007099 | 0.99 | -0.19121 | 0.99012 | -0.18884 | 1.9503
7 | 0.0077388 | 0.0019352 | -0.0077381 | -0.0019349 | 7.2949e-07 | 2.8181e-07 | 0.011628 | 0.011628 | 0.011628 | 0.99022 | -0.18686 | 0.99012 | -0.18884 | 3.1944
8 | -0.0077388 | -0.0019352 | 0.0077392 | 0.0019354 | 3.8203e-07 | 1.4756e-07 | 0.011628 | 0.011628 | 0.011628 | 0.99022 | -0.18686 | 0.99027 | -0.18582 | 3.1944
9 | -0.041298 | -0.010442 | 0.041316 | 0.010453 | 1.7686e-05 | 1.1162e-05 | 0.062089 | 0.062089 | 0.062089 | 0.99027 | -0.18582 | 0.99074 | -0.1769 | 17.0574
10 | 0.033559 | 0.008507 | -0.033542 | -0.0084959 | 1.7564e-05 | 1.1004e-05 | 0.050461 | 0.050461 | 0.050461 | 0.99027 | -0.18582 | 0.98971 | -0.19672 | 13.863
11 | 0.024814 | 0.0062612 | -0.024704 | -0.0061933 | 0.00011028 | 6.793e-05 | 0.037505 | 0.037506 | 0.037506 | 0.9849 | -0.2897 | 0.98012 | -0.38294 | 10.3039
12 | -0.024814 | -0.0062612 | 0.024854 | 0.0062859 | 4.013e-05 | 2.4713e-05 | 0.037505 | 0.037505 | 0.037505 | 0.9849 | -0.2897 | 0.98664 | -0.25599 | 10.3036
13 | 0.024704 | 0.0061933 | -0.024697 | -0.0061891 | 6.863e-06 | 4.2284e-06 | 0.037506 | 0.037506 | 0.037506 | 0.98012 | -0.38294 | 0.97983 | -0.38878 | 10.3039
14 | -0.026056 | -0.006587 | 0.026059 | 0.0065893 | 3.7843e-06 | 2.3385e-06 | 0.039316 | 0.039316 | 0.039316 | 0.98664 | -0.25599 | 0.9868 | -0.25296 | 10.8012
15 | -0.0013014 | -0.00032597 | 0.0013014 | 0.0003255 | 5.9861e-08 | -4.7251e-07 | 0.0019802 | 0.00198 | 0.0019802 | 0.9779 | -0.42658 | 0.97795 | -0.42562 | 0.544
16 | 0.0013014 | 0.00032597 | -0.0013014 | -0.00032615 | 2.2509e-08 | -1.7764e-07 | 0.0019802 | 0.0019802 | 0.0019802 | 0.9779 | -0.42658 | 0.97788 | -0.42695 | 0.54402
17 | -0.0065542 | -0.0016417 | 0.0065552 | 0.001642 | 9.4827e-07 | 2.878e-07 | 0.0099724 | 0.0099722 | 0.0099724 | 0.97795 | -0.42562 | 0.97811 | -0.42258 | 2.7397
18 | 0.0052528 | 0.0013162 | -0.005252 | -0.0013161 | 8.1852e-07 | 9.5195e-08 | 0.0079924 | 0.0079925 | 0.0079925 | 0.97795 | -0.42562 | 0.97778 | -0.42889 | 2.1957
19 | 0.043705 | 0.01106 | -0.043684 | -0.011047 | 2.0822e-05 | 1.316e-05 | 0.065645 | 0.065645 | 0.065645 | 0.99125 | -0.16697 | 0.99074 | -0.1769 | 18.0343
20 | 0.005736 | 0.001437 | -0.0057357 | -0.0014369 | 3.4257e-07 | 6.0421e-08 | 0.0086104 | 0.0086105 | 0.0086105 | 0.99125 | -0.16697 | 0.99119 | -0.16822 | 2.3655
21 | -0.049441 | -0.012497 | 0.04984 | 0.01275 | 0.0003993 | 0.00025304 | 0.074255 | 0.074254 | 0.074255 | 0.99125 | -0.16697 | 1 | 0 | 20.3998
22 | 0.0042538 | 0.0010655 | -0.0042534 | -0.0010656 | 3.8941e-07 | -7.8969e-08 | 0.0063857 | 0.0063858 | 0.0063858 | 0.99119 | -0.16822 | 0.99109 | -0.17014 | 1.7544
23 | 0.037127 | 0.0095906 | -0.036948 | -0.0094842 | 0.00017899 | 0.00010642 | 0.055347 | 0.05535 | 0.05535 | 1 | 0 | 0.99473 | -0.099323 | 7.603
24 | 0.013689 | 0.0034323 | -0.013685 | -0.00343 | 4.2137e-06 | 2.3416e-06 | 0.02037 | 0.020371 | 0.020371 | 1 | 0 | 0.99966 | -0.0064611 | 5.5963
25 | 0.036091 | 0.0092693 | -0.036064 | -0.0092524 | 2.6968e-05 | 1.694e-05 | 0.054068 | 0.054068 | 0.054068 | 0.99473 | -0.099323 | 0.99392 | -0.11473 | 14.8538
26 | 0.00085734 | 0.00021486 | -0.00085734 | -0.00021487 | 6.6642e-10 | -1.3602e-08 | 0.0012825 | 0.0012825 | 0.0012825 | 0.99473 | -0.099323 | 0.99473 | -0.09934 | 0.35233
27 | 0.0095588 | 0.0023959 | -0.0095579 | -0.0023954 | 8.7835e-07 | 4.1048e-07 | 0.014229 | 0.014229 | 0.014229 | 0.99966 | -0.0064611 | 0.99956 | -0.00839 | 3.909
28 | 0.034608 | 0.0088876 | -0.034577 | -0.0088684 | 3.055e-05 | 1.916e-05 | 0.051889 | 0.051889 | 0.051889 | 0.99392 | -0.11473 | 0.99296 | -0.13292 | 14.2552
29 | 0.030552 | 0.0077204 | -0.030544 | -0.0077152 | 8.3026e-06 | 5.1803e-06 | 0.046069 | 0.046069 | 0.046069 | 0.98732 | -0.24283 | 0.98703 | -0.2485 | 12.6563
30 | -0.030552 | -0.0077204 | 0.030566 | 0.0077288 | 1.3421e-05 | 8.3737e-06 | 0.046069 | 0.046069 | 0.046069 | 0.98732 | -0.24283 | 0.98779 | -0.23368 | 12.6563
31 | 0.0036568 | 0.00091629 | -0.0036565 | -0.00091641 | 2.4786e-07 | -1.1931e-07 | 0.0055128 | 0.0055129 | 0.0055129 | 0.98703 | -0.2485 | 0.98695 | -0.24993 | 1.5145
32 | 0.026887 | 0.0067989 | -0.026882 | -0.0067954 | 5.7434e-06 | 3.5568e-06 | 0.040556 | 0.040556 | 0.040556 | 0.98703 | -0.2485 | 0.9868 | -0.25296 | 11.1418
33 | -0.032107 | -0.0081151 | 0.032164 | 0.0081508 | 5.7002e-05 | 3.5649e-05 | 0.048391 | 0.04839 | 0.048391 | 0.98779 | -0.23368 | 0.98971 | -0.19672 | 13.2942
34 | -0.0043506 | -0.0010892 | 0.0043541 | 0.0010888 | 3.4304e-06 | -3.7318e-07 | 0.0066536 | 0.0066526 | 0.0066536 | 0.97292 | -0.52198 | 0.97376 | -0.50541 | 1.8279
35 | 0.0043506 | 0.0010892 | -0.0043486 | -0.0010894 | 1.9877e-06 | -2.1388e-07 | 0.0066536 | 0.0066541 | 0.0066541 | 0.97292 | -0.52198 | 0.97243 | -0.53157 | 1.8281
36 | -0.0047714 | -0.0011934 | 0.004772 | 0.0011934 | 5.7948e-07 | 9.1407e-09 | 0.0072904 | 0.0072903 | 0.0072904 | 0.97376 | -0.50541 | 0.97389 | -0.50286 | 2.0029
37 | 0.0043486 | 0.0010894 | -0.0043485 | -0.0010894 | 1.5549e-07 | -1.6659e-08 | 0.0066541 | 0.0066542 | 0.0066542 | 0.97243 | -0.53157 | 0.9724 | -0.53233 | 1.8281
38 | 0.034577 | 0.0088684 | -0.034203 | -0.0086334 | 0.00037466 | 0.00023504 | 0.051889 | 0.05189 | 0.05189 | 0.99296 | -0.13292 | 0.98122 | -0.35895 | 14.2556
39 | 0.033172 | 0.0083765 | -0.033156 | -0.0083665 | 1.5947e-05 | 9.9941e-06 | 0.050328 | 0.050328 | 0.050328 | 0.98122 | -0.35895 | 0.9807 | -0.36899 | 13.8265
40 | 0.0010305 | 0.00025687 | -0.0010305 | -0.000257 | 9.1686e-09 | -1.2066e-07 | 0.0015623 | 0.0015623 | 0.0015623 | 0.98122 | -0.35895 | 0.98121 | -0.35914 | 0.42921
41 | 0.0031218 | 0.000782 | -0.0031214 | -0.0007823 | 3.783e-07 | -3.0618e-07 | 0.004777 | 0.0047772 | 0.0047772 | 0.9724 | -0.53233 | 0.97227 | -0.53487 | 1.3124
42 | 0.024197 | 0.0060637 | -0.024185 | -0.0060563 | 1.2037e-05 | 7.4047e-06 | 0.036747 | 0.036747 | 0.036747 | 0.97983 | -0.38878 | 0.97929 | -0.39922 | 10.0952
43 | 0.033156 | 0.0083665 | -0.033144 | -0.0083586 | 1.2591e-05 | 7.8911e-06 | 0.050328 | 0.050328 | 0.050328 | 0.9807 | -0.36899 | 0.9803 | -0.37692 | 13.8265
44 | 0.00064976 | 0.00016157 | -0.00064972 | -0.00016281 | 3.6318e-08 | -1.2372e-06 | 0.00098491 | 0.00098536 | 0.00098536 | 0.98121 | -0.35914 | 0.98115 | -0.36032 | 0.2707
45 | -0.014752 | -0.0036866 | 0.014756 | 0.003689 | 4.1431e-06 | 2.3761e-06 | 0.022439 | 0.022439 | 0.022439 | 0.97811 | -0.42258 | 0.97841 | -0.41667 | 6.1646
46 | 0.008197 | 0.0020447 | -0.0081965 | -0.0020445 | 5.4181e-07 | 2.3009e-07 | 0.012467 | 0.012467 | 0.012467 | 0.97811 | -0.42258 | 0.97804 | -0.42397 | 3.425
47 | 0.0016646 | 0.00041699 | -0.0016646 | -0.00041712 | 2.8167e-08 | -1.2879e-07 | 0.0025332 | 0.0025332 | 0.0025332 | 0.97778 | -0.42889 | 0.97777 | -0.42924 | 0.69594
48 | 0.0033113 | 0.00082969 | -0.0033111 | -0.00082984 | 1.9454e-07 | -1.4596e-07 | 0.0049715 | 0.0049716 | 0.0049716 | 0.99109 | -0.17014 | 0.99103 | -0.17138 | 1.3658
49 | 0.00094209 | 0.0002359 | -0.00094208 | -0.00023611 | 1.2759e-08 | -2.11e-07 | 0.0014144 | 0.0014145 | 0.0014145 | 0.99109 | -0.17014 | 0.99108 | -0.17043 | 0.38859
50 | -0.0057136 | -0.0014294 | 0.0057142 | 0.0014295 | 5.6607e-07 | 1.1574e-07 | 0.008729 | 0.0087289 | 0.008729 | 0.97389 | -0.50286 | 0.97399 | -0.50078 | 2.3981
51 | 0.022274 | 0.0055774 | -0.022265 | -0.0055717 | 9.4358e-06 | 5.7627e-06 | 0.033843 | 0.033844 | 0.033844 | 0.97929 | -0.39922 | 0.97884 | -0.40813 | 9.2977
52 | -0.00060255 | -0.00015101 | 0.00060255 | 0.00015095 | 1.711e-09 | -6.696e-08 | 0.00091699 | 0.00091697 | 0.00091699 | 0.97776 | -0.4293 | 0.97777 | -0.42924 | 0.25192
53 | 0.032555 | 0.0082111 | -0.032484 | -0.0081665 | 7.1193e-05 | 4.4586e-05 | 0.049435 | 0.049435 | 0.049435 | 0.9803 | -0.37692 | 0.97796 | -0.42271 | 13.5811
54 | 0.00064972 | 0.00016281 | -0.00064972 | -0.00016284 | 7.8437e-10 | -2.6704e-08 | 0.00098536 | 0.00098537 | 0.00098537 | 0.98115 | -0.36032 | 0.98115 | -0.36034 | 0.27071
55 | 0.00021185 | 5.1983e-05 | -0.00021185 | -5.2158e-05 | 5.5548e-10 | -1.7477e-07 | 0.00032384 | 0.0003239 | 0.0003239 | 0.97223 | -0.53563 | 0.97223 | -0.53568 | 0.088983
56 | -0.0025 | -0.00062544 | 0.0025001 | 0.00062529 | 9.2325e-08 | -1.4951e-07 | 0.0038258 | 0.0038258 | 0.0038258 | 0.97223 | -0.53563 | 0.97227 | -0.53485 | 1.0511
57 | 6.2889e-05 | 1.4826e-05 | -6.2889e-05 | -1.5288e-05 | 1.2874e-10 | -4.6182e-07 | 9.5925e-05 | 9.6085e-05 | 9.6085e-05 | 0.97223 | -0.53568 | 0.97223 | -0.53573 | 0.026397
58 | -0.0025001 | -0.00062529 | 0.0025002 | 0.00062499 | 1.8259e-07 | -2.9576e-07 | 0.0038258 | 0.0038256 | 0.0038258 | 0.97227 | -0.53485 | 0.97235 | -0.53331 | 1.051
59 | 6.2889e-05 | 1.5288e-05 | -6.2889e-05 | -1.5761e-05 | 1.3251e-10 | -4.7371e-07 | 9.6085e-05 | 9.6253e-05 | 9.6253e-05 | 0.97223 | -0.53573 | 0.97223 | -0.53577 | 0.026443
60 | -0.0032313 | -0.0008082 | 0.0032313 | 0.00080815 | 7.0609e-08 | -5.0351e-08 | 0.0049443 | 0.0049443 | 0.0049443 | 0.97235 | -0.53331 | 0.97237 | -0.53285 | 1.3583
61 | -0.0037241 | -0.00093165 | 0.0037243 | 0.00093156 | 2.3788e-07 | -9.0109e-08 | 0.0056983 | 0.0056982 | 0.0056983 | 0.97237 | -0.53285 | 0.97244 | -0.53151 | 1.5655
62 | -0.0037243 | -0.00093156 | 0.0037255 | 0.00093111 | 1.1912e-06 | -4.5183e-07 | 0.0056982 | 0.0056978 | 0.0056982 | 0.97244 | -0.53151 | 0.97278 | -0.52479 | 1.5654
63 | -0.0037255 | -0.00093111 | 0.003726 | 0.00093092 | 5.0011e-07 | -1.9001e-07 | 0.0056978 | 0.0056976 | 0.0056978 | 0.97278 | -0.52479 | 0.97292 | -0.52196 | 1.5653
64 | -0.0066734 | -0.0016696 | 0.0066785 | 0.0016713 | 5.1005e-06 | 1.6411e-06 | 0.010205 | 0.010205 | 0.010205 | 0.97292 | -0.52196 | 0.97374 | -0.5059 | 2.8037
65 | -0.0099263 | -0.0024852 | 0.0099304 | 0.0024872 | 4.0821e-06 | 2.0231e-06 | 0.015164 | 0.015164 | 0.015164 | 0.97399 | -0.50078 | 0.97443 | -0.49214 | 4.1659
66 | 0.0013394 | 0.00033542 | -0.0013394 | -0.00033558 | 2.1195e-08 | -1.5473e-07 | 0.0020453 | 0.0020453 | 0.0020453 | 0.97443 | -0.49214 | 0.97441 | -0.49247 | 0.56191
67 | -0.01127 | -0.0028226 | 0.011282 | 0.0028291 | 1.2278e-05 | 6.4788e-06 | 0.017209 | 0.017209 | 0.017209 | 0.97443 | -0.49214 | 0.97559 | -0.46928 | 4.7278
68 | 0.00093929 | 0.0002353 | -0.00093928 | -0.00023541 | 6.9334e-09 | -1.0751e-07 | 0.0014343 | 0.0014344 | 0.0014344 | 0.97441 | -0.49247 | 0.9744 | -0.49263 | 0.39406
69 | -0.012407 | -0.003111 | 0.012407 | 0.0031113 | 6.4609e-07 | 3.5342e-07 | 0.018924 | 0.018924 | 0.018924 | 0.97559 | -0.46928 | 0.97564 | -0.46819 | 5.1989
70 | -0.012407 | -0.0031113 | 0.012434 | 0.0031261 | 2.6948e-05 | 1.4735e-05 | 0.018924 | 0.018923 | 0.018924 | 0.97564 | -0.46819 | 0.97796 | -0.42271 | 5.1989
71 | 0.020049 | 0.0050404 | -0.019994 | -0.0050068 | 5.56e-05 | 3.3592e-05 | 0.030512 | 0.030513 | 0.030513 | 0.97796 | -0.42271 | 0.975 | -0.48095 | 8.3826
72 | 0.0098388 | 0.0024602 | -0.0098387 | -0.0024602 | 1.7359e-07 | 8.5487e-08 | 0.015014 | 0.015014 | 0.015014 | 0.975 | -0.48095 | 0.97498 | -0.48133 | 4.1247
73 | 0.010155 | 0.0025466 | -0.010148 | -0.0025429 | 7.4429e-06 | 3.7338e-06 | 0.015499 | 0.015499 | 0.015499 | 0.975 | -0.48095 | 0.97422 | -0.49634 | 4.258
74 | 0.0083242 | 0.0020806 | -0.0083216 | -0.0020795 | 2.5994e-06 | 1.1281e-06 | 0.012702 | 0.012703 | 0.012703 | 0.97498 | -0.48133 | 0.97465 | -0.4879 | 3.4897
75 | 0.0056673 | 0.00142 | -0.0056673 | -0.00142 | 1.2746e-08 | 2.5093e-09 | 0.0086561 | 0.0086561 | 0.0086561 | 0.97422 | -0.49634 | 0.97421 | -0.49639 | 2.3781
76 | 0.0053309 | 0.0013357 | -0.0053292 | -0.0013354 | 1.7345e-06 | 2.4173e-07 | 0.0081423 | 0.0081426 | 0.0081426 | 0.97421 | -0.49639 | 0.97387 | -0.50322 | 2.237
77 | 0.0034283 | 0.00085903 | -0.0034282 | -0.00085907 | 6.987e-08 | -3.9772e-08 | 0.0052382 | 0.0052382 | 0.0052382 | 0.97387 | -0.50322 | 0.97385 | -0.50365 | 1.4391
78 | 0.0024126 | 0.00060454 | -0.0024126 | -0.00060465 | 6.179e-08 | -1.1131e-07 | 0.0036864 | 0.0036865 | 0.0036865 | 0.97385 | -0.50365 | 0.97382 | -0.50419 | 1.0128
79 | 0.0073177 | 0.0018279 | -0.0073115 | -0.0018255 | 6.2585e-06 | 2.3401e-06 | 0.01117 | 0.011171 | 0.011171 | 0.97465 | -0.4879 | 0.97374 | -0.5059 | 3.0688
80 | 0.00063295 | 0.00015428 | -0.0006329 | -0.00015605 | 5.0752e-08 | -1.7714e-06 | 0.0009657 | 0.00096634 | 0.00096634 | 0.97374 | -0.5059 | 0.97365 | -0.50762 | 0.26548
81 | 0.0006329 | 0.00015605 | -0.00063284 | -0.0001583 | 6.4475e-08 | -2.2465e-06 | 0.00096634 | 0.00096716 | 0.00096716 | 0.97365 | -0.50762 | 0.97354 | -0.50977 | 0.2657
82 | 0.00055941 | 0.0001399 | -0.0005594 | -0.0001402 | 6.7891e-09 | -3.0361e-07 | 0.00085492 | 0.00085503 | 0.00085503 | 0.97354 | -0.50977 | 0.97353 | -0.51002 | 0.2349
83 | -0.0010078 | -0.00025209 | 0.0010079 | 0.0002517 | 2.9845e-08 | -3.9567e-07 | 0.0015425 | 0.0015423 | 0.0015425 | 0.97213 | -0.54095 | 0.97216 | -0.54033 | 0.42376
84 | 0.0010078 | 0.00025209 | -0.0010078 | -0.00025232 | 1.7137e-08 | -2.2714e-07 | 0.0015425 | 0.0015426 | 0.0015426 | 0.97213 | -0.54095 | 0.97211 | -0.54131 | 0.42379
85 | -0.0012996 | -0.00032481 | 0.0012996 | 0.00032449 | 4.1736e-08 | -3.2219e-07 | 0.0019889 | 0.0019887 | 0.0019889 | 0.97216 | -0.54033 | 0.9722 | -0.53965 | 0.54639
86 | 0.00031938 | 7.9782e-05 | -0.00031938 | -8.0045e-05 | 1.9057e-09 | -2.6245e-07 | 0.00048879 | 0.00048888 | 0.00048888 | 0.97211 | -0.54131 | 0.97211 | -0.54143 | 0.13431
87 | -0.0069322 | -0.0017242 | 0.00697 | 0.0017372 | 3.782e-05 | 1.3013e-05 | 0.010605 | 0.010601 | 0.010605 | 0.97224 | -0.53875 | 0.97804 | -0.42397 | 2.9134
88 | 0.0034635 | 0.00085653 | -0.0034632 | -0.00085671 | 3.4703e-07 | -1.8689e-07 | 0.0052968 | 0.0052969 | 0.0052969 | 0.97224 | -0.53875 | 0.97214 | -0.54087 | 1.4552
89 | 0.0034687 | 0.00086769 | -0.0034685 | -0.00086775 | 1.3002e-07 | -6.9376e-08 | 0.0053082 | 0.0053083 | 0.0053083 | 0.97224 | -0.53875 | 0.9722 | -0.53954 | 1.4583
90 | 0.0012265 | 0.00030723 | -0.0012265 | -0.00030739 | 1.7338e-08 | -1.5553e-07 | 0.001866 | 0.001866 | 0.001866 | 0.97804 | -0.42397 | 0.97802 | -0.42427 | 0.51265
91 | 0.0033004 | 0.00081593 | -0.0032986 | -0.00081717 | 1.8767e-06 | -1.2321e-06 | 0.0050479 | 0.0050487 | 0.0050487 | 0.97214 | -0.54087 | 0.97153 | -0.55293 | 1.387
92 | 0.0020223 | 0.00050557 | -0.0020223 | -0.00050561 | 1.0774e-08 | -3.03e-08 | 0.0030948 | 0.0030948 | 0.0030948 | 0.9722 | -0.53954 | 0.9722 | -0.53965 | 0.85023
93 | 0.0014462 | 0.00036218 | -0.0014462 | -0.00036241 | 3.7162e-08 | -2.2702e-07 | 0.0022134 | 0.0022135 | 0.0022135 | 0.9722 | -0.53954 | 0.97218 | -0.54008 | 0.60811
94 | -0.0021706 | -0.00053533 | 0.0021707 | 0.00053508 | 1.0614e-07 | -2.4974e-07 | 0.0033216 | 0.0033215 | 0.0033216 | 0.97148 | -0.55397 | 0.97153 | -0.55293 | 0.91254
95 | 0.0021706 | 0.00053533 | -0.0021704 | -0.00053586 | 2.2725e-07 | -5.3449e-07 | 0.0033216 | 0.0033219 | 0.0033219 | 0.97148 | -0.55397 | 0.97137 | -0.55619 | 0.9126
96 | 0.0011278 | 0.00028209 | -0.0011278 | -0.00028255 | 4.4729e-08 | -4.6641e-07 | 0.0017272 | 0.0017274 | 0.0017274 | 0.97153 | -0.55293 | 0.97149 | -0.55376 | 0.47456
97 | 0.0017775 | 0.0004374 | -0.0017775 | -0.00043758 | 4.9224e-08 | -1.8811e-07 | 0.00272 | 0.0027201 | 0.0027201 | 0.97137 | -0.55619 | 0.97134 | -0.55678 | 0.74728
98 | -0.0017774 | -0.00043796 | 0.0017775 | 0.00043758 | 9.9129e-08 | -3.7874e-07 | 0.0027203 | 0.0027201 | 0.0027203 | 0.97128 | -0.55797 | 0.97134 | -0.55678 | 0.74732
99 | 0.0017774 | 0.00043796 | -0.0017773 | -0.00043823 | 6.8753e-08 | -2.6262e-07 | 0.0027203 | 0.0027204 | 0.0027204 | 0.97128 | -0.55797 | 0.97124 | -0.55879 | 0.74735
100 | 0.00077571 | 0.00018721 | -0.00077571 | -0.00018721 | 3.2805e-10 | -7.4878e-09 | 0.0011859 | 0.0011859 | 0.0011859 | 0.97124 | -0.55879 | 0.97124 | -0.5588 | 0.3258
101 | 0.00085513 | 0.00021422 | -0.00085513 | -0.00021432 | 5.2055e-09 | -9.6858e-08 | 0.0013098 | 0.0013098 | 0.0013098 | 0.97149 | -0.55376 | 0.97149 | -0.55389 | 0.35983
102 | 0.0010576 | 0.0002648 | -0.0010576 | -0.00026505 | 2.0601e-08 | -2.5391e-07 | 0.0016078 | 0.0016079 | 0.0016079 | 0.97877 | -0.40941 | 0.97875 | -0.40982 | 0.44172
103 | -0.0010576 | -0.0002648 | 0.0010577 | 0.000264 | 6.4708e-08 | -7.9779e-07 | 0.0016078 | 0.0016075 | 0.0016078 | 0.97877 | -0.40941 | 0.97884 | -0.40813 | 0.44169
104 | 0.0047282 | 0.0011848 | -0.0047279 | -0.0011848 | 2.5765e-07 | -2.2627e-09 | 0.0071877 | 0.0071877 | 0.0071877 | 0.97884 | -0.40813 | 0.97878 | -0.40927 | 1.9746
105 | 0.016479 | 0.0041229 | -0.016476 | -0.0041212 | 2.7982e-06 | 1.6414e-06 | 0.025048 | 0.025048 | 0.025048 | 0.97884 | -0.40813 | 0.97866 | -0.4117 | 6.8814
106 | 0.0039994 | 0.0010022 | -0.0039992 | -0.0010023 | 2.0229e-07 | -5.3923e-08 | 0.0060801 | 0.0060802 | 0.0060802 | 0.97878 | -0.40927 | 0.97873 | -0.41033 | 1.6704
107 | 0.015894 | 0.0039754 | -0.015893 | -0.0039748 | 1.1326e-06 | 6.599e-07 | 0.024164 | 0.024164 | 0.024164 | 0.97866 | -0.4117 | 0.97858 | -0.41319 | 6.6385
108 | 0.00014651 | 2.984e-05 | -0.0001465 | -3.5474e-05 | 8.5052e-09 | -5.6344e-06 | 0.00022221 | 0.00022403 | 0.00022403 | 0.97124 | -0.55888 | 0.97118 | -0.5602 | 0.061546
109 | -0.00014651 | -2.984e-05 | 0.00014651 | 2.9521e-05 | 4.775e-10 | -3.1898e-07 | 0.00022221 | 0.00022211 | 0.00022221 | 0.97124 | -0.55888 | 0.97124 | -0.5588 | 0.061045
110 | 0.0001465 | 3.5474e-05 | -0.0001465 | -3.6717e-05 | 1.8954e-09 | -1.2425e-06 | 0.00022403 | 0.00022447 | 0.00022447 | 0.97118 | -0.5602 | 0.97116 | -0.56047 | 0.061668
111 | 0.00057609 | 0.00014434 | -0.00057609 | -0.00014438 | 1.0507e-09 | -4.401e-08 | 0.00088175 | 0.00088177 | 0.00088177 | 0.97218 | -0.54008 | 0.97217 | -0.54012 | 0.24224
112 | 0.015586 | 0.0038976 | -0.015585 | -0.0038975 | 2.9995e-07 | 1.7407e-07 | 0.023696 | 0.023696 | 0.023696 | 0.97858 | -0.41319 | 0.97856 | -0.4136 | 6.5099
113 | -0.015067 | -0.0037669 | 0.015069 | 0.0037682 | 2.2028e-06 | 1.2693e-06 | 0.022912 | 0.022912 | 0.022912 | 0.97841 | -0.41667 | 0.97856 | -0.4136 | 6.2944

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.10231 | 0.025773

## res_load
| p_mw | q_mvar
0 | 0.0008882 | 0.00022261
1 | 0.0019697 | 0.00049365
2 | 0.00071909 | 0.00018022
3 | 0.0011405 | 0.00028584
4 | 0.0030135 | 0.00075525
5 | 0.0012012 | 0.00030105
6 | 0.0013014 | 0.00032615
7 | 0.0023677 | 0.0005934
8 | 0.0014819 | 0.00037141
9 | 0.0041262 | 0.0010341
10 | 0.0014556 | 0.0003648
11 | 0.00085734 | 0.00021487
12 | 0.0015414 | 0.00038632
13 | 0.00041735 | 0.0001046
14 | 0.0012267 | 0.00030744
15 | 0.00050018 | 0.00012536
16 | 0.00038075 | 9.5424e-05
17 | 0.0013773 | 0.00034519
18 | 0.0008222 | 0.00020606
19 | 0.0035874 | 0.00089908
20 | 0.0031214 | 0.0007823
21 | 0.0095579 | 0.0023954
22 | 0.00094161 | 0.00023599
23 | 0.0033111 | 0.00082984
24 | 0.0036565 | 0.00091641
25 | 0.0019107 | 0.00047886
26 | 0.00060255 | 0.00015101
27 | 0.001062 | 0.00026617
28 | 0.00058875 | 0.00014755
29 | 0.0022881 | 0.00057346
30 | 0.00014896 | 3.7332e-05
31 | 0.00073102 | 0.00018321
32 | 6.2889e-05 | 1.5761e-05
33 | 0.00049275 | 0.0001235
34 | 0.0029474 | 0.00073869
35 | 0.0042121 | 0.0010557
36 | 0.00040011 | 0.00010028
37 | 0.0011247 | 0.00028187
38 | 0.00093928 | 0.00023541
39 | 0.0015144 | 0.00037955
40 | 0.0044803 | 0.0011229
41 | 0.0003364 | 8.4309e-05
42 | 0.0019009 | 0.00047641
43 | 0.0010156 | 0.00025453
44 | 0.0010039 | 0.0002516
45 | 0.0024126 | 0.00060465
46 | 7.3432e-05 | 1.8404e-05
47 | 0.00029172 | 7.3112e-05
48 | 0.00068844 | 0.00017254
49 | 0.00016271 | 4.0779e-05
50 | 0.00039289 | 9.8468e-05
51 | 0.0010016 | 0.00025102
52 | 0.00027266 | 6.8335e-05
53 | 0.0010576 | 0.00026505
54 | 0.00072856 | 0.00018259
55 | 0.00058163 | 0.00014577
56 | 0.0012265 | 0.00030739
57 | 0.0006292 | 0.00015769
58 | 0.0001465 | 3.6717e-05
59 | 0.00064972 | 0.00016284
60 | 0.00072266 | 0.00018112
61 | 0.0008701 | 0.00021807
62 | 0.0005594 | 0.0001402
63 | 0.00057609 | 0.00014438
64 | 0.0039992 | 0.0010023
65 | 0.00030779 | 7.7139e-05
66 | 0.00031938 | 8.0045e-05
67 | 0.00085513 | 0.00021432
68 | 0.0003107 | 7.7869e-05
69 | 0.00051598 | 0.00012932
70 | 0.00094208 | 0.00023611

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1