## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_223-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_223-6_0_4_node_9 | 0.4 | n |  | TRUE
2 | bus_LV_223-6_0_4_node_145 | 0.4 | n |  | TRUE
3 | bus_LV_223-6_0_4_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_223-6_0_4_node_144 | 0.4 | n |  | TRUE
5 | bus_LV_223-6_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_223-6_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_223-6_0_4_node_1 | 0.4 | n |  | TRUE
8 | bus_LV_223-6_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_223-6_0_4_node_2 | 0.4 | n |  | TRUE
10 | bus_LV_223-6_0_4_node_3 | 0.4 | n |  | TRUE
11 | bus_LV_223-6_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_223-6_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_223-6_0_4_node_142 | 0.4 | n |  | TRUE
14 | bus_LV_223-6_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_223-6_0_4_node_4 | 0.4 | n |  | TRUE
16 | bus_LV_223-6_0_4_node_5 | 0.4 | n |  | TRUE
17 | bus_LV_223-6_0_4_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_223-6_0_4_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_223-6_0_4_node_140 | 0.4 | n |  | TRUE
20 | bus_LV_223-6_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_223-6_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_223-6_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_223-6_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_223-6_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_223-6_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_223-6_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_223-6_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_223-6_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_223-6_0_4_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_223-6_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_223-6_0_4_node_84 | 0.4 | n |  | TRUE
32 | bus_LV_223-6_0_4_node_60 | 0.4 | n |  | TRUE
33 | bus_LV_223-6_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_223-6_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_223-6_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_223-6_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_223-6_0_4_node_75 | 0.4 | n |  | TRUE
38 | bus_LV_223-6_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_223-6_0_4_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_223-6_0_4_node_76 | 0.4 | n |  | TRUE
41 | bus_LV_223-6_0_4_node_65 | 0.4 | n |  | TRUE
42 | bus_LV_223-6_0_4_node_63 | 0.4 | n |  | TRUE
43 | bus_LV_223-6_0_4_node_66 | 0.4 | n |  | TRUE
44 | bus_LV_223-6_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_223-6_0_4_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_223-6_0_4_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_223-6_0_4_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_223-6_0_4_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_223-6_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_223-6_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_223-6_0_4_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_223-6_0_4_node_87 | 0.4 | n |  | TRUE
53 | bus_LV_223-6_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_223-6_0_4_node_83 | 0.4 | n |  | TRUE
55 | bus_LV_223-6_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_223-6_0_4_node_80 | 0.4 | n |  | TRUE
57 | bus_LV_223-6_0_4_node_71 | 0.4 | n |  | TRUE
58 | bus_LV_223-6_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_223-6_0_4_node_120 | 0.4 | n |  | TRUE
60 | bus_LV_223-6_0_4_node_81 | 0.4 | n |  | TRUE
61 | bus_LV_223-6_0_4_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_223-6_0_4_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_223-6_0_4_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_223-6_0_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_223-6_0_4_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_223-6_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_223-6_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_223-6_0_4_node_78 | 0.4 | n |  | TRUE
69 | bus_LV_223-6_0_4_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_223-6_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_223-6_0_4_node_77 | 0.4 | n |  | TRUE
72 | bus_LV_223-6_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_223-6_0_4_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_223-6_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_223-6_0_4_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_223-6_0_4_node_143 | 0.4 | n |  | TRUE
77 | bus_LV_223-6_0_4_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_223-6_0_4_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_223-6_0_4_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_223-6_0_4_node_57 | 0.4 | n |  | TRUE
81 | bus_LV_223-6_0_4_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_223-6_0_4_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_223-6_0_4_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_223-6_0_4_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_223-6_0_4_node_141 | 0.4 | n |  | TRUE
86 | bus_LV_223-6_0_4_node_134 | 0.4 | n |  | TRUE
87 | bus_LV_223-6_0_4_node_137 | 0.4 | n |  | TRUE
88 | bus_LV_223-6_0_4_node_88 | 0.4 | n |  | TRUE
89 | bus_LV_223-6_0_4_node_89 | 0.4 | n |  | TRUE
90 | bus_LV_223-6_0_4_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_223-6_0_4_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_223-6_0_4_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_223-6_0_4_node_124 | 0.4 | n |  | TRUE
94 | bus_LV_223-6_0_4_node_122 | 0.4 | n |  | TRUE
95 | bus_LV_223-6_0_4_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_223-6_0_4_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_223-6_0_4_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_223-6_0_4_node_123 | 0.4 | n |  | TRUE
99 | bus_LV_223-6_0_4_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_223-6_0_4_node_133 | 0.4 | n |  | TRUE
101 | bus_LV_223-6_0_4_node_128 | 0.4 | n |  | TRUE
102 | bus_LV_223-6_0_4_node_135 | 0.4 | n |  | TRUE
103 | bus_LV_223-6_0_4_node_129 | 0.4 | n |  | TRUE
104 | bus_LV_223-6_0_4_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_223-6_0_4_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_223-6_0_4_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_223-6_0_4_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_223-6_0_4_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_223-6_0_4_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_223-6_0_4_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_223-6_0_4_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_223-6_0_4_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_223-6_0_4_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_223-6_0_4_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_223-6_0_4_node_138 | 0.4 | n |  | TRUE
116 | bus_LV_223-6_0_4_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_223-6_0_4_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_223-6_0_4_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_223-6_0_4_node_126 | 0.4 | n |  | TRUE
120 | bus_LV_223-6_0_4_node_107 | 0.4 | n |  | TRUE
121 | bus_LV_223-6_0_4_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_223-6_0_4_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_223-6_0_4_node_148 | 0.4 | n |  | TRUE
124 | bus_LV_223-6_0_4_node_146 | 0.4 | n |  | TRUE
125 | bus_LV_223-6_0_4_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_223-6_0_4_node_109 | 0.4 | n |  | TRUE
127 | bus_LV_223-6_0_4_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_223-6_0_4_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_223-6_0_4_node_112 | 0.4 | n |  | TRUE
130 | bus_LV_223-6_0_4_node_113 | 0.4 | n |  | TRUE
131 | bus_LV_223-6_0_4_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_223-6_0_4_node_115 | 0.4 | n |  | TRUE
133 | bus_LV_223-6_0_4_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_223-6_0_4_node_117 | 0.4 | n |  | TRUE
135 | bus_LV_223-6_0_4_node_131 | 0.4 | n |  | TRUE
136 | bus_LV_223-6_0_4_node_118 | 0.4 | n |  | TRUE
137 | bus_LV_223-6_0_4_node_119 | 0.4 | n |  | TRUE
138 | bus_LV_223-6_0_4_node_121 | 0.4 | n |  | TRUE
139 | bus_LV_223-6_0_4_node_127 | 0.4 | n |  | TRUE
140 | bus_LV_223-6_0_4_node_132 | 0.4 | n |  | TRUE
141 | bus_LV_223-6_0_4_node_136 | 0.4 | n |  | TRUE
142 | bus_LV_223-6_0_4_node_139 | 0.4 | n |  | TRUE
143 | bus_LV_223-6_0_4_node_147 | 0.4 | n |  | TRUE
144 | bus_LV_223-6_0_4_node_149 | 0.4 | n |  | TRUE
145 | bus_LV_223-6_0_4_node_150 | 0.4 | n |  | TRUE
146 | bus_LV_223-6_0_4_node_151 | 0.4 | n |  | TRUE
147 | bus_LV_223-6_0_4_node_152 | 0.4 | n |  | TRUE
148 | bus_MV_371_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_223-6_0_4_load_0 | 0 | 0.00043668 | 0.00010944 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_223-6_0_4_load_9 | 1 | 0.001226 | 0.00030726 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_223-6_0_4_load_145 | 2 | 0.0010333 | 0.00025897 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_223-6_0_4_load_10 | 3 | 0.00084859 | 0.00021268 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_223-6_0_4_load_144 | 4 | 0.0015326 | 0.0003841 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_223-6_0_4_load_8 | 5 | 0.0049117 | 0.001231 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_223-6_0_4_load_15 | 6 | 0.00017472 | 4.3789e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_223-6_0_4_load_1 | 7 | 0.00028373 | 7.1108e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_223-6_0_4_load_13 | 8 | 0.00062357 | 0.00015628 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_223-6_0_4_load_3 | 10 | 0.0072547 | 0.0018182 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_223-6_0_4_load_14 | 12 | 0.00035372 | 8.8652e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_223-6_0_4_load_142 | 13 | 0.00019596 | 4.9113e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_223-6_0_4_load_4 | 15 | 0.0032836 | 0.00082294 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_223-6_0_4_load_17 | 18 | 0.0014376 | 0.00036029 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_223-6_0_4_load_140 | 19 | 0.0006765 | 0.00016955 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_223-6_0_4_load_18 | 20 | 0.0081666 | 0.0020467 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_223-6_0_4_load_19 | 21 | 0.002232 | 0.00055939 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_223-6_0_4_load_21 | 23 | 0.0022244 | 0.00055748 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_223-6_0_4_load_22 | 24 | 0.0063396 | 0.0015889 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_223-6_0_4_load_23 | 25 | 0.0040789 | 0.0010223 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_223-6_0_4_load_24 | 26 | 0.0027455 | 0.00068809 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_223-6_0_4_load_26 | 28 | 0.0033006 | 0.00082722 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_223-6_0_4_load_62 | 29 | 0.0061523 | 0.0015419 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_223-6_0_4_load_84 | 31 | 0.0017023 | 0.00042664 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_223-6_0_4_load_60 | 32 | 0.002286 | 0.00057292 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_223-6_0_4_load_34 | 33 | 0.0016023 | 0.00040157 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_223-6_0_4_load_27 | 35 | 0.0066727 | 0.0016723 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_223-6_0_4_load_75 | 37 | 0.00059975 | 0.00015031 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_223-6_0_4_load_74 | 39 | 0.0011879 | 0.00029772 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_223-6_0_4_load_76 | 40 | 0.0062939 | 0.0015774 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_223-6_0_4_load_65 | 41 | 0.0025662 | 0.00064316 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_223-6_0_4_load_66 | 43 | 0.0022843 | 0.0005725 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_223-6_0_4_load_35 | 44 | 0.001653 | 0.00041428 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_223-6_0_4_load_36 | 45 | 0.0013708 | 0.00034355 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_223-6_0_4_load_37 | 46 | 0.0015566 | 0.00039013 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_223-6_0_4_load_40 | 49 | 0.0015719 | 0.00039394 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_223-6_0_4_load_41 | 50 | 0.0016976 | 0.00042546 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_223-6_0_4_load_42 | 51 | 0.0016057 | 0.00040244 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_223-6_0_4_load_87 | 52 | 0.0018914 | 0.00047404 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_223-6_0_4_load_47 | 53 | 0.0020443 | 0.00051236 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_223-6_0_4_load_83 | 54 | 0.0017836 | 0.00044701 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_223-6_0_4_load_43 | 55 | 0.0094409 | 0.0023661 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_223-6_0_4_load_80 | 56 | 0.0016615 | 0.00041642 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_223-6_0_4_load_45 | 58 | 0.0022452 | 0.00056271 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_223-6_0_4_load_120 | 59 | 0.0014773 | 0.00037023 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_223-6_0_4_load_81 | 60 | 0.0019615 | 0.00049159 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_223-6_0_4_load_44 | 61 | 0.0017666 | 0.00044275 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_223-6_0_4_load_48 | 63 | 0.0059437 | 0.0014896 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_223-6_0_4_load_49 | 64 | 0.0018834 | 0.00047203 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_223-6_0_4_load_50 | 65 | 0.014229 | 0.0035661 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_223-6_0_4_load_51 | 66 | 0.0023376 | 0.00058586 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_223-6_0_4_load_78 | 68 | 0.0020939 | 0.00052478 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_223-6_0_4_load_55 | 70 | 0.0045515 | 0.0011407 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_223-6_0_4_load_77 | 71 | 0.0015365 | 0.00038508 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_223-6_0_4_load_68 | 72 | 0.014406 | 0.0036105 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_223-6_0_4_load_54 | 73 | 0.0015266 | 0.0003826 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_223-6_0_4_load_143 | 76 | 0.00025689 | 6.4382e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_223-6_0_4_load_61 | 78 | 0.0043744 | 0.0010963 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_223-6_0_4_load_56 | 79 | 0.0022665 | 0.00056804 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_223-6_0_4_load_57 | 80 | 0.0063965 | 0.0016031 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_223-6_0_4_load_58 | 81 | 0.0043696 | 0.0010951 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_223-6_0_4_load_59 | 82 | 0.0060687 | 0.001521 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_223-6_0_4_load_67 | 83 | 0.0049121 | 0.0012311 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_223-6_0_4_load_73 | 84 | 0.0024993 | 0.00062638 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_223-6_0_4_load_134 | 86 | 0.0028895 | 0.00072418 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_223-6_0_4_load_89 | 89 | 0.0011554 | 0.00028956 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_223-6_0_4_load_90 | 90 | 0.0035577 | 0.00089164 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_223-6_0_4_load_79 | 91 | 0.0087721 | 0.0021985 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_223-6_0_4_load_82 | 92 | 0.001494 | 0.00037444 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_223-6_0_4_load_124 | 93 | 0.0018653 | 0.0004675 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_223-6_0_4_load_122 | 94 | 0.0017987 | 0.00045081 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_223-6_0_4_load_85 | 96 | 0.0093577 | 0.0023453 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_223-6_0_4_load_123 | 98 | 0.001812 | 0.00045412 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_223-6_0_4_load_100 | 99 | 0.0032072 | 0.00080379 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_223-6_0_4_load_133 | 100 | 0.00075745 | 0.00018984 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_223-6_0_4_load_128 | 101 | 0.0030857 | 0.00077334 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_223-6_0_4_load_135 | 102 | 0.00077843 | 0.00019509 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_223-6_0_4_load_129 | 103 | 0.0013715 | 0.00034373 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_223-6_0_4_load_91 | 104 | 0.0030971 | 0.00077621 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_223-6_0_4_load_92 | 105 | 0.0059502 | 0.0014912 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_223-6_0_4_load_94 | 107 | 0.0035251 | 0.00088346 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_223-6_0_4_load_95 | 108 | 0.0011769 | 0.00029495 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_223-6_0_4_load_96 | 109 | 0.001615 | 0.00040475 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_223-6_0_4_load_98 | 111 | 0.0034895 | 0.00087456 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_223-6_0_4_load_99 | 112 | 0.00090879 | 0.00022776 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_223-6_0_4_load_101 | 113 | 0.0015352 | 0.00038475 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_223-6_0_4_load_138 | 115 | 0.0010283 | 0.00025771 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_223-6_0_4_load_125 | 116 | 0.0018457 | 0.00046259 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_223-6_0_4_load_103 | 118 | 0.0022444 | 0.00056251 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_223-6_0_4_load_126 | 119 | 0.0016979 | 0.00042554 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_223-6_0_4_load_107 | 120 | 0.0078851 | 0.0019762 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_223-6_0_4_load_104 | 121 | 0.0021057 | 0.00052774 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_223-6_0_4_load_105 | 122 | 0.0021834 | 0.00054722 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_223-6_0_4_load_148 | 123 | 0.0016274 | 0.00040787 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_223-6_0_4_load_146 | 124 | 0.0021669 | 0.00054306 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_223-6_0_4_load_108 | 125 | 0.0012245 | 0.00030689 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_223-6_0_4_load_109 | 126 | 0.0012684 | 0.00031789 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_223-6_0_4_load_111 | 128 | 0.001684 | 0.00042205 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_223-6_0_4_load_112 | 129 | 0.0015338 | 0.00038441 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_223-6_0_4_load_113 | 130 | 0.0013599 | 0.00034082 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_223-6_0_4_load_114 | 131 | 0.0042461 | 0.0010642 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_223-6_0_4_load_115 | 132 | 0.00044364 | 0.00011119 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_223-6_0_4_load_130 | 133 | 0.00045561 | 0.00011419 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_223-6_0_4_load_117 | 134 | 0.0015607 | 0.00039115 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_223-6_0_4_load_131 | 135 | 0.00054783 | 0.0001373 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_223-6_0_4_load_118 | 136 | 0.0015241 | 0.00038199 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_223-6_0_4_load_119 | 137 | 0.0014548 | 0.00036461 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_223-6_0_4_load_121 | 138 | 0.0016629 | 0.00041676 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_223-6_0_4_load_127 | 139 | 0.0015389 | 0.00038569 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_223-6_0_4_load_132 | 140 | 0.0020203 | 0.00050634 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_223-6_0_4_load_139 | 142 | 0.0021182 | 0.00053086 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_223-6_0_4_load_147 | 143 | 0.0013727 | 0.00034403 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_223-6_0_4_load_149 | 144 | 0.0015296 | 0.00038334 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_223-6_0_4_load_150 | 145 | 0.00086345 | 0.0002164 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_223-6_0_4_load_151 | 146 | 0.0013974 | 0.00035022 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_223-6_0_4_load_152 | 147 | 0.0025007 | 0.00062673 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 61 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_223-6_0_4_line_0 |  | 0 | 1 | 0.11602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_223-6_0_4_line_1 |  | 0 | 2 | 0.13899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_223-6_0_4_line_2 |  | 1 | 3 | 0.0032981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_223-6_0_4_line_3 |  | 2 | 4 | 0.033073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_223-6_0_4_line_4 |  | 4 | 5 | 0.16351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_223-6_0_4_line_5 |  | 5 | 17 | 0.034795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_223-6_0_4_line_6 |  | 6 | 7 | 0.18604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_223-6_0_4_line_7 |  | 6 | 8 | 0.015615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_223-6_0_4_line_8 |  | 7 | 9 | 0.054511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_223-6_0_4_line_9 |  | 8 | 12 | 0.01125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_223-6_0_4_line_10 |  | 9 | 10 | 0.13628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_223-6_0_4_line_11 |  | 10 | 11 | 0.0124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_223-6_0_4_line_12 |  | 11 | 14 | 0.028164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_223-6_0_4_line_13 |  | 12 | 13 | 0.15597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_223-6_0_4_line_14 |  | 13 | 19 | 0.012265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_223-6_0_4_line_15 |  | 14 | 18 | 0.083096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_223-6_0_4_line_16 |  | 15 | 16 | 0.029065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_223-6_0_4_line_17 |  | 15 | 17 | 0.011024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_223-6_0_4_line_18 |  | 16 | 18 | 0.17956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_223-6_0_4_line_19 |  | 19 | 142 | 0.01149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_223-6_0_4_line_20 |  | 20 | 21 | 0.014225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_223-6_0_4_line_21 |  | 20 | 22 | 0.021624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_223-6_0_4_line_22 |  | 21 | 23 | 0.0073316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_223-6_0_4_line_23 |  | 22 | 24 | 0.05345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_223-6_0_4_line_24 |  | 22 | 25 | 0.018421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_223-6_0_4_line_25 |  | 23 | 26 | 0.013147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_223-6_0_4_line_26 |  | 24 | 27 | 0.02835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_223-6_0_4_line_27 |  | 25 | 28 | 0.021276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_223-6_0_4_line_28 |  | 26 | 29 | 0.0068687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_223-6_0_4_line_29 |  | 27 | 30 | 0.030945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_223-6_0_4_line_30 |  | 28 | 31 | 0.0036757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_223-6_0_4_line_31 |  | 29 | 32 | 0.0014121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_223-6_0_4_line_32 |  | 30 | 33 | 0.0067325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_223-6_0_4_line_33 |  | 30 | 34 | 0.039125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_223-6_0_4_line_34 |  | 32 | 81 | 0.017555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_223-6_0_4_line_35 |  | 34 | 35 | 0.0099586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_223-6_0_4_line_36 |  | 36 | 37 | 0.021103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_223-6_0_4_line_37 |  | 36 | 38 | 0.002725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_223-6_0_4_line_38 |  | 37 | 40 | 0.031019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_223-6_0_4_line_39 |  | 38 | 39 | 0.025595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_223-6_0_4_line_40 |  | 39 | 43 | 0.034113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_223-6_0_4_line_41 |  | 41 | 42 | 0.029319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_223-6_0_4_line_42 |  | 42 | 77 | 0.003727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_223-6_0_4_line_43 |  | 42 | 78 | 0.020016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_223-6_0_4_line_44 |  | 43 | 77 | 0.0069322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_223-6_0_4_line_45 |  | 44 | 45 | 0.0060485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_223-6_0_4_line_46 |  | 44 | 46 | 0.0064167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_223-6_0_4_line_47 |  | 45 | 47 | 0.011357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_223-6_0_4_line_48 |  | 46 | 48 | 0.015969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_223-6_0_4_line_49 |  | 47 | 49 | 0.012086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_223-6_0_4_line_50 |  | 47 | 50 | 0.010151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_223-6_0_4_line_51 |  | 48 | 51 | 0.004538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_223-6_0_4_line_52 |  | 49 | 52 | 0.0060341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_223-6_0_4_line_53 |  | 50 | 53 | 0.013954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_223-6_0_4_line_54 |  | 51 | 54 | 0.00018495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_223-6_0_4_line_55 |  | 52 | 57 | 0.017291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_223-6_0_4_line_56 |  | 53 | 58 | 0.016381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_223-6_0_4_line_57 |  | 54 | 59 | 0.016525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_223-6_0_4_line_58 |  | 55 | 56 | 0.026504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_223-6_0_4_line_59 |  | 56 | 60 | 0.0001316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_223-6_0_4_line_60 |  | 57 | 73 | 0.011536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_223-6_0_4_line_61 |  | 57 | 75 | 0.077366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_223-6_0_4_line_62 |  | 58 | 61 | 0.0021841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_223-6_0_4_line_63 |  | 59 | 95 | 0.0089162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_223-6_0_4_line_64 |  | 60 | 92 | 0.0062142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_223-6_0_4_line_65 |  | 61 | 62 | 0.016358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_223-6_0_4_line_66 |  | 62 | 63 | 0.028813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_223-6_0_4_line_67 |  | 62 | 64 | 0.0017216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_223-6_0_4_line_68 |  | 63 | 65 | 0.014079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_223-6_0_4_line_69 |  | 64 | 66 | 0.0046161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_223-6_0_4_line_70 |  | 65 | 67 | 0.02155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_223-6_0_4_line_71 |  | 66 | 68 | 0.0080059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_223-6_0_4_line_72 |  | 67 | 69 | 0.002954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_223-6_0_4_line_73 |  | 67 | 70 | 0.030601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_223-6_0_4_line_74 |  | 68 | 71 | 0.00023356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_223-6_0_4_line_75 |  | 69 | 72 | 0.021709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_223-6_0_4_line_76 |  | 71 | 91 | 0.0060558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_223-6_0_4_line_77 |  | 72 | 74 | 0.018971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_223-6_0_4_line_78 |  | 74 | 84 | 0.097152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_223-6_0_4_line_79 |  | 74 | 83 | 0.020707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_223-6_0_4_line_80 |  | 75 | 76 | 0.044884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_223-6_0_4_line_81 |  | 76 | 85 | 0.043754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_223-6_0_4_line_82 |  | 77 | 83 | 0.019162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_223-6_0_4_line_83 |  | 78 | 82 | 0.015498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_223-6_0_4_line_84 |  | 79 | 80 | 0.0042382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_223-6_0_4_line_85 |  | 79 | 81 | 0.0044981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_223-6_0_4_line_86 |  | 80 | 82 | 0.030643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_223-6_0_4_line_87 |  | 85 | 142 | 0.038668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_223-6_0_4_line_88 |  | 86 | 87 | 0.047563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_223-6_0_4_line_89 |  | 87 | 141 | 0.003557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_223-6_0_4_line_90 |  | 88 | 89 | 0.040283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_223-6_0_4_line_91 |  | 88 | 90 | 0.018991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_223-6_0_4_line_92 |  | 89 | 100 | 0.018352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_223-6_0_4_line_93 |  | 90 | 101 | 0.00338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_223-6_0_4_line_94 |  | 92 | 93 | 0.0060829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_223-6_0_4_line_95 |  | 93 | 94 | 0.0066102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_223-6_0_4_line_96 |  | 94 | 97 | 0.017978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_223-6_0_4_line_97 |  | 95 | 134 | 0.0038569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_223-6_0_4_line_98 |  | 95 | 130 | 0.017822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_223-6_0_4_line_99 |  | 96 | 97 | 0.023731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_223-6_0_4_line_100 |  | 97 | 98 | 0.015894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_223-6_0_4_line_101 |  | 98 | 99 | 0.0084778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_223-6_0_4_line_102 |  | 99 | 110 | 0.01797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_223-6_0_4_line_103 |  | 100 | 102 | 0.0064784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_223-6_0_4_line_104 |  | 101 | 103 | 0.0094162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_223-6_0_4_line_105 |  | 102 | 141 | 0.043682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_223-6_0_4_line_106 |  | 103 | 131 | 0.0028291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_223-6_0_4_line_107 |  | 104 | 105 | 0.032334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_223-6_0_4_line_108 |  | 104 | 106 | 0.016807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_223-6_0_4_line_109 |  | 105 | 107 | 0.03549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_223-6_0_4_line_110 |  | 106 | 108 | 0.013055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_223-6_0_4_line_111 |  | 106 | 109 | 0.064141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_223-6_0_4_line_112 |  | 107 | 110 | 0.042433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_223-6_0_4_line_113 |  | 108 | 111 | 0.014513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_223-6_0_4_line_114 |  | 109 | 112 | 0.0093891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_223-6_0_4_line_115 |  | 110 | 113 | 0.017544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_223-6_0_4_line_116 |  | 110 | 114 | 0.028078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_223-6_0_4_line_117 |  | 112 | 115 | 0.018654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_223-6_0_4_line_118 |  | 113 | 116 | 0.0053851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_223-6_0_4_line_119 |  | 114 | 117 | 0.036521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_223-6_0_4_line_120 |  | 114 | 118 | 0.01692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_223-6_0_4_line_121 |  | 116 | 119 | 0.0056439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_223-6_0_4_line_122 |  | 117 | 120 | 0.047342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_223-6_0_4_line_123 |  | 118 | 121 | 0.0058667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_223-6_0_4_line_124 |  | 119 | 139 | 0.0081635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_223-6_0_4_line_125 |  | 120 | 123 | 0.0075289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_223-6_0_4_line_126 |  | 121 | 122 | 0.0045232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_223-6_0_4_line_127 |  | 123 | 124 | 0.0046172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_223-6_0_4_line_128 |  | 124 | 143 | 0.0018877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_223-6_0_4_line_129 |  | 125 | 126 | 0.0050497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_223-6_0_4_line_130 |  | 125 | 127 | 0.0033068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_223-6_0_4_line_131 |  | 126 | 128 | 0.014158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_223-6_0_4_line_132 |  | 127 | 129 | 0.015437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_223-6_0_4_line_133 |  | 127 | 130 | 0.0019264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_223-6_0_4_line_134 |  | 128 | 131 | 0.0073248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_223-6_0_4_line_135 |  | 129 | 132 | 0.003262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_223-6_0_4_line_136 |  | 132 | 133 | 0.00033512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_223-6_0_4_line_137 |  | 133 | 135 | 0.00015325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_223-6_0_4_line_138 |  | 134 | 136 | 0.004578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_223-6_0_4_line_139 |  | 135 | 140 | 0.0055619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_223-6_0_4_line_140 |  | 136 | 137 | 0.013557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_223-6_0_4_line_141 |  | 137 | 138 | 0.0053729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_223-6_0_4_line_142 |  | 138 | 139 | 0.0055188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_223-6_0_4_line_143 |  | 143 | 144 | 0.013389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_223-6_0_4_line_144 |  | 144 | 145 | 0.0051667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_223-6_0_4_line_145 |  | 145 | 146 | 0.0013285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_223-6_0_4_line_146 |  | 146 | 147 | 0.0086594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_223-6_0_4_trafo_44 | 0.63 MVA 20/0.4 kV | 148 | 61 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2691633.9677 | 1264882.7367 | 2691561.7683 | 1264973.5495
1 | 2691561.7683 | 1264973.5495 | 2691540.8769 | 1265110.957
2 | 2691633.9677 | 1264882.7367 | 2691637.2409 | 1264883.1407
3 | 2691573.3385 | 1265112.6637 | 2691561.6679 | 1265109.108 | 2691540.8769 | 1265110.957
4 | 2691573.3385 | 1265112.6637 | 2691736.8322 | 1265114.95
5 | 2691736.8322 | 1265114.95 | 2691736.2614 | 1265119.7006 | 2691737.9212 | 1265125.8202 | 2691753.8027 | 1265143.4142
6 | 2691795.3541 | 1264762.468 | 2691768.3769 | 1264946.5391
7 | 2691810.9666 | 1264762.2881 | 2691796.8745 | 1264762.3964 | 2691795.3541 | 1264762.468
8 | 2691822.6608 | 1264950.1154 | 2691812.711 | 1264949.1824 | 2691789.2106 | 1264949.3065 | 2691773.4184 | 1264947.2709 | 2691768.3769 | 1264946.5391
9 | 2691810.9666 | 1264762.2881 | 2691822.2165 | 1264762.2015
10 | 2691822.6608 | 1264950.1154 | 2691843.7596 | 1264935.8871 | 2691857.9973 | 1264929.8812 | 2691871.9408 | 1264928.7525 | 2691887.5754 | 1264930.7526 | 2691905.1639 | 1264937.8762 | 2691945.3633 | 1264961.5539
11 | 2691956.0479 | 1264967.8471 | 2691945.3633 | 1264961.5539
12 | 2691956.0479 | 1264967.8471 | 2691931.7461 | 1264982.2031
13 | 2691899.5939 | 1264626.7822 | 2691822.2165 | 1264762.2015
14 | 2691899.5939 | 1264626.7822 | 2691891.9101 | 1264617.223
15 | 2691931.7461 | 1264982.2031 | 2691926.6744 | 1264990.62 | 2691920.161 | 1265035.0658 | 2691919.2563 | 1265044.3259 | 2691921.668 | 1265054.3827 | 2691925.326 | 1265062.2793
16 | 2691782.6291 | 1265171.2731 | 2691761.7295 | 1265151.075
17 | 2691753.8027 | 1265143.4142 | 2691761.7295 | 1265151.075
18 | 2691925.326 | 1265062.2793 | 2691782.6291 | 1265171.2731
19 | 2691884.7113 | 1264608.2673 | 2691891.9101 | 1264617.223
20 | 2692019.1045 | 1264437.1617 | 2692026.884 | 1264431.9376 | 2692030.4225 | 1264428.6147
21 | 2692046.1853 | 1264413.8122 | 2692030.4225 | 1264428.6147
22 | 2692019.1045 | 1264437.1617 | 2692013.0179 | 1264441.249
23 | 2692046.1853 | 1264413.8122 | 2692027.7012 | 1264394.9426 | 2692008.7877 | 1264375.6243
24 | 2692046.1853 | 1264413.8122 | 2692058.3273 | 1264427.6646
25 | 2692001.5383 | 1264447.4651 | 2692006.3625 | 1264445.7183 | 2692013.0179 | 1264441.249
26 | 2691988.578 | 1264355.78 | 2691992.3864 | 1264358.8751 | 2692006.5406 | 1264373.3292 | 2692008.7877 | 1264375.6243
27 | 2692072.3514 | 1264443.664 | 2692058.3273 | 1264427.6646
28 | 2692001.5383 | 1264447.4651 | 2691995.08 | 1264449.8036
29 | 2691988.578 | 1264355.78 | 2691973.2798 | 1264373.6898 | 2691973.9988 | 1264375.4024 | 2691970.3851 | 1264379.6385
30 | 2692074.7742 | 1264446.4281 | 2692072.3514 | 1264443.664
31 | 2691995.08 | 1264449.8036 | 2691993.7523 | 1264450.2843
32 | 2691970.3851 | 1264379.6385 | 2691968.3594 | 1264373.2181
33 | 2691937.3788 | 1264387.8541 | 2691940.7783 | 1264388.6632 | 2691942.1436 | 1264392.4097 | 2691966.3646 | 1264384.3687 | 2691970.3851 | 1264379.6385
34 | 2691977.2456 | 1264456.2613 | 2691993.7523 | 1264450.2843
35 | 2691937.3788 | 1264387.8541 | 2691934.6163 | 1264392.0924 | 2691930.4044 | 1264394.5956
36 | 2691871.2034 | 1264450.6097 | 2691888.2531 | 1264442.1011 | 2691890.0369 | 1264441.0948
37 | 2691868.7591 | 1264451.8283 | 2691871.2034 | 1264450.6097
38 | 2691914.6197 | 1264422.9732 | 2691908.9004 | 1264426.5094 | 2691903.5421 | 1264433.4762 | 2691890.0369 | 1264441.0948
39 | 2691868.7591 | 1264451.8283 | 2691878.1962 | 1264463.9847 | 2691885.2797 | 1264471.3311
40 | 2691908.9577 | 1264495.8882 | 2691885.2797 | 1264471.3311
41 | 2691916.5276 | 1264498.3638 | 2691896.1586 | 1264477.2762
42 | 2691913.7694 | 1264500.8785 | 2691916.5276 | 1264498.3638
43 | 2691916.5276 | 1264498.3638 | 2691930.9146 | 1264484.4483
44 | 2691913.7694 | 1264500.8785 | 2691908.9577 | 1264495.8882
45 | 2692063.1641 | 1264577.188 | 2692066.7424 | 1264572.3115
46 | 2692070.5384 | 1264567.1381 | 2692066.7424 | 1264572.3115
47 | 2692056.4451 | 1264586.3448 | 2692063.1641 | 1264577.188
48 | 2692079.9857 | 1264554.2631 | 2692070.5384 | 1264567.1381
49 | 2692056.4451 | 1264586.3448 | 2692049.8604 | 1264596.4799
50 | 2692056.4451 | 1264586.3448 | 2692048.2439 | 1264580.3635
51 | 2692079.9857 | 1264554.2631 | 2692083.6877 | 1264556.8877
52 | 2692049.8604 | 1264596.4799 | 2692046.5729 | 1264601.5399
53 | 2692048.2439 | 1264580.3635 | 2692036.9701 | 1264572.1413
54 | 2692083.6877 | 1264556.8877 | 2692083.8385 | 1264556.9947
55 | 2692036.3558 | 1264615.4445 | 2692041.2965 | 1264609.6612 | 2692046.5729 | 1264601.5399
56 | 2692036.9701 | 1264572.1413 | 2692036.9701 | 1264572.1413 | 2692038.3236 | 1264563.0995 | 2692032.8376 | 1264558.3778
57 | 2692097.3406 | 1264566.516 | 2692097.0978 | 1264566.395 | 2692083.8385 | 1264556.9947
58 | 2692089.2898 | 1264511.6069 | 2692089.2898 | 1264511.6069 | 2692078.1215 | 1264502.3032 | 2692070.9998 | 1264511.9215
59 | 2692089.3881 | 1264511.5194 | 2692089.2898 | 1264511.6069
60 | 2692036.3558 | 1264615.4445 | 2692027.9331 | 1264607.5625
61 | 2691972.5648 | 1264587.5294 | 2691994.9132 | 1264593.771 | 2692003.9063 | 1264590.8752 | 2692033.4681 | 1264618.5354 | 2692036.3558 | 1264615.4445
62 | 2692031.1822 | 1264556.953 | 2692032.8376 | 1264558.3778
63 | 2692105.7415 | 1264569.0095 | 2692101.5897 | 1264568.6334 | 2692097.3406 | 1264566.516
64 | 2692094.0299 | 1264507.3877 | 2692089.3881 | 1264511.5194
65 | 2692018.7837 | 1264546.2818 | 2692031.1822 | 1264556.953
66 | 2692018.7837 | 1264546.2818 | 2692009.6185 | 1264557.3147 | 2691998.2906 | 1264548.3121
67 | 2692018.7837 | 1264546.2818 | 2692017.6896 | 1264544.9526 | 2692017.6896 | 1264544.9526
68 | 2691987.2686 | 1264539.5527 | 2691987.2686 | 1264539.5527 | 2691998.2906 | 1264548.3121
69 | 2692017.6896 | 1264544.9526 | 2692020.4608 | 1264541.2608
70 | 2691972.8069 | 1264555.5295 | 2691987.2686 | 1264539.5527
71 | 2692025.2669 | 1264534.8581 | 2692020.4608 | 1264541.2608
72 | 2691970.8219 | 1264557.7227 | 2691972.8069 | 1264555.5295
73 | 2691972.8069 | 1264555.5295 | 2691951.3435 | 1264533.7185
74 | 2692025.4071 | 1264534.6713 | 2692025.2669 | 1264534.8581
75 | 2691970.8219 | 1264557.7227 | 2691955.1872 | 1264542.6614
76 | 2692029.0426 | 1264529.8281 | 2692025.4071 | 1264534.6713
77 | 2691941.5244 | 1264529.4998 | 2691955.1872 | 1264542.6614
78 | 2691861.6137 | 1264526.2664 | 2691908.8608 | 1264553.9896 | 2691917.7591 | 1264553.3163 | 2691941.5244 | 1264529.4998
79 | 2691941.5244 | 1264529.4998 | 2691927.1093 | 1264514.6348
80 | 2691972.5648 | 1264587.5294 | 2691942.1063 | 1264584.5534 | 2691927.9037 | 1264583.064
81 | 2691885.6796 | 1264571.7437 | 2691904.042 | 1264577.1223 | 2691925.1718 | 1264582.7775 | 2691927.9037 | 1264583.064
82 | 2691913.7694 | 1264500.8785 | 2691927.1093 | 1264514.6348
83 | 2691930.9146 | 1264484.4483 | 2691942.0541 | 1264473.674 | 2691942.0541 | 1264473.674
84 | 2691973.0162 | 1264457.7927 | 2691969.0312 | 1264459.2356
85 | 2691973.0162 | 1264457.7927 | 2691977.2456 | 1264456.2613
86 | 2691969.0312 | 1264459.2356 | 2691965.4049 | 1264460.5487 | 2691942.0541 | 1264473.674
87 | 2691885.6796 | 1264571.7437 | 2691883.3096 | 1264576.4218 | 2691881.055 | 1264582.3916 | 2691879.9584 | 1264595.2738 | 2691882.2962 | 1264605.2627 | 2691884.7113 | 1264608.2673
88 | 2692149.3225 | 1264696.4806 | 2692116.2422 | 1264682.9653 | 2692105.8938 | 1264677.2365
89 | 2692149.3225 | 1264696.4806 | 2692151.3342 | 1264693.5429
90 | 2692059.7643 | 1264636.7817 | 2692071.7977 | 1264648.0671 | 2692081.3058 | 1264656.1106 | 2692088.9383 | 1264662.2233 | 2692090.192 | 1264663.1405
91 | 2692059.7643 | 1264636.7817 | 2692060.9739 | 1264635.5218 | 2692063.8757 | 1264632.4978 | 2692071.9442 | 1264622.2374
92 | 2692090.192 | 1264663.1405 | 2692096.0353 | 1264667.4158 | 2692104.613 | 1264672.8093 | 2692105.4804 | 1264673.2637
93 | 2692072.6059 | 1264618.9228 | 2692071.9442 | 1264622.2374
94 | 2692094.0299 | 1264507.3877 | 2692098.5736 | 1264503.3433
95 | 2692103.5111 | 1264498.9484 | 2692098.5736 | 1264503.3433
96 | 2692116.9399 | 1264486.9954 | 2692103.5111 | 1264498.9484
97 | 2692105.7415 | 1264569.0095 | 2692108.9645 | 1264567.1249 | 2692109.0431 | 1264567.0298
98 | 2692105.7415 | 1264569.0095 | 2692101.8593 | 1264575.9769 | 2692101.3695 | 1264581.3069 | 2692098.2769 | 1264584.5666
99 | 2692116.9399 | 1264486.9954 | 2692109.2295 | 1264479.5804 | 2692099.8373 | 1264470.5434
100 | 2692116.9399 | 1264486.9954 | 2692119.7449 | 1264489.6968 | 2692128.8499 | 1264497.5122
101 | 2692128.8499 | 1264497.5122 | 2692135.2828 | 1264503.0341
102 | 2692148.9182 | 1264514.7383 | 2692135.2828 | 1264503.0341
103 | 2692111.219 | 1264676.2698 | 2692105.4804 | 1264673.2637
104 | 2692079.1735 | 1264612.1751 | 2692072.6059 | 1264618.9228 | 2692072.6059 | 1264618.9228
105 | 2692151.3342 | 1264693.5429 | 2692119.0388 | 1264679.9176 | 2692111.9644 | 1264676.6603 | 2692111.219 | 1264676.2698
106 | 2692079.1735 | 1264612.1751 | 2692079.5186 | 1264609.3671 | 2692079.5186 | 1264609.3671
107 | 2692223.9627 | 1264433.9682 | 2692202.1418 | 1264457.8294
108 | 2692235.3052 | 1264421.5652 | 2692223.9627 | 1264433.9682
109 | 2692202.1418 | 1264457.8294 | 2692179.9707 | 1264482.0736 | 2692178.1543 | 1264483.9843
110 | 2692235.3052 | 1264421.5652 | 2692225.8541 | 1264412.5588
111 | 2692235.3052 | 1264421.5652 | 2692260.9151 | 1264393.5754 | 2692241.6383 | 1264375.827
112 | 2692148.9182 | 1264514.7383 | 2692178.1543 | 1264483.9843
113 | 2692212.94 | 1264408.1723 | 2692221.686 | 1264408.5868 | 2692225.8541 | 1264412.5588
114 | 2692235.2806 | 1264382.736 | 2692241.6383 | 1264375.827
115 | 2692148.9182 | 1264514.7383 | 2692138.3121 | 1264528.713
116 | 2692171.5248 | 1264531.4708 | 2692167.6109 | 1264528.8744 | 2692148.9182 | 1264514.7383
117 | 2692235.2806 | 1264382.736 | 2692222.649 | 1264396.463
118 | 2692135.0565 | 1264533.0026 | 2692138.3121 | 1264528.713
119 | 2692171.5248 | 1264531.4708 | 2692199.3318 | 1264549.9192 | 2692201.8922 | 1264551.883
120 | 2692171.5248 | 1264531.4708 | 2692181.6589 | 1264517.9211
121 | 2692135.0565 | 1264533.0026 | 2692131.6445 | 1264537.4983
122 | 2692201.8922 | 1264551.883 | 2692194.5745 | 1264563.7229 | 2692189.9232 | 1264564.4621 | 2692182.4794 | 1264575.2214 | 2692169.2781 | 1264566.8533
123 | 2692181.6589 | 1264517.9211 | 2692185.1726 | 1264513.223
124 | 2692131.6445 | 1264537.4983 | 2692126.7092 | 1264544.001
125 | 2692165.0363 | 1264573.0736 | 2692169.2781 | 1264566.8533 | 2692169.2781 | 1264566.8533
126 | 2692185.1726 | 1264513.223 | 2692187.8817 | 1264509.6008
127 | 2692162.4349 | 1264576.8883 | 2692165.0363 | 1264573.0736
128 | 2692162.4349 | 1264576.8883 | 2692161.3714 | 1264578.4478
129 | 2692091.1993 | 1264592.0262 | 2692094.6749 | 1264588.363
130 | 2692096.9509 | 1264585.9641 | 2692094.6749 | 1264588.363
131 | 2692091.1993 | 1264592.0262 | 2692089.9746 | 1264593.317 | 2692089.1916 | 1264598.1309 | 2692084.2974 | 1264603.816
132 | 2692096.9509 | 1264585.9641 | 2692107.9491 | 1264596.7961
133 | 2692096.9509 | 1264585.9641 | 2692098.2769 | 1264584.5666
134 | 2692079.5186 | 1264609.3671 | 2692084.2974 | 1264603.816
135 | 2692107.9491 | 1264596.7961 | 2692110.2732 | 1264599.0851
136 | 2692110.2732 | 1264599.0851 | 2692110.512 | 1264599.3202
137 | 2692110.512 | 1264599.3202 | 2692110.6212 | 1264599.4278
138 | 2692109.0431 | 1264567.0298 | 2692111.3674 | 1264564.2155 | 2692111.9284 | 1264563.4763
139 | 2692114.5839 | 1264603.3306 | 2692110.6212 | 1264599.4278
140 | 2692120.1246 | 1264552.6769 | 2692111.9284 | 1264563.4763
141 | 2692123.3728 | 1264548.3971 | 2692120.1246 | 1264552.6769
142 | 2692123.3728 | 1264548.3971 | 2692126.7092 | 1264544.001
143 | 2692153.8279 | 1264589.5097 | 2692161.3714 | 1264578.4478
144 | 2692150.9169 | 1264593.7783 | 2692153.8279 | 1264589.5097
145 | 2692150.9169 | 1264593.7783 | 2692150.1684 | 1264594.8759
146 | 2692145.2897 | 1264602.0302 | 2692150.1684 | 1264594.8759

## bus_geodata
| x | y | coords
0 | 2691561.7683 | 1264973.5495
1 | 2691633.9677 | 1264882.7367
2 | 2691540.8769 | 1265110.957
3 | 2691637.2409 | 1264883.1407
4 | 2691573.3385 | 1265112.6637
5 | 2691736.8322 | 1265114.95
6 | 2691795.3541 | 1264762.468
7 | 2691768.3769 | 1264946.5391
8 | 2691810.9666 | 1264762.2881
9 | 2691822.6608 | 1264950.1154
10 | 2691945.3633 | 1264961.5539
11 | 2691956.0479 | 1264967.8471
12 | 2691822.2165 | 1264762.2015
13 | 2691899.5939 | 1264626.7822
14 | 2691931.7461 | 1264982.2031
15 | 2691761.7295 | 1265151.075
16 | 2691782.6291 | 1265171.2731
17 | 2691753.8027 | 1265143.4142
18 | 2691925.326 | 1265062.2793
19 | 2691891.9101 | 1264617.223
20 | 2692030.4225 | 1264428.6147
21 | 2692019.1045 | 1264437.1617
22 | 2692046.1853 | 1264413.8122
23 | 2692013.0179 | 1264441.249
24 | 2692008.7877 | 1264375.6243
25 | 2692058.3273 | 1264427.6646
26 | 2692001.5383 | 1264447.4651
27 | 2691988.578 | 1264355.78
28 | 2692072.3514 | 1264443.664
29 | 2691995.08 | 1264449.8036
30 | 2691970.3851 | 1264379.6385
31 | 2692074.7742 | 1264446.4281
32 | 2691993.7523 | 1264450.2843
33 | 2691968.3594 | 1264373.2181
34 | 2691937.3788 | 1264387.8541
35 | 2691930.4044 | 1264394.5956
36 | 2691871.2034 | 1264450.6097
37 | 2691890.0369 | 1264441.0948
38 | 2691868.7591 | 1264451.8283
39 | 2691885.2797 | 1264471.3311
40 | 2691914.6197 | 1264422.9732
41 | 2691896.1586 | 1264477.2762
42 | 2691916.5276 | 1264498.3638
43 | 2691908.9577 | 1264495.8882
44 | 2692066.7424 | 1264572.3115
45 | 2692063.1641 | 1264577.188
46 | 2692070.5384 | 1264567.1381
47 | 2692056.4451 | 1264586.3448
48 | 2692079.9857 | 1264554.2631
49 | 2692049.8604 | 1264596.4799
50 | 2692048.2439 | 1264580.3635
51 | 2692083.6877 | 1264556.8877
52 | 2692046.5729 | 1264601.5399
53 | 2692036.9701 | 1264572.1413
54 | 2692083.8385 | 1264556.9947
55 | 2692070.9998 | 1264511.9215
56 | 2692089.2898 | 1264511.6069
57 | 2692036.3558 | 1264615.4445
58 | 2692032.8376 | 1264558.3778
59 | 2692097.3406 | 1264566.516
60 | 2692089.3881 | 1264511.5194
61 | 2692031.1822 | 1264556.953
62 | 2692018.7837 | 1264546.2818
63 | 2691998.2906 | 1264548.3121
64 | 2692017.6896 | 1264544.9526
65 | 2691987.2686 | 1264539.5527
66 | 2692020.4608 | 1264541.2608
67 | 2691972.8069 | 1264555.5295
68 | 2692025.2669 | 1264534.8581
69 | 2691970.8219 | 1264557.7227
70 | 2691951.3435 | 1264533.7185
71 | 2692025.4071 | 1264534.6713
72 | 2691955.1872 | 1264542.6614
73 | 2692027.9331 | 1264607.5625
74 | 2691941.5244 | 1264529.4998
75 | 2691972.5648 | 1264587.5294
76 | 2691927.9037 | 1264583.064
77 | 2691913.7694 | 1264500.8785
78 | 2691930.9146 | 1264484.4483
79 | 2691973.0162 | 1264457.7927
80 | 2691969.0312 | 1264459.2356
81 | 2691977.2456 | 1264456.2613
82 | 2691942.0541 | 1264473.674
83 | 2691927.1093 | 1264514.6348
84 | 2691861.6137 | 1264526.2664
85 | 2691885.6796 | 1264571.7437
86 | 2692105.8938 | 1264677.2365
87 | 2692149.3225 | 1264696.4806
88 | 2692059.7643 | 1264636.7817
89 | 2692090.192 | 1264663.1405
90 | 2692071.9442 | 1264622.2374
91 | 2692029.0426 | 1264529.8281
92 | 2692094.0299 | 1264507.3877
93 | 2692098.5736 | 1264503.3433
94 | 2692103.5111 | 1264498.9484
95 | 2692105.7415 | 1264569.0095
96 | 2692099.8373 | 1264470.5434
97 | 2692116.9399 | 1264486.9954
98 | 2692128.8499 | 1264497.5122
99 | 2692135.2828 | 1264503.0341
100 | 2692105.4804 | 1264673.2637
101 | 2692072.6059 | 1264618.9228
102 | 2692111.219 | 1264676.2698
103 | 2692079.1735 | 1264612.1751
104 | 2692223.9627 | 1264433.9682
105 | 2692202.1418 | 1264457.8294
106 | 2692235.3052 | 1264421.5652
107 | 2692178.1543 | 1264483.9843
108 | 2692225.8541 | 1264412.5588
109 | 2692241.6383 | 1264375.827
110 | 2692148.9182 | 1264514.7383
111 | 2692212.94 | 1264408.1723
112 | 2692235.2806 | 1264382.736
113 | 2692138.3121 | 1264528.713
114 | 2692171.5248 | 1264531.4708
115 | 2692222.649 | 1264396.463
116 | 2692135.0565 | 1264533.0026
117 | 2692201.8922 | 1264551.883
118 | 2692181.6589 | 1264517.9211
119 | 2692131.6445 | 1264537.4983
120 | 2692169.2781 | 1264566.8533
121 | 2692185.1726 | 1264513.223
122 | 2692187.8817 | 1264509.6008
123 | 2692165.0363 | 1264573.0736
124 | 2692162.4349 | 1264576.8883
125 | 2692094.6749 | 1264588.363
126 | 2692091.1993 | 1264592.0262
127 | 2692096.9509 | 1264585.9641
128 | 2692084.2974 | 1264603.816
129 | 2692107.9491 | 1264596.7961
130 | 2692098.2768 | 1264584.5666
131 | 2692079.5186 | 1264609.3671
132 | 2692110.2732 | 1264599.0851
133 | 2692110.512 | 1264599.3202
134 | 2692109.0431 | 1264567.0298
135 | 2692110.6212 | 1264599.4278
136 | 2692111.9284 | 1264563.4763
137 | 2692120.1246 | 1264552.6769
138 | 2692123.3728 | 1264548.3971
139 | 2692126.7092 | 1264544.001
140 | 2692114.5839 | 1264603.3306
141 | 2692151.3342 | 1264693.5429
142 | 2691884.7114 | 1264608.2673
143 | 2692161.3714 | 1264578.4478
144 | 2692153.8279 | 1264589.5097
145 | 2692150.9169 | 1264593.7783
146 | 2692150.1684 | 1264594.8759
147 | 2692145.2897 | 1264602.0302
148 | 2692018.7837 | 1264546.2818

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97262 | -0.52907 | 0.00043668 | 0.00010944
1 | 0.97239 | -0.53351 | 0.001226 | 0.00030726
2 | 0.97294 | -0.52262 | 0.0010333 | 0.00025897
3 | 0.97239 | -0.53356 | 0.00084859 | 0.00021268
4 | 0.97305 | -0.52046 | 0.0015326 | 0.0003841
5 | 0.97382 | -0.50515 | 0.0049117 | 0.001231
6 | 0.98627 | -0.26206 | 0.00017472 | 4.3789e-05
7 | 0.98242 | -0.33664 | 0.00028373 | 7.1108e-05
8 | 0.98659 | -0.25578 | 0.00062357 | 0.00015628
9 | 0.9813 | -0.35832 | 0 | 0
10 | 0.97852 | -0.41272 | 0.0072547 | 0.0018182
11 | 0.97835 | -0.41605 | 0 | 0
12 | 0.98683 | -0.25113 | 0.00035372 | 8.8652e-05
13 | 0.99023 | -0.18592 | 0.00019596 | 4.9113e-05
14 | 0.97797 | -0.42361 | 0 | 0
15 | 0.97425 | -0.49673 | 0.0032836 | 0.00082294
16 | 0.97461 | -0.48964 | 0 | 0
17 | 0.97415 | -0.49876 | 0 | 0
18 | 0.97683 | -0.44595 | 0.0014376 | 0.00036029
19 | 0.9905 | -0.18076 | 0.0006765 | 0.00016955
20 | 0.97754 | -0.4328 | 0.0081666 | 0.0020467
21 | 0.97796 | -0.42454 | 0.002232 | 0.00055939
22 | 0.97707 | -0.44216 | 0 | 0
23 | 0.97819 | -0.41998 | 0.0022244 | 0.00055748
24 | 0.97634 | -0.45643 | 0.0063396 | 0.0015889
25 | 0.97691 | -0.44521 | 0.0040789 | 0.0010223
26 | 0.97864 | -0.41129 | 0.0027455 | 0.00068809
27 | 0.97612 | -0.46073 | 0 | 0
28 | 0.97681 | -0.44716 | 0.0033006 | 0.00082722
29 | 0.97889 | -0.40641 | 0.0061523 | 0.0015419
30 | 0.97588 | -0.46541 | 0 | 0
31 | 0.97681 | -0.44727 | 0.0017023 | 0.00042664
32 | 0.97895 | -0.40524 | 0.002286 | 0.00057292
33 | 0.97587 | -0.46561 | 0.0016023 | 0.00040157
34 | 0.97564 | -0.47019 | 0 | 0
35 | 0.97558 | -0.47141 | 0.0066727 | 0.0016723
36 | 0.9839 | -0.30867 | 0 | 0
37 | 0.98376 | -0.31129 | 0.00059975 | 0.00015031
38 | 0.98391 | -0.30833 | 0 | 0
39 | 0.98408 | -0.30516 | 0.0011879 | 0.00029772
40 | 0.98358 | -0.31481 | 0.0062939 | 0.0015774
41 | 0.98407 | -0.30519 | 0.0025662 | 0.00064316
42 | 0.98414 | -0.30383 | 0 | 0
43 | 0.98433 | -0.30019 | 0.0022843 | 0.0005725
44 | 0.9947 | -0.10077 | 0.001653 | 0.00041428
45 | 0.99541 | -0.087082 | 0.0013708 | 0.00034355
46 | 0.99394 | -0.11513 | 0.0015566 | 0.00039013
47 | 0.99677 | -0.061157 | 0 | 0
48 | 0.9921 | -0.15051 | 0 | 0
49 | 0.99642 | -0.067879 | 0.0015719 | 0.00039394
50 | 0.99753 | -0.046777 | 0.0016976 | 0.00042546
51 | 0.99157 | -0.16059 | 0.0016057 | 0.00040244
52 | 0.99625 | -0.07107 | 0.0018914 | 0.00047404
53 | 0.99858 | -0.026837 | 0.0020443 | 0.00051236
54 | 0.99155 | -0.161 | 0.0017836 | 0.00044701
55 | 0.98128 | -0.36026 | 0.0094409 | 0.0023661
56 | 0.98152 | -0.35573 | 0.0016615 | 0.00041642
57 | 0.9958 | -0.079645 | 0 | 0
58 | 0.99983 | -0.0031911 | 0.0022452 | 0.00056271
59 | 0.98969 | -0.1968 | 0.0014773 | 0.00037023
60 | 0.98152 | -0.35571 | 0.0019615 | 0.00049159
61 | 1 | 0 | -0.32077 | -0.081691
62 | 0.99889 | -0.020994 | 0 | 0
63 | 0.99542 | -0.086893 | 0.0059437 | 0.0014896
64 | 0.99887 | -0.021494 | 0.0018834 | 0.00047203
65 | 0.9938 | -0.11778 | 0.014229 | 0.0035661
66 | 0.9988 | -0.022683 | 0.0023376 | 0.00058586
67 | 0.99161 | -0.15983 | 0 | 0
68 | 0.99871 | -0.024418 | 0.0020939 | 0.00052478
69 | 0.99132 | -0.16536 | 0 | 0
70 | 0.99148 | -0.16229 | 0.0045515 | 0.0011407
71 | 0.99871 | -0.02446 | 0.0015365 | 0.00038508
72 | 0.98919 | -0.20617 | 0.014406 | 0.0036105
73 | 0.99578 | -0.079954 | 0.0015266 | 0.0003826
74 | 0.98759 | -0.23709 | 0 | 0
75 | 0.99389 | -0.11602 | 0 | 0
76 | 0.99277 | -0.13719 | 0.00025689 | 6.4382e-05
77 | 0.9844 | -0.2989 | 0 | 0
78 | 0.98283 | -0.32944 | 0.0043744 | 0.0010963
79 | 0.97994 | -0.38585 | 0.0022665 | 0.00056804
80 | 0.98015 | -0.38168 | 0.0063965 | 0.0016031
81 | 0.97972 | -0.39009 | 0.0043696 | 0.0010951
82 | 0.98187 | -0.34808 | 0.0060687 | 0.001521
83 | 0.98589 | -0.27002 | 0.0049121 | 0.0012311
84 | 0.98737 | -0.24143 | 0.0024993 | 0.00062638
85 | 0.9917 | -0.15767 | 0 | 0
86 | 0.98683 | -0.25234 | 0.0028895 | 0.00072418
87 | 0.98696 | -0.24988 | 0 | 0
88 | 0.98739 | -0.24153 | 0 | 0
89 | 0.98718 | -0.24556 | 0.0011554 | 0.00028956
90 | 0.98748 | -0.23964 | 0.0035577 | 0.00089164
91 | 0.99866 | -0.025388 | 0.0087721 | 0.0021985
92 | 0.98159 | -0.35424 | 0.001494 | 0.00037444
93 | 0.98167 | -0.35263 | 0.0018653 | 0.0004675
94 | 0.98177 | -0.35067 | 0.0017987 | 0.00045081
95 | 0.9887 | -0.21593 | 0 | 0
96 | 0.98187 | -0.34876 | 0.0093577 | 0.0023453
97 | 0.98208 | -0.34475 | 0 | 0
98 | 0.98248 | -0.33683 | 0.001812 | 0.00045412
99 | 0.98271 | -0.33233 | 0.0032072 | 0.00080379
100 | 0.98711 | -0.24701 | 0.00075745 | 0.00018984
101 | 0.98751 | -0.23908 | 0.0030857 | 0.00077334
102 | 0.98708 | -0.24744 | 0.00077843 | 0.00019509
103 | 0.98762 | -0.23703 | 0.0013715 | 0.00034373
104 | 0.98153 | -0.35538 | 0.0030971 | 0.00077621
105 | 0.98187 | -0.34876 | 0.0059502 | 0.0014912
106 | 0.98141 | -0.35788 | 0 | 0
107 | 0.98244 | -0.33769 | 0.0035251 | 0.00088346
108 | 0.98135 | -0.35898 | 0.0011769 | 0.00029495
109 | 0.9812 | -0.36201 | 0.001615 | 0.00040475
110 | 0.98325 | -0.32176 | 0 | 0
111 | 0.9813 | -0.3599 | 0.0034895 | 0.00087456
112 | 0.98118 | -0.36234 | 0.00090879 | 0.00022776
113 | 0.98454 | -0.29672 | 0.0015352 | 0.00038475
114 | 0.98258 | -0.33487 | 0 | 0
115 | 0.98116 | -0.36269 | 0.0010283 | 0.00025771
116 | 0.98494 | -0.2889 | 0.0018457 | 0.00046259
117 | 0.98193 | -0.34764 | 0 | 0
118 | 0.98248 | -0.33687 | 0.0022444 | 0.00056251
119 | 0.98537 | -0.28052 | 0.0016979 | 0.00042554
120 | 0.98108 | -0.36421 | 0.0078851 | 0.0019762
121 | 0.98246 | -0.33732 | 0.0021057 | 0.00052774
122 | 0.98245 | -0.3375 | 0.0021834 | 0.00054722
123 | 0.981 | -0.36577 | 0.0016274 | 0.00040787
124 | 0.98096 | -0.36659 | 0.0021669 | 0.00054306
125 | 0.98812 | -0.22719 | 0.0012245 | 0.00030689
126 | 0.98803 | -0.22906 | 0.0012684 | 0.00031789
127 | 0.98819 | -0.22589 | 0 | 0
128 | 0.98777 | -0.234 | 0.001684 | 0.00042205
129 | 0.98812 | -0.22727 | 0.0015338 | 0.00038441
130 | 0.98824 | -0.22496 | 0.0013599 | 0.00034082
131 | 0.98765 | -0.23634 | 0.0042461 | 0.0010642
132 | 0.98811 | -0.22747 | 0.00044364 | 0.00011119
133 | 0.98811 | -0.22749 | 0.00045561 | 0.00011419
134 | 0.98838 | -0.22227 | 0.0015607 | 0.00039115
135 | 0.98811 | -0.22749 | 0.00054783 | 0.0001373
136 | 0.98799 | -0.22967 | 0.0015241 | 0.00038199
137 | 0.98688 | -0.25124 | 0.0014548 | 0.00036461
138 | 0.98644 | -0.25967 | 0.0016629 | 0.00041676
139 | 0.98601 | -0.26816 | 0.0015389 | 0.00038569
140 | 0.9881 | -0.22769 | 0.0020203 | 0.00050634
141 | 0.98697 | -0.2497 | 0 | 0
142 | 0.99076 | -0.1758 | 0.0021182 | 0.00053086
143 | 0.98095 | -0.36685 | 0.0013727 | 0.00034403
144 | 0.98087 | -0.36838 | 0.0015296 | 0.00038334
145 | 0.98085 | -0.36883 | 0.00086345 | 0.0002164
146 | 0.98084 | -0.36892 | 0.0013974 | 0.00035022
147 | 0.98082 | -0.36931 | 0.0025007 | 0.00062673
148 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.002075 | 0.00051874 | -0.0020746 | -0.0005199 | 4.384e-07 | -1.1589e-06 | 0.0031741 | 0.0031747 | 0.0031747 | 0.97262 | -0.52907 | 0.97239 | -0.53351 | 0.87216
1 | -0.0025117 | -0.00062819 | 0.0025125 | 0.00062695 | 7.6931e-07 | -1.2331e-06 | 0.0038422 | 0.0038416 | 0.0038422 | 0.97262 | -0.52907 | 0.97294 | -0.52262 | 1.0556
2 | 0.00084859 | 0.00021264 | -0.00084859 | -0.00021268 | 2.0856e-09 | -3.9578e-08 | 0.0012986 | 0.0012986 | 0.0012986 | 0.97239 | -0.53351 | 0.97239 | -0.53356 | 0.35675
3 | -0.0035458 | -0.00088592 | 0.0035461 | 0.00088574 | 3.6459e-07 | -1.7744e-07 | 0.0054219 | 0.0054218 | 0.0054219 | 0.97294 | -0.52262 | 0.97305 | -0.52046 | 1.4895
4 | -0.0050787 | -0.0012698 | 0.0050824 | 0.0012702 | 3.6971e-06 | 3.3348e-07 | 0.0077654 | 0.0077647 | 0.0077654 | 0.97305 | -0.52046 | 0.97382 | -0.50515 | 2.1334
5 | -0.0099941 | -0.0025012 | 0.0099972 | 0.0025027 | 3.0424e-06 | 1.5141e-06 | 0.01527 | 0.01527 | 0.01527 | 0.97382 | -0.50515 | 0.97415 | -0.49876 | 4.195
6 | 0.022474 | 0.0057052 | -0.022394 | -0.0056561 | 8.0333e-05 | 4.9048e-05 | 0.033933 | 0.033934 | 0.033934 | 0.98627 | -0.26206 | 0.98242 | -0.33664 | 9.3225
7 | -0.022649 | -0.005749 | 0.022655 | 0.0057531 | 6.8475e-06 | 4.1831e-06 | 0.034197 | 0.034197 | 0.034197 | 0.98627 | -0.26206 | 0.98659 | -0.25578 | 9.3947
8 | 0.02211 | 0.005585 | -0.022087 | -0.005571 | 2.2947e-05 | 1.3997e-05 | 0.033504 | 0.033505 | 0.033505 | 0.98242 | -0.33664 | 0.9813 | -0.35832 | 9.2045
9 | -0.023279 | -0.0059094 | 0.023284 | 0.0059126 | 5.2087e-06 | 3.1898e-06 | 0.035137 | 0.035137 | 0.035137 | 0.98659 | -0.25578 | 0.98683 | -0.25113 | 9.6531
10 | 0.022087 | 0.005571 | -0.02203 | -0.005536 | 5.737e-05 | 3.5e-05 | 0.033505 | 0.033505 | 0.033505 | 0.9813 | -0.35832 | 0.97852 | -0.41272 | 9.2047
11 | 0.014775 | 0.0037178 | -0.014773 | -0.0037165 | 2.3485e-06 | 1.3473e-06 | 0.022473 | 0.022473 | 0.022473 | 0.97852 | -0.41272 | 0.97835 | -0.41605 | 6.174
12 | 0.014773 | 0.0037165 | -0.014767 | -0.0037134 | 5.3341e-06 | 3.0603e-06 | 0.022473 | 0.022473 | 0.022473 | 0.97835 | -0.41605 | 0.97797 | -0.42361 | 6.174
13 | -0.023638 | -0.0060013 | 0.023712 | 0.0060469 | 7.4417e-05 | 4.5628e-05 | 0.035671 | 0.03567 | 0.035671 | 0.98683 | -0.25113 | 0.99023 | -0.18592 | 9.7996
14 | -0.023908 | -0.006096 | 0.023914 | 0.0060996 | 5.9488e-06 | 3.6494e-06 | 0.035964 | 0.035964 | 0.035964 | 0.99023 | -0.18592 | 0.9905 | -0.18076 | 9.8803
15 | 0.014767 | 0.0037134 | -0.014751 | -0.0037044 | 1.5738e-05 | 9.031e-06 | 0.022473 | 0.022474 | 0.022474 | 0.97797 | -0.42361 | 0.97683 | -0.44595 | 6.1741
16 | -0.013282 | -0.0033261 | 0.013286 | 0.0033286 | 4.4847e-06 | 2.5082e-06 | 0.020285 | 0.020285 | 0.020285 | 0.97425 | -0.49673 | 0.97461 | -0.48964 | 5.5727
17 | 0.0099981 | 0.0025032 | -0.0099972 | -0.0025027 | 9.6388e-07 | 4.7962e-07 | 0.01527 | 0.01527 | 0.01527 | 0.97425 | -0.49673 | 0.97415 | -0.49876 | 4.195
18 | -0.013286 | -0.0033286 | 0.013314 | 0.0033441 | 2.7705e-05 | 1.5489e-05 | 0.020285 | 0.020284 | 0.020285 | 0.97461 | -0.48964 | 0.97683 | -0.44595 | 5.5727
19 | -0.024591 | -0.0062692 | 0.024597 | 0.0062728 | 5.8926e-06 | 3.6233e-06 | 0.036981 | 0.03698 | 0.036981 | 0.9905 | -0.18076 | 0.99076 | -0.1758 | 10.1595
20 | -0.031891 | -0.0080005 | 0.031903 | 0.0080083 | 1.2572e-05 | 7.8677e-06 | 0.048547 | 0.048547 | 0.048547 | 0.97754 | -0.4328 | 0.97796 | -0.42454 | 13.3371
21 | 0.023724 | 0.0059537 | -0.023714 | -0.0059472 | 1.0577e-05 | 6.4982e-06 | 0.036116 | 0.036116 | 0.036116 | 0.97754 | -0.4328 | 0.97707 | -0.44216 | 9.922
22 | -0.034135 | -0.0085677 | 0.034143 | 0.0085724 | 7.418e-06 | 4.6555e-06 | 0.051943 | 0.051943 | 0.051943 | 0.97796 | -0.42454 | 0.97819 | -0.41998 | 14.2701
23 | 0.01463 | 0.0036705 | -0.01462 | -0.0036648 | 9.9516e-06 | 5.7001e-06 | 0.022282 | 0.022282 | 0.022282 | 0.97707 | -0.44216 | 0.97634 | -0.45643 | 6.1215
24 | 0.0090836 | 0.0022767 | -0.0090823 | -0.0022761 | 1.322e-06 | 6.154e-07 | 0.013834 | 0.013834 | 0.013834 | 0.97707 | -0.44216 | 0.97691 | -0.44521 | 3.8005
25 | -0.036367 | -0.0091299 | 0.036382 | 0.0091393 | 1.5092e-05 | 9.4936e-06 | 0.055327 | 0.055327 | 0.055327 | 0.97819 | -0.41998 | 0.97864 | -0.41129 | 15.1996
26 | 0.0082804 | 0.002076 | -0.0082787 | -0.0020752 | 1.6932e-06 | 7.2922e-07 | 0.01262 | 0.01262 | 0.01262 | 0.97634 | -0.45643 | 0.97612 | -0.46073 | 3.4671
27 | 0.0050034 | 0.0012538 | -0.005003 | -0.0012538 | 4.634e-07 | 3.0221e-08 | 0.0076211 | 0.0076212 | 0.0076212 | 0.97691 | -0.44521 | 0.97681 | -0.44716 | 2.0937
28 | -0.039128 | -0.0098274 | 0.039137 | 0.0098332 | 9.1191e-06 | 5.7499e-06 | 0.059501 | 0.059501 | 0.059501 | 0.97864 | -0.41129 | 0.97889 | -0.40641 | 16.3465
29 | 0.0082787 | 0.0020752 | -0.0082769 | -0.0020744 | 1.8483e-06 | 7.9618e-07 | 0.01262 | 0.01262 | 0.01262 | 0.97612 | -0.46073 | 0.97588 | -0.46541 | 3.4672
30 | 0.0017023 | 0.0004266 | -0.0017023 | -0.00042664 | 9.2692e-09 | -4.0079e-08 | 0.0025932 | 0.0025932 | 0.0025932 | 0.97681 | -0.44716 | 0.97681 | -0.44727 | 0.71242
31 | -0.045289 | -0.011375 | 0.045292 | 0.011377 | 2.5104e-06 | 1.5889e-06 | 0.068853 | 0.068853 | 0.068853 | 0.97889 | -0.40641 | 0.97895 | -0.40524 | 18.9157
32 | 0.0016023 | 0.0004015 | -0.0016023 | -0.00040157 | 1.507e-08 | -7.4471e-08 | 0.0024431 | 0.0024432 | 0.0024432 | 0.97588 | -0.46541 | 0.97587 | -0.46561 | 0.6712
33 | 0.0066746 | 0.0016729 | -0.0066731 | -0.0016725 | 1.5197e-06 | 4.8391e-07 | 0.010177 | 0.010178 | 0.010178 | 0.97588 | -0.46541 | 0.97564 | -0.47019 | 2.796
34 | -0.047578 | -0.01195 | 0.047612 | 0.011971 | 3.4439e-05 | 2.182e-05 | 0.072328 | 0.072328 | 0.072328 | 0.97895 | -0.40524 | 0.97972 | -0.39009 | 19.8703
35 | 0.0066731 | 0.0016725 | -0.0066727 | -0.0016723 | 3.8683e-07 | 1.2322e-07 | 0.010178 | 0.010178 | 0.010178 | 0.97564 | -0.47019 | 0.97558 | -0.47141 | 2.796
36 | 0.0068956 | 0.0017283 | -0.0068947 | -0.001728 | 8.6068e-07 | 2.8286e-07 | 0.010429 | 0.010429 | 0.010429 | 0.9839 | -0.30867 | 0.98376 | -0.31129 | 2.8651
37 | -0.0068956 | -0.0017283 | 0.0068957 | 0.0017283 | 1.1114e-07 | 3.6519e-08 | 0.010429 | 0.010429 | 0.010429 | 0.9839 | -0.30867 | 0.98391 | -0.30833 | 2.865
38 | 0.006295 | 0.0015777 | -0.0062939 | -0.0015774 | 1.0546e-06 | 2.8118e-07 | 0.0095217 | 0.0095218 | 0.0095218 | 0.98376 | -0.31129 | 0.98358 | -0.31481 | 2.6159
39 | -0.0068957 | -0.0017283 | 0.0068967 | 0.0017287 | 1.0438e-06 | 3.4294e-07 | 0.010429 | 0.010429 | 0.010429 | 0.98391 | -0.30833 | 0.98408 | -0.30516 | 2.865
40 | -0.0080847 | -0.0020264 | 0.0080866 | 0.0020272 | 1.9118e-06 | 7.9001e-07 | 0.012225 | 0.012225 | 0.012225 | 0.98408 | -0.30516 | 0.98433 | -0.30019 | 3.3585
41 | -0.0025662 | -0.00064316 | 0.0025664 | 0.00064289 | 1.6554e-07 | -2.6656e-07 | 0.0038804 | 0.0038803 | 0.0038804 | 0.98407 | -0.30519 | 0.98414 | -0.30383 | 1.066
42 | -0.07392 | -0.018667 | 0.073938 | 0.018678 | 1.7475e-05 | 1.1136e-05 | 0.11182 | 0.11182 | 0.11182 | 0.98414 | -0.30383 | 0.9844 | -0.2989 | 30.719
43 | 0.071354 | 0.018024 | -0.071266 | -0.017969 | 8.7446e-05 | 5.5711e-05 | 0.10794 | 0.10794 | 0.10794 | 0.98414 | -0.30383 | 0.98283 | -0.32944 | 29.653
44 | -0.010371 | -0.0025997 | 0.010372 | 0.0026 | 6.3896e-07 | 3.2081e-07 | 0.015678 | 0.015678 | 0.015678 | 0.98433 | -0.30019 | 0.9844 | -0.2989 | 4.3071
45 | -0.12981 | -0.033018 | 0.1299 | 0.033072 | 8.569e-05 | 5.4763e-05 | 0.19437 | 0.19437 | 0.19437 | 0.9947 | -0.10077 | 0.99541 | -0.087082 | 53.3977
46 | 0.12816 | 0.032603 | -0.12807 | -0.032547 | 8.8607e-05 | 5.6625e-05 | 0.19189 | 0.1919 | 0.1919 | 0.9947 | -0.10077 | 0.99394 | -0.11513 | 52.7184
47 | -0.13127 | -0.033416 | 0.13144 | 0.033521 | 0.00016431 | 0.00010501 | 0.19642 | 0.19642 | 0.19642 | 0.99541 | -0.087082 | 0.99677 | -0.061157 | 53.9607
48 | 0.12652 | 0.032157 | -0.1263 | -0.032019 | 0.00021519 | 0.00013752 | 0.18956 | 0.18956 | 0.18956 | 0.99394 | -0.11513 | 0.9921 | -0.15051 | 52.0782
49 | 0.032114 | 0.0082129 | -0.032103 | -0.0082063 | 1.0442e-05 | 6.5255e-06 | 0.047999 | 0.047999 | 0.047999 | 0.99677 | -0.061157 | 0.99642 | -0.067879 | 13.1866
50 | -0.16355 | -0.041734 | 0.16366 | 0.041806 | 0.0001137 | 7.2502e-05 | 0.24442 | 0.24442 | 0.24442 | 0.99677 | -0.061157 | 0.99753 | -0.046777 | 33.5736
51 | 0.1263 | 0.032019 | -0.12624 | -0.03198 | 6.1152e-05 | 3.9078e-05 | 0.18956 | 0.18956 | 0.18956 | 0.9921 | -0.15051 | 0.99157 | -0.16059 | 52.0782
52 | 0.030532 | 0.0078124 | -0.030527 | -0.0078094 | 4.7159e-06 | 2.9396e-06 | 0.045652 | 0.045652 | 0.045652 | 0.99642 | -0.067879 | 0.99625 | -0.07107 | 12.5417
53 | -0.16536 | -0.042232 | 0.16552 | 0.042334 | 0.00015955 | 0.00010175 | 0.24695 | 0.24695 | 0.24695 | 0.99753 | -0.046777 | 0.99858 | -0.026837 | 33.9214
54 | 0.12463 | 0.031578 | -0.12463 | -0.031576 | 2.4293e-06 | 1.5524e-06 | 0.18716 | 0.18716 | 0.18716 | 0.99157 | -0.16059 | 0.99155 | -0.161 | 51.4162
55 | 0.028635 | 0.0073354 | -0.028624 | -0.007328 | 1.1893e-05 | 7.3865e-06 | 0.042827 | 0.042827 | 0.042827 | 0.99625 | -0.07107 | 0.9958 | -0.079645 | 11.7656
56 | -0.16756 | -0.042846 | 0.16776 | 0.042968 | 0.00019195 | 0.00012242 | 0.24999 | 0.24999 | 0.24999 | 0.99858 | -0.026837 | 0.99983 | -0.0031911 | 34.3399
57 | 0.12285 | 0.031129 | -0.12264 | -0.030994 | 0.00021089 | 0.00013476 | 0.18448 | 0.18448 | 0.18448 | 0.99155 | -0.161 | 0.98969 | -0.1968 | 50.6809
58 | -0.0094409 | -0.0023661 | 0.009443 | 0.0023671 | 2.037e-06 | 9.6878e-07 | 0.014316 | 0.014316 | 0.014316 | 0.98128 | -0.36026 | 0.98152 | -0.35573 | 3.933
59 | -0.011105 | -0.0027835 | 0.011105 | 0.0027835 | 1.3986e-08 | 7.2874e-09 | 0.016835 | 0.016835 | 0.016835 | 0.98152 | -0.35573 | 0.98152 | -0.35571 | 4.625
60 | 0.0015266 | 0.00038247 | -0.0015266 | -0.0003826 | 2.2511e-08 | -1.3566e-07 | 0.0022812 | 0.0022812 | 0.0022812 | 0.9958 | -0.079645 | 0.99578 | -0.079954 | 0.62671
61 | 0.027097 | 0.0069456 | -0.027049 | -0.006916 | 4.7695e-05 | 2.952e-05 | 0.040546 | 0.040546 | 0.040546 | 0.9958 | -0.079645 | 0.99389 | -0.11602 | 11.1391
62 | -0.17 | -0.043531 | 0.17003 | 0.043548 | 2.6283e-05 | 1.6764e-05 | 0.25334 | 0.25334 | 0.25334 | 0.99983 | -0.0031911 | 1 | 0 | 34.7988
63 | 0.12116 | 0.030624 | -0.12105 | -0.030553 | 0.00011107 | 7.0968e-05 | 0.18226 | 0.18226 | 0.18226 | 0.98969 | -0.1968 | 0.9887 | -0.21593 | 50.0707
64 | -0.013066 | -0.0032751 | 0.013067 | 0.0032756 | 9.1439e-07 | 5.0666e-07 | 0.019809 | 0.019809 | 0.019809 | 0.98152 | -0.35571 | 0.98159 | -0.35424 | 5.442
65 | 0.1491 | 0.038143 | -0.14894 | -0.038046 | 0.00015134 | 9.6432e-05 | 0.22213 | 0.22213 | 0.22213 | 1 | 0 | 0.99889 | -0.020994 | 30.5127
66 | 0.13232 | 0.033879 | -0.1319 | -0.03361 | 0.00042088 | 0.00026899 | 0.19736 | 0.19736 | 0.19736 | 0.99889 | -0.020994 | 0.99542 | -0.086893 | 54.2211
67 | 0.016626 | 0.0041677 | -0.016626 | -0.0041674 | 3.9603e-07 | 2.3092e-07 | 0.024768 | 0.024768 | 0.024768 | 0.99889 | -0.020994 | 0.99887 | -0.021494 | 6.8043
68 | 0.12595 | 0.03212 | -0.12577 | -0.032 | 0.00018755 | 0.00011985 | 0.18848 | 0.18848 | 0.18848 | 0.99542 | -0.086893 | 0.9938 | -0.11778 | 51.7803
69 | 0.014742 | 0.0036954 | -0.014742 | -0.0036949 | 8.3493e-07 | 4.7394e-07 | 0.021962 | 0.021962 | 0.021962 | 0.99887 | -0.021494 | 0.9988 | -0.022683 | 6.0335
70 | 0.11154 | 0.028434 | -0.11131 | -0.02829 | 0.00022585 | 0.00014427 | 0.16718 | 0.16718 | 0.16718 | 0.9938 | -0.11778 | 0.99161 | -0.15983 | 45.9274
71 | 0.012404 | 0.0031091 | -0.012403 | -0.0031085 | 1.0252e-06 | 5.5138e-07 | 0.018479 | 0.01848 | 0.01848 | 0.9988 | -0.022683 | 0.99871 | -0.024418 | 5.0768
72 | 0.10676 | 0.027149 | -0.10673 | -0.027131 | 2.8481e-05 | 1.819e-05 | 0.16034 | 0.16034 | 0.16034 | 0.99161 | -0.15983 | 0.99132 | -0.16536 | 44.0508
73 | 0.004552 | 0.0011407 | -0.0045515 | -0.0011407 | 5.3544e-07 | -5.2015e-08 | 0.0068308 | 0.0068309 | 0.0068309 | 0.99161 | -0.15983 | 0.99148 | -0.16229 | 1.8766
74 | 0.010309 | 0.0025838 | -0.010309 | -0.0025837 | 2.0663e-08 | 1.0168e-08 | 0.01536 | 0.01536 | 0.01536 | 0.99871 | -0.024418 | 0.99871 | -0.02446 | 4.2197
75 | 0.10673 | 0.027131 | -0.10652 | -0.026997 | 0.00020931 | 0.00013368 | 0.16034 | 0.16034 | 0.16034 | 0.99132 | -0.16536 | 0.98919 | -0.20617 | 44.0508
76 | 0.0087725 | 0.0021987 | -0.0087721 | -0.0021985 | 3.8796e-07 | 1.6906e-07 | 0.01307 | 0.013071 | 0.013071 | 0.99871 | -0.02446 | 0.99866 | -0.025388 | 3.5908
77 | 0.092116 | 0.023387 | -0.091979 | -0.0233 | 0.00013681 | 8.7315e-05 | 0.13867 | 0.13867 | 0.13867 | 0.98919 | -0.20617 | 0.98759 | -0.23709 | 38.0974
78 | 0.0024998 | 0.00062547 | -0.0024993 | -0.00062638 | 5.168e-07 | -9.1209e-07 | 0.0037661 | 0.0037666 | 0.0037666 | 0.98759 | -0.23709 | 0.98737 | -0.24143 | 1.0348
79 | 0.089479 | 0.022674 | -0.089338 | -0.022584 | 0.00014132 | 9.0183e-05 | 0.13491 | 0.13491 | 0.13491 | 0.98759 | -0.23709 | 0.98589 | -0.27002 | 37.0628
80 | 0.027049 | 0.006916 | -0.027022 | -0.0068989 | 2.7671e-05 | 1.7128e-05 | 0.040546 | 0.040546 | 0.040546 | 0.99389 | -0.11602 | 0.99277 | -0.13719 | 11.1391
81 | 0.026765 | 0.0068345 | -0.026738 | -0.0068182 | 2.6465e-05 | 1.6372e-05 | 0.040161 | 0.040162 | 0.040162 | 0.99277 | -0.13719 | 0.9917 | -0.15767 | 11.0334
82 | -0.084309 | -0.021278 | 0.084426 | 0.021353 | 0.00011681 | 7.4511e-05 | 0.12749 | 0.12749 | 0.12749 | 0.9844 | -0.2989 | 0.98589 | -0.27002 | 35.026
83 | 0.066892 | 0.016872 | -0.066832 | -0.016834 | 5.9653e-05 | 3.7982e-05 | 0.10131 | 0.10131 | 0.10131 | 0.98283 | -0.32944 | 0.98187 | -0.34808 | 27.8335
84 | -0.054259 | -0.013641 | 0.054269 | 0.013648 | 1.0793e-05 | 6.8539e-06 | 0.082406 | 0.082406 | 0.082406 | 0.97994 | -0.38585 | 0.98015 | -0.38168 | 22.6391
85 | 0.051992 | 0.013073 | -0.051982 | -0.013067 | 1.0518e-05 | 6.6747e-06 | 0.078964 | 0.078965 | 0.078965 | 0.97994 | -0.38585 | 0.97972 | -0.39009 | 21.6935
86 | -0.060666 | -0.015251 | 0.060763 | 0.015313 | 9.751e-05 | 6.2019e-05 | 0.092117 | 0.092117 | 0.092117 | 0.98015 | -0.38168 | 0.98187 | -0.34808 | 25.3069
87 | 0.026738 | 0.0068182 | -0.026715 | -0.0068037 | 2.3389e-05 | 1.447e-05 | 0.040162 | 0.040162 | 0.040162 | 0.9917 | -0.15767 | 0.99076 | -0.1758 | 11.0334
88 | -0.0028895 | -0.00072418 | 0.0028898 | 0.00072378 | 3.3857e-07 | -3.9106e-07 | 0.004357 | 0.0043568 | 0.004357 | 0.98683 | -0.25234 | 0.98696 | -0.24988 | 1.197
89 | -0.0028898 | -0.00072378 | 0.0028899 | 0.00072376 | 2.5319e-08 | -2.9253e-08 | 0.0043568 | 0.0043568 | 0.0043568 | 0.98696 | -0.24988 | 0.98697 | -0.2497 | 1.1969
90 | 0.0055829 | 0.001398 | -0.0055818 | -0.0013978 | 1.0692e-06 | 1.6918e-07 | 0.0084131 | 0.0084133 | 0.0084133 | 0.98739 | -0.24153 | 0.98718 | -0.24556 | 2.3113
91 | -0.0055829 | -0.001398 | 0.0055834 | 0.0013981 | 5.0405e-07 | 7.9672e-08 | 0.0084131 | 0.008413 | 0.0084131 | 0.98739 | -0.24153 | 0.98748 | -0.23964 | 2.3113
92 | 0.0044264 | 0.0011083 | -0.0044261 | -0.0011083 | 3.0634e-07 | -3.8559e-08 | 0.0066717 | 0.0066718 | 0.0066718 | 0.98718 | -0.24556 | 0.98711 | -0.24701 | 1.8329
93 | -0.0091411 | -0.0022897 | 0.0091413 | 0.0022898 | 2.4048e-07 | 1.1066e-07 | 0.013774 | 0.013774 | 0.013774 | 0.98748 | -0.23964 | 0.98751 | -0.23908 | 3.7841
94 | -0.014561 | -0.0036501 | 0.014562 | 0.0036507 | 1.1114e-06 | 6.3442e-07 | 0.022074 | 0.022074 | 0.022074 | 0.98159 | -0.35424 | 0.98167 | -0.35263 | 6.0642
95 | -0.016427 | -0.0041182 | 0.016429 | 0.0041191 | 1.537e-06 | 9.0011e-07 | 0.024901 | 0.024901 | 0.024901 | 0.98167 | -0.35263 | 0.98177 | -0.35067 | 6.8409
96 | -0.018228 | -0.0045699 | 0.018233 | 0.004573 | 5.1457e-06 | 3.0658e-06 | 0.027627 | 0.027627 | 0.027627 | 0.98177 | -0.35067 | 0.98208 | -0.34475 | 7.5899
97 | 0.092641 | 0.023426 | -0.092613 | -0.023408 | 2.8147e-05 | 1.7964e-05 | 0.1395 | 0.1395 | 0.1395 | 0.9887 | -0.21593 | 0.98838 | -0.22227 | 38.3243
98 | 0.028408 | 0.0071272 | -0.028396 | -0.0071196 | 1.2218e-05 | 7.591e-06 | 0.042757 | 0.042757 | 0.042757 | 0.9887 | -0.21593 | 0.98824 | -0.22496 | 11.7465
99 | -0.0093577 | -0.0023453 | 0.0093595 | 0.0023461 | 1.7898e-06 | 8.4524e-07 | 0.014182 | 0.014181 | 0.014182 | 0.98187 | -0.34876 | 0.98208 | -0.34475 | 3.896
100 | -0.027592 | -0.0069191 | 0.027603 | 0.0069256 | 1.0418e-05 | 6.4663e-06 | 0.041809 | 0.041809 | 0.041809 | 0.98208 | -0.34475 | 0.98248 | -0.33683 | 11.4859
101 | -0.029415 | -0.0073797 | 0.029421 | 0.0073836 | 6.3105e-06 | 3.9314e-06 | 0.044553 | 0.044553 | 0.044553 | 0.98248 | -0.33683 | 0.98271 | -0.33233 | 12.2398
102 | -0.032628 | -0.0081874 | 0.032645 | 0.0081977 | 1.6451e-05 | 1.0301e-05 | 0.049409 | 0.049409 | 0.049409 | 0.98271 | -0.33233 | 0.98325 | -0.32176 | 13.5739
103 | 0.0036687 | 0.00091845 | -0.0036686 | -0.00091849 | 7.4293e-08 | -3.5265e-08 | 0.00553 | 0.00553 | 0.00553 | 0.98711 | -0.24701 | 0.98708 | -0.24744 | 1.5192
104 | -0.012227 | -0.0030632 | 0.012228 | 0.0030638 | 1.1985e-06 | 6.4659e-07 | 0.018424 | 0.018424 | 0.018424 | 0.98751 | -0.23908 | 0.98762 | -0.23703 | 5.0614
105 | 0.0028902 | 0.0007234 | -0.0028899 | -0.00072376 | 3.1091e-07 | -3.5932e-07 | 0.0043566 | 0.0043568 | 0.0043568 | 0.98708 | -0.24744 | 0.98697 | -0.2497 | 1.1969
106 | -0.0136 | -0.0034075 | 0.0136 | 0.0034078 | 4.4542e-07 | 2.4886e-07 | 0.02049 | 0.02049 | 0.02049 | 0.98762 | -0.23703 | 0.98765 | -0.23634 | 5.6291
107 | -0.011318 | -0.0028356 | 0.011321 | 0.0028375 | 3.5694e-06 | 1.8756e-06 | 0.017157 | 0.017157 | 0.017157 | 0.98153 | -0.35538 | 0.98187 | -0.34876 | 4.7136
108 | 0.0082206 | 0.0020594 | -0.0082196 | -0.002059 | 9.7885e-07 | 4.1406e-07 | 0.012462 | 0.012462 | 0.012462 | 0.98153 | -0.35538 | 0.98141 | -0.35788 | 3.4237
109 | -0.017271 | -0.0043287 | 0.017281 | 0.0043341 | 9.1178e-06 | 5.3863e-06 | 0.026175 | 0.026175 | 0.026175 | 0.98187 | -0.34876 | 0.98244 | -0.33769 | 7.1908
110 | 0.0046668 | 0.0011694 | -0.0046666 | -0.0011694 | 2.4511e-07 | -8.0828e-09 | 0.0070758 | 0.0070758 | 0.0070758 | 0.98141 | -0.35788 | 0.98135 | -0.35898 | 1.9439
111 | 0.0035528 | 0.00088954 | -0.0035521 | -0.0008899 | 6.979e-07 | -3.6365e-07 | 0.0053864 | 0.0053867 | 0.0053867 | 0.98141 | -0.35788 | 0.9812 | -0.36201 | 1.4799
112 | -0.020806 | -0.0052176 | 0.020821 | 0.0052271 | 1.5803e-05 | 9.5759e-06 | 0.031514 | 0.031513 | 0.031514 | 0.98244 | -0.33769 | 0.98325 | -0.32176 | 8.6576
113 | 0.0034897 | 0.00087448 | -0.0034895 | -0.00087456 | 1.5239e-07 | -8.5835e-08 | 0.0052914 | 0.0052914 | 0.0052914 | 0.98135 | -0.35898 | 0.9813 | -0.3599 | 1.4537
114 | 0.0019371 | 0.00048515 | -0.0019371 | -0.00048525 | 3.0383e-08 | -9.9142e-08 | 0.0029376 | 0.0029376 | 0.0029376 | 0.9812 | -0.36201 | 0.98118 | -0.36234 | 0.80703
115 | -0.079389 | -0.019937 | 0.079484 | 0.019998 | 9.4986e-05 | 6.0568e-05 | 0.12016 | 0.12016 | 0.12016 | 0.98325 | -0.32176 | 0.98454 | -0.29672 | 33.0106
116 | 0.025923 | 0.0065124 | -0.025906 | -0.0065024 | 1.6209e-05 | 1.0018e-05 | 0.039236 | 0.039236 | 0.039236 | 0.98325 | -0.32176 | 0.98258 | -0.33487 | 10.7792
117 | 0.0010283 | 0.00025748 | -0.0010283 | -0.00025771 | 1.7011e-08 | -2.2472e-07 | 0.0015594 | 0.0015594 | 0.0015594 | 0.98118 | -0.36234 | 0.98116 | -0.36269 | 0.42842
118 | -0.081019 | -0.020383 | 0.081049 | 0.020402 | 3.0293e-05 | 1.9319e-05 | 0.12248 | 0.12248 | 0.12248 | 0.98454 | -0.29672 | 0.98494 | -0.2889 | 33.648
119 | 0.019372 | 0.0048648 | -0.01936 | -0.0048578 | 1.179e-05 | 7.0834e-06 | 0.029341 | 0.029341 | 0.029341 | 0.98258 | -0.33487 | 0.98193 | -0.34764 | 8.0607
120 | 0.0065343 | 0.0016376 | -0.0065337 | -0.0016374 | 6.2132e-07 | 1.8335e-07 | 0.0098955 | 0.0098955 | 0.0098955 | 0.98258 | -0.33487 | 0.98248 | -0.33687 | 2.7186
121 | -0.082895 | -0.020864 | 0.082928 | 0.020886 | 3.3211e-05 | 2.1183e-05 | 0.12527 | 0.12527 | 0.12527 | 0.98494 | -0.2889 | 0.98537 | -0.28052 | 34.414
122 | 0.01936 | 0.0048578 | -0.019345 | -0.0048486 | 1.5284e-05 | 9.1831e-06 | 0.029341 | 0.029341 | 0.029341 | 0.98193 | -0.34764 | 0.98108 | -0.36421 | 8.0607
123 | 0.0042892 | 0.0010749 | -0.0042891 | -0.0010749 | 9.2844e-08 | -1.4872e-08 | 0.0064963 | 0.0064963 | 0.0064963 | 0.98248 | -0.33687 | 0.98246 | -0.33732 | 1.7847
124 | -0.084626 | -0.021311 | 0.084676 | 0.021343 | 5.0024e-05 | 3.1911e-05 | 0.12783 | 0.12783 | 0.12783 | 0.98537 | -0.28052 | 0.98601 | -0.26816 | 35.1184
125 | 0.01146 | 0.0028724 | -0.011459 | -0.0028719 | 8.5299e-07 | 4.5085e-07 | 0.017382 | 0.017382 | 0.017382 | 0.98108 | -0.36421 | 0.981 | -0.36577 | 4.7752
126 | 0.0021834 | 0.00054717 | -0.0021834 | -0.00054722 | 1.855e-08 | -4.5404e-08 | 0.003307 | 0.003307 | 0.003307 | 0.98246 | -0.33732 | 0.98245 | -0.3375 | 0.90852
127 | 0.0098318 | 0.0024641 | -0.0098314 | -0.0024639 | 3.8508e-07 | 1.8816e-07 | 0.014913 | 0.014913 | 0.014913 | 0.981 | -0.36577 | 0.98096 | -0.36659 | 4.097
128 | 0.0076645 | 0.0019208 | -0.0076644 | -0.0019208 | 9.5684e-08 | 3.7407e-08 | 0.011626 | 0.011626 | 0.011626 | 0.98096 | -0.36659 | 0.98095 | -0.36685 | 3.194
129 | 0.020807 | 0.005217 | -0.020805 | -0.0052158 | 1.8592e-06 | 1.1252e-06 | 0.031334 | 0.031334 | 0.031334 | 0.98812 | -0.22719 | 0.98803 | -0.22906 | 8.6083
130 | -0.022032 | -0.0055239 | 0.022033 | 0.0055247 | 1.365e-06 | 8.3125e-07 | 0.033178 | 0.033178 | 0.033178 | 0.98812 | -0.22719 | 0.98819 | -0.22589 | 9.1149
131 | 0.019537 | 0.0048979 | -0.019532 | -0.0048952 | 4.5966e-06 | 2.7605e-06 | 0.029424 | 0.029424 | 0.029424 | 0.98803 | -0.22906 | 0.98777 | -0.234 | 8.0835
132 | 0.0050016 | 0.0012534 | -0.0050013 | -0.0012533 | 3.2835e-07 | 1.2395e-08 | 0.0075314 | 0.0075314 | 0.0075314 | 0.98819 | -0.22589 | 0.98812 | -0.22727 | 2.0691
133 | -0.027035 | -0.006778 | 0.027036 | 0.0067788 | 1.1972e-06 | 7.4154e-07 | 0.040709 | 0.040709 | 0.040709 | 0.98819 | -0.22589 | 0.98824 | -0.22496 | 11.1839
134 | 0.017848 | 0.0044731 | -0.017846 | -0.004472 | 1.9857e-06 | 1.1771e-06 | 0.026887 | 0.026887 | 0.026887 | 0.98777 | -0.234 | 0.98765 | -0.23634 | 7.3866
135 | 0.0034675 | 0.00086893 | -0.0034674 | -0.00086895 | 3.3353e-08 | -2.0438e-08 | 0.0052217 | 0.0052217 | 0.0052217 | 0.98812 | -0.22727 | 0.98811 | -0.22747 | 1.4345
136 | 0.0030238 | 0.00075777 | -0.0030238 | -0.00075777 | 2.6058e-09 | -2.6249e-09 | 0.0045536 | 0.0045536 | 0.0045536 | 0.98811 | -0.22747 | 0.98811 | -0.22749 | 1.251
137 | 0.0025682 | 0.00064358 | -0.0025682 | -0.00064358 | 8.5988e-10 | -1.4135e-09 | 0.0038675 | 0.0038675 | 0.0038675 | 0.98811 | -0.22749 | 0.98811 | -0.22749 | 1.0625
138 | 0.091052 | 0.023017 | -0.09102 | -0.022996 | 3.2293e-05 | 2.0609e-05 | 0.13715 | 0.13715 | 0.13715 | 0.98838 | -0.22227 | 0.98799 | -0.22967 | 37.6788
139 | 0.0020204 | 0.00050629 | -0.0020203 | -0.00050634 | 1.9307e-08 | -5.8886e-08 | 0.0030425 | 0.0030425 | 0.0030425 | 0.98811 | -0.22749 | 0.9881 | -0.22769 | 0.83585
140 | 0.089496 | 0.022614 | -0.089403 | -0.022555 | 9.2458e-05 | 5.9e-05 | 0.13486 | 0.13486 | 0.13486 | 0.98799 | -0.22967 | 0.98688 | -0.25124 | 37.0482
141 | 0.087948 | 0.022191 | -0.087913 | -0.022168 | 3.546e-05 | 2.2626e-05 | 0.13266 | 0.13266 | 0.13266 | 0.98688 | -0.25124 | 0.98644 | -0.25967 | 36.4456
142 | 0.08625 | 0.021751 | -0.086215 | -0.021729 | 3.5058e-05 | 2.2367e-05 | 0.13015 | 0.13015 | 0.13015 | 0.98644 | -0.25967 | 0.98601 | -0.26816 | 35.7564
143 | 0.0062917 | 0.0015767 | -0.0062913 | -0.0015766 | 4.5735e-07 | 1.2369e-07 | 0.009544 | 0.009544 | 0.009544 | 0.98095 | -0.36685 | 0.98087 | -0.36838 | 2.622
144 | 0.0047617 | 0.0011933 | -0.0047616 | -0.0011933 | 1.011e-07 | -5.0828e-10 | 0.0072236 | 0.0072237 | 0.0072237 | 0.98087 | -0.36838 | 0.98085 | -0.36883 | 1.9845
145 | 0.0038981 | 0.00097687 | -0.0038981 | -0.00097687 | 1.7423e-08 | -5.6172e-09 | 0.0059137 | 0.0059137 | 0.0059137 | 0.98085 | -0.36883 | 0.98084 | -0.36892 | 1.6247
146 | 0.0025007 | 0.00062665 | -0.0025007 | -0.00062673 | 4.6738e-08 | -7.9379e-08 | 0.0037938 | 0.0037938 | 0.0037938 | 0.98084 | -0.36892 | 0.98082 | -0.36931 | 1.0423

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32254 | 0.082133

## res_load
| p_mw | q_mvar
0 | 0.00043668 | 0.00010944
1 | 0.001226 | 0.00030726
2 | 0.0010333 | 0.00025897
3 | 0.00084859 | 0.00021268
4 | 0.0015326 | 0.0003841
5 | 0.0049117 | 0.001231
6 | 0.00017472 | 4.3789e-05
7 | 0.00028373 | 7.1108e-05
8 | 0.00062357 | 0.00015628
9 | 0.0072547 | 0.0018182
10 | 0.00035372 | 8.8652e-05
11 | 0.00019596 | 4.9113e-05
12 | 0.0032836 | 0.00082294
13 | 0.0014376 | 0.00036029
14 | 0.0006765 | 0.00016955
15 | 0.0081666 | 0.0020467
16 | 0.002232 | 0.00055939
17 | 0.0022244 | 0.00055748
18 | 0.0063396 | 0.0015889
19 | 0.0040789 | 0.0010223
20 | 0.0027455 | 0.00068809
21 | 0.0033006 | 0.00082722
22 | 0.0061523 | 0.0015419
23 | 0.0017023 | 0.00042664
24 | 0.002286 | 0.00057292
25 | 0.0016023 | 0.00040157
26 | 0.0066727 | 0.0016723
27 | 0.00059975 | 0.00015031
28 | 0.0011879 | 0.00029772
29 | 0.0062939 | 0.0015774
30 | 0.0025662 | 0.00064316
31 | 0.0022843 | 0.0005725
32 | 0.001653 | 0.00041428
33 | 0.0013708 | 0.00034355
34 | 0.0015566 | 0.00039013
35 | 0.0015719 | 0.00039394
36 | 0.0016976 | 0.00042546
37 | 0.0016057 | 0.00040244
38 | 0.0018914 | 0.00047404
39 | 0.0020443 | 0.00051236
40 | 0.0017836 | 0.00044701
41 | 0.0094409 | 0.0023661
42 | 0.0016615 | 0.00041642
43 | 0.0022452 | 0.00056271
44 | 0.0014773 | 0.00037023
45 | 0.0019615 | 0.00049159
46 | 0.0017666 | 0.00044275
47 | 0.0059437 | 0.0014896
48 | 0.0018834 | 0.00047203
49 | 0.014229 | 0.0035661
50 | 0.0023376 | 0.00058586
51 | 0.0020939 | 0.00052478
52 | 0.0045515 | 0.0011407
53 | 0.0015365 | 0.00038508
54 | 0.014406 | 0.0036105
55 | 0.0015266 | 0.0003826
56 | 0.00025689 | 6.4382e-05
57 | 0.0043744 | 0.0010963
58 | 0.0022665 | 0.00056804
59 | 0.0063965 | 0.0016031
60 | 0.0043696 | 0.0010951
61 | 0.0060687 | 0.001521
62 | 0.0049121 | 0.0012311
63 | 0.0024993 | 0.00062638
64 | 0.0028895 | 0.00072418
65 | 0.0011554 | 0.00028956
66 | 0.0035577 | 0.00089164
67 | 0.0087721 | 0.0021985
68 | 0.001494 | 0.00037444
69 | 0.0018653 | 0.0004675
70 | 0.0017987 | 0.00045081
71 | 0.0093577 | 0.0023453
72 | 0.001812 | 0.00045412
73 | 0.0032072 | 0.00080379
74 | 0.00075745 | 0.00018984
75 | 0.0030857 | 0.00077334
76 | 0.00077843 | 0.00019509
77 | 0.0013715 | 0.00034373
78 | 0.0030971 | 0.00077621
79 | 0.0059502 | 0.0014912
80 | 0.0035251 | 0.00088346
81 | 0.0011769 | 0.00029495
82 | 0.001615 | 0.00040475
83 | 0.0034895 | 0.00087456
84 | 0.00090879 | 0.00022776
85 | 0.0015352 | 0.00038475
86 | 0.0010283 | 0.00025771
87 | 0.0018457 | 0.00046259
88 | 0.0022444 | 0.00056251
89 | 0.0016979 | 0.00042554
90 | 0.0078851 | 0.0019762
91 | 0.0021057 | 0.00052774
92 | 0.0021834 | 0.00054722
93 | 0.0016274 | 0.00040787
94 | 0.0021669 | 0.00054306
95 | 0.0012245 | 0.00030689
96 | 0.0012684 | 0.00031789
97 | 0.001684 | 0.00042205
98 | 0.0015338 | 0.00038441
99 | 0.0013599 | 0.00034082
100 | 0.0042461 | 0.0010642
101 | 0.00044364 | 0.00011119
102 | 0.00045561 | 0.00011419
103 | 0.0015607 | 0.00039115
104 | 0.00054783 | 0.0001373
105 | 0.0015241 | 0.00038199
106 | 0.0014548 | 0.00036461
107 | 0.0016629 | 0.00041676
108 | 0.0015389 | 0.00038569
109 | 0.0020203 | 0.00050634
110 | 0.0021182 | 0.00053086
111 | 0.0013727 | 0.00034403
112 | 0.0015296 | 0.00038334
113 | 0.00086345 | 0.0002164
114 | 0.0013974 | 0.00035022
115 | 0.0025007 | 0.00062673

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1