## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2271-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2271-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2271-1_0_6_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_2271-1_0_6_node_74 | 0.4 | n |  | TRUE
4 | bus_LV_2271-1_0_6_node_75 | 0.4 | n |  | TRUE
5 | bus_LV_2271-1_0_6_node_73 | 0.4 | n |  | TRUE
6 | bus_LV_2271-1_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2271-1_0_6_node_119 | 0.4 | n |  | TRUE
8 | bus_LV_2271-1_0_6_node_2 | 0.4 | n |  | TRUE
9 | bus_LV_2271-1_0_6_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_2271-1_0_6_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_2271-1_0_6_node_85 | 0.4 | n |  | TRUE
12 | bus_LV_2271-1_0_6_node_81 | 0.4 | n |  | TRUE
13 | bus_LV_2271-1_0_6_node_86 | 0.4 | n |  | TRUE
14 | bus_LV_2271-1_0_6_node_90 | 0.4 | n |  | TRUE
15 | bus_LV_2271-1_0_6_node_88 | 0.4 | n |  | TRUE
16 | bus_LV_2271-1_0_6_node_82 | 0.4 | n |  | TRUE
17 | bus_LV_2271-1_0_6_node_89 | 0.4 | n |  | TRUE
18 | bus_LV_2271-1_0_6_node_130 | 0.4 | n |  | TRUE
19 | bus_LV_2271-1_0_6_node_131 | 0.4 | n |  | TRUE
20 | bus_LV_2271-1_0_6_node_92 | 0.4 | n |  | TRUE
21 | bus_LV_2271-1_0_6_node_134 | 0.4 | n |  | TRUE
22 | bus_LV_2271-1_0_6_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2271-1_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2271-1_0_6_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_2271-1_0_6_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_2271-1_0_6_node_8 | 0.4 | n |  | TRUE
27 | bus_LV_2271-1_0_6_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_2271-1_0_6_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_2271-1_0_6_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_2271-1_0_6_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_2271-1_0_6_node_113 | 0.4 | n |  | TRUE
32 | bus_LV_2271-1_0_6_node_114 | 0.4 | n |  | TRUE
33 | bus_LV_2271-1_0_6_node_115 | 0.4 | n |  | TRUE
34 | bus_LV_2271-1_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2271-1_0_6_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2271-1_0_6_node_14 | 0.4 | n |  | TRUE
37 | bus_LV_2271-1_0_6_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2271-1_0_6_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2271-1_0_6_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2271-1_0_6_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2271-1_0_6_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2271-1_0_6_node_108 | 0.4 | n |  | TRUE
43 | bus_LV_2271-1_0_6_node_136 | 0.4 | n |  | TRUE
44 | bus_LV_2271-1_0_6_node_109 | 0.4 | n |  | TRUE
45 | bus_LV_2271-1_0_6_node_129 | 0.4 | n |  | TRUE
46 | bus_LV_2271-1_0_6_node_120 | 0.4 | n |  | TRUE
47 | bus_LV_2271-1_0_6_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_2271-1_0_6_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_2271-1_0_6_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2271-1_0_6_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_2271-1_0_6_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_2271-1_0_6_node_87 | 0.4 | n |  | TRUE
53 | bus_LV_2271-1_0_6_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_2271-1_0_6_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_2271-1_0_6_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_2271-1_0_6_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_2271-1_0_6_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_2271-1_0_6_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_2271-1_0_6_node_66 | 0.4 | n |  | TRUE
60 | bus_LV_2271-1_0_6_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_2271-1_0_6_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_2271-1_0_6_node_64 | 0.4 | n |  | TRUE
63 | bus_LV_2271-1_0_6_node_36 | 0.4 | n |  | TRUE
64 | bus_LV_2271-1_0_6_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_2271-1_0_6_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_2271-1_0_6_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_2271-1_0_6_node_105 | 0.4 | n |  | TRUE
68 | bus_LV_2271-1_0_6_node_103 | 0.4 | n |  | TRUE
69 | bus_LV_2271-1_0_6_node_106 | 0.4 | n |  | TRUE
70 | bus_LV_2271-1_0_6_node_100 | 0.4 | n |  | TRUE
71 | bus_LV_2271-1_0_6_node_41 | 0.4 | n |  | TRUE
72 | bus_LV_2271-1_0_6_node_42 | 0.4 | n |  | TRUE
73 | bus_LV_2271-1_0_6_node_43 | 0.4 | n |  | TRUE
74 | bus_LV_2271-1_0_6_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_2271-1_0_6_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_2271-1_0_6_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_2271-1_0_6_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_2271-1_0_6_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2271-1_0_6_node_94 | 0.4 | n |  | TRUE
80 | bus_LV_2271-1_0_6_node_95 | 0.4 | n |  | TRUE
81 | bus_LV_2271-1_0_6_node_96 | 0.4 | n |  | TRUE
82 | bus_LV_2271-1_0_6_node_47 | 0.4 | n |  | TRUE
83 | bus_LV_2271-1_0_6_node_48 | 0.4 | n |  | TRUE
84 | bus_LV_2271-1_0_6_node_49 | 0.4 | n |  | TRUE
85 | bus_LV_2271-1_0_6_node_50 | 0.4 | n |  | TRUE
86 | bus_LV_2271-1_0_6_node_51 | 0.4 | n |  | TRUE
87 | bus_LV_2271-1_0_6_node_52 | 0.4 | n |  | TRUE
88 | bus_LV_2271-1_0_6_node_68 | 0.4 | n |  | TRUE
89 | bus_LV_2271-1_0_6_node_60 | 0.4 | n |  | TRUE
90 | bus_LV_2271-1_0_6_node_135 | 0.4 | n |  | TRUE
91 | bus_LV_2271-1_0_6_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_2271-1_0_6_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_2271-1_0_6_node_62 | 0.4 | n |  | TRUE
94 | bus_LV_2271-1_0_6_node_56 | 0.4 | n |  | TRUE
95 | bus_LV_2271-1_0_6_node_55 | 0.4 | n |  | TRUE
96 | bus_LV_2271-1_0_6_node_57 | 0.4 | n |  | TRUE
97 | bus_LV_2271-1_0_6_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_2271-1_0_6_node_65 | 0.4 | n |  | TRUE
99 | bus_LV_2271-1_0_6_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_2271-1_0_6_node_132 | 0.4 | n |  | TRUE
101 | bus_LV_2271-1_0_6_node_69 | 0.4 | n |  | TRUE
102 | bus_LV_2271-1_0_6_node_124 | 0.4 | n |  | TRUE
103 | bus_LV_2271-1_0_6_node_70 | 0.4 | n |  | TRUE
104 | bus_LV_2271-1_0_6_node_72 | 0.4 | n |  | TRUE
105 | bus_LV_2271-1_0_6_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_2271-1_0_6_node_76 | 0.4 | n |  | TRUE
107 | bus_LV_2271-1_0_6_node_77 | 0.4 | n |  | TRUE
108 | bus_LV_2271-1_0_6_node_78 | 0.4 | n |  | TRUE
109 | bus_LV_2271-1_0_6_node_79 | 0.4 | n |  | TRUE
110 | bus_LV_2271-1_0_6_node_80 | 0.4 | n |  | TRUE
111 | bus_LV_2271-1_0_6_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_2271-1_0_6_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_2271-1_0_6_node_83 | 0.4 | n |  | TRUE
114 | bus_LV_2271-1_0_6_node_84 | 0.4 | n |  | TRUE
115 | bus_LV_2271-1_0_6_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_2271-1_0_6_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_2271-1_0_6_node_99 | 0.4 | n |  | TRUE
118 | bus_LV_2271-1_0_6_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2271-1_0_6_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_2271-1_0_6_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_2271-1_0_6_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_2271-1_0_6_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_2271-1_0_6_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_2271-1_0_6_node_117 | 0.4 | n |  | TRUE
125 | bus_LV_2271-1_0_6_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_2271-1_0_6_node_142 | 0.4 | n |  | TRUE
127 | bus_LV_2271-1_0_6_node_140 | 0.4 | n |  | TRUE
128 | bus_LV_2271-1_0_6_node_141 | 0.4 | n |  | TRUE
129 | bus_LV_2271-1_0_6_node_138 | 0.4 | n |  | TRUE
130 | bus_LV_2271-1_0_6_node_121 | 0.4 | n |  | TRUE
131 | bus_LV_2271-1_0_6_node_123 | 0.4 | n |  | TRUE
132 | bus_LV_2271-1_0_6_node_133 | 0.4 | n |  | TRUE
133 | bus_LV_2271-1_0_6_node_128 | 0.4 | n |  | TRUE
134 | bus_LV_2271-1_0_6_node_125 | 0.4 | n |  | TRUE
135 | bus_LV_2271-1_0_6_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_2271-1_0_6_node_127 | 0.4 | n |  | TRUE
137 | bus_LV_2271-1_0_6_node_137 | 0.4 | n |  | TRUE
138 | bus_LV_2271-1_0_6_node_139 | 0.4 | n |  | TRUE
139 | bus_MV_379_0_node_217 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2271-1_0_6_load_0 | 0 | 0.0019578 | 0.00049066 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2271-1_0_6_load_5 | 2 | 0.00060454 | 0.00015151 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2271-1_0_6_load_74 | 3 | 0.0013028 | 0.00032652 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2271-1_0_6_load_75 | 4 | 0.0013454 | 0.0003372 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2271-1_0_6_load_73 | 5 | 0.0058425 | 0.0014643 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2271-1_0_6_load_119 | 7 | 0.0033318 | 0.00083502 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2271-1_0_6_load_4 | 10 | 0.0060158 | 0.0015077 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2271-1_0_6_load_81 | 12 | 0.0035959 | 0.00090123 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2271-1_0_6_load_88 | 15 | 0.0030616 | 0.00076731 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2271-1_0_6_load_130 | 18 | 0.0038969 | 0.00097664 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2271-1_0_6_load_131 | 19 | 0.0031653 | 0.00079329 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2271-1_0_6_load_92 | 20 | 0.0058988 | 0.0014784 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2271-1_0_6_load_134 | 21 | 0.0047629 | 0.0011937 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2271-1_0_6_load_19 | 22 | 0.0029418 | 0.00073728 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2271-1_0_6_load_17 | 23 | 0.0073998 | 0.0018546 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2271-1_0_6_load_9 | 24 | 0.0023491 | 0.00058874 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2271-1_0_6_load_11 | 25 | 0.0053892 | 0.0013507 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2271-1_0_6_load_8 | 26 | 0.0012892 | 0.0003231 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2271-1_0_6_load_13 | 29 | 0.0028324 | 0.00070987 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2271-1_0_6_load_113 | 31 | 0.0044824 | 0.0011234 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2271-1_0_6_load_114 | 32 | 0.0042966 | 0.0010768 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2271-1_0_6_load_115 | 33 | 0.0043092 | 0.00108 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2271-1_0_6_load_24 | 34 | 0.0035358 | 0.00088616 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2271-1_0_6_load_18 | 35 | 0.0031821 | 0.00079751 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2271-1_0_6_load_14 | 36 | 0.002071 | 0.00051904 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2271-1_0_6_load_20 | 37 | 0.0059309 | 0.0014864 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2271-1_0_6_load_25 | 40 | 0.0075981 | 0.0019043 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2271-1_0_6_load_23 | 41 | 0.0076637 | 0.0019207 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2271-1_0_6_load_136 | 43 | 0.0024284 | 0.00060861 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2271-1_0_6_load_129 | 45 | 0.0035704 | 0.00089483 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2271-1_0_6_load_120 | 46 | 0.0033991 | 0.00085191 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2271-1_0_6_load_26 | 47 | 0.005563 | 0.0013942 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2271-1_0_6_load_27 | 48 | 0.0015651 | 0.00039226 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2271-1_0_6_load_28 | 49 | 0.0018503 | 0.00046372 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2271-1_0_6_load_29 | 50 | 0.0055105 | 0.0013811 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2271-1_0_6_load_30 | 51 | 0.0030879 | 0.00077389 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2271-1_0_6_load_87 | 52 | 0.0058798 | 0.0014736 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2271-1_0_6_load_31 | 53 | 0.0020975 | 0.00052568 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2271-1_0_6_load_32 | 54 | 0.0039361 | 0.00098647 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2271-1_0_6_load_33 | 55 | 0.0022348 | 0.0005601 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2271-1_0_6_load_34 | 56 | 0.003433 | 0.0008604 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2271-1_0_6_load_58 | 58 | 0.0038172 | 0.00095668 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2271-1_0_6_load_66 | 59 | 0.002979 | 0.0007466 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2271-1_0_6_load_37 | 60 | 0.0027717 | 0.00069464 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2271-1_0_6_load_59 | 61 | 0.0049495 | 0.0012405 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2271-1_0_6_load_36 | 63 | 0.0041203 | 0.0010327 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2271-1_0_6_load_39 | 65 | 0.0034934 | 0.00087553 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2271-1_0_6_load_40 | 66 | 0.0040736 | 0.0010209 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2271-1_0_6_load_105 | 67 | 0.0017035 | 0.00042694 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2271-1_0_6_load_103 | 68 | 0.008511 | 0.0021331 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2271-1_0_6_load_106 | 69 | 0.001901 | 0.00047643 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2271-1_0_6_load_41 | 71 | 0.0023604 | 0.00059158 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2271-1_0_6_load_42 | 72 | 0.0034518 | 0.00086509 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2271-1_0_6_load_44 | 74 | 0.0022143 | 0.00055496 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2271-1_0_6_load_45 | 75 | 0.0048393 | 0.0012128 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2271-1_0_6_load_46 | 76 | 0.0060786 | 0.0015235 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2271-1_0_6_load_53 | 77 | 0.0045183 | 0.0011324 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2271-1_0_6_load_94 | 79 | 0.0093449 | 0.0023421 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2271-1_0_6_load_95 | 80 | 0.00071905 | 0.00018021 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2271-1_0_6_load_47 | 82 | 0.0050123 | 0.0012562 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2271-1_0_6_load_48 | 83 | 0.006617 | 0.0016584 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2271-1_0_6_load_51 | 86 | 0.010154 | 0.0025449 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2271-1_0_6_load_60 | 89 | 0.0058324 | 0.0014617 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2271-1_0_6_load_135 | 90 | 0.075391 | 0.018895 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2271-1_0_6_load_67 | 91 | 0.0056704 | 0.0014211 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2271-1_0_6_load_62 | 93 | 0.0061719 | 0.0015468 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2271-1_0_6_load_56 | 94 | 0.0022941 | 0.00057495 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2271-1_0_6_load_55 | 95 | 0.0022524 | 0.00056451 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2271-1_0_6_load_57 | 96 | 0.0032695 | 0.00081941 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2271-1_0_6_load_132 | 100 | 0.0049069 | 0.0012298 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2271-1_0_6_load_69 | 101 | 0.0032752 | 0.00082084 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2271-1_0_6_load_70 | 103 | 0.0033847 | 0.00084829 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2271-1_0_6_load_72 | 104 | 0.0043721 | 0.0010958 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2271-1_0_6_load_102 | 105 | 0.0026499 | 0.00066413 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2271-1_0_6_load_76 | 106 | 0.0016785 | 0.00042066 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2271-1_0_6_load_77 | 107 | 0.00066337 | 0.00016626 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2271-1_0_6_load_78 | 108 | 0.0023706 | 0.00059412 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2271-1_0_6_load_79 | 109 | 0.0028933 | 0.00072513 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2271-1_0_6_load_80 | 110 | 0.0028874 | 0.00072366 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2271-1_0_6_load_93 | 111 | 0.0017798 | 0.00044606 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2271-1_0_6_load_97 | 112 | 0.024012 | 0.0060179 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2271-1_0_6_load_83 | 113 | 0.0036764 | 0.0009214 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2271-1_0_6_load_84 | 114 | 0.0060115 | 0.0015066 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2271-1_0_6_load_91 | 115 | 0.0043362 | 0.0010867 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2271-1_0_6_load_101 | 116 | 0.0015494 | 0.00038831 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2271-1_0_6_load_99 | 117 | 0.0088247 | 0.0022117 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2271-1_0_6_load_104 | 118 | 0.0035891 | 0.00089952 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2271-1_0_6_load_110 | 119 | 0.0025095 | 0.00062895 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2271-1_0_6_load_98 | 120 | 0.0043178 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2271-1_0_6_load_111 | 121 | 0.00095702 | 0.00023985 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2271-1_0_6_load_112 | 122 | 0.0025095 | 0.00062895 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2271-1_0_6_load_117 | 124 | 0.0033166 | 0.00083121 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2271-1_0_6_load_142 | 126 | 0.0010616 | 0.00026606 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2271-1_0_6_load_141 | 128 | 0.0015006 | 0.0003761 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2271-1_0_6_load_121 | 130 | 0.0015141 | 0.00037948 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2271-1_0_6_load_123 | 131 | 0.0014388 | 0.0003606 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2271-1_0_6_load_133 | 132 | 0.0044103 | 0.0011053 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2271-1_0_6_load_128 | 133 | 0.0036214 | 0.00090761 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2271-1_0_6_load_125 | 134 | 0.0033876 | 0.000849 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2271-1_0_6_load_126 | 135 | 0.0019857 | 0.00049766 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2271-1_0_6_load_127 | 136 | 0.011482 | 0.0028776 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2271-1_0_6_load_139 | 138 | 0.0014322 | 0.00035894 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2271-1_0_6_line_0 |  | 0 | 1 | 0.0018018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2271-1_0_6_line_1 |  | 1 | 2 | 0.025363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2271-1_0_6_line_2 |  | 2 | 6 | 0.029255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2271-1_0_6_line_3 |  | 3 | 4 | 0.022595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2271-1_0_6_line_4 |  | 3 | 5 | 0.020422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2271-1_0_6_line_5 |  | 4 | 13 | 0.016791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2271-1_0_6_line_6 |  | 5 | 25 | 0.0097317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2271-1_0_6_line_7 |  | 6 | 7 | 0.015748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2271-1_0_6_line_8 |  | 7 | 19 | 0.040221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2271-1_0_6_line_9 |  | 8 | 9 | 0.006708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2271-1_0_6_line_10 |  | 8 | 10 | 0.00034487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2271-1_0_6_line_11 |  | 9 | 11 | 0.048978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2271-1_0_6_line_12 |  | 9 | 12 | 0.020959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2271-1_0_6_line_13 |  | 10 | 13 | 0.04028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2271-1_0_6_line_14 |  | 11 | 14 | 0.039774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2271-1_0_6_line_15 |  | 11 | 15 | 0.027483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2271-1_0_6_line_16 |  | 12 | 16 | 0.023339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2271-1_0_6_line_17 |  | 13 | 17 | 0.014138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2271-1_0_6_line_18 |  | 14 | 112 | 0.013089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2271-1_0_6_line_19 |  | 15 | 52 | 0.024479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2271-1_0_6_line_20 |  | 16 | 113 | 0.012477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2271-1_0_6_line_21 |  | 16 | 114 | 0.024568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2271-1_0_6_line_22 |  | 17 | 118 | 0.025116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2271-1_0_6_line_23 |  | 18 | 19 | 0.025643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2271-1_0_6_line_24 |  | 18 | 20 | 0.012593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2271-1_0_6_line_25 |  | 19 | 21 | 0.018328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2271-1_0_6_line_26 |  | 20 | 115 | 0.014722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2271-1_0_6_line_27 |  | 21 | 43 | 0.029654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2271-1_0_6_line_28 |  | 22 | 23 | 0.036301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2271-1_0_6_line_29 |  | 23 | 30 | 0.024784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2271-1_0_6_line_30 |  | 24 | 25 | 0.0075335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2271-1_0_6_line_31 |  | 24 | 26 | 0.028959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2271-1_0_6_line_32 |  | 26 | 27 | 0.009317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2271-1_0_6_line_33 |  | 27 | 28 | 0.028958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2271-1_0_6_line_34 |  | 28 | 29 | 0.022906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2271-1_0_6_line_35 |  | 30 | 35 | 0.012445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2271-1_0_6_line_36 |  | 30 | 36 | 0.036008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2271-1_0_6_line_37 |  | 31 | 32 | 0.015363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2271-1_0_6_line_38 |  | 31 | 33 | 0.011773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2271-1_0_6_line_39 |  | 32 | 34 | 0.010455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2271-1_0_6_line_40 |  | 33 | 35 | 0.0073196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2271-1_0_6_line_41 |  | 34 | 38 | 0.0065519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2271-1_0_6_line_42 |  | 37 | 38 | 0.037202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2271-1_0_6_line_43 |  | 37 | 39 | 0.014606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2271-1_0_6_line_44 |  | 38 | 41 | 0.019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2271-1_0_6_line_45 |  | 39 | 40 | 0.017254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2271-1_0_6_line_46 |  | 41 | 42 | 0.020337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2271-1_0_6_line_47 |  | 42 | 44 | 0.001165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2271-1_0_6_line_48 |  | 43 | 137 | 0.010475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2271-1_0_6_line_49 |  | 44 | 119 | 0.015849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2271-1_0_6_line_50 |  | 44 | 81 | 0.026424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2271-1_0_6_line_51 |  | 45 | 46 | 0.0027368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2271-1_0_6_line_52 |  | 46 | 69 | 0.033903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2271-1_0_6_line_53 |  | 47 | 48 | 0.050106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2271-1_0_6_line_54 |  | 47 | 49 | 0.007008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2271-1_0_6_line_55 |  | 48 | 50 | 0.039318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2271-1_0_6_line_56 |  | 49 | 51 | 0.016135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2271-1_0_6_line_57 |  | 51 | 52 | 0.0078751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2271-1_0_6_line_58 |  | 53 | 54 | 0.011349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2271-1_0_6_line_59 |  | 53 | 55 | 0.0066501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2271-1_0_6_line_60 |  | 54 | 56 | 0.0068171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2271-1_0_6_line_61 |  | 55 | 57 | 0.0075604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2271-1_0_6_line_62 |  | 56 | 58 | 0.017448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2271-1_0_6_line_63 |  | 57 | 59 | 0.015145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2271-1_0_6_line_64 |  | 57 | 60 | 0.01497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2271-1_0_6_line_65 |  | 58 | 61 | 0.0032376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2271-1_0_6_line_66 |  | 59 | 62 | 0.021645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2271-1_0_6_line_67 |  | 61 | 76 | 0.015121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2271-1_0_6_line_68 |  | 62 | 97 | 0.008897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2271-1_0_6_line_69 |  | 63 | 64 | 0.022936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2271-1_0_6_line_70 |  | 64 | 65 | 0.033635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2271-1_0_6_line_71 |  | 64 | 66 | 0.0075006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2271-1_0_6_line_72 |  | 65 | 67 | 0.021648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2271-1_0_6_line_73 |  | 66 | 68 | 0.009965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2271-1_0_6_line_74 |  | 67 | 69 | 0.013388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2271-1_0_6_line_75 |  | 68 | 70 | 0.021991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2271-1_0_6_line_76 |  | 70 | 105 | 0.018497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2271-1_0_6_line_77 |  | 70 | 120 | 0.0092986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2271-1_0_6_line_78 |  | 71 | 72 | 0.03077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2271-1_0_6_line_79 |  | 71 | 73 | 0.012699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2271-1_0_6_line_80 |  | 72 | 74 | 0.0043522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2271-1_0_6_line_81 |  | 73 | 75 | 0.020128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2271-1_0_6_line_82 |  | 73 | 76 | 0.038621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2271-1_0_6_line_83 |  | 74 | 77 | 0.0021257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2271-1_0_6_line_84 |  | 77 | 78 | 0.027373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2271-1_0_6_line_85 |  | 78 | 94 | 0.0087753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2271-1_0_6_line_86 |  | 79 | 80 | 0.024473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2271-1_0_6_line_87 |  | 80 | 81 | 0.021358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2271-1_0_6_line_88 |  | 82 | 83 | 0.0038195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2271-1_0_6_line_89 |  | 82 | 84 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2271-1_0_6_line_90 |  | 83 | 85 | 0.00242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2271-1_0_6_line_91 |  | 84 | 86 | 0.0082338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2271-1_0_6_line_92 |  | 84 | 87 | 0.032336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2271-1_0_6_line_93 |  | 85 | 88 | 0.043724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2271-1_0_6_line_94 |  | 86 | 89 | 0.0014344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2271-1_0_6_line_95 |  | 87 | 90 | 0.00695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2271-1_0_6_line_96 |  | 88 | 91 | 0.055565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2271-1_0_6_line_97 |  | 89 | 92 | 0.022538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2271-1_0_6_line_98 |  | 92 | 93 | 0.004338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2271-1_0_6_line_99 |  | 93 | 97 | 0.017505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2271-1_0_6_line_100 |  | 94 | 95 | 0.012227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2271-1_0_6_line_101 |  | 95 | 96 | 0.0068633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2271-1_0_6_line_102 |  | 97 | 98 | 0.012442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2271-1_0_6_line_103 |  | 98 | 99 | 0.009836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2271-1_0_6_line_104 |  | 98 | 100 | 0.020369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2271-1_0_6_line_105 |  | 99 | 101 | 0.013537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2271-1_0_6_line_106 |  | 100 | 102 | 0.028253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2271-1_0_6_line_107 |  | 101 | 103 | 0.010725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_2271-1_0_6_line_108 |  | 102 | 132 | 0.023628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2271-1_0_6_line_109 |  | 102 | 131 | 0.032517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2271-1_0_6_line_110 |  | 103 | 104 | 0.012261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2271-1_0_6_line_111 |  | 104 | 105 | 0.016825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2271-1_0_6_line_112 |  | 106 | 107 | 0.0034955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2271-1_0_6_line_113 |  | 106 | 108 | 0.0036165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2271-1_0_6_line_114 |  | 107 | 109 | 0.022689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2271-1_0_6_line_115 |  | 108 | 110 | 0.035337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2271-1_0_6_line_116 |  | 110 | 111 | 0.028644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2271-1_0_6_line_117 |  | 111 | 112 | 0.035086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2271-1_0_6_line_118 |  | 113 | 115 | 0.025169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2271-1_0_6_line_119 |  | 114 | 116 | 0.010191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2271-1_0_6_line_120 |  | 116 | 117 | 0.031133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2271-1_0_6_line_121 |  | 117 | 120 | 0.012906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2271-1_0_6_line_122 |  | 119 | 121 | 0.0030161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2271-1_0_6_line_123 |  | 121 | 122 | 0.0012358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2271-1_0_6_line_124 |  | 122 | 123 | 0.021917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2271-1_0_6_line_125 |  | 123 | 124 | 0.015666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2271-1_0_6_line_126 |  | 123 | 125 | 0.021818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2271-1_0_6_line_127 |  | 125 | 126 | 0.00846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2271-1_0_6_line_128 |  | 125 | 127 | 0.019218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2271-1_0_6_line_129 |  | 127 | 128 | 0.009548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2271-1_0_6_line_130 |  | 127 | 129 | 0.023839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2271-1_0_6_line_131 |  | 129 | 138 | 0.007346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2271-1_0_6_line_132 |  | 129 | 137 | 0.004608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2271-1_0_6_line_133 |  | 130 | 131 | 0.0049714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2271-1_0_6_line_134 |  | 132 | 133 | 0.012717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2271-1_0_6_line_135 |  | 133 | 135 | 0.010152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2271-1_0_6_line_136 |  | 134 | 135 | 0.0029398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2271-1_0_6_line_137 |  | 134 | 136 | 0.006599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2271-1_0_6_trafo_38 | 0.63 MVA 20/0.4 kV | 139 | 64 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2574888.7548 | 1197145.1659 | 2574886.9789 | 1197144.8614
1 | 2574888.7548 | 1197145.1659 | 2574892.7772 | 1197120.1243
2 | 2574919.9039 | 1197126.658 | 2574914.6577 | 1197123.3783 | 2574896.7372 | 1197118.1843 | 2574892.7772 | 1197120.1243
3 | 2574854.992 | 1197185.5514 | 2574837.158 | 1197171.6767
4 | 2574871.1101 | 1197198.0911 | 2574871.1101 | 1197198.0911 | 2574854.992 | 1197185.5514
5 | 2574825.1748 | 1197159.9311 | 2574835.906 | 1197170.7027 | 2574837.158 | 1197171.6767
6 | 2574871.1101 | 1197198.0911 | 2574879.4772 | 1197203.0608
7 | 2574921.3155 | 1197110.9769 | 2574919.9039 | 1197126.658
8 | 2574912.1888 | 1197071.8052 | 2574921.3155 | 1197110.9769
9 | 2574802.7917 | 1197126.074 | 2574799.264 | 1197120.3637
10 | 2574802.9853 | 1197126.3595 | 2574802.7917 | 1197126.074
11 | 2574799.264 | 1197120.3637 | 2574794.1047 | 1197112.4479 | 2574770.6102 | 1197080.6079
12 | 2574799.264 | 1197120.3637 | 2574804.0253 | 1197115.2074 | 2574813.2113 | 1197104.7211
13 | 2574825.1748 | 1197159.9311 | 2574818.8483 | 1197151.5755 | 2574808.7468 | 1197134.8536 | 2574802.9853 | 1197126.3595
14 | 2574738.1089 | 1197103.5135 | 2574747.3191 | 1197096.782 | 2574759.8019 | 1197087.6686 | 2574770.6102 | 1197080.6079
15 | 2574770.6102 | 1197080.6079 | 2574763.3993 | 1197068.4763 | 2574756.4426 | 1197057.0586
16 | 2574825.0164 | 1197084.6577 | 2574815.1979 | 1197102.4533 | 2574813.2113 | 1197104.7211
17 | 2574825.1748 | 1197159.9311 | 2574818.6677 | 1197164.6945 | 2574813.1262 | 1197167.2526
18 | 2574738.1089 | 1197103.5135 | 2574729.6555 | 1197093.5209
19 | 2574743.7056 | 1197036.1541 | 2574756.4426 | 1197057.0586
20 | 2574825.0164 | 1197084.6577 | 2574837.4126 | 1197083.2382
21 | 2574825.0164 | 1197084.6577 | 2574827.7085 | 1197060.2377
22 | 2574813.1262 | 1197167.2526 | 2574806.9747 | 1197171.4587 | 2574796.3435 | 1197157.3516
23 | 2574912.1888 | 1197071.8052 | 2574894.9085 | 1197076.4472 | 2574887.2217 | 1197077.4356
24 | 2574874.9089 | 1197076.3504 | 2574881.6782 | 1197078.1483 | 2574887.2217 | 1197077.4356
25 | 2574929.8894 | 1197067.0504 | 2574912.1888 | 1197071.8052
26 | 2574860.4552 | 1197073.691 | 2574860.4552 | 1197073.691 | 2574869.7299 | 1197074.9748 | 2574874.9089 | 1197076.3504
27 | 2574929.8894 | 1197067.0504 | 2574959.4707 | 1197064.9804
28 | 2574966.1775 | 1197181.1945 | 2575000.7338 | 1197192.3121
29 | 2575024.8046 | 1197195.6657 | 2575014.0619 | 1197196.6001 | 2575000.7338 | 1197192.3121
30 | 2574879.4772 | 1197203.0608 | 2574885.9542 | 1197206.9079
31 | 2574911.0932 | 1197221.2553 | 2574905.0648 | 1197218.2589 | 2574885.9542 | 1197206.9079
32 | 2574919.4364 | 1197225.4022 | 2574911.0932 | 1197221.2553
33 | 2574919.4364 | 1197225.4022 | 2574933.2107 | 1197231.7922 | 2574931.8531 | 1197236.7672 | 2574929.588 | 1197245.0813
34 | 2574929.588 | 1197245.0813 | 2574918.5963 | 1197265.1777
35 | 2575024.8046 | 1197195.6657 | 2575030.7091 | 1197184.7105
36 | 2575024.8046 | 1197195.6657 | 2575056.4342 | 1197212.8737
37 | 2575039.7676 | 1197167.9034 | 2575047.0567 | 1197154.3792
38 | 2575039.7676 | 1197167.9034 | 2575034.1819 | 1197178.2671
39 | 2575052.017 | 1197145.1758 | 2575047.0567 | 1197154.3792
40 | 2575034.1819 | 1197178.2671 | 2575030.7091 | 1197184.7105
41 | 2575055.1256 | 1197139.4082 | 2575052.017 | 1197145.1758
42 | 2575055.1256 | 1197139.4082 | 2575087.9855 | 1197156.8489
43 | 2575100.8873 | 1197163.6966 | 2575087.9855 | 1197156.8489
44 | 2575055.1256 | 1197139.4082 | 2575064.3333 | 1197122.3239
45 | 2575100.8873 | 1197163.6966 | 2575109.3992 | 1197148.6881
46 | 2575073.982 | 1197104.4215 | 2575064.3333 | 1197122.3239
47 | 2575073.982 | 1197104.4215 | 2575074.5566 | 1197103.4074
48 | 2574959.4707 | 1197064.9804 | 2574969.717 | 1197067.2941
49 | 2575074.5566 | 1197103.4074 | 2575060.5843 | 1197095.9269
50 | 2575091.2408 | 1197084.4052 | 2575083.8656 | 1197087.4488 | 2575074.5566 | 1197103.4074
51 | 2574968.3403 | 1197013.4041 | 2574967.3149 | 1197010.8667
52 | 2574942.7871 | 1196997.1577 | 2574961.6981 | 1196996.9676 | 2574967.3149 | 1197010.8667
53 | 2574702.9096 | 1196966.0444 | 2574703.599 | 1196967.2752 | 2574710.7689 | 1196980.463 | 2574727.8744 | 1197009.4813
54 | 2574731.4331 | 1197015.5185 | 2574727.8744 | 1197009.4813
55 | 2574702.9096 | 1196966.0444 | 2574683.6957 | 1196931.7415
56 | 2574739.6264 | 1197029.4179 | 2574731.4331 | 1197015.5185
57 | 2574743.7056 | 1197036.1541 | 2574740.3743 | 1197030.6868 | 2574739.6264 | 1197029.4179
58 | 2574888.7657 | 1196941.1588 | 2574899.213 | 1196945.5921
59 | 2574888.7657 | 1196941.1588 | 2574882.6441 | 1196938.561
60 | 2574905.4631 | 1196948.3134 | 2574901.9097 | 1196946.7365 | 2574899.213 | 1196945.5921
61 | 2574875.6843 | 1196935.6076 | 2574882.6441 | 1196938.561
62 | 2574921.4116 | 1196955.391 | 2574905.4631 | 1196948.3134
63 | 2574875.6843 | 1196935.6076 | 2574862.1072 | 1196928.8962
64 | 2574875.6843 | 1196935.6076 | 2574875.282 | 1196950.5717
65 | 2574921.4116 | 1196955.391 | 2574924.371 | 1196956.7042
66 | 2574842.704 | 1196919.3047 | 2574862.1072 | 1196928.8962
67 | 2574938.5204 | 1196961.9878 | 2574929.7776 | 1196959.1036 | 2574924.371 | 1196956.7042
68 | 2574838.3552 | 1196912.1747 | 2574840.2566 | 1196913.334 | 2574841.7033 | 1196915.0288 | 2574842.5498 | 1196917.0819 | 2574842.704 | 1196919.3047
69 | 2574874.119 | 1196997.8479 | 2574874.1833 | 1196991.433 | 2574874.6274 | 1196974.9185
70 | 2574874.119 | 1196997.8479 | 2574907.7527 | 1196997.5098
71 | 2574874.119 | 1196997.8479 | 2574866.6198 | 1196997.7042
72 | 2574907.7527 | 1196997.5098 | 2574929.3998 | 1196997.2922
73 | 2574866.6198 | 1196997.7042 | 2574856.6566 | 1196997.5132
74 | 2574929.3998 | 1196997.2922 | 2574942.7871 | 1196997.1577
75 | 2574834.6696 | 1196997.0918 | 2574856.6566 | 1196997.5132
76 | 2574834.6696 | 1196997.0918 | 2574834.3553 | 1196987.6102 | 2574834.2048 | 1196978.6014
77 | 2574834.6696 | 1196997.0918 | 2574833.6507 | 1197006.3344
78 | 2574980.3595 | 1196962.4848 | 2574992.867 | 1196934.3716
79 | 2574975.1975 | 1196974.0874 | 2574980.3595 | 1196962.4848
80 | 2574994.6361 | 1196930.3951 | 2574992.867 | 1196934.3716
81 | 2574975.1975 | 1196974.0874 | 2574989.1694 | 1196978.4311 | 2574994.5749 | 1196979.427
82 | 2574975.1975 | 1196974.0874 | 2574938.5204 | 1196961.9878
83 | 2574994.6361 | 1196930.3951 | 2574995.5002 | 1196928.4529
84 | 2575016.9451 | 1196928.9544 | 2575002.3796 | 1196921.1113 | 2574997.962 | 1196922.9197 | 2574995.5002 | 1196928.4529
85 | 2575016.9451 | 1196928.9544 | 2575015.4871 | 1196937.6077
86 | 2575083.7342 | 1197043.3014 | 2575077.4813 | 1197059.7494 | 2575080.8325 | 1197065.7544
87 | 2575091.2408 | 1197084.4052 | 2575080.8325 | 1197065.7544
88 | 2574862.4227 | 1196851.1591 | 2574864.0649 | 1196847.7107
89 | 2574857.3442 | 1196861.8229 | 2574862.4227 | 1196851.1591
90 | 2574865.1054 | 1196845.5258 | 2574864.0649 | 1196847.7107
91 | 2574857.3442 | 1196861.8229 | 2574853.5409 | 1196869.1257
92 | 2574833.855 | 1196867.4251 | 2574840.0614 | 1196868.9442 | 2574840.7292 | 1196866.54 | 2574842.2277 | 1196860.675 | 2574843.017 | 1196858.1814 | 2574857.3442 | 1196861.8229
93 | 2574865.1054 | 1196845.5258 | 2574871.4514 | 1196833.1812 | 2574885.8739 | 1196807.0285
94 | 2574852.8783 | 1196870.398 | 2574853.5409 | 1196869.1257
95 | 2574827.0844 | 1196865.775 | 2574833.855 | 1196867.4251
96 | 2574885.8739 | 1196807.0285 | 2574930.4652 | 1196840.1808
97 | 2574844.4895 | 1196891.2153 | 2574847.9905 | 1196879.7832 | 2574852.8783 | 1196870.398
98 | 2574844.4895 | 1196891.2153 | 2574843.2185 | 1196895.3629
99 | 2574838.3552 | 1196912.1747 | 2574839.929 | 1196906.0981 | 2574843.2185 | 1196895.3629
100 | 2575013.4556 | 1196949.6652 | 2575015.4871 | 1196937.6077
101 | 2575012.3153 | 1196956.4332 | 2575013.4556 | 1196949.6652
102 | 2574838.3552 | 1196912.1747 | 2574836.3347 | 1196911.683 | 2574834.2558 | 1196911.803 | 2574832.3014 | 1196912.5227 | 2574830.6463 | 1196913.7748 | 2574829.4347 | 1196915.4586 | 2574828.7651 | 1196917.4181
103 | 2574833.3074 | 1196925.2809 | 2574831.5593 | 1196924.3545 | 2574830.1444 | 1196922.993 | 2574829.1547 | 1196921.2963 | 2574828.682 | 1196919.3862 | 2574828.7651 | 1196917.4181
104 | 2574828.7651 | 1196917.4181 | 2574823.1023 | 1196914.7517 | 2574811.4934 | 1196907.2967 | 2574811.2388 | 1196907.1149
105 | 2574833.3074 | 1196925.2809 | 2574832.9414 | 1196934.1984 | 2574833.1181 | 1196938.807
106 | 2574788.2456 | 1196890.6972 | 2574811.2388 | 1196907.1149
107 | 2574833.1181 | 1196938.807 | 2574833.5289 | 1196949.5243
108 | 2574788.2456 | 1196890.6972 | 2574773.1897 | 1196908.9066
109 | 2574762.5988 | 1196870.6171 | 2574788.2456 | 1196890.6972
110 | 2574833.9238 | 1196961.7789 | 2574833.866 | 1196958.3186 | 2574833.5289 | 1196949.5243
111 | 2574833.9238 | 1196961.7789 | 2574834.2048 | 1196978.6014
112 | 2574665.9703 | 1197013.1342 | 2574664.8131 | 1197011.5195 | 2574663.8914 | 1197010.3248
113 | 2574665.9703 | 1197013.1342 | 2574668.0771 | 1197016.0737
114 | 2574650.0331 | 1196992.3605 | 2574663.8914 | 1197010.3248
115 | 2574668.0771 | 1197016.0737 | 2574688.6624 | 1197044.7953
116 | 2574688.6624 | 1197044.7953 | 2574694.4189 | 1197052.8271 | 2574706.2023 | 1197067.4276
117 | 2574729.6555 | 1197093.5209 | 2574729.2064 | 1197092.9901 | 2574706.5703 | 1197067.8836 | 2574706.2023 | 1197067.4276
118 | 2574860.4552 | 1197073.691 | 2574842.1528 | 1197082.6953 | 2574837.4126 | 1197083.2382
119 | 2574827.7085 | 1197060.2377 | 2574828.8252 | 1197050.1078
120 | 2574832.2366 | 1197019.1625 | 2574828.8252 | 1197050.1078
121 | 2574833.6507 | 1197006.3344 | 2574832.2366 | 1197019.1625
122 | 2575060.5843 | 1197095.9269 | 2575057.9253 | 1197094.5034
123 | 2575056.8358 | 1197093.9201 | 2575057.9253 | 1197094.5034
124 | 2575037.2541 | 1197084.0976 | 2575040.8634 | 1197085.6834 | 2575047.4422 | 1197088.8909 | 2575056.8358 | 1197093.9201
125 | 2575037.2541 | 1197084.0976 | 2575029.9166 | 1197097.947
126 | 2575016.2986 | 1197078.0044 | 2575018.2274 | 1197078.4521 | 2575027.7952 | 1197080.6243 | 2575034.7895 | 1197083.0074 | 2575037.2541 | 1197084.0976
127 | 2575016.2986 | 1197078.0044 | 2575013.2546 | 1197085.8992
128 | 2574997.521 | 1197073.6697 | 2575004.4434 | 1197075.2415 | 2575016.2986 | 1197078.0044
129 | 2574997.521 | 1197073.6697 | 2574994.543 | 1197082.7427
130 | 2574997.521 | 1197073.6697 | 2574994.3114 | 1197072.9384 | 2574979.2466 | 1197069.4442 | 2574974.2226 | 1197068.3202
131 | 2574974.2226 | 1197068.3202 | 2574972.4704 | 1197075.4537
132 | 2574974.2226 | 1197068.3202 | 2574969.717 | 1197067.2941
133 | 2574762.5988 | 1196870.6171 | 2574758.5907 | 1196867.676
134 | 2574765.0864 | 1196918.7071 | 2574773.1897 | 1196908.9066
135 | 2574758.6171 | 1196926.5315 | 2574765.0864 | 1196918.7071
136 | 2574756.7438 | 1196928.7971 | 2574758.6171 | 1196926.5315
137 | 2574752.5388 | 1196933.8829 | 2574756.7438 | 1196928.7971

## bus_geodata
| x | y | coords
0 | 2574886.9789 | 1197144.8614
1 | 2574888.7548 | 1197145.1659
2 | 2574892.7772 | 1197120.1242
3 | 2574854.992 | 1197185.5514
4 | 2574837.158 | 1197171.6767
5 | 2574871.1101 | 1197198.0911
6 | 2574919.9039 | 1197126.658
7 | 2574921.3155 | 1197110.9769
8 | 2574802.7917 | 1197126.0741
9 | 2574799.264 | 1197120.3637
10 | 2574802.9853 | 1197126.3595
11 | 2574770.6102 | 1197080.6079
12 | 2574813.2113 | 1197104.7211
13 | 2574825.1748 | 1197159.9311
14 | 2574738.1089 | 1197103.5135
15 | 2574756.4426 | 1197057.0586
16 | 2574825.0164 | 1197084.6577
17 | 2574813.1262 | 1197167.2526
18 | 2574887.2217 | 1197077.4356
19 | 2574912.1888 | 1197071.8052
20 | 2574874.9089 | 1197076.3504
21 | 2574929.8894 | 1197067.0504
22 | 2574966.1775 | 1197181.1945
23 | 2575000.7338 | 1197192.3121
24 | 2574885.9542 | 1197206.9079
25 | 2574879.4772 | 1197203.0608
26 | 2574911.0932 | 1197221.2553
27 | 2574919.4364 | 1197225.4022
28 | 2574929.588 | 1197245.0813
29 | 2574918.5963 | 1197265.1777
30 | 2575024.8046 | 1197195.6657
31 | 2575039.7676 | 1197167.9034
32 | 2575047.0567 | 1197154.3792
33 | 2575034.1819 | 1197178.2671
34 | 2575052.017 | 1197145.1758
35 | 2575030.7091 | 1197184.7105
36 | 2575056.4342 | 1197212.8737
37 | 2575087.9855 | 1197156.8489
38 | 2575055.1256 | 1197139.4082
39 | 2575100.8873 | 1197163.6966
40 | 2575109.3992 | 1197148.6881
41 | 2575064.3333 | 1197122.3239
42 | 2575073.982 | 1197104.4215
43 | 2574959.4707 | 1197064.9804
44 | 2575074.5566 | 1197103.4074
45 | 2574968.3403 | 1197013.4041
46 | 2574967.3149 | 1197010.8667
47 | 2574727.8744 | 1197009.4813
48 | 2574702.9096 | 1196966.0444
49 | 2574731.4331 | 1197015.5185
50 | 2574683.6957 | 1196931.7415
51 | 2574739.6264 | 1197029.4179
52 | 2574743.7056 | 1197036.1541
53 | 2574888.7657 | 1196941.1588
54 | 2574899.213 | 1196945.5921
55 | 2574882.6441 | 1196938.561
56 | 2574905.4631 | 1196948.3134
57 | 2574875.6843 | 1196935.6076
58 | 2574921.4116 | 1196955.391
59 | 2574862.1072 | 1196928.8962
60 | 2574875.282 | 1196950.5717
61 | 2574924.371 | 1196956.7042
62 | 2574842.704 | 1196919.3047
63 | 2574874.6274 | 1196974.9185
64 | 2574874.119 | 1196997.8479
65 | 2574907.7527 | 1196997.5098
66 | 2574866.6198 | 1196997.7042
67 | 2574929.3998 | 1196997.2922
68 | 2574856.6566 | 1196997.5132
69 | 2574942.7871 | 1196997.1577
70 | 2574834.6696 | 1196997.0918
71 | 2574980.3595 | 1196962.4848
72 | 2574992.867 | 1196934.3716
73 | 2574975.1975 | 1196974.0874
74 | 2574994.6361 | 1196930.3951
75 | 2574994.5749 | 1196979.427
76 | 2574938.5204 | 1196961.9878
77 | 2574995.5002 | 1196928.4529
78 | 2575016.9451 | 1196928.9544
79 | 2575083.7342 | 1197043.3014
80 | 2575080.8325 | 1197065.7544
81 | 2575091.2408 | 1197084.4052
82 | 2574862.4227 | 1196851.1591
83 | 2574864.0649 | 1196847.7107
84 | 2574857.3442 | 1196861.8229
85 | 2574865.1054 | 1196845.5258
86 | 2574853.5409 | 1196869.1257
87 | 2574833.855 | 1196867.4251
88 | 2574885.8739 | 1196807.0285
89 | 2574852.8783 | 1196870.398
90 | 2574827.0844 | 1196865.775
91 | 2574930.4652 | 1196840.1808
92 | 2574844.4895 | 1196891.2153
93 | 2574843.2185 | 1196895.3629
94 | 2575015.4871 | 1196937.6077
95 | 2575013.4556 | 1196949.6652
96 | 2575012.3153 | 1196956.4332
97 | 2574838.3552 | 1196912.1747
98 | 2574828.7651 | 1196917.4181
99 | 2574833.3074 | 1196925.2809
100 | 2574811.2388 | 1196907.1149
101 | 2574833.1181 | 1196938.807
102 | 2574788.2456 | 1196890.6972
103 | 2574833.5289 | 1196949.5243
104 | 2574833.9238 | 1196961.7789
105 | 2574834.2048 | 1196978.6014
106 | 2574665.9703 | 1197013.1342
107 | 2574663.8914 | 1197010.3248
108 | 2574668.0771 | 1197016.0737
109 | 2574650.0331 | 1196992.3605
110 | 2574688.6624 | 1197044.7953
111 | 2574706.2023 | 1197067.4276
112 | 2574729.6555 | 1197093.5209
113 | 2574837.4126 | 1197083.2382
114 | 2574827.7085 | 1197060.2377
115 | 2574860.4552 | 1197073.691
116 | 2574828.8252 | 1197050.1078
117 | 2574832.2366 | 1197019.1625
118 | 2574796.3436 | 1197157.3516
119 | 2575060.5843 | 1197095.9269
120 | 2574833.6507 | 1197006.3344
121 | 2575057.9253 | 1197094.5034
122 | 2575056.8358 | 1197093.9201
123 | 2575037.2541 | 1197084.0976
124 | 2575029.9166 | 1197097.947
125 | 2575016.2986 | 1197078.0044
126 | 2575013.2546 | 1197085.8992
127 | 2574997.521 | 1197073.6697
128 | 2574994.543 | 1197082.7427
129 | 2574974.2226 | 1197068.3202
130 | 2574758.5907 | 1196867.676
131 | 2574762.5988 | 1196870.6171
132 | 2574773.1897 | 1196908.9066
133 | 2574765.0864 | 1196918.7071
134 | 2574756.7438 | 1196928.7971
135 | 2574758.617 | 1196926.5315
136 | 2574752.5388 | 1196933.8829
137 | 2574969.717 | 1197067.2941
138 | 2574972.4704 | 1197075.4537
139 | 2574834.6696 | 1196997.0918

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98637 | -0.26024 | 0.0019578 | 0.00049066
1 | 0.98637 | -0.26018 | 0 | 0
2 | 0.98642 | -0.25929 | 0.00060454 | 0.00015151
3 | 0.98586 | -0.27107 | 0.0013028 | 0.00032652
4 | 0.98625 | -0.26337 | 0.0013454 | 0.0003372
5 | 0.98552 | -0.27755 | 0.0058425 | 0.0014643
6 | 0.98649 | -0.25794 | 0 | 0
7 | 0.98652 | -0.25722 | 0.0033318 | 0.00083502
8 | 0.98746 | -0.2398 | 0 | 0
9 | 0.98765 | -0.23621 | 0 | 0
10 | 0.98745 | -0.23999 | 0.0060158 | 0.0015077
11 | 0.98481 | -0.29134 | 0 | 0
12 | 0.98944 | -0.20153 | 0.0035959 | 0.00090123
13 | 0.98656 | -0.25724 | 0 | 0
14 | 0.98348 | -0.31731 | 0 | 0
15 | 0.98414 | -0.30445 | 0.0030616 | 0.00076731
16 | 0.99151 | -0.16156 | 0 | 0
17 | 0.98652 | -0.25815 | 0 | 0
18 | 0.98896 | -0.21036 | 0.0038969 | 0.00097664
19 | 0.98674 | -0.25297 | 0.0031653 | 0.00079329
20 | 0.99009 | -0.18863 | 0.0058988 | 0.0014784
21 | 0.98531 | -0.28056 | 0.0047629 | 0.0011937
22 | 0.97141 | -0.55206 | 0.0029418 | 0.00073728
23 | 0.97151 | -0.55008 | 0.0073998 | 0.0018546
24 | 0.98537 | -0.2805 | 0.0023491 | 0.00058874
25 | 0.98542 | -0.27963 | 0.0053892 | 0.0013507
26 | 0.98526 | -0.28264 | 0.0012892 | 0.0003231
27 | 0.98524 | -0.28312 | 0 | 0
28 | 0.98516 | -0.28459 | 0 | 0
29 | 0.9851 | -0.28576 | 0.0028324 | 0.00070987
30 | 0.97175 | -0.54535 | 0 | 0
31 | 0.97222 | -0.53607 | 0.0044824 | 0.0011234
32 | 0.97257 | -0.52916 | 0.0042966 | 0.0010768
33 | 0.972 | -0.54039 | 0.0043092 | 0.00108
34 | 0.97285 | -0.52364 | 0.0035358 | 0.00088616
35 | 0.97189 | -0.5425 | 0.0031821 | 0.00079751
36 | 0.97168 | -0.54673 | 0.002071 | 0.00051904
37 | 0.97258 | -0.52902 | 0.0059309 | 0.0014864
38 | 0.97305 | -0.51975 | 0 | 0
39 | 0.97247 | -0.53107 | 0 | 0
40 | 0.97235 | -0.53348 | 0.0075981 | 0.0019043
41 | 0.97387 | -0.50342 | 0.0076637 | 0.0019207
42 | 0.97489 | -0.48347 | 0 | 0
43 | 0.98312 | -0.32283 | 0.0024284 | 0.00060861
44 | 0.97494 | -0.48233 | 0 | 0
45 | 0.99903 | -0.018617 | 0.0035704 | 0.00089483
46 | 0.99904 | -0.018446 | 0.0033991 | 0.00085191
47 | 0.98318 | -0.3231 | 0.005563 | 0.0013942
48 | 0.98285 | -0.32949 | 0.0015651 | 0.00039226
49 | 0.98326 | -0.3215 | 0.0018503 | 0.00046372
50 | 0.98265 | -0.3334 | 0.0055105 | 0.0013811
51 | 0.98348 | -0.31728 | 0.0030879 | 0.00077389
52 | 0.98361 | -0.31479 | 0.0058798 | 0.0014736
53 | 0.98789 | -0.23208 | 0.0020975 | 0.00052568
54 | 0.98739 | -0.2417 | 0.0039361 | 0.00098647
55 | 0.98819 | -0.2262 | 0.0022348 | 0.0005601
56 | 0.98712 | -0.247 | 0.003433 | 0.0008604
57 | 0.98855 | -0.21922 | 0 | 0
58 | 0.98647 | -0.25951 | 0.0038172 | 0.00095668
59 | 0.98931 | -0.2045 | 0.002979 | 0.0007466
60 | 0.98851 | -0.21996 | 0.0027717 | 0.00069464
61 | 0.98637 | -0.26161 | 0.0049495 | 0.0012405
62 | 0.99045 | -0.18236 | 0 | 0
63 | 0.99991 | -0.0016474 | 0.0041203 | 0.0010327
64 | 1 | 0 | -0.48576 | -0.12389
65 | 0.99957 | -0.0082522 | 0.0034934 | 0.00087553
66 | 0.99921 | -0.015024 | 0.0040736 | 0.0010209
67 | 0.99936 | -0.012247 | 0.0017035 | 0.00042694
68 | 0.99816 | -0.034845 | 0.008511 | 0.0021331
69 | 0.99926 | -0.01432 | 0.001901 | 0.00047643
70 | 0.99589 | -0.077909 | 0 | 0
71 | 0.9848 | -0.2922 | 0.0023604 | 0.00059158
72 | 0.98429 | -0.30217 | 0.0034518 | 0.00086509
73 | 0.98503 | -0.28756 | 0 | 0
74 | 0.98423 | -0.3033 | 0.0022143 | 0.00055496
75 | 0.98494 | -0.28931 | 0.0048393 | 0.0012128
76 | 0.98593 | -0.27009 | 0.0060786 | 0.0015235
77 | 0.9842 | -0.30378 | 0.0045183 | 0.0011324
78 | 0.98401 | -0.30763 | 0 | 0
79 | 0.97428 | -0.49535 | 0.0093449 | 0.0023421
80 | 0.9745 | -0.49115 | 0.00071905 | 0.00018021
81 | 0.9747 | -0.48721 | 0 | 0
82 | 0.98535 | -0.28121 | 0.0050123 | 0.0012562
83 | 0.98531 | -0.28206 | 0.006617 | 0.0016584
84 | 0.98554 | -0.27755 | 0 | 0
85 | 0.98529 | -0.2823 | 0 | 0
86 | 0.98624 | -0.26386 | 0.010154 | 0.0025449
87 | 0.98329 | -0.32139 | 0 | 0
88 | 0.98506 | -0.28676 | 0 | 0
89 | 0.98638 | -0.26122 | 0.0058324 | 0.0014617
90 | 0.9828 | -0.33084 | 0.075391 | 0.018895
91 | 0.98477 | -0.29242 | 0.0056704 | 0.0014211
92 | 0.98863 | -0.21744 | 0 | 0
93 | 0.98907 | -0.20903 | 0.0061719 | 0.0015468
94 | 0.98394 | -0.30886 | 0.0022941 | 0.00057495
95 | 0.98388 | -0.31008 | 0.0022524 | 0.00056451
96 | 0.98386 | -0.31048 | 0.0032695 | 0.00081941
97 | 0.99092 | -0.17328 | 0 | 0
98 | 0.99191 | -0.15426 | 0 | 0
99 | 0.99238 | -0.14533 | 0 | 0
100 | 0.9913 | -0.16609 | 0.0049069 | 0.0012298
101 | 0.99301 | -0.13306 | 0.0032752 | 0.00082084
102 | 0.99058 | -0.18005 | 0 | 0
103 | 0.99353 | -0.12318 | 0.0033847 | 0.00084829
104 | 0.99413 | -0.11173 | 0.0043721 | 0.0010958
105 | 0.99496 | -0.095707 | 0.0026499 | 0.00066413
106 | 0.9821 | -0.34428 | 0.0016785 | 0.00042066
107 | 0.98209 | -0.3445 | 0.00066337 | 0.00016626
108 | 0.98212 | -0.34393 | 0.0023706 | 0.00059412
109 | 0.98203 | -0.34569 | 0.0028933 | 0.00072513
110 | 0.98236 | -0.33908 | 0.0028874 | 0.00072366
111 | 0.98264 | -0.33365 | 0.0017798 | 0.00044606
112 | 0.98304 | -0.32588 | 0.024012 | 0.0060179
113 | 0.99119 | -0.1677 | 0.0036764 | 0.0009214
114 | 0.99269 | -0.13902 | 0.0060115 | 0.0015066
115 | 0.99056 | -0.17967 | 0.0043362 | 0.0010867
116 | 0.99319 | -0.12942 | 0.0015494 | 0.00038831
117 | 0.99474 | -0.099926 | 0.0088247 | 0.0022117
118 | 0.98644 | -0.25977 | 0.0035891 | 0.00089952
119 | 0.97588 | -0.4639 | 0.0025095 | 0.00062895
120 | 0.9954 | -0.087226 | 0.0043178 | 0.0010821
121 | 0.97607 | -0.46026 | 0.00095702 | 0.00023985
122 | 0.97614 | -0.45874 | 0.0025095 | 0.00062895
123 | 0.97756 | -0.43094 | 0 | 0
124 | 0.97752 | -0.43188 | 0.0033166 | 0.00083121
125 | 0.97904 | -0.40202 | 0 | 0
126 | 0.97904 | -0.40218 | 0.0010616 | 0.00026606
127 | 0.98037 | -0.37625 | 0 | 0
128 | 0.98035 | -0.37651 | 0.0015006 | 0.0003761
129 | 0.98204 | -0.34373 | 0 | 0
130 | 0.99048 | -0.18189 | 0.0015141 | 0.00037948
131 | 0.99049 | -0.18176 | 0.0014388 | 0.0003606
132 | 0.99004 | -0.1905 | 0.0044103 | 0.0011053
133 | 0.9898 | -0.19513 | 0.0036214 | 0.00090761
134 | 0.98961 | -0.19896 | 0.0033876 | 0.000849
135 | 0.98965 | -0.19818 | 0.0019857 | 0.00049766
136 | 0.98954 | -0.2003 | 0.011482 | 0.0028776
137 | 0.98237 | -0.33734 | 0 | 0
138 | 0.98203 | -0.34392 | 0.0014322 | 0.00035894
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0019578 | -0.00049066 | 0.0019578 | 0.00049064 | 5.8936e-09 | -1.9226e-08 | 0.0029535 | 0.0029534 | 0.0029535 | 0.98637 | -0.26024 | 0.98637 | -0.26018 | 0.81139
1 | -0.0019578 | -0.00049064 | 0.0019579 | 0.00049037 | 8.296e-08 | -2.7065e-07 | 0.0029534 | 0.0029533 | 0.0029534 | 0.98637 | -0.26018 | 0.98642 | -0.25929 | 0.81139
2 | -0.0025624 | -0.00064188 | 0.0025626 | 0.00064162 | 1.639e-07 | -2.6858e-07 | 0.0038653 | 0.0038651 | 0.0038653 | 0.98642 | -0.25929 | 0.98649 | -0.25794 | 1.0619
3 | -0.019013 | -0.0047665 | 0.01902 | 0.0047707 | 6.9784e-06 | 4.1779e-06 | 0.028698 | 0.028698 | 0.028698 | 0.98586 | -0.27107 | 0.98625 | -0.26337 | 7.8841
4 | 0.01771 | 0.00444 | -0.017705 | -0.0044367 | 5.4723e-06 | 3.242e-06 | 0.026732 | 0.026732 | 0.026732 | 0.98586 | -0.27107 | 0.98552 | -0.27755 | 7.3439
5 | -0.020365 | -0.0051079 | 0.020371 | 0.0051115 | 5.9453e-06 | 3.5907e-06 | 0.030728 | 0.030728 | 0.030728 | 0.98625 | -0.26337 | 0.98656 | -0.25724 | 8.4417
6 | 0.011862 | 0.0029725 | -0.011861 | -0.0029718 | 1.1706e-06 | 6.2522e-07 | 0.01791 | 0.01791 | 0.01791 | 0.98552 | -0.27755 | 0.98542 | -0.27963 | 4.9204
7 | -0.0025626 | -0.00064162 | 0.0025626 | 0.00064147 | 8.8223e-08 | -1.446e-07 | 0.0038651 | 0.0038651 | 0.0038651 | 0.98649 | -0.25794 | 0.98652 | -0.25722 | 1.0619
8 | -0.0058944 | -0.0014765 | 0.0058956 | 0.0014767 | 1.1921e-06 | 2.4932e-07 | 0.0088905 | 0.0088904 | 0.0088905 | 0.98652 | -0.25722 | 0.98674 | -0.25297 | 2.4425
9 | -0.029997 | -0.0075307 | 0.030002 | 0.0075339 | 5.1408e-06 | 3.2043e-06 | 0.045207 | 0.045207 | 0.045207 | 0.98746 | -0.2398 | 0.98765 | -0.23621 | 12.4195
10 | 0.029997 | 0.0075307 | -0.029996 | -0.0075306 | 2.643e-07 | 1.6474e-07 | 0.045207 | 0.045207 | 0.045207 | 0.98746 | -0.2398 | 0.98745 | -0.23999 | 12.4195
11 | 0.063075 | 0.015909 | -0.062909 | -0.015804 | 0.00016599 | 0.00010561 | 0.095067 | 0.095067 | 0.095067 | 0.98765 | -0.23621 | 0.98481 | -0.29134 | 26.1174
12 | -0.093077 | -0.023443 | 0.093232 | 0.023542 | 0.00015465 | 9.8709e-05 | 0.14027 | 0.14027 | 0.14027 | 0.98765 | -0.23621 | 0.98944 | -0.20153 | 38.5368
13 | 0.023981 | 0.0060229 | -0.023961 | -0.0060107 | 1.9731e-05 | 1.2113e-05 | 0.036141 | 0.036142 | 0.036142 | 0.98745 | -0.23999 | 0.98656 | -0.25724 | 9.929
14 | 0.036354 | 0.0091357 | -0.036309 | -0.0091074 | 4.5017e-05 | 2.8306e-05 | 0.054938 | 0.054938 | 0.054938 | 0.98481 | -0.29134 | 0.98348 | -0.31731 | 15.093
15 | 0.026555 | 0.0066678 | -0.026539 | -0.0066575 | 1.6596e-05 | 1.0272e-05 | 0.040129 | 0.040129 | 0.040129 | 0.98481 | -0.29134 | 0.98414 | -0.30445 | 11.0245
16 | -0.096828 | -0.024443 | 0.097013 | 0.024562 | 0.00018575 | 0.00011858 | 0.14568 | 0.14568 | 0.14568 | 0.98944 | -0.20153 | 0.99151 | -0.16156 | 40.0224
17 | 0.0035895 | 0.00089929 | -0.0035894 | -0.00089937 | 1.554e-07 | -8.1066e-08 | 0.0054139 | 0.005414 | 0.005414 | 0.98656 | -0.25724 | 0.98652 | -0.25815 | 1.4874
18 | 0.036309 | 0.0091074 | -0.036294 | -0.0090981 | 1.4814e-05 | 9.3151e-06 | 0.054938 | 0.054939 | 0.054939 | 0.98348 | -0.31731 | 0.98304 | -0.32588 | 15.093
19 | 0.023477 | 0.0058902 | -0.023466 | -0.0058831 | 1.1569e-05 | 7.0931e-06 | 0.0355 | 0.0355 | 0.0355 | 0.98414 | -0.30445 | 0.98361 | -0.31479 | 9.7528
20 | 0.11223 | 0.028662 | -0.11219 | -0.028642 | 3.3257e-05 | 2.0641e-05 | 0.16862 | 0.16862 | 0.16862 | 0.99151 | -0.16156 | 0.99119 | -0.1677 | 11.5807
21 | -0.20924 | -0.053224 | 0.20947 | 0.053368 | 0.00022752 | 0.00014434 | 0.3143 | 0.3143 | 0.3143 | 0.99151 | -0.16156 | 0.99269 | -0.13902 | 21.5863
22 | 0.0035894 | 0.00089937 | -0.0035891 | -0.00089952 | 2.7608e-07 | -1.4397e-07 | 0.005414 | 0.0054141 | 0.0054141 | 0.98652 | -0.25815 | 0.98644 | -0.25977 | 1.4874
23 | 0.094174 | 0.024045 | -0.09398 | -0.023922 | 0.0001935 | 0.00012351 | 0.14185 | 0.14186 | 0.14186 | 0.98896 | -0.21036 | 0.98674 | -0.25297 | 38.9712
24 | -0.098071 | -0.025022 | 0.098174 | 0.025088 | 0.00010305 | 6.5788e-05 | 0.14772 | 0.14772 | 0.14772 | 0.98896 | -0.21036 | 0.99009 | -0.18863 | 40.5819
25 | 0.084919 | 0.021652 | -0.084806 | -0.02158 | 0.00011295 | 7.2051e-05 | 0.12819 | 0.12819 | 0.12819 | 0.98674 | -0.25297 | 0.98531 | -0.28056 | 35.2175
26 | -0.10407 | -0.026566 | 0.10412 | 0.026594 | 4.5119e-05 | 2.8308e-05 | 0.15658 | 0.15658 | 0.15658 | 0.99009 | -0.18863 | 0.99056 | -0.17967 | 14.3391
27 | 0.080044 | 0.020386 | -0.079881 | -0.020282 | 0.00016281 | 0.00010382 | 0.121 | 0.121 | 0.121 | 0.98531 | -0.28056 | 0.98312 | -0.32283 | 33.2415
28 | -0.0029418 | -0.00073728 | 0.002942 | 0.00073701 | 2.7641e-07 | -2.7254e-07 | 0.0045062 | 0.0045061 | 0.0045062 | 0.97141 | -0.55206 | 0.97151 | -0.55008 | 1.238
29 | -0.010342 | -0.0025916 | 0.010344 | 0.0025928 | 2.3319e-06 | 1.1855e-06 | 0.01584 | 0.01584 | 0.01584 | 0.97151 | -0.55008 | 0.97175 | -0.54535 | 4.3517
30 | -0.0064715 | -0.0016211 | 0.0064718 | 0.0016212 | 2.6979e-07 | 7.6698e-08 | 0.0097724 | 0.0097724 | 0.0097724 | 0.98537 | -0.2805 | 0.98542 | -0.27963 | 2.6847
31 | 0.0041224 | 0.0010324 | -0.004122 | -0.0010325 | 4.2083e-07 | -9.9519e-08 | 0.006225 | 0.0062251 | 0.0062251 | 0.98537 | -0.2805 | 0.98526 | -0.28264 | 1.7102
32 | 0.0028328 | 0.00070936 | -0.0028328 | -0.00070944 | 6.3947e-08 | -7.7727e-08 | 0.0042781 | 0.0042782 | 0.0042782 | 0.98526 | -0.28264 | 0.98524 | -0.28312 | 1.1753
33 | 0.0028328 | 0.00070944 | -0.0028326 | -0.00070968 | 1.9876e-07 | -2.4154e-07 | 0.0042782 | 0.0042783 | 0.0042783 | 0.98524 | -0.28312 | 0.98516 | -0.28459 | 1.1754
34 | 0.0028326 | 0.00070968 | -0.0028324 | -0.00070987 | 1.5723e-07 | -1.9101e-07 | 0.0042783 | 0.0042784 | 0.0042784 | 0.98516 | -0.28459 | 0.9851 | -0.28576 | 1.1754
35 | -0.012415 | -0.0031114 | 0.012417 | 0.0031124 | 1.6867e-06 | 9.2531e-07 | 0.019011 | 0.019011 | 0.019011 | 0.97175 | -0.54535 | 0.97189 | -0.5425 | 5.2229
36 | 0.0020711 | 0.00051868 | -0.002071 | -0.00051904 | 1.3581e-07 | -3.5913e-07 | 0.0031713 | 0.0031715 | 0.0031715 | 0.97175 | -0.54535 | 0.97168 | -0.54673 | 0.87129
37 | -0.024396 | -0.0061167 | 0.024404 | 0.0061216 | 8.033e-06 | 4.9505e-06 | 0.03734 | 0.03734 | 0.03734 | 0.97222 | -0.53607 | 0.97257 | -0.52916 | 10.2584
38 | 0.019914 | 0.0049933 | -0.01991 | -0.0049908 | 4.1016e-06 | 2.4791e-06 | 0.03048 | 0.03048 | 0.03048 | 0.97222 | -0.53607 | 0.972 | -0.54039 | 8.3736
39 | -0.028701 | -0.0071984 | 0.028709 | 0.0072031 | 7.5607e-06 | 4.7091e-06 | 0.043914 | 0.043914 | 0.043914 | 0.97257 | -0.52916 | 0.97285 | -0.52364 | 12.0643
40 | 0.015601 | 0.0039108 | -0.015599 | -0.0039099 | 1.5657e-06 | 9.1132e-07 | 0.023883 | 0.023883 | 0.023883 | 0.972 | -0.54039 | 0.97189 | -0.5425 | 6.5613
41 | -0.032244 | -0.0080893 | 0.03225 | 0.008093 | 5.977e-06 | 3.7439e-06 | 0.049322 | 0.049322 | 0.049322 | 0.97285 | -0.52364 | 0.97305 | -0.51975 | 13.5501
42 | -0.013531 | -0.0033913 | 0.013537 | 0.0033947 | 5.9786e-06 | 3.3644e-06 | 0.020702 | 0.020701 | 0.020702 | 0.97258 | -0.52902 | 0.97305 | -0.51975 | 5.6873
43 | 0.0075997 | 0.0019049 | -0.007599 | -0.0019046 | 7.4054e-07 | 2.9271e-07 | 0.011627 | 0.011628 | 0.011628 | 0.97258 | -0.52902 | 0.97247 | -0.53107 | 3.1944
44 | -0.045787 | -0.011488 | 0.045823 | 0.01151 | 3.5686e-05 | 2.2598e-05 | 0.070024 | 0.070024 | 0.070024 | 0.97305 | -0.51975 | 0.97387 | -0.50342 | 19.2373
45 | 0.007599 | 0.0019046 | -0.0075981 | -0.0019043 | 8.7479e-07 | 3.4582e-07 | 0.011628 | 0.011628 | 0.011628 | 0.97247 | -0.53107 | 0.97235 | -0.53348 | 3.1944
46 | -0.053486 | -0.013431 | 0.053537 | 0.013463 | 5.0947e-05 | 3.2353e-05 | 0.081733 | 0.081733 | 0.081733 | 0.97387 | -0.50342 | 0.97489 | -0.48347 | 22.4542
47 | -0.053537 | -0.013463 | 0.05354 | 0.013465 | 2.9185e-06 | 1.8533e-06 | 0.081733 | 0.081733 | 0.081733 | 0.97489 | -0.48347 | 0.97494 | -0.48233 | 22.4542
48 | 0.077452 | 0.019674 | -0.077398 | -0.019639 | 5.407e-05 | 3.4472e-05 | 0.11732 | 0.11732 | 0.11732 | 0.98312 | -0.32283 | 0.98237 | -0.33734 | 32.2317
49 | -0.06361 | -0.015991 | 0.063666 | 0.016026 | 5.6039e-05 | 3.5667e-05 | 0.097103 | 0.097103 | 0.097103 | 0.97494 | -0.48233 | 0.97588 | -0.4639 | 26.6767
50 | 0.01007 | 0.0025253 | -0.010068 | -0.0025241 | 2.3409e-06 | 1.1688e-06 | 0.01537 | 0.01537 | 0.01537 | 0.97494 | -0.48233 | 0.9747 | -0.48721 | 4.2226
51 | -0.0035704 | -0.00089483 | 0.0035704 | 0.00089481 | 2.9024e-08 | -1.726e-08 | 0.005318 | 0.0053179 | 0.005318 | 0.99903 | -0.018617 | 0.99904 | -0.018446 | 1.461
52 | -0.0069696 | -0.0017467 | 0.0069709 | 0.0017471 | 1.37e-06 | 4.3278e-07 | 0.010381 | 0.010381 | 0.010381 | 0.99904 | -0.018446 | 0.99926 | -0.01432 | 2.8519
53 | 0.0070788 | 0.0017742 | -0.0070767 | -0.0017735 | 2.1568e-06 | 7.4512e-07 | 0.010714 | 0.010714 | 0.010714 | 0.98318 | -0.3231 | 0.98285 | -0.32949 | 2.9434
54 | -0.012642 | -0.0031684 | 0.012643 | 0.003169 | 9.6203e-07 | 5.2682e-07 | 0.019133 | 0.019133 | 0.019133 | 0.98318 | -0.3231 | 0.98326 | -0.3215 | 5.2563
55 | 0.0055115 | 0.0013812 | -0.0055105 | -0.0013811 | 1.0266e-06 | 1.5885e-07 | 0.0083443 | 0.0083445 | 0.0083445 | 0.98285 | -0.32949 | 0.98265 | -0.3334 | 2.2924
56 | -0.014493 | -0.0036327 | 0.014496 | 0.0036343 | 2.9106e-06 | 1.6581e-06 | 0.021933 | 0.021933 | 0.021933 | 0.98326 | -0.3215 | 0.98348 | -0.31728 | 6.0256
57 | -0.017584 | -0.0044082 | 0.017586 | 0.0044095 | 2.0903e-06 | 1.2379e-06 | 0.026605 | 0.026605 | 0.026605 | 0.98348 | -0.31728 | 0.98361 | -0.31479 | 7.3091
58 | 0.047525 | 0.011951 | -0.047504 | -0.011938 | 2.1818e-05 | 1.3818e-05 | 0.0716 | 0.0716 | 0.0716 | 0.98789 | -0.23208 | 0.98739 | -0.2417 | 19.6704
59 | -0.049623 | -0.012477 | 0.049637 | 0.012486 | 1.3938e-05 | 8.835e-06 | 0.07476 | 0.07476 | 0.07476 | 0.98789 | -0.23208 | 0.98819 | -0.2262 | 20.5384
60 | 0.043568 | 0.010951 | -0.043557 | -0.010944 | 1.1024e-05 | 6.9683e-06 | 0.065669 | 0.065669 | 0.065669 | 0.98739 | -0.2417 | 0.98712 | -0.247 | 18.0408
61 | -0.051872 | -0.013046 | 0.051889 | 0.013057 | 1.7304e-05 | 1.0978e-05 | 0.078125 | 0.078125 | 0.078125 | 0.98819 | -0.2262 | 0.98855 | -0.21922 | 21.4629
62 | 0.040124 | 0.010084 | -0.0401 | -0.010069 | 2.3945e-05 | 1.5102e-05 | 0.060494 | 0.060494 | 0.060494 | 0.98712 | -0.247 | 0.98647 | -0.25951 | 16.6191
63 | -0.054661 | -0.013752 | 0.054699 | 0.013776 | 3.8466e-05 | 2.4424e-05 | 0.082297 | 0.082297 | 0.082297 | 0.98855 | -0.21922 | 0.98931 | -0.2045 | 22.609
64 | 0.0027718 | 0.00069451 | -0.0027717 | -0.00069464 | 9.7716e-08 | -1.2937e-07 | 0.0041721 | 0.0041722 | 0.0041722 | 0.98855 | -0.21922 | 0.98851 | -0.21996 | 1.1462
65 | 0.036282 | 0.009112 | -0.036279 | -0.0091097 | 3.6375e-06 | 2.2866e-06 | 0.054736 | 0.054736 | 0.054736 | 0.98647 | -0.25951 | 0.98637 | -0.26161 | 15.0373
66 | -0.057678 | -0.014523 | 0.057739 | 0.014561 | 6.1121e-05 | 3.8839e-05 | 0.086777 | 0.086777 | 0.086777 | 0.98931 | -0.2045 | 0.99045 | -0.18236 | 23.84
67 | 0.031329 | 0.0078692 | -0.031317 | -0.0078613 | 1.267e-05 | 7.9159e-06 | 0.047269 | 0.047269 | 0.047269 | 0.98637 | -0.26161 | 0.98593 | -0.27009 | 12.986
68 | -0.057739 | -0.014561 | 0.057764 | 0.014577 | 2.5124e-05 | 1.5965e-05 | 0.086777 | 0.086777 | 0.086777 | 0.99045 | -0.18236 | 0.99092 | -0.17328 | 23.8399
69 | -0.0041203 | -0.0010327 | 0.0041207 | 0.0010326 | 3.2336e-07 | -9.3921e-08 | 0.0061317 | 0.0061316 | 0.0061317 | 0.99991 | -0.0016474 | 1 | 0 | 1.6845
70 | 0.014077 | 0.0035305 | -0.014072 | -0.0035274 | 5.535e-06 | 3.1013e-06 | 0.020948 | 0.020948 | 0.020948 | 1 | 0 | 0.99957 | -0.0082522 | 5.755
71 | 0.46591 | 0.11933 | -0.46557 | -0.11911 | 0.00033887 | 0.00021648 | 0.69419 | 0.69419 | 0.69419 | 1 | 0 | 0.99921 | -0.015024 | 47.6782
72 | 0.010578 | 0.0026519 | -0.010576 | -0.0026509 | 2.0132e-06 | 1.0047e-06 | 0.015748 | 0.015748 | 0.015748 | 0.99957 | -0.0082522 | 0.99936 | -0.012247 | 4.3263
73 | 0.4615 | 0.11809 | -0.46106 | -0.11781 | 0.00044237 | 0.0002826 | 0.68813 | 0.68813 | 0.68813 | 0.99921 | -0.015024 | 0.99816 | -0.034845 | 47.2615
74 | 0.0088728 | 0.002224 | -0.0088719 | -0.0022236 | 8.7628e-07 | 3.8542e-07 | 0.013211 | 0.013211 | 0.013211 | 0.99936 | -0.012247 | 0.99926 | -0.01432 | 3.6295
75 | 0.45255 | 0.11568 | -0.45161 | -0.11507 | 0.00094057 | 0.00060082 | 0.67544 | 0.67544 | 0.67544 | 0.99816 | -0.034845 | 0.99589 | -0.077909 | 46.3902
76 | 0.22078 | 0.056103 | -0.2206 | -0.055983 | 0.00018902 | 0.00012001 | 0.33016 | 0.33016 | 0.33016 | 0.99589 | -0.077909 | 0.99496 | -0.095707 | 22.6757
77 | 0.23082 | 0.058971 | -0.23072 | -0.058905 | 0.00010393 | 6.6031e-05 | 0.34528 | 0.34528 | 0.34528 | 0.99589 | -0.077909 | 0.9954 | -0.087226 | 23.7145
78 | 0.018012 | 0.0045177 | -0.018004 | -0.0045127 | 8.5478e-06 | 5.0793e-06 | 0.027217 | 0.027218 | 0.027218 | 0.9848 | -0.2922 | 0.98429 | -0.30217 | 7.4774
79 | -0.020373 | -0.0051093 | 0.020377 | 0.005112 | 4.5129e-06 | 2.7266e-06 | 0.030784 | 0.030784 | 0.030784 | 0.9848 | -0.2922 | 0.98503 | -0.28756 | 8.4572
80 | 0.014552 | 0.0036476 | -0.014551 | -0.0036471 | 7.8988e-07 | 4.5021e-07 | 0.021999 | 0.021999 | 0.021999 | 0.98429 | -0.30217 | 0.98423 | -0.3033 | 6.0438
81 | 0.0048397 | 0.0012129 | -0.0048393 | -0.0012128 | 4.0345e-07 | 2.0098e-09 | 0.007311 | 0.0073111 | 0.0073111 | 0.98503 | -0.28756 | 0.98494 | -0.28931 | 2.0085
82 | -0.025217 | -0.0063249 | 0.025238 | 0.0063379 | 2.1018e-05 | 1.2959e-05 | 0.038095 | 0.038095 | 0.038095 | 0.98503 | -0.28756 | 0.98593 | -0.27009 | 10.4657
83 | 0.012337 | 0.0030922 | -0.012337 | -0.003092 | 2.7732e-07 | 1.5047e-07 | 0.018652 | 0.018652 | 0.018652 | 0.98423 | -0.3033 | 0.9842 | -0.30378 | 5.1241
84 | 0.0078183 | 0.0019596 | -0.0078168 | -0.0019591 | 1.4342e-06 | 5.7013e-07 | 0.01182 | 0.011821 | 0.011821 | 0.9842 | -0.30378 | 0.98401 | -0.30763 | 3.2474
85 | 0.0078168 | 0.0019591 | -0.0078164 | -0.0019589 | 4.598e-07 | 1.8281e-07 | 0.011821 | 0.011821 | 0.011821 | 0.98401 | -0.30763 | 0.98394 | -0.30886 | 3.2474
86 | -0.0093449 | -0.0023421 | 0.0093468 | 0.002343 | 1.8695e-06 | 8.9162e-07 | 0.014272 | 0.014272 | 0.014272 | 0.97428 | -0.49535 | 0.9745 | -0.49115 | 3.921
87 | -0.010066 | -0.0025232 | 0.010068 | 0.0025241 | 1.8922e-06 | 9.4484e-07 | 0.01537 | 0.01537 | 0.01537 | 0.9745 | -0.49115 | 0.9747 | -0.48721 | 4.2226
88 | 0.012291 | 0.0030803 | -0.01229 | -0.00308 | 4.9342e-07 | 2.6714e-07 | 0.018561 | 0.018561 | 0.018561 | 0.98535 | -0.28121 | 0.98531 | -0.28206 | 5.0991
89 | -0.017303 | -0.0043365 | 0.017306 | 0.0043383 | 3.0242e-06 | 1.785e-06 | 0.02613 | 0.02613 | 0.02613 | 0.98535 | -0.28121 | 0.98554 | -0.27755 | 7.1786
90 | 0.0056732 | 0.0014216 | -0.0056731 | -0.0014216 | 6.6614e-08 | 1.1811e-08 | 0.0085676 | 0.0085676 | 0.0085676 | 0.98531 | -0.28206 | 0.98529 | -0.2823 | 2.3537
91 | -0.092889 | -0.023355 | 0.092949 | 0.023394 | 6.0757e-05 | 3.8779e-05 | 0.14027 | 0.14027 | 0.14027 | 0.98554 | -0.27755 | 0.98624 | -0.26386 | 38.5371
92 | 0.075583 | 0.019017 | -0.075425 | -0.018916 | 0.00015799 | 0.0001007 | 0.11415 | 0.11415 | 0.11415 | 0.98554 | -0.27755 | 0.98329 | -0.32139 | 31.3586
93 | 0.0056731 | 0.0014216 | -0.0056719 | -0.0014214 | 1.2036e-06 | 2.1355e-07 | 0.0085676 | 0.0085678 | 0.0085678 | 0.98529 | -0.2823 | 0.98506 | -0.28676 | 2.3538
94 | -0.1031 | -0.025939 | 0.10312 | 0.025947 | 1.3023e-05 | 8.3163e-06 | 0.1556 | 0.1556 | 0.1556 | 0.98624 | -0.26386 | 0.98638 | -0.26122 | 42.7461
95 | 0.075425 | 0.018916 | -0.075391 | -0.018895 | 3.3957e-05 | 2.1644e-05 | 0.11415 | 0.11415 | 0.11415 | 0.98329 | -0.32139 | 0.9828 | -0.33084 | 31.3586
96 | 0.0056719 | 0.0014214 | -0.0056704 | -0.0014211 | 1.5296e-06 | 2.718e-07 | 0.0085678 | 0.008568 | 0.008568 | 0.98506 | -0.28676 | 0.98477 | -0.29242 | 2.3539
97 | -0.10895 | -0.027409 | 0.10918 | 0.027555 | 0.00022841 | 0.00014589 | 0.16439 | 0.16439 | 0.16439 | 0.98638 | -0.26122 | 0.98863 | -0.21744 | 45.1632
98 | -0.10918 | -0.027555 | 0.10922 | 0.027583 | 4.3963e-05 | 2.8081e-05 | 0.16439 | 0.16439 | 0.16439 | 0.98863 | -0.21744 | 0.98907 | -0.20903 | 45.1632
99 | -0.11539 | -0.02913 | 0.11559 | 0.029256 | 0.00019801 | 0.0001265 | 0.17368 | 0.17368 | 0.17368 | 0.98907 | -0.20903 | 0.99092 | -0.17328 | 47.7141
100 | 0.0055223 | 0.0013839 | -0.005522 | -0.0013839 | 3.198e-07 | 4.9377e-08 | 0.0083513 | 0.0083514 | 0.0083514 | 0.98394 | -0.30886 | 0.98388 | -0.31008 | 2.2943
101 | 0.0032695 | 0.00081936 | -0.0032695 | -0.00081941 | 6.2931e-08 | -4.6885e-08 | 0.0049448 | 0.0049448 | 0.0049448 | 0.98388 | -0.31008 | 0.98386 | -0.31048 | 1.3585
102 | -0.17336 | -0.043834 | 0.17351 | 0.043935 | 0.00015826 | 0.00010096 | 0.26046 | 0.26046 | 0.26046 | 0.99092 | -0.17328 | 0.99191 | -0.15426 | 35.777
103 | -0.20632 | -0.052177 | 0.20641 | 0.052233 | 8.8431e-05 | 5.6088e-05 | 0.30968 | 0.30968 | 0.30968 | 0.99191 | -0.15426 | 0.99238 | -0.14533 | 21.2689
104 | 0.032804 | 0.0082423 | -0.032786 | -0.0082307 | 1.8504e-05 | 1.158e-05 | 0.049219 | 0.049219 | 0.049219 | 0.99191 | -0.15426 | 0.9913 | -0.16609 | 13.5217
105 | -0.20641 | -0.052233 | 0.20653 | 0.05231 | 0.0001217 | 7.719e-05 | 0.30968 | 0.30967 | 0.30968 | 0.99238 | -0.14533 | 0.99301 | -0.13306 | 21.2689
106 | 0.027879 | 0.0070009 | -0.02786 | -0.0069894 | 1.8559e-05 | 1.1514e-05 | 0.041853 | 0.041853 | 0.041853 | 0.9913 | -0.16609 | 0.99058 | -0.18005 | 11.4982
107 | -0.2098 | -0.053131 | 0.2099 | 0.053194 | 9.9506e-05 | 6.3128e-05 | 0.31458 | 0.31458 | 0.31458 | 0.99301 | -0.13306 | 0.99353 | -0.12318 | 21.606
108 | 0.024907 | 0.0062497 | -0.024895 | -0.006242 | 1.2405e-05 | 7.6352e-06 | 0.037417 | 0.037418 | 0.037418 | 0.99058 | -0.18005 | 0.99004 | -0.1905 | 10.2795
109 | 0.0029532 | 0.00073975 | -0.0029529 | -0.00074002 | 2.3996e-07 | -2.6499e-07 | 0.004436 | 0.0044362 | 0.0044362 | 0.99058 | -0.18005 | 0.99049 | -0.18176 | 1.2187
110 | -0.21329 | -0.054042 | 0.21341 | 0.054117 | 0.00011745 | 7.4535e-05 | 0.31965 | 0.31965 | 0.31965 | 0.99353 | -0.12318 | 0.99413 | -0.11173 | 21.9541
111 | -0.21778 | -0.055213 | 0.21795 | 0.055319 | 0.00016783 | 0.00010654 | 0.3262 | 0.3262 | 0.3262 | 0.99413 | -0.11173 | 0.99496 | -0.095707 | 22.4036
112 | 0.0035569 | 0.00089118 | -0.0035568 | -0.0008912 | 3.8069e-08 | -1.9867e-08 | 0.0053891 | 0.0053891 | 0.0053891 | 0.9821 | -0.34428 | 0.98209 | -0.3445 | 1.4805
113 | -0.0052353 | -0.0013118 | 0.0052354 | 0.0013119 | 8.533e-08 | 8.848e-09 | 0.0079322 | 0.0079321 | 0.0079322 | 0.9821 | -0.34428 | 0.98212 | -0.34393 | 2.1792
114 | 0.0028935 | 0.00072495 | -0.0028933 | -0.00072513 | 1.6352e-07 | -1.8242e-07 | 0.004384 | 0.0043841 | 0.0043841 | 0.98209 | -0.3445 | 0.98203 | -0.34569 | 1.2044
115 | -0.007606 | -0.001906 | 0.0076077 | 0.0019066 | 1.7597e-06 | 6.7895e-07 | 0.011524 | 0.011524 | 0.011524 | 0.98212 | -0.34393 | 0.98236 | -0.33908 | 3.1659
116 | -0.010495 | -0.0026303 | 0.010498 | 0.0026317 | 2.7146e-06 | 1.3746e-06 | 0.015897 | 0.015897 | 0.015897 | 0.98236 | -0.33908 | 0.98264 | -0.33365 | 4.3674
117 | -0.012278 | -0.0030777 | 0.012282 | 0.0030802 | 4.548e-06 | 2.4661e-06 | 0.018592 | 0.018592 | 0.018592 | 0.98264 | -0.33365 | 0.98304 | -0.32588 | 5.1078
118 | 0.10852 | 0.02772 | -0.10845 | -0.027681 | 6.2766e-05 | 3.8873e-05 | 0.1631 | 0.1631 | 0.1631 | 0.99119 | -0.1677 | 0.99056 | -0.17967 | 11.2017
119 | -0.21548 | -0.054875 | 0.21558 | 0.054938 | 9.9869e-05 | 6.3389e-05 | 0.32331 | 0.32331 | 0.32331 | 0.99269 | -0.13902 | 0.99319 | -0.12942 | 22.2052
120 | -0.21713 | -0.055326 | 0.21744 | 0.055523 | 0.00030948 | 0.00019645 | 0.32563 | 0.32563 | 0.32563 | 0.99319 | -0.12942 | 0.99474 | -0.099926 | 22.3646
121 | -0.22626 | -0.057735 | 0.2264 | 0.057823 | 0.0001389 | 8.8229e-05 | 0.33883 | 0.33883 | 0.33883 | 0.99474 | -0.099926 | 0.9954 | -0.087226 | 23.2712
122 | -0.066176 | -0.016655 | 0.066188 | 0.016663 | 1.1522e-05 | 7.3361e-06 | 0.10093 | 0.10093 | 0.10093 | 0.97588 | -0.4639 | 0.97607 | -0.46026 | 27.728
123 | -0.067145 | -0.016902 | 0.067149 | 0.016905 | 4.8582e-06 | 3.0938e-06 | 0.10239 | 0.10239 | 0.10239 | 0.97607 | -0.46026 | 0.97614 | -0.45874 | 28.1288
124 | -0.069659 | -0.017534 | 0.069752 | 0.017593 | 9.2719e-05 | 5.9066e-05 | 0.10621 | 0.10621 | 0.10621 | 0.97614 | -0.45874 | 0.97756 | -0.43094 | 29.1797
125 | 0.0033167 | 0.00083111 | -0.0033166 | -0.00083121 | 1.4974e-07 | -1.0057e-07 | 0.0050485 | 0.0050486 | 0.0050486 | 0.97756 | -0.43094 | 0.97752 | -0.43188 | 1.387
126 | -0.073068 | -0.018425 | 0.07317 | 0.018489 | 0.00010128 | 6.4548e-05 | 0.11126 | 0.11126 | 0.11126 | 0.97756 | -0.43094 | 0.97904 | -0.40202 | 30.5667
127 | 0.0010616 | 0.00026596 | -0.0010616 | -0.00026606 | 8.2588e-09 | -1.011e-07 | 0.0016134 | 0.0016135 | 0.0016135 | 0.97904 | -0.40202 | 0.97904 | -0.40218 | 0.44326
128 | -0.074231 | -0.018755 | 0.074323 | 0.018814 | 9.1821e-05 | 5.8523e-05 | 0.11288 | 0.11288 | 0.11288 | 0.97904 | -0.40202 | 0.98037 | -0.37625 | 31.0099
129 | 0.0015007 | 0.00037599 | -0.0015006 | -0.0003761 | 1.8576e-08 | -1.085e-07 | 0.0022777 | 0.0022777 | 0.0022777 | 0.98037 | -0.37625 | 0.98035 | -0.37651 | 0.62575
130 | -0.075824 | -0.01919 | 0.075942 | 0.019265 | 0.00011854 | 7.5566e-05 | 0.11515 | 0.11515 | 0.11515 | 0.98037 | -0.37625 | 0.98204 | -0.34373 | 31.6356
131 | 0.0014322 | 0.00035886 | -0.0014322 | -0.00035894 | 1.2973e-08 | -8.464e-08 | 0.0021701 | 0.0021701 | 0.0021701 | 0.98204 | -0.34373 | 0.98203 | -0.34392 | 0.59619
132 | -0.077374 | -0.019624 | 0.077398 | 0.019639 | 2.3786e-05 | 1.5164e-05 | 0.11732 | 0.11732 | 0.11732 | 0.98204 | -0.34373 | 0.98237 | -0.33734 | 32.2317
133 | -0.0015141 | -0.00037948 | 0.0015141 | 0.00037942 | 9.6461e-09 | -5.7813e-08 | 0.0022747 | 0.0022747 | 0.0022747 | 0.99048 | -0.18189 | 0.99049 | -0.18176 | 0.62491
134 | 0.020485 | 0.0051367 | -0.02048 | -0.005134 | 4.5206e-06 | 2.7297e-06 | 0.030789 | 0.030789 | 0.030789 | 0.99004 | -0.1905 | 0.9898 | -0.19513 | 8.4585
135 | 0.016859 | 0.0042264 | -0.016856 | -0.0042249 | 2.4456e-06 | 1.4347e-06 | 0.025345 | 0.025345 | 0.025345 | 0.9898 | -0.19513 | 0.98965 | -0.19818 | 6.9629
136 | -0.01487 | -0.003727 | 0.01487 | 0.0037273 | 5.5114e-07 | 3.1496e-07 | 0.022359 | 0.022359 | 0.022359 | 0.98961 | -0.19896 | 0.98965 | -0.19818 | 6.1426
137 | 0.011482 | 0.002878 | -0.011482 | -0.0028776 | 7.3768e-07 | 3.8734e-07 | 0.017266 | 0.017266 | 0.017266 | 0.98961 | -0.19896 | 0.98954 | -0.2003 | 4.7433

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48576 | 0.12389

## res_load
| p_mw | q_mvar
0 | 0.0019578 | 0.00049066
1 | 0.00060454 | 0.00015151
2 | 0.0013028 | 0.00032652
3 | 0.0013454 | 0.0003372
4 | 0.0058425 | 0.0014643
5 | 0.0033318 | 0.00083502
6 | 0.0060158 | 0.0015077
7 | 0.0035959 | 0.00090123
8 | 0.0030616 | 0.00076731
9 | 0.0038969 | 0.00097664
10 | 0.0031653 | 0.00079329
11 | 0.0058988 | 0.0014784
12 | 0.0047629 | 0.0011937
13 | 0.0029418 | 0.00073728
14 | 0.0073998 | 0.0018546
15 | 0.0023491 | 0.00058874
16 | 0.0053892 | 0.0013507
17 | 0.0012892 | 0.0003231
18 | 0.0028324 | 0.00070987
19 | 0.0044824 | 0.0011234
20 | 0.0042966 | 0.0010768
21 | 0.0043092 | 0.00108
22 | 0.0035358 | 0.00088616
23 | 0.0031821 | 0.00079751
24 | 0.002071 | 0.00051904
25 | 0.0059309 | 0.0014864
26 | 0.0075981 | 0.0019043
27 | 0.0076637 | 0.0019207
28 | 0.0024284 | 0.00060861
29 | 0.0035704 | 0.00089483
30 | 0.0033991 | 0.00085191
31 | 0.005563 | 0.0013942
32 | 0.0015651 | 0.00039226
33 | 0.0018503 | 0.00046372
34 | 0.0055105 | 0.0013811
35 | 0.0030879 | 0.00077389
36 | 0.0058798 | 0.0014736
37 | 0.0020975 | 0.00052568
38 | 0.0039361 | 0.00098647
39 | 0.0022348 | 0.0005601
40 | 0.003433 | 0.0008604
41 | 0.0038172 | 0.00095668
42 | 0.002979 | 0.0007466
43 | 0.0027717 | 0.00069464
44 | 0.0049495 | 0.0012405
45 | 0.0041203 | 0.0010327
46 | 0.0034934 | 0.00087553
47 | 0.0040736 | 0.0010209
48 | 0.0017035 | 0.00042694
49 | 0.008511 | 0.0021331
50 | 0.001901 | 0.00047643
51 | 0.0023604 | 0.00059158
52 | 0.0034518 | 0.00086509
53 | 0.0022143 | 0.00055496
54 | 0.0048393 | 0.0012128
55 | 0.0060786 | 0.0015235
56 | 0.0045183 | 0.0011324
57 | 0.0093449 | 0.0023421
58 | 0.00071905 | 0.00018021
59 | 0.0050123 | 0.0012562
60 | 0.006617 | 0.0016584
61 | 0.010154 | 0.0025449
62 | 0.0058324 | 0.0014617
63 | 0.075391 | 0.018895
64 | 0.0056704 | 0.0014211
65 | 0.0061719 | 0.0015468
66 | 0.0022941 | 0.00057495
67 | 0.0022524 | 0.00056451
68 | 0.0032695 | 0.00081941
69 | 0.0049069 | 0.0012298
70 | 0.0032752 | 0.00082084
71 | 0.0033847 | 0.00084829
72 | 0.0043721 | 0.0010958
73 | 0.0026499 | 0.00066413
74 | 0.0016785 | 0.00042066
75 | 0.00066337 | 0.00016626
76 | 0.0023706 | 0.00059412
77 | 0.0028933 | 0.00072513
78 | 0.0028874 | 0.00072366
79 | 0.0017798 | 0.00044606
80 | 0.024012 | 0.0060179
81 | 0.0036764 | 0.0009214
82 | 0.0060115 | 0.0015066
83 | 0.0043362 | 0.0010867
84 | 0.0015494 | 0.00038831
85 | 0.0088247 | 0.0022117
86 | 0.0035891 | 0.00089952
87 | 0.0025095 | 0.00062895
88 | 0.0043178 | 0.0010821
89 | 0.00095702 | 0.00023985
90 | 0.0025095 | 0.00062895
91 | 0.0033166 | 0.00083121
92 | 0.0010616 | 0.00026606
93 | 0.0015006 | 0.0003761
94 | 0.0015141 | 0.00037948
95 | 0.0014388 | 0.0003606
96 | 0.0044103 | 0.0011053
97 | 0.0036214 | 0.00090761
98 | 0.0033876 | 0.000849
99 | 0.0019857 | 0.00049766
100 | 0.011482 | 0.0028776
101 | 0.0014322 | 0.00035894

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1