## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2275-11_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2275-11_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2275-11_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2275-11_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2275-11_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2275-11_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2275-11_0_8_node_99 | 0.4 | n |  | TRUE
7 | bus_LV_2275-11_0_8_node_104 | 0.4 | n |  | TRUE
8 | bus_LV_2275-11_0_8_node_98 | 0.4 | n |  | TRUE
9 | bus_LV_2275-11_0_8_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2275-11_0_8_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2275-11_0_8_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2275-11_0_8_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2275-11_0_8_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2275-11_0_8_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_2275-11_0_8_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_2275-11_0_8_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2275-11_0_8_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_2275-11_0_8_node_139 | 0.4 | n |  | TRUE
19 | bus_LV_2275-11_0_8_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2275-11_0_8_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_2275-11_0_8_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_2275-11_0_8_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2275-11_0_8_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2275-11_0_8_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2275-11_0_8_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2275-11_0_8_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2275-11_0_8_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_2275-11_0_8_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_2275-11_0_8_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2275-11_0_8_node_90 | 0.4 | n |  | TRUE
31 | bus_LV_2275-11_0_8_node_91 | 0.4 | n |  | TRUE
32 | bus_LV_2275-11_0_8_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_2275-11_0_8_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_2275-11_0_8_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_2275-11_0_8_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_2275-11_0_8_node_147 | 0.4 | n |  | TRUE
37 | bus_LV_2275-11_0_8_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2275-11_0_8_node_146 | 0.4 | n |  | TRUE
39 | bus_LV_2275-11_0_8_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_2275-11_0_8_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2275-11_0_8_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_2275-11_0_8_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2275-11_0_8_node_73 | 0.4 | n |  | TRUE
44 | bus_LV_2275-11_0_8_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2275-11_0_8_node_60 | 0.4 | n |  | TRUE
46 | bus_LV_2275-11_0_8_node_78 | 0.4 | n |  | TRUE
47 | bus_LV_2275-11_0_8_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2275-11_0_8_node_58 | 0.4 | n |  | TRUE
49 | bus_LV_2275-11_0_8_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_2275-11_0_8_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2275-11_0_8_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_2275-11_0_8_node_84 | 0.4 | n |  | TRUE
53 | bus_LV_2275-11_0_8_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2275-11_0_8_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_2275-11_0_8_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_2275-11_0_8_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_2275-11_0_8_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2275-11_0_8_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_2275-11_0_8_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_2275-11_0_8_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_2275-11_0_8_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_2275-11_0_8_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_2275-11_0_8_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_2275-11_0_8_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_2275-11_0_8_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2275-11_0_8_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_2275-11_0_8_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_2275-11_0_8_node_148 | 0.4 | n |  | TRUE
69 | bus_LV_2275-11_0_8_node_76 | 0.4 | n |  | TRUE
70 | bus_LV_2275-11_0_8_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_2275-11_0_8_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_2275-11_0_8_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_2275-11_0_8_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_2275-11_0_8_node_114 | 0.4 | n |  | TRUE
75 | bus_LV_2275-11_0_8_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_2275-11_0_8_node_113 | 0.4 | n |  | TRUE
77 | bus_LV_2275-11_0_8_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_2275-11_0_8_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_2275-11_0_8_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_2275-11_0_8_node_134 | 0.4 | n |  | TRUE
81 | bus_LV_2275-11_0_8_node_135 | 0.4 | n |  | TRUE
82 | bus_LV_2275-11_0_8_node_85 | 0.4 | n |  | TRUE
83 | bus_LV_2275-11_0_8_node_137 | 0.4 | n |  | TRUE
84 | bus_LV_2275-11_0_8_node_136 | 0.4 | n |  | TRUE
85 | bus_LV_2275-11_0_8_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_2275-11_0_8_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_2275-11_0_8_node_68 | 0.4 | n |  | TRUE
88 | bus_LV_2275-11_0_8_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_2275-11_0_8_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_2275-11_0_8_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_2275-11_0_8_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_2275-11_0_8_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_2275-11_0_8_node_144 | 0.4 | n |  | TRUE
94 | bus_LV_2275-11_0_8_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_2275-11_0_8_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_2275-11_0_8_node_108 | 0.4 | n |  | TRUE
97 | bus_LV_2275-11_0_8_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_2275-11_0_8_node_143 | 0.4 | n |  | TRUE
99 | bus_LV_2275-11_0_8_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_2275-11_0_8_node_74 | 0.4 | n |  | TRUE
101 | bus_LV_2275-11_0_8_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_2275-11_0_8_node_140 | 0.4 | n |  | TRUE
103 | bus_LV_2275-11_0_8_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_2275-11_0_8_node_149 | 0.4 | n |  | TRUE
105 | bus_LV_2275-11_0_8_node_141 | 0.4 | n |  | TRUE
106 | bus_LV_2275-11_0_8_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_2275-11_0_8_node_83 | 0.4 | n |  | TRUE
108 | bus_LV_2275-11_0_8_node_105 | 0.4 | n |  | TRUE
109 | bus_LV_2275-11_0_8_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_2275-11_0_8_node_125 | 0.4 | n |  | TRUE
111 | bus_LV_2275-11_0_8_node_124 | 0.4 | n |  | TRUE
112 | bus_LV_2275-11_0_8_node_87 | 0.4 | n |  | TRUE
113 | bus_LV_2275-11_0_8_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_2275-11_0_8_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_2275-11_0_8_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_2275-11_0_8_node_92 | 0.4 | n |  | TRUE
117 | bus_LV_2275-11_0_8_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_2275-11_0_8_node_95 | 0.4 | n |  | TRUE
119 | bus_LV_2275-11_0_8_node_101 | 0.4 | n |  | TRUE
120 | bus_LV_2275-11_0_8_node_100 | 0.4 | n |  | TRUE
121 | bus_LV_2275-11_0_8_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_2275-11_0_8_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_2275-11_0_8_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_2275-11_0_8_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_2275-11_0_8_node_110 | 0.4 | n |  | TRUE
126 | bus_LV_2275-11_0_8_node_111 | 0.4 | n |  | TRUE
127 | bus_LV_2275-11_0_8_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_2275-11_0_8_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_2275-11_0_8_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_2275-11_0_8_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_2275-11_0_8_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_2275-11_0_8_node_119 | 0.4 | n |  | TRUE
133 | bus_LV_2275-11_0_8_node_120 | 0.4 | n |  | TRUE
134 | bus_LV_2275-11_0_8_node_121 | 0.4 | n |  | TRUE
135 | bus_LV_2275-11_0_8_node_122 | 0.4 | n |  | TRUE
136 | bus_LV_2275-11_0_8_node_123 | 0.4 | n |  | TRUE
137 | bus_LV_2275-11_0_8_node_132 | 0.4 | n |  | TRUE
138 | bus_LV_2275-11_0_8_node_130 | 0.4 | n |  | TRUE
139 | bus_LV_2275-11_0_8_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_2275-11_0_8_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_2275-11_0_8_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_2275-11_0_8_node_129 | 0.4 | n |  | TRUE
143 | bus_LV_2275-11_0_8_node_131 | 0.4 | n |  | TRUE
144 | bus_LV_2275-11_0_8_node_133 | 0.4 | n |  | TRUE
145 | bus_LV_2275-11_0_8_node_145 | 0.4 | n |  | TRUE
146 | bus_LV_2275-11_0_8_node_138 | 0.4 | n |  | TRUE
147 | bus_MV_381_0_node_154 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2275-11_0_8_load_0 | 0 | 0.00093795 | 0.00023507 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2275-11_0_8_load_1 | 1 | 0.0027498 | 0.00068916 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2275-11_0_8_load_3 | 3 | 0.0010227 | 0.00025632 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2275-11_0_8_load_4 | 4 | 0.0031218 | 0.00078238 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2275-11_0_8_load_5 | 5 | 0.00059333 | 0.0001487 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2275-11_0_8_load_104 | 7 | 0.0018439 | 0.00046211 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2275-11_0_8_load_98 | 8 | 0.0048057 | 0.0012044 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2275-11_0_8_load_6 | 9 | 0.0033186 | 0.00083173 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2275-11_0_8_load_8 | 10 | 0.0024785 | 0.00062116 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2275-11_0_8_load_9 | 11 | 0.00092932 | 0.00023291 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2275-11_0_8_load_11 | 13 | 0.0028698 | 0.00071924 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2275-11_0_8_load_13 | 14 | 0.0018568 | 0.00046537 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2275-11_0_8_load_22 | 15 | 0.0011696 | 0.00029313 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2275-11_0_8_load_12 | 16 | 0.00039904 | 0.00010001 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2275-11_0_8_load_19 | 17 | 0.00077501 | 0.00019424 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2275-11_0_8_load_139 | 18 | 0.0022425 | 0.00056204 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2275-11_0_8_load_21 | 19 | 0.0069579 | 0.0017438 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2275-11_0_8_load_20 | 20 | 0.00090215 | 0.0002261 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2275-11_0_8_load_59 | 21 | 0.0019243 | 0.00048227 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2275-11_0_8_load_14 | 22 | 0.0019406 | 0.00048637 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2275-11_0_8_load_15 | 23 | 0.0017195 | 0.00043096 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2275-11_0_8_load_16 | 24 | 0.002221 | 0.00055664 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2275-11_0_8_load_17 | 25 | 0.00091911 | 0.00023035 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2275-11_0_8_load_18 | 26 | 0.0021302 | 0.00053387 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2275-11_0_8_load_24 | 29 | 0.014108 | 0.0035359 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2275-11_0_8_load_90 | 30 | 0.0011304 | 0.0002833 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2275-11_0_8_load_26 | 32 | 0.0024154 | 0.00060535 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2275-11_0_8_load_27 | 33 | 0.0013996 | 0.00035078 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2275-11_0_8_load_28 | 34 | 0.0026025 | 0.00065225 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2275-11_0_8_load_29 | 35 | 0.00040943 | 0.00010261 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2275-11_0_8_load_33 | 37 | 0.00054245 | 0.00013595 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2275-11_0_8_load_146 | 38 | 0.002811 | 0.00070449 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2275-11_0_8_load_31 | 39 | 0.0018185 | 0.00045576 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2275-11_0_8_load_30 | 40 | 0.00095039 | 0.00023819 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2275-11_0_8_load_32 | 41 | 0.00059048 | 0.00014799 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2275-11_0_8_load_73 | 43 | 0.0022136 | 0.00055479 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2275-11_0_8_load_37 | 44 | 0.0016645 | 0.00041716 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2275-11_0_8_load_60 | 45 | 0.0015127 | 0.00037912 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2275-11_0_8_load_35 | 47 | 0.0019443 | 0.0004873 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2275-11_0_8_load_58 | 48 | 0.00055832 | 0.00013993 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2275-11_0_8_load_36 | 49 | 0.0023661 | 0.00059299 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2275-11_0_8_load_63 | 51 | 0.0056062 | 0.001405 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2275-11_0_8_load_84 | 52 | 0.0016028 | 0.0004017 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2275-11_0_8_load_39 | 53 | 0.0020988 | 0.000526 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2275-11_0_8_load_40 | 54 | 0.0045816 | 0.0011483 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2275-11_0_8_load_42 | 56 | 0.0071253 | 0.0017858 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2275-11_0_8_load_43 | 57 | 0.0050103 | 0.0012557 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2275-11_0_8_load_44 | 58 | 0.0036352 | 0.00091108 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2275-11_0_8_load_48 | 59 | 0.0032154 | 0.00080585 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2275-11_0_8_load_46 | 61 | 0.0017273 | 0.0004329 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2275-11_0_8_load_55 | 62 | 0.00175 | 0.00043859 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2275-11_0_8_load_51 | 63 | 0.0034462 | 0.0008637 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2275-11_0_8_load_45 | 64 | 0.001694 | 0.00042456 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2275-11_0_8_load_50 | 67 | 0.0037217 | 0.00093274 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2275-11_0_8_load_148 | 68 | 0.0030639 | 0.00076789 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2275-11_0_8_load_77 | 70 | 0.00070437 | 0.00017653 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2275-11_0_8_load_52 | 71 | 0.0024434 | 0.00061238 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2275-11_0_8_load_54 | 72 | 0.0027778 | 0.00069619 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2275-11_0_8_load_61 | 73 | 0.0018056 | 0.00045253 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2275-11_0_8_load_114 | 74 | 0.0039359 | 0.00098643 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2275-11_0_8_load_64 | 75 | 0.0018128 | 0.00045432 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2275-11_0_8_load_113 | 76 | 0.0038996 | 0.00097734 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2275-11_0_8_load_56 | 77 | 0.0013543 | 0.00033942 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2275-11_0_8_load_57 | 78 | 0.0023145 | 0.00058008 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2275-11_0_8_load_65 | 79 | 0.0044187 | 0.0011074 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2275-11_0_8_load_134 | 80 | 0.0033027 | 0.00082772 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2275-11_0_8_load_85 | 82 | 0.011986 | 0.003004 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2275-11_0_8_load_137 | 83 | 0.0036595 | 0.00091716 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2275-11_0_8_load_136 | 84 | 0.0027313 | 0.00068454 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2275-11_0_8_load_66 | 85 | 0.0023769 | 0.00059571 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2275-11_0_8_load_69 | 88 | 0.0014685 | 0.00036804 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2275-11_0_8_load_70 | 89 | 0.00071312 | 0.00017873 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2275-11_0_8_load_71 | 90 | 0.000763 | 0.00019123 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2275-11_0_8_load_82 | 92 | 0.0016884 | 0.00042315 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2275-11_0_8_load_144 | 93 | 0.0018888 | 0.00047337 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2275-11_0_8_load_88 | 94 | 0.00061149 | 0.00015325 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2275-11_0_8_load_75 | 95 | 0.00051411 | 0.00012885 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2275-11_0_8_load_108 | 96 | 0.00023284 | 5.8355e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2275-11_0_8_load_80 | 97 | 0.0037211 | 0.0009326 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2275-11_0_8_load_143 | 98 | 0.0032941 | 0.00082559 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2275-11_0_8_load_86 | 99 | 0.002147 | 0.0005381 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2275-11_0_8_load_74 | 100 | 0.0009037 | 0.00022649 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2275-11_0_8_load_93 | 101 | 0.00063744 | 0.00015976 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2275-11_0_8_load_149 | 104 | 0.0028643 | 0.00071785 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2275-11_0_8_load_141 | 105 | 0.0066655 | 0.0016705 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2275-11_0_8_load_81 | 106 | 0.0019453 | 0.00048754 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2275-11_0_8_load_83 | 107 | 0.0036307 | 0.00090994 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2275-11_0_8_load_105 | 108 | 0.002128 | 0.00053332 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2275-11_0_8_load_125 | 110 | 0.00046828 | 0.00011736 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2275-11_0_8_load_124 | 111 | 0.00025231 | 6.3234e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2275-11_0_8_load_87 | 112 | 0.002224 | 0.0005574 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2275-11_0_8_load_89 | 113 | 0.0023812 | 0.00059678 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2275-11_0_8_load_96 | 114 | 0.0055337 | 0.0013869 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2275-11_0_8_load_97 | 115 | 0.0029417 | 0.00073725 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2275-11_0_8_load_92 | 116 | 0.0012099 | 0.00030322 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2275-11_0_8_load_94 | 117 | 0.0017434 | 0.00043694 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2275-11_0_8_load_95 | 118 | 0.0023368 | 0.00058566 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2275-11_0_8_load_101 | 119 | 0.0014468 | 0.00036261 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2275-11_0_8_load_100 | 120 | 0.0043414 | 0.0010881 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2275-11_0_8_load_103 | 122 | 0.0052032 | 0.001304 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2275-11_0_8_load_109 | 124 | 0.00049852 | 0.00012494 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2275-11_0_8_load_110 | 125 | 0.0044773 | 0.0011221 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2275-11_0_8_load_111 | 126 | 0.0042098 | 0.0010551 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2275-11_0_8_load_112 | 127 | 0.0014648 | 0.00036712 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2275-11_0_8_load_115 | 128 | 0.0026522 | 0.00066471 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2275-11_0_8_load_116 | 129 | 0.00049892 | 0.00012504 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2275-11_0_8_load_117 | 130 | 0.072184 | 0.018091 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2275-11_0_8_load_118 | 131 | 0.034284 | 0.0085924 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2275-11_0_8_load_120 | 133 | 0.059841 | 0.014998 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2275-11_0_8_load_121 | 134 | 0.028988 | 0.0072652 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2275-11_0_8_load_122 | 135 | 0.014721 | 0.0036895 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2275-11_0_8_load_123 | 136 | 0.00038607 | 9.6759e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2275-11_0_8_load_132 | 137 | 5.2152e-05 | 1.3071e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2275-11_0_8_load_126 | 139 | 4.8166e-05 | 1.2072e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2275-11_0_8_load_127 | 140 | 0.00014205 | 3.56e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2275-11_0_8_load_128 | 141 | 0.0001341 | 3.361e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2275-11_0_8_load_129 | 142 | 0.00016299 | 4.0849e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2275-11_0_8_load_145 | 145 | 0.00018692 | 4.6846e-05 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2275-11_0_8_load_138 | 146 | 0.014559 | 0.0036489 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2275-11_0_8_line_0 |  | 0 | 1 | 0.059619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2275-11_0_8_line_1 |  | 0 | 2 | 0.028746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2275-11_0_8_line_2 |  | 2 | 3 | 0.058579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2275-11_0_8_line_3 |  | 2 | 4 | 0.039231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2275-11_0_8_line_4 |  | 2 | 5 | 0.032251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2275-11_0_8_line_5 |  | 3 | 6 | 0.292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2275-11_0_8_line_6 |  | 4 | 9 | 0.047233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2275-11_0_8_line_7 |  | 6 | 7 | 0.0094026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2275-11_0_8_line_8 |  | 6 | 8 | 0.022863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2275-11_0_8_line_9 |  | 8 | 118 | 0.014266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2275-11_0_8_line_10 |  | 10 | 11 | 0.0036577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2275-11_0_8_line_11 |  | 10 | 12 | 0.028728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2275-11_0_8_line_12 |  | 11 | 13 | 0.0045646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2275-11_0_8_line_13 |  | 12 | 14 | 0.011443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2275-11_0_8_line_14 |  | 13 | 15 | 0.020316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2275-11_0_8_line_15 |  | 14 | 18 | 6.7166e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2275-11_0_8_line_16 |  | 15 | 19 | 0.024449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2275-11_0_8_line_17 |  | 16 | 17 | 0.022118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2275-11_0_8_line_18 |  | 17 | 20 | 0.0016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2275-11_0_8_line_19 |  | 18 | 21 | 0.00047532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2275-11_0_8_line_20 |  | 19 | 28 | 0.030109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2275-11_0_8_line_21 |  | 20 | 25 | 0.022672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2275-11_0_8_line_22 |  | 21 | 78 | 0.00072706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2275-11_0_8_line_23 |  | 22 | 23 | 0.018249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2275-11_0_8_line_24 |  | 22 | 24 | 0.014558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2275-11_0_8_line_25 |  | 23 | 25 | 0.003477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2275-11_0_8_line_26 |  | 24 | 26 | 0.0096027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2275-11_0_8_line_27 |  | 26 | 27 | 0.017056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2275-11_0_8_line_28 |  | 27 | 28 | 0.051174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2275-11_0_8_line_29 |  | 28 | 29 | 0.007919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2275-11_0_8_line_30 |  | 30 | 31 | 0.026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2275-11_0_8_line_31 |  | 31 | 116 | 0.047764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2275-11_0_8_line_32 |  | 31 | 101 | 0.01958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2275-11_0_8_line_33 |  | 32 | 33 | 0.013263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2275-11_0_8_line_34 |  | 32 | 34 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2275-11_0_8_line_35 |  | 33 | 35 | 0.00063531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2275-11_0_8_line_36 |  | 34 | 36 | 0.069174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2275-11_0_8_line_37 |  | 35 | 37 | 0.012095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2275-11_0_8_line_38 |  | 36 | 38 | 0.005536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2275-11_0_8_line_39 |  | 37 | 39 | 0.0091664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2275-11_0_8_line_40 |  | 39 | 40 | 0.0090265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2275-11_0_8_line_41 |  | 40 | 41 | 0.021492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2275-11_0_8_line_42 |  | 41 | 42 | 0.015142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2275-11_0_8_line_43 |  | 42 | 43 | 0.020229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2275-11_0_8_line_44 |  | 42 | 44 | 0.026767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2275-11_0_8_line_45 |  | 42 | 45 | 0.018397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2275-11_0_8_line_46 |  | 43 | 46 | 0.0097688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2275-11_0_8_line_47 |  | 44 | 47 | 0.020441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2275-11_0_8_line_48 |  | 45 | 48 | 0.027243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2275-11_0_8_line_49 |  | 46 | 69 | 0.0086836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2275-11_0_8_line_50 |  | 47 | 49 | 0.02474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2275-11_0_8_line_51 |  | 48 | 77 | 0.031937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2275-11_0_8_line_52 |  | 49 | 50 | 0.015302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2275-11_0_8_line_53 |  | 50 | 51 | 0.021779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2275-11_0_8_line_54 |  | 51 | 52 | 0.012751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2275-11_0_8_line_55 |  | 52 | 82 | 0.039766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2275-11_0_8_line_56 |  | 53 | 54 | 0.0064683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2275-11_0_8_line_57 |  | 53 | 55 | 0.018283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2275-11_0_8_line_58 |  | 54 | 56 | 0.0091566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2275-11_0_8_line_59 |  | 55 | 57 | 0.020961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2275-11_0_8_line_60 |  | 55 | 58 | 0.045494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2275-11_0_8_line_61 |  | 57 | 59 | 0.031576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2275-11_0_8_line_62 |  | 58 | 60 | 0.014383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2275-11_0_8_line_63 |  | 59 | 61 | 0.041297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2275-11_0_8_line_64 |  | 60 | 62 | 0.042352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2275-11_0_8_line_65 |  | 60 | 63 | 0.027382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2275-11_0_8_line_66 |  | 61 | 64 | 0.0063251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2275-11_0_8_line_67 |  | 62 | 74 | 0.036821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2275-11_0_8_line_68 |  | 63 | 71 | 0.021164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2275-11_0_8_line_69 |  | 64 | 65 | 0.024396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2275-11_0_8_line_70 |  | 65 | 66 | 0.004655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2275-11_0_8_line_71 |  | 65 | 67 | 0.021971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2275-11_0_8_line_72 |  | 66 | 68 | 0.024951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2275-11_0_8_line_73 |  | 67 | 69 | 0.013093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2275-11_0_8_line_74 |  | 69 | 70 | 0.020975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2275-11_0_8_line_75 |  | 70 | 102 | 0.014335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2275-11_0_8_line_76 |  | 71 | 72 | 0.033746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2275-11_0_8_line_77 |  | 72 | 73 | 0.035604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2275-11_0_8_line_78 |  | 73 | 75 | 0.037374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2275-11_0_8_line_79 |  | 74 | 76 | 0.027412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2275-11_0_8_line_80 |  | 75 | 79 | 0.031758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2275-11_0_8_line_81 |  | 76 | 126 | 0.0056497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2275-11_0_8_line_82 |  | 77 | 78 | 0.003886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2275-11_0_8_line_83 |  | 79 | 83 | 0.032991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2275-11_0_8_line_84 |  | 80 | 81 | 0.010953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2275-11_0_8_line_85 |  | 81 | 144 | 0.042276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2275-11_0_8_line_86 |  | 82 | 110 | 0.030143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2275-11_0_8_line_87 |  | 83 | 84 | 0.026716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2275-11_0_8_line_88 |  | 84 | 123 | 0.017537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2275-11_0_8_line_89 |  | 85 | 86 | 0.023875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2275-11_0_8_line_90 |  | 85 | 87 | 0.019724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2275-11_0_8_line_91 |  | 86 | 88 | 0.012827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2275-11_0_8_line_92 |  | 86 | 89 | 0.011373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2275-11_0_8_line_93 |  | 87 | 90 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2275-11_0_8_line_94 |  | 87 | 91 | 0.005648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2275-11_0_8_line_95 |  | 88 | 92 | 0.0056386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2275-11_0_8_line_96 |  | 89 | 93 | 0.021877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2275-11_0_8_line_97 |  | 90 | 94 | 0.019957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2275-11_0_8_line_98 |  | 91 | 95 | 0.013129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2275-11_0_8_line_99 |  | 91 | 96 | 0.024344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2275-11_0_8_line_100 |  | 92 | 97 | 0.046325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2275-11_0_8_line_101 |  | 93 | 98 | 0.046554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2275-11_0_8_line_102 |  | 94 | 99 | 0.0083146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2275-11_0_8_line_103 |  | 95 | 100 | 0.013997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2275-11_0_8_line_104 |  | 96 | 101 | 0.028199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2275-11_0_8_line_105 |  | 97 | 106 | 0.022946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_2275-11_0_8_line_106 |  | 99 | 112 | 0.015391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2275-11_0_8_line_107 |  | 102 | 105 | 0.013258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2275-11_0_8_line_108 |  | 102 | 103 | 0.008106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2275-11_0_8_line_109 |  | 103 | 104 | 0.007198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2275-11_0_8_line_110 |  | 106 | 107 | 0.020004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2275-11_0_8_line_111 |  | 107 | 108 | 0.027885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2275-11_0_8_line_112 |  | 108 | 109 | 0.022972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2275-11_0_8_line_113 |  | 109 | 123 | 0.039626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2275-11_0_8_line_114 |  | 110 | 111 | 0.05836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2275-11_0_8_line_115 |  | 111 | 139 | 0.0054203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2275-11_0_8_line_116 |  | 112 | 113 | 0.008194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2275-11_0_8_line_117 |  | 113 | 114 | 0.022936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2275-11_0_8_line_118 |  | 114 | 115 | 0.001208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2275-11_0_8_line_119 |  | 115 | 119 | 0.0012613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2275-11_0_8_line_120 |  | 116 | 117 | 0.0026413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2275-11_0_8_line_121 |  | 117 | 118 | 0.01491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2275-11_0_8_line_122 |  | 119 | 120 | 0.025953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2275-11_0_8_line_123 |  | 120 | 121 | 0.020879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2275-11_0_8_line_124 |  | 121 | 122 | 0.023752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2275-11_0_8_line_125 |  | 124 | 125 | 0.012996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2275-11_0_8_line_126 |  | 124 | 126 | 0.043295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2275-11_0_8_line_127 |  | 125 | 127 | 0.075017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2275-11_0_8_line_128 |  | 127 | 128 | 0.009699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2275-11_0_8_line_129 |  | 128 | 129 | 0.010291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2275-11_0_8_line_130 |  | 130 | 131 | 0.036471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2275-11_0_8_line_131 |  | 130 | 132 | 0.023985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2275-11_0_8_line_132 |  | 131 | 133 | 0.00020693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2275-11_0_8_line_133 |  | 132 | 134 | 0.012561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2275-11_0_8_line_134 |  | 133 | 135 | 0.035754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
135 | LV_2275-11_0_8_line_135 |  | 135 | 136 | 0.002818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_2275-11_0_8_line_136 |  | 136 | 137 | 0.0071777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_2275-11_0_8_line_137 |  | 137 | 138 | 0.0048597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_2275-11_0_8_line_138 |  | 138 | 141 | 0.017736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2275-11_0_8_line_139 |  | 138 | 140 | 0.01076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_2275-11_0_8_line_140 |  | 139 | 140 | 0.0090503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_2275-11_0_8_line_141 |  | 141 | 142 | 0.050113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2275-11_0_8_line_142 |  | 142 | 143 | 0.027394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2275-11_0_8_line_143 |  | 143 | 144 | 0.019099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2275-11_0_8_line_144 |  | 144 | 145 | 0.034978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2275-11_0_8_line_145 |  | 145 | 146 | 0.16108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2275-11_0_8_trafo_50 | 0.63 MVA 20/0.4 kV | 147 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2581053.5036 | 1198530.1829 | 2581067.8747 | 1198507.3819 | 2581085.7295 | 1198485.4244 | 2581089.1099 | 1198482.6612
1 | 2581038.1757 | 1198554.5019 | 2581053.5036 | 1198530.1829
2 | 2581038.1757 | 1198554.5019 | 2581073.5213 | 1198558.9584 | 2581096.3365 | 1198561.4752
3 | 2581038.1757 | 1198554.5019 | 2581030.6789 | 1198550.8126 | 2581016.7425 | 1198547.8555 | 2581000.451 | 1198544.5209
4 | 2581038.1757 | 1198554.5019 | 2581028.6436 | 1198573.9983 | 2581023.8943 | 1198583.4175
5 | 2581243.9296 | 1198813.4338 | 2581096.3365 | 1198561.4752
6 | 2581000.451 | 1198544.5209 | 2580988.0246 | 1198541.9773 | 2580954.1091 | 1198535.3946
7 | 2581243.9296 | 1198813.4338 | 2581243.8704 | 1198816.4134 | 2581243.5955 | 1198818.5599 | 2581242.4278 | 1198820.1089 | 2581240.2757 | 1198820.9717
8 | 2581243.9296 | 1198813.4338 | 2581266.7829 | 1198812.764
9 | 2581281.043 | 1198812.3461 | 2581266.7829 | 1198812.764
10 | 2581524.3489 | 1198820.1002 | 2581520.8233 | 1198819.1261
11 | 2581551.8329 | 1198828.4348 | 2581544.2487 | 1198825.8458 | 2581535.9033 | 1198823.2926 | 2581524.3489 | 1198820.1002
12 | 2581520.8233 | 1198819.1261 | 2581518.9929 | 1198818.6203 | 2581516.3854 | 1198818.0673
13 | 2581551.8329 | 1198828.4348 | 2581561.7578 | 1198832.0727 | 2581562.5728 | 1198832.3851
14 | 2581496.476 | 1198814.0295 | 2581502.7716 | 1198815.18 | 2581516.3854 | 1198818.0673
15 | 2581562.6355 | 1198832.4092 | 2581562.5728 | 1198832.3851
16 | 2581496.476 | 1198814.0295 | 2581486.2623 | 1198812.1631 | 2581475.6898 | 1198810.8842 | 2581472.2896 | 1198810.5513
17 | 2581551.7585 | 1198774.3343 | 2581549.9235 | 1198767.6635 | 2581548.6567 | 1198766.7559 | 2581546.4471 | 1198766.2736 | 2581535.0984 | 1198765.4414
18 | 2581533.4272 | 1198765.3188 | 2581535.0984 | 1198765.4414
19 | 2581563.0793 | 1198832.5793 | 2581562.6355 | 1198832.4092
20 | 2581442.256 | 1198808.4759 | 2581464.9048 | 1198809.8283 | 2581472.2896 | 1198810.5513
21 | 2581533.4272 | 1198765.3188 | 2581530.1565 | 1198765.079 | 2581510.8414 | 1198763.3516
22 | 2581563.7582 | 1198832.8396 | 2581563.0793 | 1198832.5793
23 | 2581507.3791 | 1198763.0331 | 2581489.2076 | 1198761.349
24 | 2581474.7113 | 1198760.0055 | 2581489.2076 | 1198761.349
25 | 2581507.3791 | 1198763.0331 | 2581510.095 | 1198763.2848 | 2581510.8414 | 1198763.3516
26 | 2581465.1437 | 1198759.1848 | 2581474.4653 | 1198759.9827 | 2581474.7113 | 1198760.0055
27 | 2581448.151 | 1198757.7191 | 2581461.4338 | 1198758.8672 | 2581465.1437 | 1198759.1848
28 | 2581442.256 | 1198808.4759 | 2581443.4062 | 1198786.6606 | 2581443.9302 | 1198783.7685 | 2581448.151 | 1198757.7191
29 | 2581442.256 | 1198808.4759 | 2581434.3371 | 1198808.5007
30 | 2581346.331 | 1198810.4325 | 2581372.3223 | 1198809.7684
31 | 2581346.331 | 1198810.4325 | 2581298.5873 | 1198811.8319
32 | 2581346.331 | 1198810.4325 | 2581346.6487 | 1198830.0104
33 | 2581640.316 | 1198782.4106 | 2581640.3432 | 1198787.5723 | 2581641.1564 | 1198794.4847 | 2581641.2533 | 1198795.6218
34 | 2581636.935 | 1198766.3492 | 2581639.757 | 1198772.8106 | 2581640.3064 | 1198780.602 | 2581640.316 | 1198782.4106
35 | 2581641.2533 | 1198795.6218 | 2581641.3073 | 1198796.2548
36 | 2581636.935 | 1198766.3492 | 2581636.0133 | 1198697.1814
37 | 2581641.3073 | 1198796.2548 | 2581642.3345 | 1198808.306
38 | 2581636.0133 | 1198697.1814 | 2581630.5582 | 1198696.1532
39 | 2581642.3345 | 1198808.306 | 2581643.113 | 1198817.4392
40 | 2581643.0311 | 1198826.448 | 2581643.3448 | 1198820.1584 | 2581643.113 | 1198817.4392
41 | 2581641.2056 | 1198847.8508 | 2581642.5417 | 1198836.2585 | 2581643.0311 | 1198826.448
42 | 2581639.4717 | 1198862.8934 | 2581641.2056 | 1198847.8508
43 | 2581639.4717 | 1198862.8934 | 2581637.667 | 1198883.0415
44 | 2581639.4717 | 1198862.8934 | 2581665.2187 | 1198870.2138
45 | 2581639.4717 | 1198862.8934 | 2581630.2779 | 1198859.2754 | 2581622.3292 | 1198856.2166
46 | 2581637.4854 | 1198892.8046 | 2581637.5433 | 1198884.4221 | 2581637.667 | 1198883.0415
47 | 2581684.8805 | 1198875.8041 | 2581665.2187 | 1198870.2138
48 | 2581597.0062 | 1198846.1725 | 2581610.5033 | 1198851.6657 | 2581622.3292 | 1198856.2166
49 | 2581637.3676 | 1198901.4874 | 2581637.4483 | 1198895.5617 | 2581637.4854 | 1198892.8046
50 | 2581684.8805 | 1198875.8041 | 2581689.0221 | 1198876.9816 | 2581709.0229 | 1198881.1664
51 | 2581597.0062 | 1198846.1725 | 2581591.0933 | 1198843.7659 | 2581571.5384 | 1198835.8222 | 2581567.3867 | 1198834.2306
52 | 2581724.0009 | 1198884.3003 | 2581709.0229 | 1198881.1664
53 | 2581724.0009 | 1198884.3003 | 2581724.4287 | 1198889.7019 | 2581727.4287 | 1198894.6731 | 2581733.6502 | 1198899.8901 | 2581735.4519 | 1198901.5279
54 | 2581744.8873 | 1198910.1046 | 2581735.4519 | 1198901.5279
55 | 2581744.8873 | 1198910.1046 | 2581770.8267 | 1198933.6832 | 2581775.1773 | 1198935.4934
56 | 2581494.8361 | 1198949.6022 | 2581488.3726 | 1198949.8513
57 | 2581512.3156 | 1198953.4138 | 2581506.3217 | 1198950.4197 | 2581500.5623 | 1198949.3815 | 2581494.8361 | 1198949.6022
58 | 2581479.2227 | 1198950.2039 | 2581488.3726 | 1198949.8513
59 | 2581512.3156 | 1198953.4138 | 2581532.2347 | 1198946.8888
60 | 2581512.3156 | 1198953.4138 | 2581485.757 | 1198967.7931 | 2581474.855 | 1198978.5173
61 | 2581562.7246 | 1198938.8841 | 2581546.6807 | 1198942.1566 | 2581532.2347 | 1198946.8888
62 | 2581464.6017 | 1198988.6035 | 2581474.855 | 1198978.5173
63 | 2581562.7246 | 1198938.8841 | 2581564.5015 | 1198938.5216 | 2581576.1584 | 1198938.4633 | 2581590.0045 | 1198939.6988 | 2581601.0796 | 1198941.0987 | 2581603.8411 | 1198941.1448
64 | 2581464.6017 | 1198988.6035 | 2581460.3001 | 1198996.032 | 2581458.5114 | 1199001.0848 | 2581457.0654 | 1199006.1698 | 2581455.3703 | 1199016.8475 | 2581453.7566 | 1199029.0516
65 | 2581464.6017 | 1198988.6035 | 2581460.1648 | 1198986.8164 | 2581457.498 | 1198986.191 | 2581454.801 | 1198985.6769 | 2581437.6947 | 1198985.1712
66 | 2581610.1653 | 1198941.2506 | 2581603.8411 | 1198941.1448
67 | 2581453.7566 | 1199029.0516 | 2581453.4512 | 1199031.3613 | 2581451.4795 | 1199046.0976 | 2581446.7647 | 1199065.1466
68 | 2581437.6947 | 1198985.1712 | 2581416.5404 | 1198984.5458
69 | 2581633.6513 | 1198935.7952 | 2581623.7354 | 1198939.9391 | 2581612.3033 | 1198941.2863 | 2581610.1653 | 1198941.2506
70 | 2581633.6513 | 1198935.7952 | 2581635.8264 | 1198939.9129
71 | 2581633.6513 | 1198935.7952 | 2581636.7013 | 1198929.8159 | 2581637.4477 | 1198917.5736 | 2581637.4328 | 1198914.5801
72 | 2581635.8264 | 1198939.9129 | 2581636.5376 | 1198948.3264 | 2581638.0658 | 1198957.4488 | 2581637.8216 | 1198964.6979
73 | 2581637.3676 | 1198901.4874 | 2581637.4328 | 1198914.5801
74 | 2581637.3676 | 1198901.4874 | 2581629.4139 | 1198902.4569 | 2581616.6435 | 1198900.2353
75 | 2581602.5217 | 1198897.7708 | 2581603.7558 | 1198897.9894 | 2581604.99 | 1198898.2079 | 2581616.6435 | 1198900.2353
76 | 2581416.5404 | 1198984.5458 | 2581382.8092 | 1198983.5486
77 | 2581347.2188 | 1198983.9836 | 2581347.4768 | 1198983.967 | 2581361.3935 | 1198983.4342 | 2581377.2608 | 1198983.3845 | 2581382.8092 | 1198983.5486
78 | 2581309.9174 | 1198986.3145 | 2581316.0907 | 1198985.9777 | 2581347.2188 | 1198983.9836
79 | 2581440.2021 | 1199091.7612 | 2581441.3513 | 1199087.018 | 2581446.7647 | 1199065.1466
80 | 2581309.9174 | 1198986.3145 | 2581278.2062 | 1198988.0447
81 | 2581440.2021 | 1199091.7612 | 2581439.6073 | 1199094.2162 | 2581439.3076 | 1199097.3255
82 | 2581567.3867 | 1198834.2306 | 2581563.7582 | 1198832.8396
83 | 2581278.2062 | 1198988.0447 | 2581262.4672 | 1198988.9035 | 2581245.2604 | 1198989.7628
84 | 2581780.4438 | 1198859.3137 | 2581774.3536 | 1198859.6881 | 2581769.5341 | 1198859.1354
85 | 2581780.4438 | 1198859.3137 | 2581783.6801 | 1198861.9051 | 2581787.7076 | 1198864.2719 | 2581798.2965 | 1198870.9542 | 2581810.4867 | 1198878.4209 | 2581815.8372 | 1198880.1833 | 2581816.9189 | 1198880.369
86 | 2581775.1773 | 1198935.4934 | 2581796.8466 | 1198944.5094 | 2581803.4733 | 1198945.2963
87 | 2581218.5773 | 1198991.0954 | 2581245.2604 | 1198989.7628
88 | 2581201.0627 | 1198991.9766 | 2581208.7667 | 1198991.5854 | 2581218.5773 | 1198991.0954
89 | 2581353.5696 | 1198931.0527 | 2581353.4944 | 1198926.4949 | 2581351.481 | 1198920.5981 | 2581348.9568 | 1198912.0569 | 2581348.7187 | 1198907.8847
90 | 2581347.5952 | 1198888.1927 | 2581348.7187 | 1198907.8847
91 | 2581353.5696 | 1198931.0527 | 2581351.5517 | 1198938.2852 | 2581348.2577 | 1198942.4601
92 | 2581353.5696 | 1198931.0527 | 2581364.938 | 1198931.3686
93 | 2581347.5952 | 1198888.1927 | 2581331.5284 | 1198887.8763 | 2581330.7616 | 1198887.8397
94 | 2581347.5013 | 1198882.5456 | 2581347.5194 | 1198883.4571 | 2581347.5952 | 1198888.1927
95 | 2581348.2577 | 1198942.4601 | 2581346.4781 | 1198944.7156 | 2581344.1312 | 1198946.1787
96 | 2581386.8067 | 1198931.9763 | 2581364.938 | 1198931.3686
97 | 2581310.8278 | 1198886.8873 | 2581330.7616 | 1198887.8397
98 | 2581347.5013 | 1198882.5456 | 2581350.4218 | 1198881.4803 | 2581353.8027 | 1198881.5475 | 2581360.0079 | 1198883.9071
99 | 2581347.5013 | 1198882.5456 | 2581347.1063 | 1198858.2052
100 | 2581344.1312 | 1198946.1787 | 2581339.8288 | 1198948.861 | 2581330.9707 | 1198950.334 | 2581308.3437 | 1198950.9053 | 2581298.7033 | 1198951.0451
101 | 2581433.3411 | 1198932.2958 | 2581417.3426 | 1198932.8097 | 2581396.3566 | 1198932.2416 | 2581386.8067 | 1198931.9763
102 | 2581310.8278 | 1198886.8873 | 2581302.5227 | 1198886.4906
103 | 2581360.0079 | 1198883.9071 | 2581360.0079 | 1198883.9071 | 2581365.1608 | 1198888.1821 | 2581368.2672 | 1198890.5515 | 2581370.9338 | 1198892.6515
104 | 2581347.1063 | 1198858.2052 | 2581346.6487 | 1198830.0104
105 | 2581298.7033 | 1198951.0451 | 2581275.76 | 1198951.3776
106 | 2581287.1492 | 1198885.7561 | 2581302.5227 | 1198886.4906
107 | 2581599.2841 | 1198909.5428 | 2581600.3811 | 1198909.7283 | 2581602.5217 | 1198897.7708
108 | 2581603.9056 | 1198889.7845 | 2581602.5217 | 1198897.7708
109 | 2581601.8273 | 1198884.9772 | 2581601.1403 | 1198889.3261 | 2581603.9056 | 1198889.7845
110 | 2581275.76 | 1198951.3776 | 2581256.4109 | 1198951.658 | 2581255.7579 | 1198951.6718
111 | 2581227.8789 | 1198952.2664 | 2581230.4488 | 1198952.2068 | 2581255.7579 | 1198951.6718
112 | 2581204.9133 | 1198952.7989 | 2581227.8789 | 1198952.2664
113 | 2581204.9133 | 1198952.7989 | 2581203.1749 | 1198956.851 | 2581202.4222 | 1198962.0228 | 2581201.0627 | 1198991.9766
114 | 2581861.4259 | 1198952.1776 | 2581803.4733 | 1198945.2963
115 | 2581866.8084 | 1198952.8168 | 2581861.4259 | 1198952.1776
116 | 2581287.1492 | 1198885.7561 | 2581278.9645 | 1198885.3651
117 | 2581278.9645 | 1198885.3651 | 2581269.3043 | 1198884.9036 | 2581256.052 | 1198884.3325
118 | 2581256.052 | 1198884.3325 | 2581254.8452 | 1198884.2805
119 | 2581254.8452 | 1198884.2805 | 2581253.585 | 1198884.2262
120 | 2581298.5873 | 1198811.8319 | 2581295.9471 | 1198811.9092
121 | 2581281.043 | 1198812.3461 | 2581295.9471 | 1198811.9092
122 | 2581227.6567 | 1198883.0868 | 2581238.0518 | 1198883.5569 | 2581253.585 | 1198884.2262
123 | 2581206.7991 | 1198882.1436 | 2581227.6567 | 1198883.0868
124 | 2581206.7991 | 1198882.1436 | 2581206.1654 | 1198905.8877
125 | 2581442.0746 | 1199140.4302 | 2581442.2477 | 1199142.4785 | 2581442.8395 | 1199153.4031
126 | 2581442.0746 | 1199140.4302 | 2581441.1646 | 1199129.6638 | 2581439.2227 | 1199114.8952 | 2581438.8772 | 1199101.7892 | 2581439.3076 | 1199097.3255
127 | 2581442.7852 | 1199228.4119 | 2581442.6499 | 1199222.5538 | 2581442.6822 | 1199210.9585 | 2581442.7486 | 1199193.2043 | 2581442.8455 | 1199175.4722 | 2581443.0233 | 1199156.7949 | 2581442.8395 | 1199153.4031
128 | 2581442.7852 | 1199228.4119 | 2581443.0092 | 1199238.1083
129 | 2581443.1071 | 1199248.3987 | 2581443.0636 | 1199240.4622 | 2581443.0092 | 1199238.1083
130 | 2581970.9661 | 1198975.9908 | 2581969.6638 | 1198975.2664 | 2581959.2418 | 1198970.7622 | 2581948.4207 | 1198967.7156 | 2581936.283 | 1198965.2538
131 | 2581991.9265 | 1198987.6501 | 2581970.9661 | 1198975.9908
132 | 2581936.283 | 1198965.2538 | 2581936.0802 | 1198965.2127
133 | 2581991.9265 | 1198987.6501 | 2581987.4477 | 1198999.3855
134 | 2581936.0802 | 1198965.2127 | 2581901.0396 | 1198958.1056
135 | 2581901.0396 | 1198958.1056 | 2581898.2778 | 1198957.5454
136 | 2581891.2434 | 1198956.1187 | 2581898.2778 | 1198957.5454
137 | 2581886.4807 | 1198955.1527 | 2581891.2434 | 1198956.1187
138 | 2581886.4807 | 1198955.1527 | 2581870.5844 | 1198947.2873
139 | 2581886.4807 | 1198955.1527 | 2581875.7955 | 1198953.8839
140 | 2581866.8084 | 1198952.8168 | 2581875.7955 | 1198953.8839
141 | 2581870.5844 | 1198947.2873 | 2581854.9721 | 1198939.5625 | 2581833.6873 | 1198914.7464
142 | 2581818.7291 | 1198892.1809 | 2581820.1752 | 1198896.9791 | 2581822.0282 | 1198900.3641 | 2581826.8217 | 1198906.7418 | 2581833.6873 | 1198914.7464
143 | 2581816.9189 | 1198880.369 | 2581816.899 | 1198881.3251 | 2581817.2301 | 1198882.547 | 2581821.9851 | 1198886.2567 | 2581823.339 | 1198888.3092 | 2581823.2898 | 1198892.1336 | 2581821.4626 | 1198892.1948 | 2581818.7291 | 1198892.1809
144 | 2581816.9189 | 1198880.369 | 2581822.6782 | 1198881.3519 | 2581830.7116 | 1198881.5386 | 2581840.9966 | 1198880.9847 | 2581851.524 | 1198880.0298 | 2581851.7516 | 1198880.0055
145 | 2581851.7516 | 1198880.0055 | 2581877.989 | 1198721.0766

## bus_geodata
| x | y | coords
0 | 2581053.5036 | 1198530.1829
1 | 2581089.1099 | 1198482.6612
2 | 2581038.1757 | 1198554.5019
3 | 2581096.3365 | 1198561.4752
4 | 2581000.451 | 1198544.5209
5 | 2581023.8943 | 1198583.4175
6 | 2581243.9296 | 1198813.4338
7 | 2581240.2757 | 1198820.9717
8 | 2581266.7829 | 1198812.764
9 | 2580954.1091 | 1198535.3946
10 | 2581524.3489 | 1198820.1002
11 | 2581520.8233 | 1198819.1261
12 | 2581551.8329 | 1198828.4348
13 | 2581516.3854 | 1198818.0673
14 | 2581562.5728 | 1198832.3851
15 | 2581496.476 | 1198814.0295
16 | 2581551.7585 | 1198774.3343
17 | 2581535.0984 | 1198765.4414
18 | 2581562.6355 | 1198832.4092
19 | 2581472.2896 | 1198810.5513
20 | 2581533.4272 | 1198765.3188
21 | 2581563.0793 | 1198832.5793
22 | 2581489.2076 | 1198761.349
23 | 2581507.3791 | 1198763.0331
24 | 2581474.7113 | 1198760.0055
25 | 2581510.8414 | 1198763.3516
26 | 2581465.1437 | 1198759.1848
27 | 2581448.151 | 1198757.7191
28 | 2581442.256 | 1198808.4759
29 | 2581434.3371 | 1198808.5007
30 | 2581372.3223 | 1198809.7684
31 | 2581346.331 | 1198810.4325
32 | 2581640.316 | 1198782.4106
33 | 2581641.2533 | 1198795.6218
34 | 2581636.935 | 1198766.3492
35 | 2581641.3073 | 1198796.2548
36 | 2581636.0133 | 1198697.1814
37 | 2581642.3345 | 1198808.306
38 | 2581630.5582 | 1198696.1532
39 | 2581643.113 | 1198817.4392
40 | 2581643.0311 | 1198826.448
41 | 2581641.2056 | 1198847.8508
42 | 2581639.4717 | 1198862.8934
43 | 2581637.667 | 1198883.0415
44 | 2581665.2187 | 1198870.2138
45 | 2581622.3292 | 1198856.2166
46 | 2581637.4854 | 1198892.8046
47 | 2581684.8805 | 1198875.8041
48 | 2581597.0062 | 1198846.1725
49 | 2581709.0229 | 1198881.1664
50 | 2581724.0009 | 1198884.3003
51 | 2581735.4519 | 1198901.5279
52 | 2581744.8873 | 1198910.1046
53 | 2581494.8361 | 1198949.6022
54 | 2581488.3726 | 1198949.8513
55 | 2581512.3156 | 1198953.4138
56 | 2581479.2227 | 1198950.2039
57 | 2581532.2347 | 1198946.8888
58 | 2581474.855 | 1198978.5173
59 | 2581562.7246 | 1198938.8841
60 | 2581464.6017 | 1198988.6035
61 | 2581603.8411 | 1198941.1448
62 | 2581453.7566 | 1199029.0516
63 | 2581437.6947 | 1198985.1712
64 | 2581610.1653 | 1198941.2506
65 | 2581633.6513 | 1198935.7952
66 | 2581635.8264 | 1198939.9129
67 | 2581637.4328 | 1198914.5801
68 | 2581637.8216 | 1198964.6979
69 | 2581637.3676 | 1198901.4874
70 | 2581616.6435 | 1198900.2353
71 | 2581416.5404 | 1198984.5458
72 | 2581382.8092 | 1198983.5486
73 | 2581347.2188 | 1198983.9836
74 | 2581446.7647 | 1199065.1466
75 | 2581309.9174 | 1198986.3145
76 | 2581440.2021 | 1199091.7612
77 | 2581567.3867 | 1198834.2306
78 | 2581563.7582 | 1198832.8396
79 | 2581278.2062 | 1198988.0447
80 | 2581769.5341 | 1198859.1353
81 | 2581780.4438 | 1198859.3137
82 | 2581775.1773 | 1198935.4934
83 | 2581245.2604 | 1198989.7628
84 | 2581218.5773 | 1198991.0954
85 | 2581348.7187 | 1198907.8847
86 | 2581353.5696 | 1198931.0527
87 | 2581347.5952 | 1198888.1927
88 | 2581348.2577 | 1198942.4601
89 | 2581364.938 | 1198931.3686
90 | 2581330.7616 | 1198887.8397
91 | 2581347.5013 | 1198882.5456
92 | 2581344.1312 | 1198946.1787
93 | 2581386.8067 | 1198931.9763
94 | 2581310.8278 | 1198886.8873
95 | 2581360.0079 | 1198883.9071
96 | 2581347.1063 | 1198858.2052
97 | 2581298.7033 | 1198951.0451
98 | 2581433.3411 | 1198932.2958
99 | 2581302.5227 | 1198886.4906
100 | 2581370.9338 | 1198892.6515
101 | 2581346.6487 | 1198830.0104
102 | 2581602.5217 | 1198897.7708
103 | 2581603.9056 | 1198889.7845
104 | 2581601.8273 | 1198884.9772
105 | 2581599.2841 | 1198909.5428
106 | 2581275.76 | 1198951.3776
107 | 2581255.7579 | 1198951.6718
108 | 2581227.8789 | 1198952.2664
109 | 2581204.9133 | 1198952.7989
110 | 2581803.4733 | 1198945.2963
111 | 2581861.4259 | 1198952.1776
112 | 2581287.1492 | 1198885.7561
113 | 2581278.9645 | 1198885.3651
114 | 2581256.052 | 1198884.3325
115 | 2581254.8452 | 1198884.2805
116 | 2581298.5873 | 1198811.8319
117 | 2581295.9471 | 1198811.9092
118 | 2581281.043 | 1198812.3461
119 | 2581253.585 | 1198884.2262
120 | 2581227.6567 | 1198883.0868
121 | 2581206.7991 | 1198882.1436
122 | 2581206.1654 | 1198905.8877
123 | 2581201.0627 | 1198991.9766
124 | 2581442.0746 | 1199140.4302
125 | 2581442.8395 | 1199153.4031
126 | 2581439.3076 | 1199097.3255
127 | 2581442.7852 | 1199228.4119
128 | 2581443.0092 | 1199238.1083
129 | 2581443.1071 | 1199248.3987
130 | 2581970.9661 | 1198975.9908
131 | 2581936.283 | 1198965.2538
132 | 2581991.9265 | 1198987.6501
133 | 2581936.0802 | 1198965.2127
134 | 2581987.4477 | 1198999.3855
135 | 2581901.0396 | 1198958.1056
136 | 2581898.2778 | 1198957.5454
137 | 2581891.2434 | 1198956.1187
138 | 2581886.4807 | 1198955.1527
139 | 2581866.8084 | 1198952.8168
140 | 2581875.7955 | 1198953.8839
141 | 2581870.5844 | 1198947.2873
142 | 2581833.6873 | 1198914.7464
143 | 2581818.7291 | 1198892.1809
144 | 2581816.9189 | 1198880.369
145 | 2581851.7516 | 1198880.0055
146 | 2581877.989 | 1198721.0766
147 | 2581637.3676 | 1198901.4874

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97102 | -0.56077 | 0.00093795 | 0.00023507
1 | 0.97087 | -0.5638 | 0.0027498 | 0.00068916
2 | 0.97112 | -0.55881 | 0 | 0
3 | 0.97171 | -0.5472 | 0.0010227 | 0.00025632
4 | 0.97089 | -0.56348 | 0.0031218 | 0.00078238
5 | 0.97111 | -0.55916 | 0.00059333 | 0.0001487
6 | 0.97491 | -0.48404 | 0 | 0
7 | 0.9749 | -0.48435 | 0.0018439 | 0.00046211
8 | 0.9752 | -0.47833 | 0.0048057 | 0.0012044
9 | 0.97074 | -0.56638 | 0.0033186 | 0.00083173
10 | 0.99089 | -0.17401 | 0.0024785 | 0.00062116
11 | 0.99077 | -0.17642 | 0.00092932 | 0.00023291
12 | 0.99193 | -0.15388 | 0 | 0
13 | 0.99061 | -0.17935 | 0.0028698 | 0.00071924
14 | 0.99235 | -0.14587 | 0.0018568 | 0.00046537
15 | 0.98999 | -0.19135 | 0.0011696 | 0.00029313
16 | 0.98758 | -0.23821 | 0.00039904 | 0.00010001
17 | 0.98759 | -0.23805 | 0.00077501 | 0.00019424
18 | 0.99235 | -0.14582 | 0.0022425 | 0.00056204
19 | 0.98928 | -0.20531 | 0.0069579 | 0.0017438
20 | 0.98759 | -0.23802 | 0.00090215 | 0.0002261
21 | 0.99237 | -0.14545 | 0.0019243 | 0.00048227
22 | 0.98773 | -0.23545 | 0.0019406 | 0.00048637
23 | 0.98765 | -0.23699 | 0.0017195 | 0.00043096
24 | 0.98781 | -0.23372 | 0.002221 | 0.00055664
25 | 0.98764 | -0.23718 | 0.00091911 | 0.00023035
26 | 0.98789 | -0.2322 | 0.0021302 | 0.00053387
27 | 0.98806 | -0.22884 | 0 | 0
28 | 0.98858 | -0.21879 | 0 | 0
29 | 0.98848 | -0.22078 | 0.014108 | 0.0035359
30 | 0.97682 | -0.4466 | 0.0011304 | 0.0002833
31 | 0.97684 | -0.44606 | 0 | 0
32 | 0.99529 | -0.089341 | 0.0024154 | 0.00060535
33 | 0.99538 | -0.087513 | 0.0013996 | 0.00035078
34 | 0.9952 | -0.09093 | 0.0026025 | 0.00065225
35 | 0.99539 | -0.08741 | 0.00040943 | 0.00010261
36 | 0.99503 | -0.094354 | 0 | 0
37 | 0.99549 | -0.085359 | 0.00054245 | 0.00013595
38 | 0.99501 | -0.094628 | 0.002811 | 0.00070449
39 | 0.99558 | -0.083717 | 0.0018185 | 0.00045576
40 | 0.99568 | -0.081812 | 0.00095039 | 0.00023819
41 | 0.99593 | -0.076919 | 0.00059048 | 0.00014799
42 | 0.99612 | -0.073315 | 0 | 0
43 | 0.99762 | -0.044951 | 0.0022136 | 0.00055479
44 | 0.99453 | -0.10333 | 0.0016645 | 0.00041716
45 | 0.99525 | -0.089906 | 0.0015127 | 0.00037912
46 | 0.99834 | -0.031189 | 0 | 0
47 | 0.99333 | -0.12616 | 0.0019443 | 0.0004873
48 | 0.99401 | -0.1138 | 0.00055832 | 0.00013993
49 | 0.99188 | -0.15366 | 0.0023661 | 0.00059299
50 | 0.99099 | -0.17055 | 0 | 0
51 | 0.98973 | -0.19464 | 0.0056062 | 0.001405
52 | 0.98901 | -0.20845 | 0.0016028 | 0.0004017
53 | 0.99472 | -0.10042 | 0.0020988 | 0.000526
54 | 0.99465 | -0.10175 | 0.0045816 | 0.0011483
55 | 0.99495 | -0.095974 | 0 | 0
56 | 0.99459 | -0.1029 | 0.0071253 | 0.0017858
57 | 0.99564 | -0.08292 | 0.0050103 | 0.0012557
58 | 0.99361 | -0.12159 | 0.0036352 | 0.00091108
59 | 0.9967 | -0.062596 | 0.0032154 | 0.00080585
60 | 0.9932 | -0.12948 | 0 | 0
61 | 0.99813 | -0.035497 | 0.0017273 | 0.0004329
62 | 0.99229 | -0.147 | 0.00175 | 0.00043859
63 | 0.99256 | -0.14167 | 0.0034462 | 0.0008637
64 | 0.99835 | -0.031306 | 0.001694 | 0.00042456
65 | 0.99921 | -0.014976 | 0 | 0
66 | 0.9992 | -0.015225 | 0 | 0
67 | 1 | 0 | -0.49828 | -0.12762
68 | 0.99913 | -0.01656 | 0.0030639 | 0.00076789
69 | 0.99899 | -0.018973 | 0 | 0
70 | 0.9988 | -0.022723 | 0.00070437 | 0.00017653
71 | 0.99209 | -0.15078 | 0.0024434 | 0.00061238
72 | 0.99134 | -0.16496 | 0.0027778 | 0.00069619
73 | 0.99059 | -0.1795 | 0.0018056 | 0.00045253
74 | 0.99156 | -0.16112 | 0.0039359 | 0.00098643
75 | 0.98981 | -0.19449 | 0.0018128 | 0.00045432
76 | 0.99112 | -0.16973 | 0.0038996 | 0.00097734
77 | 0.99257 | -0.14157 | 0.0013543 | 0.00033942
78 | 0.9924 | -0.14486 | 0.0023145 | 0.00058008
79 | 0.98916 | -0.20699 | 0.0044187 | 0.0011074
80 | 0.97862 | -0.40974 | 0.0033027 | 0.00082772
81 | 0.97865 | -0.40908 | 0 | 0
82 | 0.98678 | -0.25137 | 0.011986 | 0.003004
83 | 0.98851 | -0.21934 | 0.0036595 | 0.00091716
84 | 0.98802 | -0.22891 | 0.0027313 | 0.00068454
85 | 0.97969 | -0.39028 | 0.0023769 | 0.00059571
86 | 0.98096 | -0.36555 | 0 | 0
87 | 0.97869 | -0.4099 | 0 | 0
88 | 0.98171 | -0.35092 | 0.0014685 | 0.00036804
89 | 0.9809 | -0.36677 | 0.00071312 | 0.00017873
90 | 0.97826 | -0.41836 | 0.000763 | 0.00019123
91 | 0.97855 | -0.41269 | 0 | 0
92 | 0.98205 | -0.34435 | 0.0016884 | 0.00042315
93 | 0.98079 | -0.36882 | 0.0018888 | 0.00047337
94 | 0.97776 | -0.42812 | 0.00061149 | 0.00015325
95 | 0.97853 | -0.41303 | 0.00051411 | 0.00012885
96 | 0.97797 | -0.42408 | 0.00023284 | 5.8355e-05
97 | 0.9849 | -0.28912 | 0.0037211 | 0.0009326
98 | 0.98065 | -0.3716 | 0.0032941 | 0.00082559
99 | 0.97756 | -0.43209 | 0.002147 | 0.0005381
100 | 0.97852 | -0.41326 | 0.0009037 | 0.00022649
101 | 0.9773 | -0.43718 | 0.00063744 | 0.00015976
102 | 0.99867 | -0.025111 | 0 | 0
103 | 0.99865 | -0.025517 | 0 | 0
104 | 0.99863 | -0.025877 | 0.0028643 | 0.00071785
105 | 0.99859 | -0.026655 | 0.0066655 | 0.0016705
106 | 0.98564 | -0.27472 | 0.0019453 | 0.00048754
107 | 0.98608 | -0.26614 | 0.0036307 | 0.00090994
108 | 0.98657 | -0.25671 | 0.002128 | 0.00053332
109 | 0.98699 | -0.24873 | 0 | 0
110 | 0.98517 | -0.28241 | 0.00046828 | 0.00011736
111 | 0.98205 | -0.34267 | 0.00025231 | 6.3234e-05
112 | 0.97722 | -0.43885 | 0.002224 | 0.0005574
113 | 0.97705 | -0.44212 | 0.0023812 | 0.00059678
114 | 0.97664 | -0.45028 | 0.0055337 | 0.0013869
115 | 0.97662 | -0.45058 | 0.0029417 | 0.00073725
116 | 0.97579 | -0.46677 | 0.0012099 | 0.00030322
117 | 0.97573 | -0.46785 | 0.0017434 | 0.00043694
118 | 0.97545 | -0.47352 | 0.0023368 | 0.00058566
119 | 0.97661 | -0.45084 | 0.0014468 | 0.00036261
120 | 0.97638 | -0.45537 | 0.0043414 | 0.0010881
121 | 0.97628 | -0.45735 | 0 | 0
122 | 0.97616 | -0.45961 | 0.0052032 | 0.001304
123 | 0.9877 | -0.23499 | 0 | 0
124 | 0.99067 | -0.17849 | 0.00049852 | 0.00012494
125 | 0.99056 | -0.18059 | 0.0044773 | 0.0011221
126 | 0.99105 | -0.17111 | 0.0042098 | 0.0010551
127 | 0.99024 | -0.18674 | 0.0014648 | 0.00036712
128 | 0.99022 | -0.18728 | 0.0026522 | 0.00066471
129 | 0.99021 | -0.18738 | 0.00049892 | 0.00012504
130 | 0.97327 | -0.51471 | 0.072184 | 0.018091
131 | 0.97671 | -0.44706 | 0.034284 | 0.0085924
132 | 0.97262 | -0.52751 | 0 | 0
133 | 0.97674 | -0.44654 | 0.059841 | 0.014998
134 | 0.97228 | -0.53422 | 0.028988 | 0.0072652
135 | 0.97999 | -0.38297 | 0.014721 | 0.0036895
136 | 0.98012 | -0.38028 | 0.00038607 | 9.6759e-05
137 | 0.98047 | -0.37344 | 5.2152e-05 | 1.3071e-05
138 | 0.98071 | -0.3688 | 0 | 0
139 | 0.98177 | -0.34828 | 4.8166e-05 | 1.2072e-05
140 | 0.98128 | -0.35765 | 0.00014205 | 3.56e-05
141 | 0.98041 | -0.3747 | 0.0001341 | 3.361e-05
142 | 0.97956 | -0.39128 | 0.00016299 | 4.0849e-05
143 | 0.9791 | -0.40027 | 0 | 0
144 | 0.97878 | -0.40654 | 0 | 0
145 | 0.9783 | -0.41593 | 0.00018692 | 4.6846e-05
146 | 0.97613 | -0.45874 | 0.014559 | 0.0036489
147 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0027502 | 0.00068868 | -0.0027498 | -0.00068916 | 3.9708e-07 | -4.8324e-07 | 0.0042142 | 0.0042145 | 0.0042145 | 0.97102 | -0.56077 | 0.97087 | -0.5638 | 1.1578
1 | -0.0036881 | -0.00092375 | 0.0036885 | 0.00092361 | 3.443e-07 | -1.3528e-07 | 0.0056515 | 0.0056514 | 0.0056515 | 0.97102 | -0.56077 | 0.97112 | -0.55881 | 1.5526
2 | -0.010724 | -0.0026862 | 0.01073 | 0.0026892 | 5.9309e-06 | 3.0706e-06 | 0.016432 | 0.016431 | 0.016432 | 0.97112 | -0.55881 | 0.97171 | -0.5472 | 4.5142
3 | 0.0064423 | 0.0016143 | -0.0064408 | -0.0016138 | 1.4335e-06 | 4.3218e-07 | 0.0098711 | 0.0098713 | 0.0098713 | 0.97112 | -0.55881 | 0.97089 | -0.56348 | 2.7119
4 | 0.00059334 | 0.00014831 | -0.00059333 | -0.0001487 | 9.995e-09 | -3.9262e-07 | 0.00090901 | 0.00090916 | 0.00090916 | 0.97112 | -0.55881 | 0.97111 | -0.55916 | 0.24977
5 | -0.011753 | -0.0029456 | 0.011788 | 0.0029646 | 3.5466e-05 | 1.9069e-05 | 0.017997 | 0.017996 | 0.017997 | 0.97171 | -0.5472 | 0.97491 | -0.48404 | 4.9444
6 | 0.0033191 | 0.00083144 | -0.0033186 | -0.00083173 | 4.5833e-07 | -2.9068e-07 | 0.0050868 | 0.005087 | 0.005087 | 0.97089 | -0.56348 | 0.97074 | -0.56638 | 1.3975
7 | 0.0018439 | 0.00046202 | -0.0018439 | -0.00046211 | 2.7927e-08 | -9.9368e-08 | 0.0028143 | 0.0028143 | 0.0028143 | 0.97491 | -0.48404 | 0.9749 | -0.48435 | 0.77317
8 | -0.013632 | -0.0034267 | 0.013636 | 0.0034287 | 3.713e-06 | 2.0912e-06 | 0.02081 | 0.02081 | 0.02081 | 0.97491 | -0.48404 | 0.9752 | -0.47833 | 5.7172
9 | -0.018442 | -0.0046332 | 0.018446 | 0.0046357 | 4.2373e-06 | 2.5338e-06 | 0.028143 | 0.028143 | 0.028143 | 0.9752 | -0.47833 | 0.97545 | -0.47352 | 7.7316
10 | 0.037118 | 0.0093289 | -0.037113 | -0.0093262 | 4.2629e-06 | 2.6811e-06 | 0.055749 | 0.055749 | 0.055749 | 0.99089 | -0.17401 | 0.99077 | -0.17642 | 15.3156
11 | -0.039596 | -0.0099501 | 0.039634 | 0.0099741 | 3.8102e-05 | 2.4015e-05 | 0.059471 | 0.059471 | 0.059471 | 0.99089 | -0.17401 | 0.99193 | -0.15388 | 16.3381
12 | 0.036184 | 0.0090933 | -0.036179 | -0.0090901 | 5.0568e-06 | 3.1776e-06 | 0.054353 | 0.054353 | 0.054353 | 0.99077 | -0.17642 | 0.99061 | -0.17935 | 14.9322
13 | -0.039634 | -0.0099741 | 0.039649 | 0.0099836 | 1.5177e-05 | 9.5656e-06 | 0.059471 | 0.05947 | 0.059471 | 0.99193 | -0.15388 | 0.99235 | -0.14587 | 16.3381
14 | 0.033309 | 0.0083709 | -0.03329 | -0.0083589 | 1.9079e-05 | 1.1949e-05 | 0.050042 | 0.050042 | 0.050042 | 0.99061 | -0.17935 | 0.98999 | -0.19135 | 13.7479
15 | -0.041506 | -0.010449 | 0.041506 | 0.010449 | 9.7617e-08 | 6.1609e-08 | 0.062255 | 0.062255 | 0.062255 | 0.99235 | -0.14587 | 0.99235 | -0.14582 | 17.103
16 | 0.03212 | 0.0080658 | -0.032099 | -0.0080524 | 2.1375e-05 | 1.3366e-05 | 0.048284 | 0.048284 | 0.048284 | 0.98999 | -0.19135 | 0.98928 | -0.20531 | 13.265
17 | -0.00039904 | -0.00010001 | 0.00039904 | 9.9728e-05 | 2.9978e-09 | -2.8109e-07 | 0.00060125 | 0.00060115 | 0.00060125 | 0.98758 | -0.23821 | 0.98759 | -0.23805 | 0.16518
18 | -0.0011741 | -0.00029396 | 0.0011741 | 0.00029394 | 1.9662e-09 | -2.0183e-08 | 0.0017689 | 0.0017689 | 0.0017689 | 0.98759 | -0.23805 | 0.98759 | -0.23802 | 0.48595
19 | -0.043749 | -0.011011 | 0.04375 | 0.011012 | 7.6746e-07 | 4.8503e-07 | 0.065617 | 0.065617 | 0.065617 | 0.99235 | -0.14582 | 0.99237 | -0.14545 | 18.0268
20 | 0.025141 | 0.0063086 | -0.025125 | -0.0062987 | 1.6149e-05 | 9.9491e-06 | 0.037819 | 0.037819 | 0.037819 | 0.98928 | -0.20531 | 0.98858 | -0.21879 | 10.3898
21 | -0.0020762 | -0.00052004 | 0.0020763 | 0.00051981 | 8.319e-08 | -2.3687e-07 | 0.0031281 | 0.003128 | 0.0031281 | 0.98759 | -0.23802 | 0.98764 | -0.23718 | 0.85938
22 | -0.045674 | -0.011494 | 0.045675 | 0.011495 | 1.2794e-06 | 8.0944e-07 | 0.068503 | 0.068503 | 0.068503 | 0.99237 | -0.14545 | 0.9924 | -0.14486 | 18.8195
23 | 0.0047153 | 0.0011811 | -0.004715 | -0.0011811 | 3.4531e-07 | -1.2557e-08 | 0.0071034 | 0.0071035 | 0.0071035 | 0.98773 | -0.23545 | 0.98765 | -0.23699 | 1.9515
24 | -0.0066559 | -0.0016674 | 0.0066565 | 0.0016676 | 5.4889e-07 | 1.6494e-07 | 0.010027 | 0.010027 | 0.010027 | 0.98773 | -0.23545 | 0.98781 | -0.23372 | 2.7547
25 | 0.0029954 | 0.00075013 | -0.0029954 | -0.00075016 | 2.6553e-08 | -2.7501e-08 | 0.0045128 | 0.0045128 | 0.0045128 | 0.98765 | -0.23699 | 0.98764 | -0.23718 | 1.2398
26 | -0.0088775 | -0.0022243 | 0.0088782 | 0.0022245 | 6.4396e-07 | 2.8919e-07 | 0.013373 | 0.013373 | 0.013373 | 0.98781 | -0.23372 | 0.98789 | -0.2322 | 3.6738
27 | -0.011008 | -0.0027584 | 0.01101 | 0.0027593 | 1.7585e-06 | 9.07e-07 | 0.016581 | 0.016581 | 0.016581 | 0.98789 | -0.2322 | 0.98806 | -0.22884 | 4.5553
28 | -0.01101 | -0.0027593 | 0.011015 | 0.002762 | 5.2759e-06 | 2.7208e-06 | 0.016581 | 0.016581 | 0.016581 | 0.98806 | -0.22884 | 0.98858 | -0.21879 | 4.5552
29 | 0.01411 | 0.0035366 | -0.014108 | -0.0035359 | 1.3395e-06 | 7.5574e-07 | 0.021238 | 0.021238 | 0.021238 | 0.98858 | -0.21879 | 0.98848 | -0.22078 | 5.8347
30 | -0.0011304 | -0.0002833 | 0.0011304 | 0.000283 | 2.8908e-08 | -3.0698e-07 | 0.001722 | 0.0017218 | 0.001722 | 0.97682 | -0.4466 | 0.97684 | -0.44606 | 0.47307
31 | 0.023766 | 0.0059801 | -0.023743 | -0.0059657 | 2.3487e-05 | 1.4434e-05 | 0.036211 | 0.036211 | 0.036211 | 0.97684 | -0.44606 | 0.97579 | -0.46677 | 9.9482
32 | -0.024897 | -0.0062631 | 0.024907 | 0.0062696 | 1.0566e-05 | 6.5167e-06 | 0.037933 | 0.037933 | 0.037933 | 0.97684 | -0.44606 | 0.9773 | -0.43718 | 10.4212
33 | -0.0078297 | -0.0019615 | 0.0078304 | 0.0019617 | 6.815e-07 | 2.6378e-07 | 0.011706 | 0.011706 | 0.011706 | 0.99529 | -0.089341 | 0.99538 | -0.087513 | 3.2158
34 | 0.0054144 | 0.0013561 | -0.0054139 | -0.0013561 | 4.096e-07 | 4.5516e-08 | 0.0080945 | 0.0080946 | 0.0080946 | 0.99529 | -0.089341 | 0.9952 | -0.09093 | 2.2238
35 | -0.0092301 | -0.0023125 | 0.0092301 | 0.0023126 | 4.5357e-08 | 2.0771e-08 | 0.013798 | 0.013798 | 0.013798 | 0.99538 | -0.087513 | 0.99539 | -0.08741 | 3.7907
36 | 0.0028115 | 0.00070384 | -0.002811 | -0.00070444 | 4.5836e-07 | -6.0532e-07 | 0.0042034 | 0.0042037 | 0.0042037 | 0.9952 | -0.09093 | 0.99503 | -0.094354 | 1.1549
37 | -0.0096396 | -0.0024152 | 0.0096405 | 0.0024156 | 9.4181e-07 | 4.4552e-07 | 0.01441 | 0.01441 | 0.01441 | 0.99539 | -0.08741 | 0.99549 | -0.085359 | 3.9588
38 | 0.002811 | 0.00070444 | -0.002811 | -0.00070449 | 3.6685e-08 | -4.8428e-08 | 0.0042037 | 0.0042037 | 0.0042037 | 0.99503 | -0.094354 | 0.99501 | -0.094628 | 1.1549
39 | -0.010183 | -0.0025516 | 0.010184 | 0.002552 | 7.9635e-07 | 3.9048e-07 | 0.015221 | 0.015221 | 0.015221 | 0.99549 | -0.085359 | 0.99558 | -0.083717 | 4.1815
40 | -0.012002 | -0.0030077 | 0.012003 | 0.0030083 | 1.0893e-06 | 5.7974e-07 | 0.017939 | 0.017939 | 0.017939 | 0.99558 | -0.083717 | 0.99568 | -0.081812 | 4.9282
41 | -0.012954 | -0.0032465 | 0.012957 | 0.0032481 | 3.0204e-06 | 1.6535e-06 | 0.019359 | 0.019359 | 0.019359 | 0.99568 | -0.081812 | 0.99593 | -0.076919 | 5.3184
42 | -0.013547 | -0.0033961 | 0.01355 | 0.0033974 | 2.3264e-06 | 1.2918e-06 | 0.020241 | 0.020241 | 0.020241 | 0.99593 | -0.076919 | 0.99612 | -0.073315 | 5.5608
43 | -0.32467 | -0.083272 | 0.32511 | 0.083557 | 0.00044732 | 0.00028523 | 0.48567 | 0.48567 | 0.48567 | 0.99612 | -0.073315 | 0.99762 | -0.044951 | 33.3564
44 | 0.25953 | 0.066832 | -0.25915 | -0.066592 | 0.00037842 | 0.0002408 | 0.38833 | 0.38833 | 0.38833 | 0.99612 | -0.073315 | 0.99453 | -0.10333 | 26.671
45 | 0.051586 | 0.013042 | -0.051545 | -0.013016 | 4.1011e-05 | 2.6008e-05 | 0.077101 | 0.077101 | 0.077101 | 0.99612 | -0.073315 | 0.99525 | -0.089906 | 21.1815
46 | -0.32733 | -0.084112 | 0.32755 | 0.084251 | 0.00021897 | 0.00013963 | 0.48897 | 0.48897 | 0.48897 | 0.99762 | -0.044951 | 0.99834 | -0.031189 | 33.5832
47 | 0.25749 | 0.066175 | -0.2572 | -0.065993 | 0.00028529 | 0.00018153 | 0.38584 | 0.38584 | 0.38584 | 0.99453 | -0.10333 | 0.99333 | -0.12616 | 26.5
48 | 0.050033 | 0.012637 | -0.049975 | -0.0126 | 5.722e-05 | 3.6267e-05 | 0.074839 | 0.074839 | 0.074839 | 0.99525 | -0.089906 | 0.99401 | -0.1138 | 20.5602
49 | -0.32755 | -0.084251 | 0.32774 | 0.084375 | 0.00019464 | 0.00012412 | 0.48897 | 0.48897 | 0.48897 | 0.99834 | -0.031189 | 0.99899 | -0.018973 | 33.5832
50 | 0.25526 | 0.065506 | -0.25492 | -0.065289 | 0.00034009 | 0.00021638 | 0.38293 | 0.38293 | 0.38293 | 0.99333 | -0.12616 | 0.99188 | -0.15366 | 26.3
51 | 0.049417 | 0.012461 | -0.049352 | -0.012419 | 6.5589e-05 | 4.1563e-05 | 0.074003 | 0.074004 | 0.074004 | 0.99401 | -0.1138 | 0.99257 | -0.14157 | 20.3307
52 | 0.25255 | 0.064696 | -0.25235 | -0.064565 | 0.00020648 | 0.00013136 | 0.37938 | 0.37938 | 0.37938 | 0.99188 | -0.15366 | 0.99099 | -0.17055 | 26.0562
53 | 0.25235 | 0.064565 | -0.25205 | -0.064378 | 0.00029387 | 0.00018696 | 0.37938 | 0.37938 | 0.37938 | 0.99099 | -0.17055 | 0.98973 | -0.19464 | 26.0562
54 | 0.24645 | 0.062973 | -0.24628 | -0.062868 | 0.00016449 | 0.00010462 | 0.37095 | 0.37095 | 0.37095 | 0.98973 | -0.19464 | 0.98901 | -0.20845 | 25.4774
55 | 0.24468 | 0.062467 | -0.24417 | -0.062145 | 0.00050635 | 0.00032203 | 0.36854 | 0.36854 | 0.36854 | 0.98901 | -0.20845 | 0.98678 | -0.25137 | 25.3118
56 | 0.011708 | 0.0029345 | -0.011707 | -0.0029342 | 7.4406e-07 | 3.9224e-07 | 0.017514 | 0.017514 | 0.017514 | 0.99472 | -0.10042 | 0.99465 | -0.10175 | 4.8116
57 | -0.013807 | -0.0034605 | 0.01381 | 0.0034622 | 2.9246e-06 | 1.6344e-06 | 0.020654 | 0.020654 | 0.020654 | 0.99472 | -0.10042 | 0.99495 | -0.095974 | 5.6741
58 | 0.0071257 | 0.0017859 | -0.0071253 | -0.0017858 | 3.902e-07 | 1.3089e-07 | 0.01066 | 0.01066 | 0.01066 | 0.99465 | -0.10175 | 0.99459 | -0.1029 | 2.9286
59 | -0.14293 | -0.036348 | 0.14302 | 0.036405 | 8.995e-05 | 5.6478e-05 | 0.21395 | 0.21395 | 0.21395 | 0.99495 | -0.095974 | 0.99564 | -0.08292 | 14.6944
60 | 0.12912 | 0.032886 | -0.12896 | -0.032787 | 0.00015936 | 9.9629e-05 | 0.1933 | 0.1933 | 0.1933 | 0.99495 | -0.095974 | 0.99361 | -0.12159 | 13.2759
61 | -0.14803 | -0.037661 | 0.14818 | 0.037752 | 0.00014515 | 9.1253e-05 | 0.22144 | 0.22144 | 0.22144 | 0.99564 | -0.08292 | 0.9967 | -0.062596 | 15.2086
62 | 0.12533 | 0.031876 | -0.12528 | -0.031846 | 4.7583e-05 | 2.9708e-05 | 0.18785 | 0.18785 | 0.18785 | 0.99361 | -0.12159 | 0.9932 | -0.12948 | 12.902
63 | -0.15139 | -0.038558 | 0.15159 | 0.038682 | 0.00019816 | 0.00012467 | 0.22624 | 0.22624 | 0.22624 | 0.9967 | -0.062596 | 0.99813 | -0.035497 | 15.5383
64 | 0.023435 | 0.0058887 | -0.023416 | -0.0058767 | 1.9585e-05 | 1.1987e-05 | 0.035116 | 0.035116 | 0.035116 | 0.9932 | -0.12948 | 0.99229 | -0.147 | 9.6473
65 | 0.10184 | 0.025957 | -0.10178 | -0.02592 | 5.9886e-05 | 3.6911e-05 | 0.15274 | 0.15274 | 0.15274 | 0.9932 | -0.12948 | 0.99256 | -0.14167 | 10.4902
66 | -0.15332 | -0.039115 | 0.15335 | 0.039135 | 3.1045e-05 | 1.9538e-05 | 0.22881 | 0.22881 | 0.22881 | 0.99813 | -0.035497 | 0.99835 | -0.031306 | 15.7151
67 | 0.021666 | 0.0054382 | -0.021651 | -0.0054293 | 1.4578e-05 | 8.8544e-06 | 0.032492 | 0.032492 | 0.032492 | 0.99229 | -0.147 | 0.99156 | -0.16112 | 8.9264
68 | 0.098338 | 0.025057 | -0.098295 | -0.02503 | 4.3208e-05 | 2.656e-05 | 0.14757 | 0.14757 | 0.14757 | 0.99256 | -0.14167 | 0.99209 | -0.15078 | 10.1354
69 | -0.15504 | -0.039559 | 0.15517 | 0.039636 | 0.0001224 | 7.7059e-05 | 0.23134 | 0.23134 | 0.23134 | 0.99835 | -0.031306 | 0.99921 | -0.014976 | 15.8885
70 | 0.0030642 | 0.00076765 | -0.0030641 | -0.00076769 | 3.6346e-08 | -3.7712e-08 | 0.004563 | 0.004563 | 0.004563 | 0.99921 | -0.014976 | 0.9992 | -0.015225 | 1.2536
71 | -0.15823 | -0.040404 | 0.15834 | 0.040476 | 0.00011462 | 7.2206e-05 | 0.2359 | 0.2359 | 0.2359 | 0.99921 | -0.014976 | 1 | 0 | 16.2018
72 | 0.0030641 | 0.00076769 | -0.0030639 | -0.00076789 | 1.9482e-07 | -2.021e-07 | 0.004563 | 0.0045631 | 0.0045631 | 0.9992 | -0.015225 | 0.99913 | -0.01656 | 1.2536
73 | 0.33829 | 0.087141 | -0.33798 | -0.086942 | 0.00031206 | 0.00019903 | 0.50422 | 0.50422 | 0.50422 | 1 | 0 | 0.99899 | -0.018973 | 34.6305
74 | 0.010238 | 0.0025663 | -0.010236 | -0.0025654 | 1.8291e-06 | 8.9605e-07 | 0.015249 | 0.015249 | 0.015249 | 0.99899 | -0.018973 | 0.9988 | -0.022723 | 4.1894
75 | 0.0095314 | 0.0023889 | -0.0095304 | -0.0023884 | 1.084e-06 | 5.0615e-07 | 0.0142 | 0.0142 | 0.0142 | 0.9988 | -0.022723 | 0.99867 | -0.025111 | 3.9011
76 | 0.095852 | 0.024418 | -0.095786 | -0.024377 | 6.5518e-05 | 4.019e-05 | 0.14391 | 0.14391 | 0.14391 | 0.99209 | -0.15078 | 0.99134 | -0.16496 | 9.8838
77 | 0.093008 | 0.023681 | -0.092943 | -0.023641 | 6.5178e-05 | 3.9879e-05 | 0.13974 | 0.13974 | 0.13974 | 0.99134 | -0.16496 | 0.99059 | -0.1795 | 9.5975
78 | 0.091137 | 0.023189 | -0.091072 | -0.023149 | 6.579e-05 | 4.0182e-05 | 0.13703 | 0.13703 | 0.13703 | 0.99059 | -0.1795 | 0.98981 | -0.19449 | 9.4112
79 | 0.017715 | 0.0044429 | -0.017708 | -0.0044386 | 7.2655e-06 | 4.2965e-06 | 0.026586 | 0.026586 | 0.026586 | 0.99156 | -0.16112 | 0.99112 | -0.16973 | 7.3038
80 | 0.089259 | 0.022694 | -0.089205 | -0.022662 | 5.3703e-05 | 3.2738e-05 | 0.1343 | 0.1343 | 0.1343 | 0.98981 | -0.19449 | 0.98916 | -0.20699 | 9.2241
81 | 0.013808 | 0.0034612 | -0.013807 | -0.0034607 | 9.1055e-07 | 5.0995e-07 | 0.020731 | 0.020731 | 0.020731 | 0.99112 | -0.16973 | 0.99105 | -0.17111 | 5.6954
82 | 0.047997 | 0.01208 | -0.04799 | -0.012075 | 7.5488e-06 | 4.781e-06 | 0.071973 | 0.071973 | 0.071973 | 0.99257 | -0.14157 | 0.9924 | -0.14486 | 19.7729
83 | 0.084786 | 0.021554 | -0.084736 | -0.021524 | 5.0402e-05 | 3.0564e-05 | 0.12766 | 0.12766 | 0.12766 | 0.98916 | -0.20699 | 0.98851 | -0.21934 | 8.7676
84 | -0.0033027 | -0.00082772 | 0.0033028 | 0.00082765 | 1.0358e-07 | -7.133e-08 | 0.0050218 | 0.0050217 | 0.0050218 | 0.97862 | -0.40974 | 0.97865 | -0.40908 | 1.3796
85 | -0.0033028 | -0.00082765 | 0.0033032 | 0.00082738 | 3.9977e-07 | -2.7542e-07 | 0.0050217 | 0.0050215 | 0.0050217 | 0.97865 | -0.40908 | 0.97878 | -0.40654 | 1.3796
86 | 0.23219 | 0.059141 | -0.23184 | -0.05892 | 0.0003471 | 0.00022061 | 0.35047 | 0.35047 | 0.35047 | 0.98678 | -0.25137 | 0.98517 | -0.28241 | 24.0705
87 | 0.081076 | 0.020606 | -0.081039 | -0.020584 | 3.737e-05 | 2.2547e-05 | 0.12215 | 0.12215 | 0.12215 | 0.98851 | -0.21934 | 0.98802 | -0.22891 | 8.3893
88 | 0.078308 | 0.019899 | -0.078285 | -0.019886 | 2.2906e-05 | 1.3762e-05 | 0.11803 | 0.11803 | 0.11803 | 0.98802 | -0.22891 | 0.9877 | -0.23499 | 8.1068
89 | -0.057302 | -0.014438 | 0.05737 | 0.014481 | 6.786e-05 | 4.313e-05 | 0.087061 | 0.087061 | 0.087061 | 0.97969 | -0.39028 | 0.98096 | -0.36555 | 23.9178
90 | 0.054925 | 0.013842 | -0.054873 | -0.01381 | 5.1509e-05 | 3.2718e-05 | 0.083451 | 0.083451 | 0.083451 | 0.97969 | -0.39028 | 0.97869 | -0.4099 | 22.926
91 | -0.063267 | -0.015959 | 0.063311 | 0.015987 | 4.4334e-05 | 2.8212e-05 | 0.096006 | 0.096006 | 0.096006 | 0.98096 | -0.36555 | 0.98171 | -0.35092 | 26.3753
92 | 0.0058973 | 0.0014775 | -0.005897 | -0.0014774 | 3.4127e-07 | 7.4848e-08 | 0.0089454 | 0.0089455 | 0.0089455 | 0.98096 | -0.36555 | 0.9809 | -0.36677 | 2.4575
93 | 0.027644 | 0.006946 | -0.027633 | -0.0069391 | 1.1158e-05 | 6.9295e-06 | 0.042037 | 0.042037 | 0.042037 | 0.97869 | -0.4099 | 0.97826 | -0.41836 | 11.5487
94 | 0.027229 | 0.0068636 | -0.027225 | -0.0068613 | 3.6325e-06 | 2.2539e-06 | 0.041413 | 0.041414 | 0.041414 | 0.97869 | -0.4099 | 0.97855 | -0.41269 | 11.3773
95 | -0.06478 | -0.016355 | 0.0648 | 0.016368 | 2.0404e-05 | 1.2987e-05 | 0.098232 | 0.098232 | 0.098232 | 0.98171 | -0.35092 | 0.98205 | -0.34435 | 26.9868
96 | 0.0051838 | 0.0012987 | -0.0051833 | -0.0012986 | 5.0731e-07 | 4.8558e-08 | 0.0078637 | 0.0078638 | 0.0078638 | 0.9809 | -0.36677 | 0.98079 | -0.36882 | 2.1604
97 | 0.02687 | 0.0067479 | -0.026858 | -0.0067401 | 1.2505e-05 | 7.7525e-06 | 0.040877 | 0.040877 | 0.040877 | 0.97826 | -0.41836 | 0.97776 | -0.42812 | 11.2299
98 | 0.0014178 | 0.00035502 | -0.0014178 | -0.00035517 | 2.2884e-08 | -1.5028e-07 | 0.0021559 | 0.002156 | 0.002156 | 0.97855 | -0.41269 | 0.97853 | -0.41303 | 0.5923
99 | 0.025808 | 0.0065063 | -0.025793 | -0.0064976 | 1.4069e-05 | 8.6986e-06 | 0.039258 | 0.039258 | 0.039258 | 0.97855 | -0.41269 | 0.97797 | -0.42408 | 10.7851
100 | -0.066488 | -0.016791 | 0.066665 | 0.016903 | 0.00017648 | 0.00011236 | 0.10079 | 0.10079 | 0.10079 | 0.98205 | -0.34435 | 0.9849 | -0.28912 | 27.6896
101 | 0.0032946 | 0.00082528 | -0.0032941 | -0.00082559 | 4.3615e-07 | -3.083e-07 | 0.0049982 | 0.0049984 | 0.0049984 | 0.98079 | -0.36882 | 0.98065 | -0.3716 | 1.3732
102 | 0.026246 | 0.0065869 | -0.026241 | -0.0065838 | 4.9753e-06 | 3.0799e-06 | 0.039946 | 0.039946 | 0.039946 | 0.97776 | -0.42812 | 0.97756 | -0.43209 | 10.9742
103 | 0.00090371 | 0.00022632 | -0.0009037 | -0.00022649 | 9.9118e-09 | -1.6948e-07 | 0.0013742 | 0.0013742 | 0.0013742 | 0.97853 | -0.41303 | 0.97852 | -0.41326 | 0.37754
104 | 0.025561 | 0.0064393 | -0.025545 | -0.0064294 | 1.6004e-05 | 9.8891e-06 | 0.038903 | 0.038904 | 0.038904 | 0.97797 | -0.42408 | 0.9773 | -0.43718 | 10.6878
105 | -0.070386 | -0.017836 | 0.070435 | 0.017867 | 4.8717e-05 | 3.0594e-05 | 0.10641 | 0.10641 | 0.10641 | 0.9849 | -0.28912 | 0.98564 | -0.27472 | 14.617
106 | 0.024094 | 0.0060457 | -0.024086 | -0.0060409 | 7.7645e-06 | 4.7764e-06 | 0.036678 | 0.036678 | 0.036678 | 0.97756 | -0.43209 | 0.97722 | -0.43885 | 10.0764
107 | 0.006666 | 0.0016707 | -0.0066655 | -0.0016705 | 4.9047e-07 | 1.4044e-07 | 0.0099323 | 0.0099324 | 0.0099324 | 0.99867 | -0.025111 | 0.99859 | -0.026655 | 2.7287
108 | 0.0028644 | 0.00071772 | -0.0028643 | -0.00071779 | 5.5367e-08 | -7.0626e-08 | 0.0042678 | 0.0042679 | 0.0042679 | 0.99867 | -0.025111 | 0.99865 | -0.025517 | 1.1725
109 | 0.0028643 | 0.00071779 | -0.0028643 | -0.00071785 | 4.9166e-08 | -6.271e-08 | 0.0042679 | 0.0042679 | 0.0042679 | 0.99865 | -0.025517 | 0.99863 | -0.025877 | 1.1725
110 | -0.07238 | -0.018354 | 0.07241 | 0.018373 | 2.9899e-05 | 1.837e-05 | 0.10935 | 0.10935 | 0.10935 | 0.98564 | -0.27472 | 0.98608 | -0.26614 | 10.0136
111 | -0.076041 | -0.019282 | 0.076075 | 0.019303 | 3.4469e-05 | 2.0637e-05 | 0.11483 | 0.11483 | 0.11483 | 0.98608 | -0.26614 | 0.98657 | -0.25671 | 7.8865
112 | -0.078203 | -0.019836 | 0.078233 | 0.019854 | 3.0005e-05 | 1.8029e-05 | 0.11804 | 0.11804 | 0.11804 | 0.98657 | -0.25671 | 0.98699 | -0.24873 | 8.1069
113 | -0.078233 | -0.019854 | 0.078285 | 0.019886 | 5.1758e-05 | 3.1098e-05 | 0.11804 | 0.11803 | 0.11804 | 0.98699 | -0.24873 | 0.9877 | -0.23499 | 8.1068
114 | 0.23137 | 0.058803 | -0.2307 | -0.058377 | 0.0006693 | 0.00042539 | 0.34976 | 0.34976 | 0.34976 | 0.98517 | -0.28241 | 0.98205 | -0.34267 | 24.0219
115 | 0.23045 | 0.058314 | -0.23039 | -0.058275 | 6.2027e-05 | 3.9423e-05 | 0.34938 | 0.34938 | 0.34938 | 0.98205 | -0.34267 | 0.98177 | -0.34828 | 23.9957
116 | 0.021862 | 0.0054835 | -0.021859 | -0.0054815 | 3.4056e-06 | 2.077e-06 | 0.033292 | 0.033292 | 0.033292 | 0.97722 | -0.43885 | 0.97705 | -0.44212 | 9.146
117 | 0.019478 | 0.0048847 | -0.01947 | -0.0048801 | 7.569e-06 | 4.557e-06 | 0.029665 | 0.029665 | 0.029665 | 0.97705 | -0.44212 | 0.97664 | -0.45028 | 8.1498
118 | 0.013936 | 0.0034932 | -0.013936 | -0.0034931 | 2.0424e-07 | 1.156e-07 | 0.021234 | 0.021234 | 0.021234 | 0.97664 | -0.45028 | 0.97662 | -0.45058 | 5.8335
119 | 0.010995 | 0.0027559 | -0.010994 | -0.0027558 | 1.3274e-07 | 6.9169e-08 | 0.016752 | 0.016752 | 0.016752 | 0.97662 | -0.45058 | 0.97661 | -0.45084 | 4.6022
120 | 0.022533 | 0.0056624 | -0.022532 | -0.0056617 | 1.1698e-06 | 7.1569e-07 | 0.034367 | 0.034367 | 0.034367 | 0.97579 | -0.46677 | 0.97573 | -0.46785 | 9.4414
121 | 0.020788 | 0.0052248 | -0.020783 | -0.0052214 | 5.6215e-06 | 3.4116e-06 | 0.031708 | 0.031708 | 0.031708 | 0.97573 | -0.46785 | 0.97545 | -0.47352 | 8.7109
122 | 0.0095477 | 0.0023932 | -0.0095456 | -0.0023922 | 2.0597e-06 | 9.9355e-07 | 0.014548 | 0.014548 | 0.014548 | 0.97661 | -0.45084 | 0.97638 | -0.45537 | 3.9966
123 | 0.0052042 | 0.0013042 | -0.0052037 | -0.0013041 | 4.9253e-07 | 5.4116e-08 | 0.0079313 | 0.0079314 | 0.0079314 | 0.97638 | -0.45537 | 0.97628 | -0.45735 | 2.1789
124 | 0.0052037 | 0.0013041 | -0.0052032 | -0.001304 | 5.6033e-07 | 6.1639e-08 | 0.0079314 | 0.0079315 | 0.0079315 | 0.97628 | -0.45735 | 0.97616 | -0.45961 | 2.179
125 | 0.0090956 | 0.0022791 | -0.0090947 | -0.0022787 | 9.0963e-07 | 4.1485e-07 | 0.013662 | 0.013662 | 0.013662 | 0.99067 | -0.17849 | 0.99056 | -0.18059 | 3.7532
126 | -0.0095941 | -0.002404 | 0.0095975 | 0.0024056 | 3.3715e-06 | 1.6001e-06 | 0.014411 | 0.01441 | 0.014411 | 0.99067 | -0.17849 | 0.99105 | -0.17111 | 3.9589
127 | 0.0046174 | 0.0011566 | -0.0046161 | -0.0011567 | 1.3534e-06 | -9.9178e-08 | 0.006936 | 0.0069364 | 0.0069364 | 0.99056 | -0.18059 | 0.99024 | -0.18674 | 1.9056
128 | 0.0031512 | 0.00078955 | -0.0031512 | -0.00078962 | 8.1553e-08 | -7.2576e-08 | 0.0047352 | 0.0047353 | 0.0047353 | 0.99024 | -0.18674 | 0.99022 | -0.18728 | 1.3009
129 | 0.00049892 | 0.00012491 | -0.00049892 | -0.00012504 | 2.1692e-09 | -1.3099e-07 | 0.0007497 | 0.00074974 | 0.00074974 | 0.99022 | -0.18728 | 0.99021 | -0.18738 | 0.20597
130 | -0.1012 | -0.025373 | 0.10153 | 0.025582 | 0.00032742 | 0.00020909 | 0.15473 | 0.15473 | 0.15473 | 0.97327 | -0.51471 | 0.97671 | -0.44706 | 42.5071
131 | 0.029015 | 0.007282 | -0.028998 | -0.007271 | 1.7703e-05 | 1.1032e-05 | 0.044365 | 0.044365 | 0.044365 | 0.97327 | -0.51471 | 0.97262 | -0.52751 | 12.1881
132 | -0.13581 | -0.034175 | 0.13581 | 0.034177 | 3.3236e-06 | 2.1245e-06 | 0.20696 | 0.20696 | 0.20696 | 0.97671 | -0.44706 | 0.97674 | -0.44654 | 56.8564
133 | 0.028998 | 0.007271 | -0.028988 | -0.0072652 | 9.2712e-06 | 5.7777e-06 | 0.044365 | 0.044365 | 0.044365 | 0.97262 | -0.52751 | 0.97228 | -0.53422 | 12.1881
134 | -0.19566 | -0.049174 | 0.19625 | 0.049555 | 0.00059582 | 0.00038043 | 0.29812 | 0.29812 | 0.29812 | 0.97674 | -0.44654 | 0.97999 | -0.38297 | 40.9508
135 | -0.21097 | -0.053244 | 0.211 | 0.053261 | 2.7133e-05 | 1.7223e-05 | 0.32047 | 0.32047 | 0.32047 | 0.97999 | -0.38297 | 0.98012 | -0.38028 | 22.0106
136 | -0.21139 | -0.053358 | 0.21145 | 0.053402 | 6.9363e-05 | 4.403e-05 | 0.32106 | 0.32106 | 0.32106 | 0.98012 | -0.38028 | 0.98047 | -0.37344 | 22.0509
137 | -0.21151 | -0.053415 | 0.21155 | 0.053445 | 4.6985e-05 | 2.9826e-05 | 0.32114 | 0.32114 | 0.32114 | 0.98047 | -0.37344 | 0.98071 | -0.3688 | 22.0563
138 | 0.018416 | 0.004638 | -0.018411 | -0.0046349 | 5.1957e-06 | 3.1015e-06 | 0.02795 | 0.02795 | 0.02795 | 0.98071 | -0.3688 | 0.98041 | -0.3747 | 7.6786
139 | -0.22997 | -0.058083 | 0.23009 | 0.058161 | 0.00012293 | 7.8133e-05 | 0.34909 | 0.34909 | 0.34909 | 0.98071 | -0.3688 | 0.98128 | -0.35765 | 23.9759
140 | 0.23034 | 0.058263 | -0.23023 | -0.058197 | 0.00010352 | 6.5798e-05 | 0.3493 | 0.3493 | 0.3493 | 0.98177 | -0.34828 | 0.98128 | -0.35765 | 23.9907
141 | 0.018276 | 0.0046013 | -0.018262 | -0.0045927 | 1.4468e-05 | 8.6279e-06 | 0.027746 | 0.027747 | 0.027747 | 0.98041 | -0.3747 | 0.97956 | -0.39128 | 7.6227
142 | 0.018099 | 0.0045518 | -0.018091 | -0.0045472 | 7.7684e-06 | 4.6271e-06 | 0.027499 | 0.027499 | 0.027499 | 0.97956 | -0.39128 | 0.9791 | -0.40027 | 7.5547
143 | 0.018091 | 0.0045472 | -0.018086 | -0.004544 | 5.4159e-06 | 3.2261e-06 | 0.027499 | 0.027499 | 0.027499 | 0.9791 | -0.40027 | 0.97878 | -0.40654 | 7.5548
144 | 0.014783 | 0.0037166 | -0.014776 | -0.0037128 | 6.6272e-06 | 3.802e-06 | 0.022478 | 0.022478 | 0.022478 | 0.97878 | -0.40654 | 0.9783 | -0.41593 | 6.1753
145 | 0.014589 | 0.0036659 | -0.014559 | -0.0036489 | 2.9754e-05 | 1.7025e-05 | 0.022194 | 0.022194 | 0.022194 | 0.9783 | -0.41593 | 0.97613 | -0.45874 | 6.0974

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50201 | 0.12855

## res_load
| p_mw | q_mvar
0 | 0.00093795 | 0.00023507
1 | 0.0027498 | 0.00068916
2 | 0.0010227 | 0.00025632
3 | 0.0031218 | 0.00078238
4 | 0.00059333 | 0.0001487
5 | 0.0018439 | 0.00046211
6 | 0.0048057 | 0.0012044
7 | 0.0033186 | 0.00083173
8 | 0.0024785 | 0.00062116
9 | 0.00092932 | 0.00023291
10 | 0.0028698 | 0.00071924
11 | 0.0018568 | 0.00046537
12 | 0.0011696 | 0.00029313
13 | 0.00039904 | 0.00010001
14 | 0.00077501 | 0.00019424
15 | 0.0022425 | 0.00056204
16 | 0.0069579 | 0.0017438
17 | 0.00090215 | 0.0002261
18 | 0.0019243 | 0.00048227
19 | 0.0019406 | 0.00048637
20 | 0.0017195 | 0.00043096
21 | 0.002221 | 0.00055664
22 | 0.00091911 | 0.00023035
23 | 0.0021302 | 0.00053387
24 | 0.014108 | 0.0035359
25 | 0.0011304 | 0.0002833
26 | 0.0024154 | 0.00060535
27 | 0.0013996 | 0.00035078
28 | 0.0026025 | 0.00065225
29 | 0.00040943 | 0.00010261
30 | 0.00054245 | 0.00013595
31 | 0.002811 | 0.00070449
32 | 0.0018185 | 0.00045576
33 | 0.00095039 | 0.00023819
34 | 0.00059048 | 0.00014799
35 | 0.0022136 | 0.00055479
36 | 0.0016645 | 0.00041716
37 | 0.0015127 | 0.00037912
38 | 0.0019443 | 0.0004873
39 | 0.00055832 | 0.00013993
40 | 0.0023661 | 0.00059299
41 | 0.0056062 | 0.001405
42 | 0.0016028 | 0.0004017
43 | 0.0020988 | 0.000526
44 | 0.0045816 | 0.0011483
45 | 0.0071253 | 0.0017858
46 | 0.0050103 | 0.0012557
47 | 0.0036352 | 0.00091108
48 | 0.0032154 | 0.00080585
49 | 0.0017273 | 0.0004329
50 | 0.00175 | 0.00043859
51 | 0.0034462 | 0.0008637
52 | 0.001694 | 0.00042456
53 | 0.0037217 | 0.00093274
54 | 0.0030639 | 0.00076789
55 | 0.00070437 | 0.00017653
56 | 0.0024434 | 0.00061238
57 | 0.0027778 | 0.00069619
58 | 0.0018056 | 0.00045253
59 | 0.0039359 | 0.00098643
60 | 0.0018128 | 0.00045432
61 | 0.0038996 | 0.00097734
62 | 0.0013543 | 0.00033942
63 | 0.0023145 | 0.00058008
64 | 0.0044187 | 0.0011074
65 | 0.0033027 | 0.00082772
66 | 0.011986 | 0.003004
67 | 0.0036595 | 0.00091716
68 | 0.0027313 | 0.00068454
69 | 0.0023769 | 0.00059571
70 | 0.0014685 | 0.00036804
71 | 0.00071312 | 0.00017873
72 | 0.000763 | 0.00019123
73 | 0.0016884 | 0.00042315
74 | 0.0018888 | 0.00047337
75 | 0.00061149 | 0.00015325
76 | 0.00051411 | 0.00012885
77 | 0.00023284 | 5.8355e-05
78 | 0.0037211 | 0.0009326
79 | 0.0032941 | 0.00082559
80 | 0.002147 | 0.0005381
81 | 0.0009037 | 0.00022649
82 | 0.00063744 | 0.00015976
83 | 0.0028643 | 0.00071785
84 | 0.0066655 | 0.0016705
85 | 0.0019453 | 0.00048754
86 | 0.0036307 | 0.00090994
87 | 0.002128 | 0.00053332
88 | 0.00046828 | 0.00011736
89 | 0.00025231 | 6.3234e-05
90 | 0.002224 | 0.0005574
91 | 0.0023812 | 0.00059678
92 | 0.0055337 | 0.0013869
93 | 0.0029417 | 0.00073725
94 | 0.0012099 | 0.00030322
95 | 0.0017434 | 0.00043694
96 | 0.0023368 | 0.00058566
97 | 0.0014468 | 0.00036261
98 | 0.0043414 | 0.0010881
99 | 0.0052032 | 0.001304
100 | 0.00049852 | 0.00012494
101 | 0.0044773 | 0.0011221
102 | 0.0042098 | 0.0010551
103 | 0.0014648 | 0.00036712
104 | 0.0026522 | 0.00066471
105 | 0.00049892 | 0.00012504
106 | 0.072184 | 0.018091
107 | 0.034284 | 0.0085924
108 | 0.059841 | 0.014998
109 | 0.028988 | 0.0072652
110 | 0.014721 | 0.0036895
111 | 0.00038607 | 9.6759e-05
112 | 5.2152e-05 | 1.3071e-05
113 | 4.8166e-05 | 1.2072e-05
114 | 0.00014205 | 3.56e-05
115 | 0.0001341 | 3.361e-05
116 | 0.00016299 | 4.0849e-05
117 | 0.00018692 | 4.6846e-05
118 | 0.014559 | 0.0036489

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1