## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2275-15_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2275-15_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2275-15_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2275-15_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2275-15_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2275-15_0_5_node_90 | 0.4 | n |  | TRUE
6 | bus_LV_2275-15_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2275-15_0_5_node_91 | 0.4 | n |  | TRUE
8 | bus_LV_2275-15_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2275-15_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2275-15_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2275-15_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2275-15_0_5_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_2275-15_0_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2275-15_0_5_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_2275-15_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2275-15_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2275-15_0_5_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2275-15_0_5_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_2275-15_0_5_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2275-15_0_5_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_2275-15_0_5_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2275-15_0_5_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_2275-15_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2275-15_0_5_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2275-15_0_5_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2275-15_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_2275-15_0_5_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_2275-15_0_5_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_2275-15_0_5_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2275-15_0_5_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2275-15_0_5_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2275-15_0_5_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2275-15_0_5_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_2275-15_0_5_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_2275-15_0_5_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2275-15_0_5_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_2275-15_0_5_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_2275-15_0_5_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_2275-15_0_5_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_2275-15_0_5_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2275-15_0_5_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_2275-15_0_5_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_2275-15_0_5_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_2275-15_0_5_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_2275-15_0_5_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_2275-15_0_5_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_2275-15_0_5_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_2275-15_0_5_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_2275-15_0_5_node_50 | 0.4 | n |  | TRUE
50 | bus_LV_2275-15_0_5_node_55 | 0.4 | n |  | TRUE
51 | bus_LV_2275-15_0_5_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_2275-15_0_5_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_2275-15_0_5_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_2275-15_0_5_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_2275-15_0_5_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_2275-15_0_5_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_2275-15_0_5_node_59 | 0.4 | n |  | TRUE
58 | bus_LV_2275-15_0_5_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_2275-15_0_5_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_2275-15_0_5_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_2275-15_0_5_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_2275-15_0_5_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_2275-15_0_5_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_2275-15_0_5_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_2275-15_0_5_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_2275-15_0_5_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_2275-15_0_5_node_73 | 0.4 | n |  | TRUE
68 | bus_LV_2275-15_0_5_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_2275-15_0_5_node_68 | 0.4 | n |  | TRUE
70 | bus_LV_2275-15_0_5_node_75 | 0.4 | n |  | TRUE
71 | bus_LV_2275-15_0_5_node_76 | 0.4 | n |  | TRUE
72 | bus_LV_2275-15_0_5_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_2275-15_0_5_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_2275-15_0_5_node_74 | 0.4 | n |  | TRUE
75 | bus_LV_2275-15_0_5_node_81 | 0.4 | n |  | TRUE
76 | bus_LV_2275-15_0_5_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_2275-15_0_5_node_82 | 0.4 | n |  | TRUE
78 | bus_LV_2275-15_0_5_node_85 | 0.4 | n |  | TRUE
79 | bus_LV_2275-15_0_5_node_80 | 0.4 | n |  | TRUE
80 | bus_LV_2275-15_0_5_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_2275-15_0_5_node_117 | 0.4 | n |  | TRUE
82 | bus_LV_2275-15_0_5_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_2275-15_0_5_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_2275-15_0_5_node_114 | 0.4 | n |  | TRUE
85 | bus_LV_2275-15_0_5_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_2275-15_0_5_node_86 | 0.4 | n |  | TRUE
87 | bus_LV_2275-15_0_5_node_88 | 0.4 | n |  | TRUE
88 | bus_LV_2275-15_0_5_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_2275-15_0_5_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_2275-15_0_5_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_2275-15_0_5_node_94 | 0.4 | n |  | TRUE
92 | bus_LV_2275-15_0_5_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_2275-15_0_5_node_118 | 0.4 | n |  | TRUE
94 | bus_LV_2275-15_0_5_node_95 | 0.4 | n |  | TRUE
95 | bus_LV_2275-15_0_5_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_2275-15_0_5_node_119 | 0.4 | n |  | TRUE
97 | bus_LV_2275-15_0_5_node_97 | 0.4 | n |  | TRUE
98 | bus_LV_2275-15_0_5_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_2275-15_0_5_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_2275-15_0_5_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_2275-15_0_5_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_2275-15_0_5_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_2275-15_0_5_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_2275-15_0_5_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_2275-15_0_5_node_105 | 0.4 | n |  | TRUE
106 | bus_LV_2275-15_0_5_node_106 | 0.4 | n |  | TRUE
107 | bus_LV_2275-15_0_5_node_107 | 0.4 | n |  | TRUE
108 | bus_LV_2275-15_0_5_node_108 | 0.4 | n |  | TRUE
109 | bus_LV_2275-15_0_5_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_2275-15_0_5_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_2275-15_0_5_node_111 | 0.4 | n |  | TRUE
112 | bus_LV_2275-15_0_5_node_115 | 0.4 | n |  | TRUE
113 | bus_LV_2275-15_0_5_node_116 | 0.4 | n |  | TRUE
114 | bus_LV_2275-15_0_5_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_2275-15_0_5_node_113 | 0.4 | n |  | TRUE
116 | bus_MV_379_0_node_235 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2275-15_0_5_load_0 | 0 | 0.00040939 | 0.0001026 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2275-15_0_5_load_1 | 1 | 0.00035105 | 8.7982e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2275-15_0_5_load_2 | 2 | 0.0022615 | 0.00056678 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2275-15_0_5_load_3 | 3 | 0.0010701 | 0.00026819 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2275-15_0_5_load_90 | 5 | 0.0013654 | 0.0003422 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2275-15_0_5_load_91 | 7 | 0.00065241 | 0.00016351 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2275-15_0_5_load_6 | 8 | 0.0011947 | 0.00029942 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2275-15_0_5_load_8 | 9 | 0.0003373 | 8.4536e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2275-15_0_5_load_10 | 11 | 0.0011274 | 0.00028256 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2275-15_0_5_load_14 | 12 | 0.00048364 | 0.00012121 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2275-15_0_5_load_15 | 13 | 0.00034688 | 8.6936e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2275-15_0_5_load_11 | 16 | 0.0013146 | 0.00032946 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2275-15_0_5_load_17 | 17 | 0.00083277 | 0.00020871 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2275-15_0_5_load_23 | 18 | 0.00091953 | 0.00023046 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2275-15_0_5_load_18 | 19 | 0.00041035 | 0.00010284 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2275-15_0_5_load_29 | 20 | 0.00066702 | 0.00016717 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2275-15_0_5_load_28 | 22 | 0.0013423 | 0.00033642 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2275-15_0_5_load_19 | 23 | 0.00079396 | 0.00019899 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2275-15_0_5_load_22 | 25 | 0.00069291 | 0.00017366 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2275-15_0_5_load_24 | 26 | 0.00070362 | 0.00017634 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2275-15_0_5_load_25 | 27 | 0.00099567 | 0.00024954 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2275-15_0_5_load_26 | 28 | 0.00053622 | 0.00013439 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2275-15_0_5_load_31 | 30 | 0.00083331 | 0.00020885 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2275-15_0_5_load_33 | 32 | 0.00057847 | 0.00014498 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2275-15_0_5_load_39 | 33 | 0.00080983 | 0.00020296 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2275-15_0_5_load_36 | 34 | 0.0010376 | 0.00026005 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2275-15_0_5_load_34 | 35 | 0.00041013 | 0.00010279 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2275-15_0_5_load_44 | 36 | 0.00032373 | 8.1134e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2275-15_0_5_load_35 | 37 | 0.0013817 | 0.00034629 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2275-15_0_5_load_37 | 38 | 0.00041502 | 0.00010401 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2275-15_0_5_load_38 | 39 | 0.022989 | 0.0057615 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2275-15_0_5_load_40 | 40 | 0.027925 | 0.0069986 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2275-15_0_5_load_41 | 41 | 0.090585 | 0.022703 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2275-15_0_5_load_43 | 42 | 0.0029638 | 0.00074279 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2275-15_0_5_load_45 | 43 | 0.0014089 | 0.00035311 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2275-15_0_5_load_46 | 44 | 0.0027468 | 0.0006884 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2275-15_0_5_load_49 | 47 | 0.0024729 | 0.00061976 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2275-15_0_5_load_50 | 49 | 0.014865 | 0.0037256 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2275-15_0_5_load_55 | 50 | 0.00476 | 0.001193 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2275-15_0_5_load_52 | 51 | 0.0032268 | 0.00080872 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2275-15_0_5_load_57 | 52 | 0.0012888 | 0.00032301 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2275-15_0_5_load_53 | 53 | 0.0043996 | 0.0011026 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2275-15_0_5_load_54 | 54 | 0.0014879 | 0.0003729 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2275-15_0_5_load_56 | 55 | 0.0049247 | 0.0012342 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2275-15_0_5_load_58 | 56 | 0.00087379 | 0.00021899 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2275-15_0_5_load_59 | 57 | 0.0036781 | 0.00092182 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2275-15_0_5_load_64 | 58 | 0.0018221 | 0.00045665 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2275-15_0_5_load_60 | 60 | 0.0012798 | 0.00032075 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2275-15_0_5_load_61 | 61 | 0.0020211 | 0.00050653 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2275-15_0_5_load_63 | 62 | 0.00025502 | 6.3913e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2275-15_0_5_load_65 | 63 | 0.0032909 | 0.00082477 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2275-15_0_5_load_66 | 64 | 0.0004145 | 0.00010388 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2275-15_0_5_load_67 | 66 | 0.0030909 | 0.00077465 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2275-15_0_5_load_73 | 67 | 0.0027855 | 0.0006981 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2275-15_0_5_load_69 | 68 | 0.0042483 | 0.0010647 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2275-15_0_5_load_68 | 69 | 0.00036943 | 9.2588e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2275-15_0_5_load_75 | 70 | 0.0077841 | 0.0019509 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2275-15_0_5_load_70 | 72 | 0.0054489 | 0.0013656 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2275-15_0_5_load_72 | 73 | 0.0018787 | 0.00047085 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2275-15_0_5_load_74 | 74 | 0.0022416 | 0.00056179 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2275-15_0_5_load_81 | 75 | 0.0053254 | 0.0013347 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2275-15_0_5_load_84 | 76 | 0.0023646 | 0.00059262 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2275-15_0_5_load_82 | 77 | 0.0022025 | 0.00055199 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2275-15_0_5_load_85 | 78 | 0.0057493 | 0.0014409 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2275-15_0_5_load_80 | 79 | 0.0058429 | 0.0014644 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2275-15_0_5_load_77 | 80 | 0.0054126 | 0.0013565 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2275-15_0_5_load_78 | 82 | 0.0028033 | 0.00070256 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2275-15_0_5_load_79 | 83 | 0.0018288 | 0.00045833 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2275-15_0_5_load_83 | 85 | 0.0020643 | 0.00051736 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2275-15_0_5_load_93 | 90 | 0.0020514 | 0.00051412 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2275-15_0_5_load_94 | 91 | 0.00090129 | 0.00022588 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2275-15_0_5_load_92 | 92 | 0.0020879 | 0.00052328 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2275-15_0_5_load_118 | 93 | 0.0012049 | 0.00030197 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2275-15_0_5_load_95 | 94 | 0.0023776 | 0.00059588 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2275-15_0_5_load_96 | 95 | 0.0033105 | 0.00082969 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2275-15_0_5_load_119 | 96 | 0.00098279 | 0.00024631 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2275-15_0_5_load_97 | 97 | 0.0033384 | 0.00083668 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2275-15_0_5_load_98 | 98 | 0.0018022 | 0.00045168 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2275-15_0_5_load_99 | 99 | 0.0041756 | 0.0010465 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2275-15_0_5_load_100 | 100 | 0.0047903 | 0.0012006 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2275-15_0_5_load_101 | 101 | 0.0028126 | 0.00070491 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2275-15_0_5_load_102 | 102 | 0.0041545 | 0.0010412 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2275-15_0_5_load_103 | 103 | 0.002602 | 0.00065213 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2275-15_0_5_load_104 | 104 | 0.003758 | 0.00094185 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2275-15_0_5_load_105 | 105 | 0.0034518 | 0.00086509 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2275-15_0_5_load_106 | 106 | 0.0026074 | 0.00065348 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2275-15_0_5_load_107 | 107 | 0.0037685 | 0.00094447 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2275-15_0_5_load_108 | 108 | 0.0035394 | 0.00088705 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2275-15_0_5_load_110 | 110 | 0.0030697 | 0.00076935 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2275-15_0_5_load_111 | 111 | 0.0045345 | 0.0011365 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2275-15_0_5_load_115 | 112 | 0.0022793 | 0.00057124 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2275-15_0_5_load_116 | 113 | 0.0034776 | 0.00087157 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2275-15_0_5_load_112 | 114 | 0.0043933 | 0.0011011 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2275-15_0_5_load_113 | 115 | 0.0021237 | 0.00053225 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2275-15_0_5_line_0 |  | 0 | 1 | 0.02241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2275-15_0_5_line_1 |  | 0 | 2 | 0.0039441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2275-15_0_5_line_2 |  | 1 | 3 | 0.0074981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2275-15_0_5_line_3 |  | 2 | 4 | 0.031838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2275-15_0_5_line_4 |  | 4 | 5 | 0.026191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2275-15_0_5_line_5 |  | 4 | 6 | 0.97649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2275-15_0_5_line_6 |  | 5 | 7 | 0.051809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2275-15_0_5_line_7 |  | 6 | 8 | 0.010671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2275-15_0_5_line_8 |  | 7 | 92 | 0.019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2275-15_0_5_line_9 |  | 9 | 10 | 0.044939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2275-15_0_5_line_10 |  | 10 | 11 | 0.024033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2275-15_0_5_line_11 |  | 11 | 15 | 0.02904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2275-15_0_5_line_12 |  | 12 | 13 | 0.034248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2275-15_0_5_line_13 |  | 12 | 14 | 0.019744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2275-15_0_5_line_14 |  | 13 | 17 | 0.014426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2275-15_0_5_line_15 |  | 13 | 15 | 0.24233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2275-15_0_5_line_16 |  | 14 | 19 | 0.027415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2275-15_0_5_line_17 |  | 15 | 16 | 0.063009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2275-15_0_5_line_18 |  | 17 | 18 | 0.014754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2275-15_0_5_line_19 |  | 18 | 21 | 0.021306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2275-15_0_5_line_20 |  | 19 | 20 | 0.048747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2275-15_0_5_line_21 |  | 20 | 22 | 0.035026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2275-15_0_5_line_22 |  | 21 | 25 | 0.04295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2275-15_0_5_line_23 |  | 21 | 23 | 0.0050618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2275-15_0_5_line_24 |  | 22 | 29 | 0.02659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2275-15_0_5_line_25 |  | 23 | 24 | 0.010032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2275-15_0_5_line_26 |  | 24 | 26 | 0.004719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2275-15_0_5_line_27 |  | 24 | 27 | 0.038132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2275-15_0_5_line_28 |  | 25 | 28 | 0.0044161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2275-15_0_5_line_29 |  | 29 | 30 | 0.024106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2275-15_0_5_line_30 |  | 29 | 31 | 0.033894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2275-15_0_5_line_31 |  | 30 | 32 | 0.017502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2275-15_0_5_line_32 |  | 31 | 33 | 0.0026988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2275-15_0_5_line_33 |  | 31 | 34 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2275-15_0_5_line_34 |  | 32 | 35 | 0.0032222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2275-15_0_5_line_35 |  | 33 | 36 | 0.015712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2275-15_0_5_line_36 |  | 34 | 37 | 0.0096552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2275-15_0_5_line_37 |  | 36 | 42 | 0.004021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2275-15_0_5_line_38 |  | 37 | 38 | 0.017733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2275-15_0_5_line_39 |  | 38 | 39 | 0.014813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2275-15_0_5_line_40 |  | 39 | 40 | 0.024785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2275-15_0_5_line_41 |  | 40 | 41 | 0.029107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2275-15_0_5_line_42 |  | 42 | 43 | 0.027087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2275-15_0_5_line_43 |  | 43 | 44 | 0.02998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2275-15_0_5_line_44 |  | 44 | 45 | 0.014235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2275-15_0_5_line_45 |  | 45 | 46 | 0.013809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2275-15_0_5_line_46 |  | 45 | 47 | 0.014972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2275-15_0_5_line_47 |  | 46 | 48 | 0.042282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2275-15_0_5_line_48 |  | 46 | 49 | 0.043339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2275-15_0_5_line_49 |  | 48 | 50 | 0.024911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2275-15_0_5_line_50 |  | 48 | 51 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2275-15_0_5_line_51 |  | 50 | 52 | 0.025795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_2275-15_0_5_line_52 |  | 51 | 53 | 0.0014503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2275-15_0_5_line_53 |  | 52 | 56 | 0.0020102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2275-15_0_5_line_54 |  | 53 | 54 | 0.030148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2275-15_0_5_line_55 |  | 54 | 55 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2275-15_0_5_line_56 |  | 56 | 57 | 0.012146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_2275-15_0_5_line_57 |  | 57 | 58 | 0.028463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_2275-15_0_5_line_58 |  | 58 | 59 | 0.0028306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_2275-15_0_5_line_59 |  | 59 | 63 | 0.0044131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2275-15_0_5_line_60 |  | 59 | 60 | 0.019063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_2275-15_0_5_line_61 |  | 60 | 61 | 0.0026721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_2275-15_0_5_line_62 |  | 61 | 62 | 0.017717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_2275-15_0_5_line_63 |  | 62 | 64 | 0.0071505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2275-15_0_5_line_64 |  | 63 | 65 | 0.040591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2275-15_0_5_line_65 |  | 64 | 66 | 0.0067281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_2275-15_0_5_line_66 |  | 65 | 67 | 0.042834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2275-15_0_5_line_67 |  | 65 | 68 | 0.016663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2275-15_0_5_line_68 |  | 66 | 69 | 0.0078896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2275-15_0_5_line_69 |  | 67 | 75 | 0.0029631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2275-15_0_5_line_70 |  | 68 | 72 | 0.029239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2275-15_0_5_line_71 |  | 69 | 70 | 0.080639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_2275-15_0_5_line_72 |  | 70 | 71 | 0.012465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2275-15_0_5_line_73 |  | 71 | 79 | 0.070663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2275-15_0_5_line_74 |  | 71 | 80 | 0.064517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2275-15_0_5_line_75 |  | 72 | 73 | 0.014168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2275-15_0_5_line_76 |  | 73 | 74 | 0.026725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2275-15_0_5_line_77 |  | 74 | 76 | 0.036939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2275-15_0_5_line_78 |  | 75 | 77 | 0.02688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2275-15_0_5_line_79 |  | 76 | 78 | 0.039097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2275-15_0_5_line_80 |  | 77 | 85 | 0.019868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2275-15_0_5_line_81 |  | 78 | 86 | 0.030688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2275-15_0_5_line_82 |  | 79 | 81 | 0.041707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_2275-15_0_5_line_83 |  | 80 | 82 | 0.040509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2275-15_0_5_line_84 |  | 81 | 84 | 0.0227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_2275-15_0_5_line_85 |  | 82 | 83 | 0.0029401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2275-15_0_5_line_86 |  | 84 | 113 | 0.0075634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2275-15_0_5_line_87 |  | 84 | 115 | 0.018824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2275-15_0_5_line_88 |  | 86 | 87 | 0.043065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2275-15_0_5_line_89 |  | 86 | 88 | 0.058737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2275-15_0_5_line_90 |  | 87 | 90 | 0.034491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2275-15_0_5_line_91 |  | 88 | 93 | 0.047487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2275-15_0_5_line_92 |  | 89 | 90 | 0.032241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2275-15_0_5_line_93 |  | 89 | 91 | 0.023542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2275-15_0_5_line_94 |  | 89 | 92 | 0.040483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2275-15_0_5_line_95 |  | 94 | 95 | 0.0063975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2275-15_0_5_line_96 |  | 94 | 96 | 0.10479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2275-15_0_5_line_97 |  | 95 | 97 | 0.021612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2275-15_0_5_line_98 |  | 97 | 98 | 0.0051907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2275-15_0_5_line_99 |  | 98 | 99 | 0.020279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2275-15_0_5_line_100 |  | 99 | 100 | 0.011676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2275-15_0_5_line_101 |  | 100 | 101 | 0.01666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2275-15_0_5_line_102 |  | 101 | 102 | 0.014382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2275-15_0_5_line_103 |  | 102 | 103 | 0.0069158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2275-15_0_5_line_104 |  | 103 | 104 | 0.023715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2275-15_0_5_line_105 |  | 104 | 105 | 0.0010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2275-15_0_5_line_106 |  | 105 | 106 | 0.026122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2275-15_0_5_line_107 |  | 106 | 107 | 0.0024378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2275-15_0_5_line_108 |  | 107 | 108 | 0.021687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2275-15_0_5_line_109 |  | 108 | 109 | 0.0073898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2275-15_0_5_line_110 |  | 109 | 110 | 0.008847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2275-15_0_5_line_111 |  | 109 | 111 | 0.01775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2275-15_0_5_line_112 |  | 111 | 112 | 0.039459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_2275-15_0_5_line_113 |  | 112 | 113 | 0.0024866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_2275-15_0_5_line_114 |  | 114 | 115 | 0.051716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2275-15_0_5_trafo_47 | 0.63 MVA 20/0.4 kV | 116 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2578265.1406 | 1199992.5736 | 2578280.2002 | 1200009.1688
1 | 2578265.1406 | 1199992.5736 | 2578262.4902 | 1199989.6529
2 | 2578280.2002 | 1200009.1688 | 2578280.8157 | 1200009.8471 | 2578285.5861 | 1200014.3822
3 | 2578241.9805 | 1199965.3536 | 2578248.2774 | 1199973.9909 | 2578262.4902 | 1199989.6529
4 | 2578241.9805 | 1199965.3536 | 2578261.17 | 1199947.5284
5 | 2578241.9805 | 1199965.3536 | 2577364.3831 | 1200393.5592
6 | 2578261.17 | 1199947.5284 | 2578269.3393 | 1199939.9399 | 2578278.3624 | 1199930.0571 | 2578286.5795 | 1199920.4441 | 2578294.3029 | 1199909.0209 | 2578294.8054 | 1199908.3466
7 | 2577364.3831 | 1200393.5592 | 2577365.4915 | 1200398.78 | 2577363.1559 | 1200403.5748
8 | 2578294.8054 | 1199908.3466 | 2578297.659 | 1199904.5173 | 2578302.1577 | 1199900.2097 | 2578308.9454 | 1199894.801
9 | 2577887.5354 | 1199327.4247 | 2577856.7757 | 1199294.6624
10 | 2577887.5354 | 1199327.4247 | 2577904.9466 | 1199310.858
11 | 2577925.9852 | 1199290.8399 | 2577904.9466 | 1199310.858
12 | 2578092.5215 | 1199466.8781 | 2578069.539 | 1199492.2701
13 | 2578056.2896 | 1199506.9087 | 2578069.539 | 1199492.2701
14 | 2578092.5215 | 1199466.8781 | 2578099.6917 | 1199458.9562 | 2578102.9972 | 1199457.2047
15 | 2578092.5215 | 1199466.8781 | 2577925.9852 | 1199290.8399
16 | 2578056.2896 | 1199506.9087 | 2578062.1752 | 1199511.1782 | 2578079.8811 | 1199520.7844
17 | 2577925.9852 | 1199290.8399 | 2577971.3333 | 1199247.0945
18 | 2578117.1342 | 1199454.8565 | 2578107.6778 | 1199454.7245 | 2578102.9972 | 1199457.2047
19 | 2578137.8573 | 1199458.8491 | 2578131.6682 | 1199459.0053 | 2578117.1342 | 1199454.8565
20 | 2578125.1799 | 1199538.4986 | 2578122.8832 | 1199537.9137 | 2578088.715 | 1199525.5771 | 2578079.8811 | 1199520.7844
21 | 2578159.1222 | 1199547.1428 | 2578125.1799 | 1199538.4986
22 | 2578137.8573 | 1199458.8491 | 2578144.3406 | 1199455.8904 | 2578149.8824 | 1199451.5344 | 2578167.487 | 1199428.7733
23 | 2578137.8573 | 1199458.8491 | 2578139.1771 | 1199463.7358
24 | 2578185.107 | 1199552.5488 | 2578175.8984 | 1199551.4153 | 2578159.1222 | 1199547.1428
25 | 2578147.4736 | 1199469.3751 | 2578139.1771 | 1199463.7358
26 | 2578147.4736 | 1199469.3751 | 2578151.373 | 1199472.0328
27 | 2578125.4617 | 1199497.927 | 2578131.5572 | 1199495.0919 | 2578141.1392 | 1199485.9407 | 2578144.6419 | 1199481.9479 | 2578147.4736 | 1199469.3751
28 | 2578167.487 | 1199428.7733 | 2578170.1888 | 1199425.28
29 | 2578185.107 | 1199552.5488 | 2578173.1277 | 1199573.4673
30 | 2578218.8414 | 1199556.7165 | 2578185.107 | 1199552.5488
31 | 2578173.1277 | 1199573.4673 | 2578164.4299 | 1199588.6555
32 | 2578218.8414 | 1199556.7165 | 2578221.5137 | 1199557.0936
33 | 2578218.8414 | 1199556.7165 | 2578212.5959 | 1199570.9737
34 | 2578162.8287 | 1199591.4516 | 2578164.4299 | 1199588.6555
35 | 2578237.0713 | 1199559.2896 | 2578221.5137 | 1199557.0936
36 | 2578208.7218 | 1199579.8176 | 2578212.5959 | 1199570.9737
37 | 2578241.0528 | 1199559.8516 | 2578237.0713 | 1199559.2896
38 | 2578208.7218 | 1199579.8176 | 2578201.6065 | 1199596.0605
39 | 2578201.6065 | 1199596.0605 | 2578195.6629 | 1199609.6287
40 | 2578184.7628 | 1199631.7978 | 2578187.9994 | 1199627.1231 | 2578195.6629 | 1199609.6287
41 | 2578184.7628 | 1199631.7978 | 2578168.194 | 1199655.7285
42 | 2578241.0528 | 1199559.8516 | 2578267.8742 | 1199563.6373
43 | 2578267.8742 | 1199563.6373 | 2578271.3543 | 1199564.1285 | 2578285.1759 | 1199567.1686 | 2578296.963 | 1199570.7286
44 | 2578310.2776 | 1199575.7596 | 2578297.6144 | 1199570.9253 | 2578296.963 | 1199570.7286
45 | 2578310.2776 | 1199575.7596 | 2578322.936 | 1199581.3609
46 | 2578310.2776 | 1199575.7596 | 2578315.885 | 1199561.8769
47 | 2578359.761 | 1199602.2271 | 2578343.3549 | 1199591.8701 | 2578331.2947 | 1199585.3549 | 2578322.936 | 1199581.3609
48 | 2578322.936 | 1199581.3609 | 2578310.8914 | 1199622.9928
49 | 2578359.761 | 1199602.2271 | 2578372.8834 | 1199611.9292 | 2578379.7355 | 1199617.1117
50 | 2578359.761 | 1199602.2271 | 2578362.3815 | 1199594.28 | 2578364.0421 | 1199586.1695 | 2578364.5462 | 1199581.2524
51 | 2578379.7355 | 1199617.1117 | 2578400.3085 | 1199632.6718
52 | 2578364.5462 | 1199581.2524 | 2578364.6941 | 1199579.8096
53 | 2578400.3085 | 1199632.6718 | 2578401.9118 | 1199633.8844
54 | 2578364.9424 | 1199549.758 | 2578365.1228 | 1199550.4796 | 2578365.8582 | 1199568.4533 | 2578364.6941 | 1199579.8096
55 | 2578362.2257 | 1199538.8949 | 2578364.9424 | 1199549.758
56 | 2578411.5409 | 1199641.2865 | 2578408.1379 | 1199638.5934 | 2578401.9118 | 1199633.8844
57 | 2578433.4349 | 1199659.464 | 2578422.0795 | 1199649.6266 | 2578411.5409 | 1199641.2865
58 | 2578435.5743 | 1199661.3174 | 2578433.4349 | 1199659.464
59 | 2578435.5743 | 1199661.3174 | 2578438.769 | 1199664.362
60 | 2578435.5743 | 1199661.3174 | 2578447.6401 | 1199646.5588
61 | 2578447.6401 | 1199646.5588 | 2578449.3313 | 1199644.4901
62 | 2578460.5451 | 1199630.7736 | 2578449.3313 | 1199644.4901
63 | 2578460.5451 | 1199630.7736 | 2578465.0709 | 1199625.2377
64 | 2578467.5043 | 1199693.019 | 2578452.3201 | 1199677.2765 | 2578438.769 | 1199664.362
65 | 2578465.0709 | 1199625.2377 | 2578469.3294 | 1199620.0288
66 | 2578467.5043 | 1199693.019 | 2578476.0781 | 1199701.8372 | 2578483.5815 | 1199709.4031 | 2578490.9376 | 1199716.2246 | 2578498.1919 | 1199722.2906 | 2578498.4957 | 1199722.5355
67 | 2578467.5043 | 1199693.019 | 2578464.169 | 1199697.011 | 2578461.103 | 1199701.7691 | 2578458.9426 | 1199706.4684 | 2578458.719 | 1199707.0555
68 | 2578474.323 | 1199613.9207 | 2578469.3294 | 1199620.0288
69 | 2578500.8026 | 1199724.3952 | 2578498.4957 | 1199722.5355
70 | 2578458.719 | 1199707.0555 | 2578456.2881 | 1199713.4373 | 2578448.7541 | 1199734.5423
71 | 2578474.323 | 1199613.9207 | 2578484.9175 | 1199600.9616 | 2578495.6854 | 1199587.004 | 2578506.8013 | 1199574.5238 | 2578509.9735 | 1199571.6997 | 2578513.3782 | 1199570.0309 | 2578516.8486 | 1199569.696 | 2578520.8739 | 1199571.2379 | 2578531.7159 | 1199579.6509
72 | 2578542.1243 | 1199586.5028 | 2578532.6389 | 1199580.367 | 2578531.7159 | 1199579.6509
73 | 2578542.1243 | 1199586.5028 | 2578541.491 | 1199575.5659 | 2578540.9722 | 1199558.3695 | 2578541.0827 | 1199546.7962 | 2578542.2953 | 1199517.8317 | 2578542.3199 | 1199515.8917
74 | 2578542.1243 | 1199586.5028 | 2578545.0209 | 1199598.0653 | 2578548.6453 | 1199606.6347 | 2578552.6728 | 1199615.1137 | 2578562.8498 | 1199633.6204 | 2578568.819 | 1199644.9274
75 | 2578448.7541 | 1199734.5423 | 2578443.9911 | 1199747.8852
76 | 2578443.9911 | 1199747.8852 | 2578435.0064 | 1199773.0543
77 | 2578435.0064 | 1199773.0543 | 2578422.5878 | 1199807.8429
78 | 2578500.8026 | 1199724.3952 | 2578505.3996 | 1199728.101 | 2578512.5599 | 1199733.4225 | 2578520.0992 | 1199738.3091 | 2578522.7447 | 1199739.8663
79 | 2578412.5103 | 1199845.5908 | 2578414.6767 | 1199835.5766 | 2578418.0096 | 1199822.5574 | 2578422.1026 | 1199809.202 | 2578422.5878 | 1199807.8429
80 | 2578522.7447 | 1199739.8663 | 2578527.2326 | 1199742.5078 | 2578533.8696 | 1199746.3082 | 2578540.0225 | 1199749.6724
81 | 2578406.0214 | 1199875.5853 | 2578412.5103 | 1199845.5908
82 | 2578540.6231 | 1199474.2696 | 2578541.093 | 1199482.1055 | 2578541.4754 | 1199486.8289 | 2578542.0235 | 1199491.0292 | 2578542.5443 | 1199498.2201 | 2578542.3199 | 1199515.8917
83 | 2578568.819 | 1199644.9274 | 2578572.1403 | 1199651.2187 | 2578583.8302 | 1199679.7254 | 2578584.8268 | 1199682.1093
84 | 2578521.3027 | 1199462.2661 | 2578530.5055 | 1199468.0805 | 2578536.1745 | 1199471.4953 | 2578540.6231 | 1199474.2696
85 | 2578584.8268 | 1199682.1093 | 2578585.9609 | 1199684.8219
86 | 2578521.3027 | 1199462.2661 | 2578514.9001 | 1199458.2398
87 | 2578521.3027 | 1199462.2661 | 2578530.1974 | 1199445.6759
88 | 2578391.4606 | 1199916.1045 | 2578393.7703 | 1199910.671 | 2578400.396 | 1199892.4815 | 2578406.0214 | 1199875.5853
89 | 2578406.0214 | 1199875.5853 | 2578449.1874 | 1199886.3902 | 2578462.6786 | 1199890.9439
90 | 2578391.4606 | 1199916.1045 | 2578373.804 | 1199909.1538 | 2578367.661 | 1199905.1072 | 2578361.7234 | 1199899.51
91 | 2578462.6786 | 1199890.9439 | 2578480.7067 | 1199846.9992
92 | 2578343.5521 | 1199874.0003 | 2578345.1168 | 1199881.3763 | 2578350.4503 | 1199888.8832 | 2578361.7234 | 1199899.51
93 | 2578343.5521 | 1199874.0003 | 2578325.5649 | 1199858.8112
94 | 2578343.5521 | 1199874.0003 | 2578329.0222 | 1199881.0903 | 2578310.0065 | 1199893.9555 | 2578308.9454 | 1199894.801
95 | 2578343.4597 | 1199285.9108 | 2578347.3189 | 1199291.0132
96 | 2578343.4597 | 1199285.9108 | 2578354.9195 | 1199181.7501
97 | 2578347.3189 | 1199291.0132 | 2578360.3559 | 1199308.2498
98 | 2578360.3559 | 1199308.2498 | 2578363.4871 | 1199312.3897
99 | 2578375.7276 | 1199328.5583 | 2578375.0171 | 1199327.6339 | 2578363.4871 | 1199312.3897
100 | 2578375.7276 | 1199328.5583 | 2578382.8431 | 1199337.8152
101 | 2578382.8431 | 1199337.8152 | 2578392.9965 | 1199351.024
102 | 2578392.9965 | 1199351.024 | 2578393.7818 | 1199352.0457 | 2578402.1156 | 1199362.1445
103 | 2578406.5174 | 1199367.4785 | 2578402.1156 | 1199362.1445
104 | 2578406.5174 | 1199367.4785 | 2578413.5114 | 1199375.9537 | 2578422.2998 | 1199385.1582
105 | 2578423.0017 | 1199385.8933 | 2578422.2998 | 1199385.1582
106 | 2578423.0017 | 1199385.8933 | 2578426.1521 | 1199389.1928 | 2578439.3328 | 1199402.2855 | 2578441.568 | 1199404.2585
107 | 2578441.568 | 1199404.2585 | 2578443.3956 | 1199405.8717
108 | 2578443.3956 | 1199405.8717 | 2578452.1645 | 1199413.6119 | 2578459.8724 | 1199419.9679
109 | 2578465.5737 | 1199424.6693 | 2578459.8724 | 1199419.9679
110 | 2578465.5737 | 1199424.6693 | 2578459.4529 | 1199431.0727
111 | 2578465.5737 | 1199424.6693 | 2578473.5516 | 1199430.7104 | 2578479.9069 | 1199435.1328
112 | 2578479.9069 | 1199435.1328 | 2578496.3426 | 1199446.57 | 2578512.7951 | 1199456.9161
113 | 2578512.7951 | 1199456.9161 | 2578514.9001 | 1199458.2398
114 | 2578504.9512 | 1199407.4318 | 2578529.5236 | 1199428.0846 | 2578532.2303 | 1199431.2655 | 2578533.6202 | 1199434.5622 | 2578533.5799 | 1199438.1643 | 2578532.291 | 1199441.7709 | 2578530.1974 | 1199445.6759

## bus_geodata
| x | y | coords
0 | 2578265.1406 | 1199992.5736
1 | 2578280.2002 | 1200009.1688
2 | 2578262.4902 | 1199989.6529
3 | 2578285.5861 | 1200014.3822
4 | 2578241.9805 | 1199965.3536
5 | 2578261.17 | 1199947.5284
6 | 2577364.3831 | 1200393.5592
7 | 2578294.8054 | 1199908.3466
8 | 2577363.1559 | 1200403.5748
9 | 2577856.7757 | 1199294.6624
10 | 2577887.5354 | 1199327.4247
11 | 2577904.9466 | 1199310.858
12 | 2578069.539 | 1199492.2701
13 | 2578092.5215 | 1199466.8781
14 | 2578056.2896 | 1199506.9087
15 | 2577925.9852 | 1199290.8399
16 | 2577971.3333 | 1199247.0945
17 | 2578102.9972 | 1199457.2047
18 | 2578117.1342 | 1199454.8565
19 | 2578079.8811 | 1199520.7844
20 | 2578125.1799 | 1199538.4986
21 | 2578137.8573 | 1199458.8491
22 | 2578159.1222 | 1199547.1428
23 | 2578139.1771 | 1199463.7358
24 | 2578147.4736 | 1199469.3751
25 | 2578167.487 | 1199428.7733
26 | 2578151.373 | 1199472.0328
27 | 2578125.4617 | 1199497.927
28 | 2578170.1888 | 1199425.28
29 | 2578185.107 | 1199552.5488
30 | 2578173.1277 | 1199573.4673
31 | 2578218.8414 | 1199556.7165
32 | 2578164.4299 | 1199588.6555
33 | 2578221.5137 | 1199557.0936
34 | 2578212.5959 | 1199570.9737
35 | 2578162.8287 | 1199591.4516
36 | 2578237.0713 | 1199559.2896
37 | 2578208.7218 | 1199579.8176
38 | 2578201.6065 | 1199596.0605
39 | 2578195.6629 | 1199609.6287
40 | 2578184.7628 | 1199631.7978
41 | 2578168.194 | 1199655.7285
42 | 2578241.0528 | 1199559.8516
43 | 2578267.8742 | 1199563.6373
44 | 2578296.963 | 1199570.7286
45 | 2578310.2776 | 1199575.7596
46 | 2578322.936 | 1199581.3609
47 | 2578315.885 | 1199561.8769
48 | 2578359.761 | 1199602.2271
49 | 2578310.8914 | 1199622.9928
50 | 2578379.7355 | 1199617.1117
51 | 2578364.5462 | 1199581.2524
52 | 2578400.3085 | 1199632.6718
53 | 2578364.6941 | 1199579.8096
54 | 2578364.9424 | 1199549.758
55 | 2578362.2257 | 1199538.8949
56 | 2578401.9118 | 1199633.8844
57 | 2578411.5409 | 1199641.2865
58 | 2578433.4349 | 1199659.464
59 | 2578435.5743 | 1199661.3174
60 | 2578447.6401 | 1199646.5588
61 | 2578449.3313 | 1199644.4901
62 | 2578460.5451 | 1199630.7736
63 | 2578438.769 | 1199664.362
64 | 2578465.0709 | 1199625.2377
65 | 2578467.5043 | 1199693.019
66 | 2578469.3294 | 1199620.0288
67 | 2578498.4957 | 1199722.5355
68 | 2578458.719 | 1199707.0555
69 | 2578474.323 | 1199613.9207
70 | 2578531.7159 | 1199579.6509
71 | 2578542.1243 | 1199586.5028
72 | 2578448.7541 | 1199734.5423
73 | 2578443.9911 | 1199747.8852
74 | 2578435.0064 | 1199773.0543
75 | 2578500.8026 | 1199724.3952
76 | 2578422.5878 | 1199807.8429
77 | 2578522.7447 | 1199739.8663
78 | 2578412.5103 | 1199845.5908
79 | 2578542.3199 | 1199515.8917
80 | 2578568.819 | 1199644.9274
81 | 2578540.6231 | 1199474.2696
82 | 2578584.8268 | 1199682.1093
83 | 2578585.9609 | 1199684.8219
84 | 2578521.3027 | 1199462.2661
85 | 2578540.0225 | 1199749.6724
86 | 2578406.0214 | 1199875.5853
87 | 2578391.4606 | 1199916.1045
88 | 2578462.6786 | 1199890.9439
89 | 2578343.5521 | 1199874.0003
90 | 2578361.7234 | 1199899.51
91 | 2578325.5649 | 1199858.8112
92 | 2578308.9454 | 1199894.801
93 | 2578480.7067 | 1199846.9992
94 | 2578343.4597 | 1199285.9108
95 | 2578347.3189 | 1199291.0132
96 | 2578354.9195 | 1199181.7501
97 | 2578360.3559 | 1199308.2498
98 | 2578363.4871 | 1199312.3897
99 | 2578375.7276 | 1199328.5583
100 | 2578382.8431 | 1199337.8152
101 | 2578392.9965 | 1199351.024
102 | 2578402.1156 | 1199362.1445
103 | 2578406.5174 | 1199367.4785
104 | 2578422.2998 | 1199385.1582
105 | 2578423.0017 | 1199385.8933
106 | 2578441.568 | 1199404.2585
107 | 2578443.3956 | 1199405.8717
108 | 2578459.8724 | 1199419.9679
109 | 2578465.5737 | 1199424.6693
110 | 2578459.4529 | 1199431.0727
111 | 2578479.9069 | 1199435.1328
112 | 2578512.7951 | 1199456.9161
113 | 2578514.9001 | 1199458.2398
114 | 2578504.9512 | 1199407.4318
115 | 2578530.1974 | 1199445.6759
116 | 2578322.936 | 1199581.3609

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97999 | -0.38529 | 0.00040939 | 0.0001026
1 | 0.97996 | -0.38587 | 0.00035105 | 8.7982e-05
2 | 0.98 | -0.38516 | 0.0022615 | 0.00056678
3 | 0.97995 | -0.38602 | 0.0010701 | 0.00026819
4 | 0.98012 | -0.3828 | 0 | 0
5 | 0.98024 | -0.38027 | 0.0013654 | 0.0003422
6 | 0.97904 | -0.40427 | 0 | 0
7 | 0.98056 | -0.37399 | 0.00065241 | 0.00016351
8 | 0.97903 | -0.4045 | 0.0011947 | 0.00029942
9 | 0.99023 | -0.18732 | 0.0003373 | 8.4536e-05
10 | 0.99025 | -0.18705 | 0 | 0
11 | 0.99025 | -0.1869 | 0.0011274 | 0.00028256
12 | 0.99118 | -0.16891 | 0.00048364 | 0.00012121
13 | 0.99091 | -0.17414 | 0.00034688 | 8.6936e-05
14 | 0.99134 | -0.16572 | 0 | 0
15 | 0.99029 | -0.18615 | 0 | 0
16 | 0.99022 | -0.18762 | 0.0013146 | 0.00032946
17 | 0.99084 | -0.17555 | 0.00083277 | 0.00020871
18 | 0.99077 | -0.17676 | 0.00091953 | 0.00023046
19 | 0.99157 | -0.16129 | 0.00041035 | 0.00010284
20 | 0.99199 | -0.15307 | 0.00066702 | 0.00016717
21 | 0.9907 | -0.17817 | 0 | 0
22 | 0.99232 | -0.14675 | 0.0013423 | 0.00033642
23 | 0.99069 | -0.1784 | 0.00079396 | 0.00019899
24 | 0.99067 | -0.1787 | 0 | 0
25 | 0.99065 | -0.17911 | 0.00069291 | 0.00017366
26 | 0.99067 | -0.17876 | 0.00070362 | 0.00017634
27 | 0.99064 | -0.17938 | 0.00099567 | 0.00024954
28 | 0.99065 | -0.17915 | 0.00053622 | 0.00013439
29 | 0.9926 | -0.14133 | 0 | 0
30 | 0.99256 | -0.14211 | 0.00083331 | 0.00020885
31 | 0.99301 | -0.13333 | 0 | 0
32 | 0.99254 | -0.14241 | 0.00057847 | 0.00014498
33 | 0.99321 | -0.12957 | 0.00080983 | 0.00020296
34 | 0.99198 | -0.1532 | 0.0010376 | 0.00026005
35 | 0.99254 | -0.14244 | 0.00041013 | 0.00010279
36 | 0.99435 | -0.10759 | 0.00032373 | 8.1134e-05
37 | 0.99134 | -0.16546 | 0.0013817 | 0.00034629
38 | 0.99018 | -0.18781 | 0.00041502 | 0.00010401
39 | 0.98922 | -0.20645 | 0.022989 | 0.0057615
40 | 0.98651 | -0.25892 | 0.027925 | 0.0069986
41 | 0.98408 | -0.30625 | 0.090585 | 0.022703
42 | 0.99465 | -0.10196 | 0.0029638 | 0.00074279
43 | 0.99666 | -0.063437 | 0.0014089 | 0.00035311
44 | 0.99891 | -0.020609 | 0.0027468 | 0.0006884
45 | 1 | 0 | -0.36618 | -0.093336
46 | 0.99878 | -0.023018 | 0 | 0
47 | 0.99997 | -0.0006454 | 0.0024729 | 0.00061976
48 | 0.99534 | -0.088315 | 0 | 0
49 | 0.9982 | -0.034281 | 0.014865 | 0.0037256
50 | 0.99347 | -0.12391 | 0.00476 | 0.001193
51 | 0.99506 | -0.09365 | 0.0032268 | 0.00080872
52 | 0.99159 | -0.15982 | 0.0012888 | 0.00032301
53 | 0.99505 | -0.093926 | 0.0043996 | 0.0011026
54 | 0.99487 | -0.09733 | 0.0014879 | 0.0003729
55 | 0.99482 | -0.098301 | 0.0049247 | 0.0012342
56 | 0.99144 | -0.1626 | 0.00087379 | 0.00021899
57 | 0.99057 | -0.17933 | 0.0036781 | 0.00092182
58 | 0.98857 | -0.21771 | 0.0018221 | 0.00045665
59 | 0.98837 | -0.22149 | 0 | 0
60 | 0.9875 | -0.23825 | 0.0012798 | 0.00032075
61 | 0.98738 | -0.24057 | 0.0020211 | 0.00050653
62 | 0.9866 | -0.25566 | 0.00025502 | 6.3913e-05
63 | 0.98817 | -0.22552 | 0.0032909 | 0.00082477
64 | 0.98628 | -0.26174 | 0.0004145 | 0.00010388
65 | 0.98637 | -0.2603 | 0 | 0
66 | 0.98599 | -0.26744 | 0.0030909 | 0.00077465
67 | 0.98589 | -0.2698 | 0.0027855 | 0.0006981
68 | 0.98583 | -0.27091 | 0.0042483 | 0.0010647
69 | 0.98565 | -0.2739 | 0.00036943 | 9.2588e-05
70 | 0.98224 | -0.34 | 0.0077841 | 0.0019509
71 | 0.98175 | -0.34938 | 0 | 0
72 | 0.98499 | -0.28733 | 0.0054489 | 0.0013656
73 | 0.98465 | -0.29391 | 0.0018787 | 0.00047085
74 | 0.98406 | -0.30542 | 0.0022416 | 0.00056179
75 | 0.98586 | -0.27031 | 0.0053254 | 0.0013347
76 | 0.98332 | -0.31987 | 0.0023646 | 0.00059262
77 | 0.98576 | -0.27237 | 0.0022025 | 0.00055199
78 | 0.98262 | -0.33351 | 0.0057493 | 0.0014409
79 | 0.97934 | -0.39627 | 0.0058429 | 0.0014644
80 | 0.98115 | -0.36111 | 0.0054126 | 0.0013565
81 | 0.97804 | -0.42183 | 0 | 0
82 | 0.98098 | -0.3645 | 0.0028033 | 0.00070256
83 | 0.98098 | -0.3646 | 0.0018288 | 0.00045833
84 | 0.97732 | -0.43578 | 0 | 0
85 | 0.98572 | -0.27311 | 0.0020643 | 0.00051736
86 | 0.98224 | -0.34105 | 0 | 0
87 | 0.98175 | -0.35069 | 0 | 0
88 | 0.98217 | -0.34233 | 0 | 0
89 | 0.98105 | -0.36445 | 0 | 0
90 | 0.98135 | -0.35842 | 0.0020514 | 0.00051412
91 | 0.98103 | -0.36484 | 0.00090129 | 0.00022588
92 | 0.9807 | -0.37137 | 0.0020879 | 0.00052328
93 | 0.98212 | -0.34336 | 0.0012049 | 0.00030197
94 | 0.97085 | -0.56334 | 0.0023776 | 0.00059588
95 | 0.97087 | -0.56295 | 0.0033105 | 0.00082969
96 | 0.97075 | -0.56525 | 0.00098279 | 0.00024631
97 | 0.971 | -0.56028 | 0.0033384 | 0.00083668
98 | 0.97105 | -0.55932 | 0.0018022 | 0.00045168
99 | 0.97127 | -0.55489 | 0.0041756 | 0.0010465
100 | 0.97145 | -0.55144 | 0.0047903 | 0.0012006
101 | 0.97177 | -0.54505 | 0.0028126 | 0.00070491
102 | 0.97209 | -0.53879 | 0.0041545 | 0.0010412
103 | 0.97227 | -0.53525 | 0.002602 | 0.00065213
104 | 0.97294 | -0.52198 | 0.003758 | 0.00094185
105 | 0.97297 | -0.52135 | 0.0034518 | 0.00086509
106 | 0.97389 | -0.5033 | 0.0026074 | 0.00065348
107 | 0.97398 | -0.5015 | 0.0037685 | 0.00094447
108 | 0.97487 | -0.48401 | 0.0035394 | 0.00088705
109 | 0.97519 | -0.47757 | 0 | 0
110 | 0.97517 | -0.47807 | 0.0030697 | 0.00076935
111 | 0.97603 | -0.46114 | 0.0045345 | 0.0011365
112 | 0.97704 | -0.44128 | 0.0022793 | 0.00057124
113 | 0.97711 | -0.43998 | 0.0034776 | 0.00087157
114 | 0.977 | -0.44216 | 0.0043933 | 0.0011011
115 | 0.97721 | -0.43802 | 0.0021237 | 0.00053225
116 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0014212 | 0.00035583 | -0.0014212 | -0.00035609 | 3.9131e-08 | -2.573e-07 | 0.0021578 | 0.0021579 | 0.0021579 | 0.97999 | -0.38529 | 0.97996 | -0.38587 | 0.59284
1 | -0.0018306 | -0.00045843 | 0.0018306 | 0.00045839 | 1.1426e-08 | -4.2381e-08 | 0.0027794 | 0.0027794 | 0.0027794 | 0.97999 | -0.38529 | 0.98 | -0.38516 | 0.76358
2 | 0.0010701 | 0.0002681 | -0.0010701 | -0.00026819 | 7.4239e-09 | -8.9714e-08 | 0.0016249 | 0.0016249 | 0.0016249 | 0.97996 | -0.38587 | 0.97995 | -0.38602 | 0.4464
3 | -0.0040921 | -0.0010252 | 0.0040925 | 0.0010251 | 4.609e-07 | -1.0623e-07 | 0.0062132 | 0.0062131 | 0.0062132 | 0.98 | -0.38516 | 0.98012 | -0.3828 | 1.7069
4 | -0.0052884 | -0.0013128 | 0.0052891 | 0.0013129 | 6.3242e-07 | 7.4626e-08 | 0.0080244 | 0.0080243 | 0.0080244 | 0.98012 | -0.3828 | 0.98024 | -0.38027 | 2.2045
5 | 0.0011959 | 0.00028777 | -0.0011947 | -0.00029929 | 1.2044e-06 | -1.1522e-05 | 0.0018114 | 0.0018157 | 0.0018157 | 0.98012 | -0.3828 | 0.97904 | -0.40427 | 0.49883
6 | -0.0066544 | -0.0016551 | 0.0066564 | 0.0016557 | 1.9806e-06 | 6.1429e-07 | 0.010097 | 0.010097 | 0.010097 | 0.98024 | -0.38027 | 0.98056 | -0.37399 | 2.7739
7 | 0.0011947 | 0.00029929 | -0.0011947 | -0.00029942 | 1.3193e-08 | -1.2574e-07 | 0.0018157 | 0.0018158 | 0.0018158 | 0.97904 | -0.40427 | 0.97903 | -0.4045 | 0.49884
8 | -0.0073088 | -0.0018192 | 0.0073097 | 0.0018196 | 9.0726e-07 | 3.3232e-07 | 0.011087 | 0.011087 | 0.011087 | 0.98056 | -0.37399 | 0.9807 | -0.37137 | 3.0458
9 | -0.0003373 | -8.4536e-05 | 0.00033731 | 8.396e-05 | 4.3277e-09 | -5.7535e-07 | 0.00050686 | 0.00050666 | 0.00050686 | 0.99023 | -0.18732 | 0.99025 | -0.18705 | 0.13925
10 | -0.00033731 | -8.396e-05 | 0.00033731 | 8.3653e-05 | 2.313e-09 | -3.077e-07 | 0.00050666 | 0.00050655 | 0.00050666 | 0.99025 | -0.18705 | 0.99025 | -0.1869 | 0.13919
11 | -0.0014647 | -0.00036621 | 0.0014648 | 0.00036587 | 5.2737e-08 | -3.3986e-07 | 0.0022007 | 0.0022005 | 0.0022007 | 0.99025 | -0.1869 | 0.99029 | -0.18615 | 0.60458
12 | 0.0086058 | 0.0021511 | -0.0086036 | -0.0021501 | 2.143e-06 | 9.3025e-07 | 0.012917 | 0.012918 | 0.012918 | 0.99118 | -0.16891 | 0.99091 | -0.17414 | 3.5488
13 | -0.0090894 | -0.0022723 | 0.0090908 | 0.0022729 | 1.3782e-06 | 6.2755e-07 | 0.013644 | 0.013643 | 0.013644 | 0.99118 | -0.16891 | 0.99134 | -0.16572 | 3.7482
14 | 0.0054757 | 0.0013707 | -0.0054753 | -0.0013707 | 3.6572e-07 | 4.8241e-08 | 0.0082221 | 0.0082222 | 0.0082222 | 0.99091 | -0.17414 | 0.99084 | -0.17555 | 2.2588
15 | 0.002781 | 0.00069248 | -0.0027794 | -0.00069458 | 1.5841e-06 | -2.1059e-06 | 0.0041746 | 0.0041757 | 0.0041757 | 0.99091 | -0.17414 | 0.99029 | -0.18615 | 1.1472
16 | -0.0090908 | -0.0022729 | 0.0090927 | 0.0022738 | 1.9137e-06 | 8.712e-07 | 0.013643 | 0.013643 | 0.013643 | 0.99134 | -0.16572 | 0.99157 | -0.16129 | 3.7482
17 | 0.0013147 | 0.00032871 | -0.0013146 | -0.00032946 | 9.2193e-08 | -7.5159e-07 | 0.0019752 | 0.0019754 | 0.0019754 | 0.99029 | -0.18615 | 0.99022 | -0.18762 | 0.5427
18 | 0.0046426 | 0.001162 | -0.0046423 | -0.001162 | 2.6892e-07 | -1.7917e-08 | 0.0069716 | 0.0069716 | 0.0069716 | 0.99084 | -0.17555 | 0.99077 | -0.17676 | 1.9153
19 | 0.0037228 | 0.00093154 | -0.0037225 | -0.00093165 | 2.4972e-07 | -1.1454e-07 | 0.0055906 | 0.0055907 | 0.0055907 | 0.99077 | -0.17676 | 0.9907 | -0.17817 | 1.5359
20 | -0.009503 | -0.0023766 | 0.0095068 | 0.0023784 | 3.7167e-06 | 1.7496e-06 | 0.014259 | 0.014259 | 0.014259 | 0.99157 | -0.16129 | 0.99199 | -0.15307 | 3.9173
21 | -0.010174 | -0.0025456 | 0.010177 | 0.0025471 | 3.0584e-06 | 1.505e-06 | 0.015259 | 0.015259 | 0.015259 | 0.99199 | -0.15307 | 0.99232 | -0.14675 | 4.1922
22 | 0.0012292 | 0.00030748 | -0.0012291 | -0.00030799 | 5.4892e-08 | -5.1789e-07 | 0.001846 | 0.0018462 | 0.0018462 | 0.9907 | -0.17817 | 0.99065 | -0.17911 | 0.5072
23 | 0.0024933 | 0.00062418 | -0.0024933 | -0.00062422 | 2.6618e-08 | -4.8142e-08 | 0.0037447 | 0.0037447 | 0.0037447 | 0.9907 | -0.17817 | 0.99069 | -0.1784 | 1.0288
24 | -0.011519 | -0.0028835 | 0.011522 | 0.002885 | 2.9747e-06 | 1.5602e-06 | 0.017272 | 0.017272 | 0.017272 | 0.99232 | -0.14675 | 0.9926 | -0.14133 | 4.7451
25 | 0.0016994 | 0.00042524 | -0.0016993 | -0.00042535 | 2.4504e-08 | -1.1348e-07 | 0.0025522 | 0.0025522 | 0.0025522 | 0.99069 | -0.1784 | 0.99067 | -0.1787 | 0.70116
26 | 0.00070362 | 0.00017628 | -0.00070362 | -0.00017634 | 1.9766e-09 | -5.9495e-08 | 0.0010568 | 0.0010569 | 0.0010569 | 0.99067 | -0.1787 | 0.99067 | -0.17876 | 0.29035
27 | 0.00099571 | 0.00024907 | -0.00099567 | -0.00024954 | 3.1981e-08 | -4.7049e-07 | 0.0014954 | 0.0014956 | 0.0014956 | 0.99067 | -0.1787 | 0.99064 | -0.17938 | 0.41087
28 | 0.00053622 | 0.00013433 | -0.00053622 | -0.00013439 | 1.0743e-09 | -5.6171e-08 | 0.00080541 | 0.00080543 | 0.00080543 | 0.99065 | -0.17911 | 0.99065 | -0.17915 | 0.22127
29 | 0.001822 | 0.00045609 | -0.0018219 | -0.00045636 | 6.7433e-08 | -2.6842e-07 | 0.0027312 | 0.0027313 | 0.0027313 | 0.9926 | -0.14133 | 0.99256 | -0.14211 | 0.75036
30 | -0.013344 | -0.0033411 | 0.013349 | 0.0033439 | 5.0857e-06 | 2.8166e-06 | 0.020003 | 0.020003 | 0.020003 | 0.9926 | -0.14133 | 0.99301 | -0.13333 | 5.4954
31 | 0.00098861 | 0.00024751 | -0.0009886 | -0.00024773 | 1.4416e-08 | -2.1698e-07 | 0.001482 | 0.0014821 | 0.0014821 | 0.99256 | -0.14211 | 0.99254 | -0.14241 | 0.40717
32 | -0.15869 | -0.040159 | 0.15872 | 0.040177 | 2.8646e-05 | 1.8264e-05 | 0.23793 | 0.23793 | 0.23793 | 0.99301 | -0.13333 | 0.99321 | -0.12957 | 32.6826
33 | 0.14534 | 0.036815 | -0.1452 | -0.036726 | 0.0001386 | 8.8304e-05 | 0.21793 | 0.21793 | 0.21793 | 0.99301 | -0.13333 | 0.99198 | -0.1532 | 29.9349
34 | 0.00041013 | 0.00010275 | -0.00041013 | -0.00010279 | 4.5676e-10 | -4.1352e-08 | 0.00061485 | 0.00061487 | 0.00061487 | 0.99254 | -0.14241 | 0.99254 | -0.14244 | 0.16892
35 | -0.15953 | -0.04038 | 0.15969 | 0.040487 | 0.00016848 | 0.00010742 | 0.23914 | 0.23914 | 0.23914 | 0.99321 | -0.12957 | 0.99435 | -0.10759 | 32.8492
36 | 0.14416 | 0.036466 | -0.14408 | -0.036412 | 8.4753e-05 | 5.3993e-05 | 0.21637 | 0.21637 | 0.21637 | 0.99198 | -0.1532 | 0.99134 | -0.16546 | 29.7211
37 | -0.16002 | -0.040568 | 0.16006 | 0.040596 | 4.3292e-05 | 2.7602e-05 | 0.23963 | 0.23963 | 0.23963 | 0.99435 | -0.10759 | 0.99465 | -0.10196 | 32.9157
38 | 0.1427 | 0.036066 | -0.14254 | -0.035969 | 0.00015269 | 9.7265e-05 | 0.2143 | 0.2143 | 0.2143 | 0.99134 | -0.16546 | 0.99018 | -0.18781 | 29.4363
39 | 0.14213 | 0.035865 | -0.142 | -0.035784 | 0.00012681 | 8.0775e-05 | 0.21367 | 0.21367 | 0.21367 | 0.99018 | -0.18781 | 0.98922 | -0.20645 | 29.3506
40 | 0.11901 | 0.030022 | -0.11871 | -0.029832 | 0.00029811 | 0.00019047 | 0.17909 | 0.17909 | 0.17909 | 0.98922 | -0.20645 | 0.98651 | -0.25892 | 49.2012
41 | 0.09079 | 0.022833 | -0.090585 | -0.022703 | 0.00020478 | 0.00013069 | 0.13697 | 0.13697 | 0.13697 | 0.98651 | -0.25892 | 0.98408 | -0.30625 | 37.6297
42 | -0.16303 | -0.041339 | 0.16333 | 0.041532 | 0.00030252 | 0.00019291 | 0.24406 | 0.24406 | 0.24406 | 0.99465 | -0.10196 | 0.99666 | -0.063437 | 33.5248
43 | -0.16474 | -0.041885 | 0.16508 | 0.042102 | 0.00034062 | 0.00021722 | 0.24616 | 0.24616 | 0.24616 | 0.99666 | -0.063437 | 0.99891 | -0.020609 | 33.8137
44 | -0.16782 | -0.04279 | 0.16799 | 0.042897 | 0.00016716 | 0.00010661 | 0.25026 | 0.25025 | 0.25026 | 0.99891 | -0.020609 | 1 | 0 | 34.3757
45 | 0.19407 | 0.049819 | -0.19385 | -0.049681 | 0.00021655 | 0.00013823 | 0.2892 | 0.2892 | 0.2892 | 1 | 0 | 0.99878 | -0.023018 | 39.725
46 | 0.0024729 | 0.00061961 | -0.0024729 | -0.00061976 | 7.6025e-08 | -1.4776e-07 | 0.0036797 | 0.0036798 | 0.0036798 | 1 | 0 | 0.99997 | -0.0006454 | 1.0109
47 | 0.17898 | 0.045951 | -0.17841 | -0.04559 | 0.00056534 | 0.00036071 | 0.26704 | 0.26704 | 0.26704 | 0.99878 | -0.023018 | 0.99534 | -0.088315 | 36.6812
48 | 0.014873 | 0.0037301 | -0.014865 | -0.0037256 | 7.9806e-06 | 4.5407e-06 | 0.022159 | 0.02216 | 0.02216 | 0.99878 | -0.023018 | 0.9982 | -0.034281 | 6.0878
49 | 0.16437 | 0.042069 | -0.16409 | -0.041889 | 0.00028276 | 0.00018032 | 0.24604 | 0.24604 | 0.24604 | 0.99534 | -0.088315 | 0.99347 | -0.12391 | 33.7972
50 | 0.014044 | 0.0035208 | -0.01404 | -0.0035188 | 3.569e-06 | 2.0037e-06 | 0.020996 | 0.020996 | 0.020996 | 0.99534 | -0.088315 | 0.99506 | -0.09365 | 5.7681
51 | 0.15933 | 0.040696 | -0.15905 | -0.04052 | 0.00027607 | 0.00017602 | 0.23891 | 0.23891 | 0.23891 | 0.99347 | -0.12391 | 0.99159 | -0.15982 | 32.8179
52 | 0.010814 | 0.0027101 | -0.010813 | -0.0027101 | 1.4221e-07 | 7.2178e-08 | 0.016171 | 0.016171 | 0.016171 | 0.99506 | -0.09365 | 0.99505 | -0.093926 | 4.4425
53 | 0.15776 | 0.040197 | -0.15774 | -0.040183 | 2.1167e-05 | 1.3495e-05 | 0.23698 | 0.23698 | 0.23698 | 0.99159 | -0.15982 | 0.99144 | -0.1626 | 32.5523
54 | 0.0064138 | 0.0016074 | -0.0064128 | -0.0016071 | 1.0401e-06 | 2.741e-07 | 0.0095913 | 0.0095915 | 0.0095915 | 0.99505 | -0.093926 | 0.99487 | -0.09733 | 2.635
55 | 0.0049249 | 0.0012342 | -0.0049247 | -0.0012342 | 2.2784e-07 | 4.2448e-10 | 0.0073661 | 0.0073661 | 0.0073661 | 0.99487 | -0.09733 | 0.99482 | -0.098301 | 2.0237
56 | 0.15687 | 0.039964 | -0.15674 | -0.039884 | 0.00012649 | 8.0638e-05 | 0.23567 | 0.23567 | 0.23567 | 0.99144 | -0.1626 | 0.99057 | -0.17933 | 32.3722
57 | 0.15306 | 0.038962 | -0.15278 | -0.038782 | 0.00028268 | 0.00018018 | 0.23014 | 0.23014 | 0.23014 | 0.99057 | -0.17933 | 0.98857 | -0.21771 | 31.6132
58 | 0.15096 | 0.038325 | -0.15093 | -0.038308 | 2.7445e-05 | 1.7492e-05 | 0.2274 | 0.2274 | 0.2274 | 0.98857 | -0.21771 | 0.98837 | -0.22149 | 31.2365
59 | 0.051364 | 0.012934 | -0.051354 | -0.012928 | 9.9016e-06 | 6.2805e-06 | 0.077351 | 0.077351 | 0.077351 | 0.98837 | -0.22149 | 0.98817 | -0.22552 | 21.2501
60 | 0.099568 | 0.025374 | -0.099487 | -0.025323 | 8.0478e-05 | 5.1017e-05 | 0.15005 | 0.15005 | 0.15005 | 0.98837 | -0.22149 | 0.9875 | -0.23825 | 20.6115
61 | 0.098208 | 0.025002 | -0.098197 | -0.024995 | 1.0992e-05 | 6.9668e-06 | 0.14812 | 0.14812 | 0.14812 | 0.9875 | -0.23825 | 0.98738 | -0.24057 | 20.3466
62 | 0.096175 | 0.024488 | -0.096106 | -0.024444 | 6.9918e-05 | 4.4295e-05 | 0.14508 | 0.14508 | 0.14508 | 0.98738 | -0.24057 | 0.9866 | -0.25566 | 19.9282
63 | 0.095851 | 0.02438 | -0.095822 | -0.024362 | 2.8069e-05 | 1.7782e-05 | 0.14469 | 0.14469 | 0.14469 | 0.9866 | -0.25566 | 0.98628 | -0.26174 | 19.8754
64 | 0.048063 | 0.012103 | -0.047983 | -0.012052 | 7.9778e-05 | 5.0539e-05 | 0.072395 | 0.072395 | 0.072395 | 0.98817 | -0.22552 | 0.98637 | -0.2603 | 19.8888
65 | 0.095408 | 0.024259 | -0.095382 | -0.024242 | 2.6183e-05 | 1.6586e-05 | 0.14407 | 0.14407 | 0.14407 | 0.98628 | -0.26174 | 0.98599 | -0.26744 | 19.7895
66 | 0.012384 | 0.003105 | -0.012378 | -0.0031019 | 5.6065e-06 | 3.0417e-06 | 0.018682 | 0.018683 | 0.018683 | 0.98637 | -0.2603 | 0.98589 | -0.2698 | 5.1326
67 | 0.035599 | 0.0089474 | -0.035581 | -0.008936 | 1.8027e-05 | 1.1325e-05 | 0.053713 | 0.053713 | 0.053713 | 0.98637 | -0.2603 | 0.98583 | -0.27091 | 14.7563
68 | 0.092291 | 0.023467 | -0.092262 | -0.023449 | 2.8747e-05 | 1.8197e-05 | 0.1394 | 0.1394 | 0.1394 | 0.98599 | -0.26744 | 0.98565 | -0.2739 | 19.1488
69 | 0.0095928 | 0.0024038 | -0.0095926 | -0.0024037 | 2.3293e-07 | 1.1129e-07 | 0.014479 | 0.014479 | 0.014479 | 0.98589 | -0.2698 | 0.98586 | -0.27031 | 3.9776
70 | 0.031333 | 0.0078713 | -0.031308 | -0.007856 | 2.4531e-05 | 1.5327e-05 | 0.0473 | 0.047301 | 0.047301 | 0.98583 | -0.27091 | 0.98499 | -0.28733 | 12.9947
71 | 0.091893 | 0.023357 | -0.091601 | -0.023172 | 0.00029148 | 0.0001845 | 0.13885 | 0.13885 | 0.13885 | 0.98565 | -0.2739 | 0.98224 | -0.34 | 19.0723
72 | 0.083817 | 0.021221 | -0.083779 | -0.021197 | 3.7729e-05 | 2.3831e-05 | 0.12705 | 0.12705 | 0.12705 | 0.98224 | -0.34 | 0.98175 | -0.34938 | 17.4525
73 | 0.073728 | 0.018677 | -0.073563 | -0.018573 | 0.00016567 | 0.00010424 | 0.11182 | 0.11182 | 0.11182 | 0.98175 | -0.34938 | 0.97934 | -0.39627 | 15.3599
74 | 0.010051 | 0.0025201 | -0.010045 | -0.0025174 | 5.6152e-06 | 2.7784e-06 | 0.015234 | 0.015235 | 0.015235 | 0.98175 | -0.34938 | 0.98115 | -0.36111 | 4.1853
75 | 0.025859 | 0.0064904 | -0.025851 | -0.0064853 | 8.1094e-06 | 5.0098e-06 | 0.039069 | 0.039069 | 0.039069 | 0.98499 | -0.28733 | 0.98465 | -0.29391 | 10.7332
76 | 0.023972 | 0.0060145 | -0.023959 | -0.0060064 | 1.3155e-05 | 8.0792e-06 | 0.03623 | 0.03623 | 0.03623 | 0.98465 | -0.29391 | 0.98406 | -0.30542 | 9.9533
77 | 0.021718 | 0.0054446 | -0.021703 | -0.0054355 | 1.4939e-05 | 9.0923e-06 | 0.03284 | 0.032841 | 0.032841 | 0.98406 | -0.30542 | 0.98332 | -0.31987 | 9.0221
78 | 0.0042673 | 0.0010691 | -0.0042668 | -0.0010691 | 4.1815e-07 | -7.5094e-08 | 0.0064407 | 0.0064408 | 0.0064408 | 0.98586 | -0.27031 | 0.98576 | -0.27237 | 1.7694
79 | 0.019338 | 0.0048429 | -0.019326 | -0.0048354 | 1.2554e-05 | 7.5391e-06 | 0.029262 | 0.029263 | 0.029263 | 0.98332 | -0.31987 | 0.98262 | -0.33351 | 8.0392
80 | 0.0020644 | 0.00051716 | -0.0020643 | -0.00051736 | 7.2349e-08 | -2.0697e-07 | 0.0031161 | 0.0031162 | 0.0031162 | 0.98576 | -0.27237 | 0.98572 | -0.27311 | 0.8561
81 | 0.013576 | 0.0033945 | -0.013572 | -0.0033918 | 4.8629e-06 | 2.7237e-06 | 0.020556 | 0.020556 | 0.020556 | 0.98262 | -0.33351 | 0.98224 | -0.34105 | 5.6474
82 | 0.06772 | 0.017109 | -0.067637 | -0.017057 | 8.2872e-05 | 5.199e-05 | 0.10294 | 0.10294 | 0.10294 | 0.97934 | -0.39627 | 0.97804 | -0.42183 | 14.1405
83 | 0.0046328 | 0.0011608 | -0.004632 | -0.0011609 | 7.499e-07 | -3.1577e-08 | 0.007026 | 0.0070262 | 0.0070262 | 0.98115 | -0.36111 | 0.98098 | -0.3645 | 1.9303
84 | 0.067637 | 0.017057 | -0.067592 | -0.017028 | 4.5105e-05 | 2.8298e-05 | 0.10294 | 0.10294 | 0.10294 | 0.97804 | -0.42183 | 0.97732 | -0.43578 | 14.1405
85 | 0.0018288 | 0.0004583 | -0.0018288 | -0.00045833 | 8.4842e-09 | -3.1689e-08 | 0.002774 | 0.002774 | 0.002774 | 0.98098 | -0.3645 | 0.98098 | -0.3646 | 0.76209
86 | 0.061073 | 0.015395 | -0.061061 | -0.015387 | 1.227e-05 | 7.6635e-06 | 0.093018 | 0.093018 | 0.093018 | 0.97732 | -0.43578 | 0.97711 | -0.43998 | 12.7773
87 | 0.0065186 | 0.0016334 | -0.0065179 | -0.0016332 | 6.9532e-07 | 2.0915e-07 | 0.0099247 | 0.0099248 | 0.0099248 | 0.97732 | -0.43578 | 0.97721 | -0.43802 | 2.7266
88 | 0.012367 | 0.003091 | -0.012361 | -0.003088 | 5.6663e-06 | 3.0816e-06 | 0.018731 | 0.018732 | 0.018732 | 0.98224 | -0.34105 | 0.98175 | -0.35069 | 5.146
89 | 0.001205 | 0.00030071 | -0.0012049 | -0.00030141 | 7.3374e-08 | -6.9645e-07 | 0.001825 | 0.0018253 | 0.0018253 | 0.98224 | -0.34105 | 0.98217 | -0.34233 | 0.50145
90 | 0.012361 | 0.003088 | -0.012356 | -0.0030855 | 4.5383e-06 | 2.4686e-06 | 0.018732 | 0.018732 | 0.018732 | 0.98175 | -0.35069 | 0.98135 | -0.35842 | 5.1461
91 | 0.0012049 | 0.00030141 | -0.0012049 | -0.00030197 | 5.9336e-08 | -5.6298e-07 | 0.0018253 | 0.0018255 | 0.0018255 | 0.98217 | -0.34233 | 0.98212 | -0.34336 | 0.50151
92 | -0.010302 | -0.0025699 | 0.010305 | 0.0025714 | 2.9504e-06 | 1.481e-06 | 0.015621 | 0.015621 | 0.015621 | 0.98105 | -0.36445 | 0.98135 | -0.35842 | 4.2916
93 | 0.00090131 | 0.0002256 | -0.00090129 | -0.00022588 | 1.6498e-08 | -2.867e-07 | 0.001367 | 0.0013671 | 0.0013671 | 0.98105 | -0.36445 | 0.98103 | -0.36484 | 0.37557
94 | 0.0094007 | 0.0023443 | -0.0093976 | -0.0023428 | 3.0847e-06 | 1.4632e-06 | 0.014254 | 0.014255 | 0.014255 | 0.98105 | -0.36445 | 0.9807 | -0.37137 | 3.9161
95 | -0.0033605 | -0.00084095 | 0.0033605 | 0.00084091 | 6.3632e-08 | -3.8385e-08 | 0.0051501 | 0.0051501 | 0.0051501 | 0.97085 | -0.56334 | 0.97087 | -0.56295 | 1.4149
96 | 0.00098288 | 0.00024507 | -0.00098279 | -0.00024631 | 8.9153e-08 | -1.2386e-06 | 0.001506 | 0.0015065 | 0.0015065 | 0.97085 | -0.56334 | 0.97075 | -0.56525 | 0.41387
97 | -0.006671 | -0.0016706 | 0.0066719 | 0.0016709 | 8.4714e-07 | 2.7488e-07 | 0.010224 | 0.010224 | 0.010224 | 0.97087 | -0.56295 | 0.971 | -0.56028 | 2.8088
98 | -0.01001 | -0.0025076 | 0.010011 | 0.0025078 | 4.5803e-07 | 2.2893e-07 | 0.01534 | 0.01534 | 0.01534 | 0.971 | -0.56028 | 0.97105 | -0.55932 | 4.2142
99 | -0.011813 | -0.0029595 | 0.011815 | 0.0029608 | 2.4918e-06 | 1.3438e-06 | 0.018102 | 0.018101 | 0.018102 | 0.97105 | -0.55932 | 0.97127 | -0.55489 | 4.9729
100 | -0.015991 | -0.0040073 | 0.015994 | 0.0040089 | 2.6278e-06 | 1.5373e-06 | 0.024499 | 0.024499 | 0.024499 | 0.97127 | -0.55489 | 0.97145 | -0.55144 | 6.7304
101 | -0.020784 | -0.0052094 | 0.02079 | 0.0052133 | 6.3321e-06 | 3.8462e-06 | 0.031836 | 0.031836 | 0.031836 | 0.97145 | -0.55144 | 0.97177 | -0.54505 | 8.7462
102 | -0.023603 | -0.0059182 | 0.02361 | 0.0059225 | 7.0452e-06 | 4.3307e-06 | 0.036143 | 0.036143 | 0.036143 | 0.97177 | -0.54505 | 0.97209 | -0.53879 | 9.9293
103 | -0.027765 | -0.0069637 | 0.027769 | 0.0069666 | 4.6849e-06 | 2.9126e-06 | 0.042502 | 0.042502 | 0.042502 | 0.97209 | -0.53879 | 0.97227 | -0.53525 | 11.6765
104 | -0.030371 | -0.0076188 | 0.03039 | 0.0076308 | 1.9216e-05 | 1.2004e-05 | 0.046485 | 0.046484 | 0.046485 | 0.97227 | -0.53525 | 0.97294 | -0.52198 | 12.7705
105 | -0.034149 | -0.0085726 | 0.03415 | 0.0085733 | 1.0398e-06 | 6.5285e-07 | 0.052232 | 0.052232 | 0.052232 | 0.97294 | -0.52198 | 0.97297 | -0.52135 | 14.3495
106 | -0.037601 | -0.0094384 | 0.037634 | 0.0094588 | 3.2399e-05 | 2.0411e-05 | 0.057511 | 0.057511 | 0.057511 | 0.97297 | -0.52135 | 0.97389 | -0.5033 | 15.7997
107 | -0.040241 | -0.010112 | 0.040245 | 0.010114 | 3.457e-06 | 2.1821e-06 | 0.061495 | 0.061495 | 0.061495 | 0.97389 | -0.5033 | 0.97398 | -0.5015 | 16.8942
108 | -0.044013 | -0.011059 | 0.04405 | 0.011082 | 3.6782e-05 | 2.327e-05 | 0.067252 | 0.067252 | 0.067252 | 0.97398 | -0.5015 | 0.97487 | -0.48401 | 18.4759
109 | -0.047589 | -0.011969 | 0.047604 | 0.011979 | 1.4628e-05 | 9.2698e-06 | 0.072654 | 0.072654 | 0.072654 | 0.97487 | -0.48401 | 0.97519 | -0.47757 | 19.96
110 | 0.0030698 | 0.00076929 | -0.0030697 | -0.00076935 | 7.2792e-08 | -6.379e-08 | 0.0046841 | 0.0046841 | 0.0046841 | 0.97519 | -0.47757 | 0.97517 | -0.47807 | 1.2869
111 | -0.050674 | -0.012748 | 0.050713 | 0.012773 | 3.9812e-05 | 2.5258e-05 | 0.077339 | 0.077338 | 0.077339 | 0.97519 | -0.47757 | 0.97603 | -0.46114 | 21.2468
112 | -0.055248 | -0.01391 | 0.0553 | 0.013942 | 5.2517e-05 | 3.2623e-05 | 0.084252 | 0.084251 | 0.084252 | 0.97603 | -0.46114 | 0.97704 | -0.44128 | 11.573
113 | -0.05758 | -0.014513 | 0.057583 | 0.014516 | 3.5879e-06 | 2.2339e-06 | 0.087722 | 0.087722 | 0.087722 | 0.97704 | -0.44128 | 0.97711 | -0.43998 | 12.0498
114 | -0.0043933 | -0.0011011 | 0.0043942 | 0.001101 | 8.6827e-07 | -9.2076e-08 | 0.0066912 | 0.006691 | 0.0066912 | 0.977 | -0.44216 | 0.97721 | -0.43802 | 1.8382

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36618 | 0.093336

## res_load
| p_mw | q_mvar
0 | 0.00040939 | 0.0001026
1 | 0.00035105 | 8.7982e-05
2 | 0.0022615 | 0.00056678
3 | 0.0010701 | 0.00026819
4 | 0.0013654 | 0.0003422
5 | 0.00065241 | 0.00016351
6 | 0.0011947 | 0.00029942
7 | 0.0003373 | 8.4536e-05
8 | 0.0011274 | 0.00028256
9 | 0.00048364 | 0.00012121
10 | 0.00034688 | 8.6936e-05
11 | 0.0013146 | 0.00032946
12 | 0.00083277 | 0.00020871
13 | 0.00091953 | 0.00023046
14 | 0.00041035 | 0.00010284
15 | 0.00066702 | 0.00016717
16 | 0.0013423 | 0.00033642
17 | 0.00079396 | 0.00019899
18 | 0.00069291 | 0.00017366
19 | 0.00070362 | 0.00017634
20 | 0.00099567 | 0.00024954
21 | 0.00053622 | 0.00013439
22 | 0.00083331 | 0.00020885
23 | 0.00057847 | 0.00014498
24 | 0.00080983 | 0.00020296
25 | 0.0010376 | 0.00026005
26 | 0.00041013 | 0.00010279
27 | 0.00032373 | 8.1134e-05
28 | 0.0013817 | 0.00034629
29 | 0.00041502 | 0.00010401
30 | 0.022989 | 0.0057615
31 | 0.027925 | 0.0069986
32 | 0.090585 | 0.022703
33 | 0.0029638 | 0.00074279
34 | 0.0014089 | 0.00035311
35 | 0.0027468 | 0.0006884
36 | 0.0024729 | 0.00061976
37 | 0.014865 | 0.0037256
38 | 0.00476 | 0.001193
39 | 0.0032268 | 0.00080872
40 | 0.0012888 | 0.00032301
41 | 0.0043996 | 0.0011026
42 | 0.0014879 | 0.0003729
43 | 0.0049247 | 0.0012342
44 | 0.00087379 | 0.00021899
45 | 0.0036781 | 0.00092182
46 | 0.0018221 | 0.00045665
47 | 0.0012798 | 0.00032075
48 | 0.0020211 | 0.00050653
49 | 0.00025502 | 6.3913e-05
50 | 0.0032909 | 0.00082477
51 | 0.0004145 | 0.00010388
52 | 0.0030909 | 0.00077465
53 | 0.0027855 | 0.0006981
54 | 0.0042483 | 0.0010647
55 | 0.00036943 | 9.2588e-05
56 | 0.0077841 | 0.0019509
57 | 0.0054489 | 0.0013656
58 | 0.0018787 | 0.00047085
59 | 0.0022416 | 0.00056179
60 | 0.0053254 | 0.0013347
61 | 0.0023646 | 0.00059262
62 | 0.0022025 | 0.00055199
63 | 0.0057493 | 0.0014409
64 | 0.0058429 | 0.0014644
65 | 0.0054126 | 0.0013565
66 | 0.0028033 | 0.00070256
67 | 0.0018288 | 0.00045833
68 | 0.0020643 | 0.00051736
69 | 0.0020514 | 0.00051412
70 | 0.00090129 | 0.00022588
71 | 0.0020879 | 0.00052328
72 | 0.0012049 | 0.00030197
73 | 0.0023776 | 0.00059588
74 | 0.0033105 | 0.00082969
75 | 0.00098279 | 0.00024631
76 | 0.0033384 | 0.00083668
77 | 0.0018022 | 0.00045168
78 | 0.0041756 | 0.0010465
79 | 0.0047903 | 0.0012006
80 | 0.0028126 | 0.00070491
81 | 0.0041545 | 0.0010412
82 | 0.002602 | 0.00065213
83 | 0.003758 | 0.00094185
84 | 0.0034518 | 0.00086509
85 | 0.0026074 | 0.00065348
86 | 0.0037685 | 0.00094447
87 | 0.0035394 | 0.00088705
88 | 0.0030697 | 0.00076935
89 | 0.0045345 | 0.0011365
90 | 0.0022793 | 0.00057124
91 | 0.0034776 | 0.00087157
92 | 0.0043933 | 0.0011011
93 | 0.0021237 | 0.00053225

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1