## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2275-18_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2275-18_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2275-18_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2275-18_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2275-18_0_4_node_114 | 0.4 | n |  | TRUE
5 | bus_LV_2275-18_0_4_node_113 | 0.4 | n |  | TRUE
6 | bus_LV_2275-18_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2275-18_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2275-18_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2275-18_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2275-18_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2275-18_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2275-18_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2275-18_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2275-18_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_2275-18_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2275-18_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2275-18_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2275-18_0_4_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_2275-18_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_2275-18_0_4_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_2275-18_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2275-18_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_2275-18_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_2275-18_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2275-18_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2275-18_0_4_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_2275-18_0_4_node_83 | 0.4 | n |  | TRUE
28 | bus_LV_2275-18_0_4_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_2275-18_0_4_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_2275-18_0_4_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_2275-18_0_4_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_2275-18_0_4_node_45 | 0.4 | n |  | TRUE
33 | bus_LV_2275-18_0_4_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_2275-18_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_2275-18_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2275-18_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_2275-18_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2275-18_0_4_node_78 | 0.4 | n |  | TRUE
39 | bus_LV_2275-18_0_4_node_79 | 0.4 | n |  | TRUE
40 | bus_LV_2275-18_0_4_node_65 | 0.4 | n |  | TRUE
41 | bus_LV_2275-18_0_4_node_80 | 0.4 | n |  | TRUE
42 | bus_LV_2275-18_0_4_node_134 | 0.4 | n |  | TRUE
43 | bus_LV_2275-18_0_4_node_73 | 0.4 | n |  | TRUE
44 | bus_LV_2275-18_0_4_node_63 | 0.4 | n |  | TRUE
45 | bus_LV_2275-18_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_2275-18_0_4_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2275-18_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2275-18_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2275-18_0_4_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2275-18_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2275-18_0_4_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_2275-18_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_2275-18_0_4_node_84 | 0.4 | n |  | TRUE
54 | bus_LV_2275-18_0_4_node_85 | 0.4 | n |  | TRUE
55 | bus_LV_2275-18_0_4_node_82 | 0.4 | n |  | TRUE
56 | bus_LV_2275-18_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_2275-18_0_4_node_95 | 0.4 | n |  | TRUE
58 | bus_LV_2275-18_0_4_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_2275-18_0_4_node_89 | 0.4 | n |  | TRUE
60 | bus_LV_2275-18_0_4_node_81 | 0.4 | n |  | TRUE
61 | bus_LV_2275-18_0_4_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_2275-18_0_4_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_2275-18_0_4_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_2275-18_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_2275-18_0_4_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_2275-18_0_4_node_99 | 0.4 | n |  | TRUE
67 | bus_LV_2275-18_0_4_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2275-18_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_2275-18_0_4_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_2275-18_0_4_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_2275-18_0_4_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_2275-18_0_4_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_2275-18_0_4_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_2275-18_0_4_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_2275-18_0_4_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_2275-18_0_4_node_90 | 0.4 | n |  | TRUE
77 | bus_LV_2275-18_0_4_node_91 | 0.4 | n |  | TRUE
78 | bus_LV_2275-18_0_4_node_96 | 0.4 | n |  | TRUE
79 | bus_LV_2275-18_0_4_node_97 | 0.4 | n |  | TRUE
80 | bus_LV_2275-18_0_4_node_98 | 0.4 | n |  | TRUE
81 | bus_LV_2275-18_0_4_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_2275-18_0_4_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_2275-18_0_4_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_2275-18_0_4_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_2275-18_0_4_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_2275-18_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_2275-18_0_4_node_135 | 0.4 | n |  | TRUE
88 | bus_LV_2275-18_0_4_node_127 | 0.4 | n |  | TRUE
89 | bus_LV_2275-18_0_4_node_131 | 0.4 | n |  | TRUE
90 | bus_LV_2275-18_0_4_node_129 | 0.4 | n |  | TRUE
91 | bus_LV_2275-18_0_4_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_2275-18_0_4_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_2275-18_0_4_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_2275-18_0_4_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_2275-18_0_4_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_2275-18_0_4_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_2275-18_0_4_node_125 | 0.4 | n |  | TRUE
98 | bus_LV_2275-18_0_4_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_2275-18_0_4_node_126 | 0.4 | n |  | TRUE
100 | bus_LV_2275-18_0_4_node_74 | 0.4 | n |  | TRUE
101 | bus_LV_2275-18_0_4_node_75 | 0.4 | n |  | TRUE
102 | bus_LV_2275-18_0_4_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_2275-18_0_4_node_128 | 0.4 | n |  | TRUE
104 | bus_LV_2275-18_0_4_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_2275-18_0_4_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_2275-18_0_4_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_2275-18_0_4_node_132 | 0.4 | n |  | TRUE
108 | bus_LV_2275-18_0_4_node_133 | 0.4 | n |  | TRUE
109 | bus_LV_2275-18_0_4_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_2275-18_0_4_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_2275-18_0_4_node_101 | 0.4 | n |  | TRUE
112 | bus_LV_2275-18_0_4_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_2275-18_0_4_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_2275-18_0_4_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_2275-18_0_4_node_116 | 0.4 | n |  | TRUE
116 | bus_LV_2275-18_0_4_node_108 | 0.4 | n |  | TRUE
117 | bus_LV_2275-18_0_4_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_2275-18_0_4_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2275-18_0_4_node_124 | 0.4 | n |  | TRUE
120 | bus_LV_2275-18_0_4_node_123 | 0.4 | n |  | TRUE
121 | bus_LV_2275-18_0_4_node_122 | 0.4 | n |  | TRUE
122 | bus_LV_2275-18_0_4_node_107 | 0.4 | n |  | TRUE
123 | bus_LV_2275-18_0_4_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_2275-18_0_4_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_2275-18_0_4_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_2275-18_0_4_node_118 | 0.4 | n |  | TRUE
127 | bus_LV_2275-18_0_4_node_117 | 0.4 | n |  | TRUE
128 | bus_LV_2275-18_0_4_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_2275-18_0_4_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_2275-18_0_4_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_2275-18_0_4_node_121 | 0.4 | n |  | TRUE
132 | bus_LV_2275-18_0_4_node_130 | 0.4 | n |  | TRUE
133 | bus_MV_379_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2275-18_0_4_load_0 | 0 | 0.010742 | 0.0026923 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2275-18_0_4_load_3 | 3 | 0.00055661 | 0.0001395 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2275-18_0_4_load_114 | 4 | 0.0014087 | 0.00035306 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2275-18_0_4_load_4 | 6 | 0.0067453 | 0.0016905 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2275-18_0_4_load_5 | 7 | 0.00088725 | 0.00022237 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2275-18_0_4_load_7 | 9 | 0.006121 | 0.0015341 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2275-18_0_4_load_9 | 11 | 0.012341 | 0.0030929 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2275-18_0_4_load_10 | 12 | 0.0041263 | 0.0010341 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2275-18_0_4_load_11 | 13 | 0.0046717 | 0.0011708 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2275-18_0_4_load_13 | 15 | 0.0042229 | 0.0010584 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2275-18_0_4_load_14 | 16 | 0.0014622 | 0.00036647 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2275-18_0_4_load_37 | 18 | 0.00098973 | 0.00024805 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2275-18_0_4_load_23 | 23 | 0.0022026 | 0.00055202 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2275-18_0_4_load_19 | 24 | 0.0014657 | 0.00036734 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2275-18_0_4_load_18 | 25 | 0.0020662 | 0.00051784 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2275-18_0_4_load_83 | 27 | 0.0030183 | 0.00075646 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2275-18_0_4_load_36 | 29 | 0.0057375 | 0.001438 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2275-18_0_4_load_72 | 30 | 0.002881 | 0.00072205 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2275-18_0_4_load_43 | 31 | 0.002438 | 0.00061102 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2275-18_0_4_load_45 | 32 | 0.00046338 | 0.00011613 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2275-18_0_4_load_26 | 33 | 0.0021491 | 0.00053861 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2275-18_0_4_load_27 | 34 | 0.0022918 | 0.00057437 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2275-18_0_4_load_20 | 35 | 0.0017092 | 0.00042836 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2275-18_0_4_load_21 | 36 | 0.0053799 | 0.0013483 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2275-18_0_4_load_78 | 38 | 0.0011703 | 0.00029331 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2275-18_0_4_load_80 | 41 | 0.0091494 | 0.0022931 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2275-18_0_4_load_134 | 42 | 0.0030715 | 0.0007698 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2275-18_0_4_load_73 | 43 | 0.0016661 | 0.00041756 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2275-18_0_4_load_63 | 44 | 0.0059885 | 0.0015009 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2275-18_0_4_load_28 | 45 | 0.0033951 | 0.00085088 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2275-18_0_4_load_29 | 46 | 0.0030068 | 0.00075357 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2275-18_0_4_load_30 | 47 | 0.0012653 | 0.00031712 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2275-18_0_4_load_32 | 49 | 0.001552 | 0.00038896 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2275-18_0_4_load_34 | 51 | 0.0013366 | 0.00033498 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2275-18_0_4_load_35 | 52 | 0.00082089 | 0.00020573 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2275-18_0_4_load_85 | 54 | 0.0028279 | 0.00070874 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2275-18_0_4_load_82 | 55 | 0.00098678 | 0.00024731 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2275-18_0_4_load_56 | 56 | 0.0010577 | 0.0002651 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2275-18_0_4_load_95 | 57 | 0.0024526 | 0.00061469 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2275-18_0_4_load_89 | 59 | 0.0013531 | 0.00033912 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2275-18_0_4_load_81 | 60 | 0.00064152 | 0.00016078 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2275-18_0_4_load_55 | 61 | 0.0008812 | 0.00022085 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2275-18_0_4_load_38 | 62 | 0.0011817 | 0.00029617 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2275-18_0_4_load_39 | 63 | 0.0017826 | 0.00044676 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2275-18_0_4_load_41 | 64 | 0.0012503 | 0.00031336 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2275-18_0_4_load_61 | 65 | 0.001819 | 0.00045589 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2275-18_0_4_load_99 | 66 | 0.0033817 | 0.00084754 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2275-18_0_4_load_47 | 67 | 0.0027532 | 0.00069003 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2275-18_0_4_load_54 | 69 | 0.0033261 | 0.00083359 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2275-18_0_4_load_51 | 70 | 0.0029121 | 0.00072985 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2275-18_0_4_load_46 | 71 | 0.00099574 | 0.00024956 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2275-18_0_4_load_48 | 72 | 0.00066284 | 0.00016612 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2275-18_0_4_load_49 | 73 | 0.00033204 | 8.3217e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2275-18_0_4_load_50 | 74 | 0.0020102 | 0.00050379 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2275-18_0_4_load_52 | 75 | 0.0025454 | 0.00063793 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2275-18_0_4_load_91 | 77 | 0.0024057 | 0.00060293 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2275-18_0_4_load_96 | 78 | 0.0031509 | 0.0007897 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2275-18_0_4_load_97 | 79 | 0.0018849 | 0.00047239 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2275-18_0_4_load_98 | 80 | 0.0017769 | 0.00044534 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2275-18_0_4_load_59 | 82 | 0.0025996 | 0.00065151 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2275-18_0_4_load_62 | 83 | 0.0031926 | 0.00080013 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2275-18_0_4_load_76 | 85 | 0.0024336 | 0.00060993 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2275-18_0_4_load_135 | 87 | 0.0025635 | 0.00064248 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2275-18_0_4_load_127 | 88 | 0.00083667 | 0.00020969 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2275-18_0_4_load_131 | 89 | 0.0071064 | 0.001781 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2275-18_0_4_load_129 | 90 | 0.0006067 | 0.00015205 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2275-18_0_4_load_64 | 91 | 0.0070024 | 0.001755 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2275-18_0_4_load_66 | 92 | 0.0019118 | 0.00047914 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2275-18_0_4_load_68 | 93 | 0.002164 | 0.00054236 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2275-18_0_4_load_70 | 94 | 0.0025404 | 0.00063669 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2275-18_0_4_load_88 | 96 | 0.0010214 | 0.00025599 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2275-18_0_4_load_125 | 97 | 0.0014084 | 0.00035298 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2275-18_0_4_load_87 | 98 | 0.0047492 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2275-18_0_4_load_126 | 99 | 0.002066 | 0.00051779 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2275-18_0_4_load_74 | 100 | 0.0041607 | 0.0010428 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2275-18_0_4_load_75 | 101 | 0.0027652 | 0.00069303 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2275-18_0_4_load_86 | 102 | 0.0026865 | 0.00067331 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2275-18_0_4_load_128 | 103 | 0.0044779 | 0.0011223 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2275-18_0_4_load_93 | 105 | 0.0014572 | 0.00036521 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2275-18_0_4_load_94 | 106 | 0.00086116 | 0.00021583 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2275-18_0_4_load_132 | 107 | 0.0091169 | 0.0022849 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2275-18_0_4_load_133 | 108 | 0.0021865 | 0.00054799 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2275-18_0_4_load_100 | 109 | 0.0061165 | 0.001533 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2275-18_0_4_load_106 | 110 | 0.0046837 | 0.0011738 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2275-18_0_4_load_101 | 111 | 0.0026043 | 0.00065269 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2275-18_0_4_load_105 | 112 | 0.0054167 | 0.0013575 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2275-18_0_4_load_116 | 115 | 0.002998 | 0.00075137 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2275-18_0_4_load_103 | 117 | 0.0021932 | 0.00054967 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2275-18_0_4_load_104 | 118 | 0.0026563 | 0.00066573 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2275-18_0_4_load_124 | 119 | 0.0011791 | 0.00029552 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2275-18_0_4_load_123 | 120 | 0.0018979 | 0.00047566 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2275-18_0_4_load_122 | 121 | 0.0021533 | 0.00053968 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2275-18_0_4_load_107 | 122 | 0.0014084 | 0.00035298 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2275-18_0_4_load_109 | 123 | 0.0043056 | 0.0010791 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2275-18_0_4_load_111 | 124 | 0.00066469 | 0.00016659 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2275-18_0_4_load_112 | 125 | 0.00061753 | 0.00015477 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2275-18_0_4_load_118 | 126 | 0.0010315 | 0.00025852 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2275-18_0_4_load_117 | 127 | 0.0019441 | 0.00048724 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2275-18_0_4_load_120 | 129 | 0.00087689 | 0.00021977 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2275-18_0_4_load_119 | 130 | 0.0025489 | 0.00063882 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2275-18_0_4_load_121 | 131 | 0.0018382 | 0.00046071 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2275-18_0_4_load_130 | 132 | 0.0047642 | 0.001194 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2275-18_0_4_line_0 |  | 0 | 1 | 0.066877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2275-18_0_4_line_1 |  | 1 | 2 | 0.025446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2275-18_0_4_line_2 |  | 2 | 3 | 0.04399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2275-18_0_4_line_3 |  | 3 | 4 | 0.0092627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2275-18_0_4_line_4 |  | 4 | 5 | 0.041509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2275-18_0_4_line_5 |  | 5 | 128 | 0.005217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2275-18_0_4_line_6 |  | 5 | 125 | 0.051095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2275-18_0_4_line_7 |  | 6 | 7 | 0.0043244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2275-18_0_4_line_8 |  | 6 | 8 | 0.046271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2275-18_0_4_line_9 |  | 7 | 9 | 0.084107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2275-18_0_4_line_10 |  | 8 | 10 | 0.008321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2275-18_0_4_line_11 |  | 8 | 11 | 0.044688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2275-18_0_4_line_12 |  | 8 | 12 | 0.015354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2275-18_0_4_line_13 |  | 9 | 13 | 0.0081782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2275-18_0_4_line_14 |  | 10 | 14 | 0.034729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2275-18_0_4_line_15 |  | 10 | 15 | 0.0027256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2275-18_0_4_line_16 |  | 11 | 16 | 0.045615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2275-18_0_4_line_17 |  | 13 | 17 | 0.050245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2275-18_0_4_line_18 |  | 14 | 18 | 0.028283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2275-18_0_4_line_19 |  | 15 | 19 | 0.041291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2275-18_0_4_line_20 |  | 16 | 20 | 0.059033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2275-18_0_4_line_21 |  | 17 | 25 | 0.048585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2275-18_0_4_line_22 |  | 18 | 29 | 0.030788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2275-18_0_4_line_23 |  | 19 | 30 | 0.018381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2275-18_0_4_line_24 |  | 19 | 22 | 0.030898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2275-18_0_4_line_25 |  | 20 | 31 | 0.01975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2275-18_0_4_line_26 |  | 20 | 28 | 0.005095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2275-18_0_4_line_27 |  | 20 | 32 | 0.089797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2275-18_0_4_line_28 |  | 21 | 22 | 0.004312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2275-18_0_4_line_29 |  | 21 | 23 | 0.011741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2275-18_0_4_line_30 |  | 21 | 24 | 0.048985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2275-18_0_4_line_31 |  | 22 | 33 | 0.013908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2275-18_0_4_line_32 |  | 23 | 34 | 0.031828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2275-18_0_4_line_33 |  | 24 | 35 | 0.00084603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2275-18_0_4_line_34 |  | 26 | 27 | 0.026883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2275-18_0_4_line_35 |  | 26 | 28 | 0.019833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2275-18_0_4_line_36 |  | 27 | 66 | 0.031062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2275-18_0_4_line_37 |  | 28 | 67 | 0.013778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2275-18_0_4_line_38 |  | 29 | 62 | 0.003746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2275-18_0_4_line_39 |  | 30 | 43 | 0.0021466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2275-18_0_4_line_40 |  | 31 | 69 | 0.016865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2275-18_0_4_line_41 |  | 32 | 70 | 0.011857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2275-18_0_4_line_42 |  | 33 | 40 | 0.022969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2275-18_0_4_line_43 |  | 35 | 36 | 0.084731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2275-18_0_4_line_44 |  | 36 | 37 | 0.068266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2275-18_0_4_line_45 |  | 37 | 38 | 0.020919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2275-18_0_4_line_46 |  | 37 | 39 | 0.24941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2275-18_0_4_line_47 |  | 39 | 41 | 0.05494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2275-18_0_4_line_48 |  | 40 | 44 | 0.022957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2275-18_0_4_line_49 |  | 41 | 42 | 0.42196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2275-18_0_4_line_50 |  | 42 | 108 | 0.030094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2275-18_0_4_line_51 |  | 43 | 100 | 0.02142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2275-18_0_4_line_52 |  | 45 | 46 | 0.057656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2275-18_0_4_line_53 |  | 45 | 47 | 0.006149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2275-18_0_4_line_54 |  | 46 | 48 | 0.011583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2275-18_0_4_line_55 |  | 47 | 49 | 0.036404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2275-18_0_4_line_56 |  | 48 | 50 | 0.004942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2275-18_0_4_line_57 |  | 48 | 51 | 0.099241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2275-18_0_4_line_58 |  | 49 | 52 | 0.0027397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2275-18_0_4_line_59 |  | 50 | 53 | 0.010221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2275-18_0_4_line_60 |  | 50 | 54 | 0.031111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2275-18_0_4_line_61 |  | 51 | 55 | 0.021658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2275-18_0_4_line_62 |  | 52 | 56 | 0.040325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2275-18_0_4_line_63 |  | 53 | 57 | 0.011625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2275-18_0_4_line_64 |  | 53 | 58 | 0.005717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2275-18_0_4_line_65 |  | 54 | 59 | 0.0023361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2275-18_0_4_line_66 |  | 55 | 60 | 0.015451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2275-18_0_4_line_67 |  | 56 | 61 | 0.018795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2275-18_0_4_line_68 |  | 57 | 110 | 0.036927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2275-18_0_4_line_69 |  | 58 | 76 | 0.048378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2275-18_0_4_line_70 |  | 58 | 77 | 0.015749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2275-18_0_4_line_71 |  | 58 | 75 | 0.057734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2275-18_0_4_line_72 |  | 60 | 74 | 0.045654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2275-18_0_4_line_73 |  | 62 | 63 | 0.023573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2275-18_0_4_line_74 |  | 63 | 64 | 0.027376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2275-18_0_4_line_75 |  | 64 | 65 | 0.021864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2275-18_0_4_line_76 |  | 65 | 68 | 0.063791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2275-18_0_4_line_77 |  | 66 | 109 | 0.012812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2275-18_0_4_line_78 |  | 67 | 71 | 0.026023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2275-18_0_4_line_79 |  | 68 | 81 | 0.036789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2275-18_0_4_line_80 |  | 71 | 72 | 0.012904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_2275-18_0_4_line_81 |  | 72 | 73 | 0.005875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2275-18_0_4_line_82 |  | 73 | 74 | 0.014031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2275-18_0_4_line_83 |  | 76 | 78 | 0.014461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2275-18_0_4_line_84 |  | 76 | 79 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2275-18_0_4_line_85 |  | 77 | 80 | 0.026252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2275-18_0_4_line_86 |  | 79 | 111 | 0.019002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2275-18_0_4_line_87 |  | 81 | 82 | 0.047185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2275-18_0_4_line_88 |  | 82 | 83 | 0.023311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2275-18_0_4_line_89 |  | 83 | 87 | 0.0086051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2275-18_0_4_line_90 |  | 84 | 85 | 0.024204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2275-18_0_4_line_91 |  | 84 | 86 | 0.068877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2275-18_0_4_line_92 |  | 85 | 88 | 0.040189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2275-18_0_4_line_93 |  | 86 | 89 | 0.085687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2275-18_0_4_line_94 |  | 86 | 90 | 0.025357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2275-18_0_4_line_95 |  | 88 | 99 | 0.02322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2275-18_0_4_line_96 |  | 90 | 103 | 0.019686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2275-18_0_4_line_97 |  | 91 | 92 | 0.0037423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2275-18_0_4_line_98 |  | 92 | 93 | 0.024151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2275-18_0_4_line_99 |  | 93 | 94 | 0.025541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2275-18_0_4_line_100 |  | 94 | 95 | 0.015359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2275-18_0_4_line_101 |  | 95 | 96 | 0.010942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2275-18_0_4_line_102 |  | 95 | 97 | 0.0040374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2275-18_0_4_line_103 |  | 96 | 98 | 0.015889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2275-18_0_4_line_104 |  | 97 | 99 | 0.0064697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2275-18_0_4_line_105 |  | 98 | 102 | 0.0031718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2275-18_0_4_line_106 |  | 100 | 101 | 0.011076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2275-18_0_4_line_107 |  | 101 | 102 | 0.020615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2275-18_0_4_line_108 |  | 103 | 132 | 0.023652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2275-18_0_4_line_109 |  | 104 | 105 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2275-18_0_4_line_110 |  | 104 | 106 | 0.0099072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2275-18_0_4_line_111 |  | 106 | 107 | 0.0024016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2275-18_0_4_line_112 |  | 107 | 108 | 0.023062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2275-18_0_4_line_113 |  | 110 | 112 | 0.025847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2275-18_0_4_line_114 |  | 111 | 113 | 0.015717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2275-18_0_4_line_115 |  | 113 | 117 | 0.015932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2275-18_0_4_line_116 |  | 113 | 118 | 0.0072472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2275-18_0_4_line_117 |  | 114 | 115 | 0.03028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2275-18_0_4_line_118 |  | 114 | 116 | 0.006226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2275-18_0_4_line_119 |  | 115 | 126 | 0.007019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2275-18_0_4_line_120 |  | 116 | 123 | 0.022253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2275-18_0_4_line_121 |  | 116 | 122 | 0.0043471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2275-18_0_4_line_122 |  | 117 | 119 | 0.020731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2275-18_0_4_line_123 |  | 118 | 120 | 0.011663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2275-18_0_4_line_124 |  | 120 | 121 | 0.014869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2275-18_0_4_line_125 |  | 121 | 131 | 0.025385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2275-18_0_4_line_126 |  | 123 | 124 | 0.021686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2275-18_0_4_line_127 |  | 124 | 125 | 0.0015824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2275-18_0_4_line_128 |  | 126 | 131 | 0.019766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2275-18_0_4_line_129 |  | 127 | 128 | 0.022273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2275-18_0_4_line_130 |  | 128 | 129 | 0.037622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2275-18_0_4_line_131 |  | 129 | 130 | 0.018635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2275-18_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 133 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2577824.1555 | 1196467.0821 | 2577840.2993 | 1196467.8446 | 2577873.8717 | 1196429.8327
1 | 2577806.9956 | 1196485.9117 | 2577822.5931 | 1196468.8889 | 2577824.1555 | 1196467.0821
2 | 2577806.9956 | 1196485.9117 | 2577769.8427 | 1196462.3574
3 | 2577769.8427 | 1196462.3574 | 2577762.0197 | 1196457.3978
4 | 2577726.9624 | 1196435.172 | 2577762.0197 | 1196457.3978
5 | 2577722.4432 | 1196432.5431 | 2577726.9624 | 1196435.172
6 | 2577726.9624 | 1196435.172 | 2577728.0817 | 1196433.0222 | 2577750.567 | 1196389.8562
7 | 2577874.7081 | 1195820.3665 | 2577870.5575 | 1195819.1528
8 | 2577918.5574 | 1195835.0472 | 2577895.214 | 1195826.3624 | 2577874.7081 | 1195820.3665
9 | 2577870.5575 | 1195819.1528 | 2577856.3198 | 1195814.9897 | 2577819.7075 | 1195812.947 | 2577787.8774 | 1195820.0063
10 | 2577918.5574 | 1195835.0472 | 2577926.3766 | 1195837.9531
11 | 2577918.5574 | 1195835.0472 | 2577916.5254 | 1195839.6905 | 2577916.9062 | 1195845.848 | 2577910.4134 | 1195857.5339 | 2577900.3082 | 1195874.888
12 | 2577918.5574 | 1195835.0472 | 2577928.0836 | 1195825.7847 | 2577929.2854 | 1195824.1024
13 | 2577787.8774 | 1195820.0063 | 2577779.8932 | 1195821.777
14 | 2577926.3766 | 1195837.9531 | 2577913.8355 | 1195860.0226 | 2577908.9668 | 1195868.0227
15 | 2577926.3766 | 1195837.9531 | 2577927.9141 | 1195835.7025
16 | 2577878.9494 | 1195915.1369 | 2577879.1629 | 1195914.5472 | 2577887.182 | 1195897.4304 | 2577900.3082 | 1195874.888
17 | 2577730.8405 | 1195832.6559 | 2577779.8932 | 1195821.777
18 | 2577908.9668 | 1195868.0227 | 2577930.3085 | 1195886.5816
19 | 2577951.2062 | 1195801.6083 | 2577927.9141 | 1195835.7025
20 | 2577865.9251 | 1195972.4941 | 2577867.06 | 1195962.1955 | 2577873.025 | 1195931.5013 | 2577878.9494 | 1195915.1369
21 | 2577730.8405 | 1195832.6559 | 2577687.4992 | 1195840.1443 | 2577682.9113 | 1195839.7861
22 | 2577953.5406 | 1195906.7844 | 2577930.3085 | 1195886.5816
23 | 2577951.2062 | 1195801.6083 | 2577966.4987 | 1195811.8071
24 | 2577971.7809 | 1195778.5086 | 2577951.2062 | 1195801.6083
25 | 2577865.9251 | 1195972.4941 | 2577861.9991 | 1195971.7194 | 2577854.2372 | 1195969.8695 | 2577846.9746 | 1195967.1106
26 | 2577865.9251 | 1195972.4941 | 2577870.986 | 1195973.1979
27 | 2577865.9251 | 1195972.4941 | 2577865.7263 | 1195974.3292 | 2577864.3958 | 1196018.0576 | 2577863.7283 | 1196062.2553
28 | 2577971.7809 | 1195778.5086 | 2577968.3659 | 1195775.8643
29 | 2577968.3659 | 1195775.8643 | 2577976.7918 | 1195767.6879
30 | 2577968.3659 | 1195775.8643 | 2577929.6304 | 1195745.8797
31 | 2577971.7809 | 1195778.5086 | 2577980.9537 | 1195768.0548
32 | 2577976.7918 | 1195767.6879 | 2577979.866 | 1195764.7047 | 2577999.4001 | 1195745.2847
33 | 2577928.9614 | 1195745.3618 | 2577929.6304 | 1195745.8797
34 | 2577873.5868 | 1195953.5444 | 2577893.0602 | 1195958.219 | 2577899.7619 | 1195959.6666
35 | 2577873.5868 | 1195953.5444 | 2577872.2767 | 1195961.7759 | 2577870.986 | 1195973.1979
36 | 2577930.1233 | 1195966.2248 | 2577899.7619 | 1195959.6666
37 | 2577870.986 | 1195973.1979 | 2577870.2585 | 1195986.9567
38 | 2577953.5406 | 1195906.7844 | 2577956.3673 | 1195909.2425
39 | 2577966.4987 | 1195811.8071 | 2577968.2846 | 1195812.9982
40 | 2577846.9746 | 1195967.1106 | 2577842.5578 | 1195965.4328 | 2577831.5793 | 1195960.2494
41 | 2577863.329 | 1196074.104 | 2577863.6561 | 1196067.0311 | 2577863.7283 | 1196062.2553
42 | 2577996.9659 | 1195751.6011 | 2577984.6697 | 1195763.8198 | 2577980.9537 | 1195768.0548
43 | 2577928.9614 | 1195745.3618 | 2577915.8101 | 1195735.1815 | 2577903.8791 | 1195726.699 | 2577885.1645 | 1195700.9102 | 2577872.7026 | 1195683.2716
44 | 2577821.018 | 1195639.1822 | 2577840.4396 | 1195654.2402 | 2577867.3739 | 1195675.7294 | 2577872.7026 | 1195683.2716
45 | 2577821.018 | 1195639.1822 | 2577812.1807 | 1195658.1423
46 | 2577821.018 | 1195639.1822 | 2577647.9044 | 1195459.6329
47 | 2577647.9044 | 1195459.6329 | 2577609.8914 | 1195419.9671
48 | 2577996.9659 | 1195751.6011 | 2578013.3902 | 1195767.6403
49 | 2577609.8914 | 1195419.9671 | 2577189.7971 | 1195380.2975
50 | 2577189.7971 | 1195380.2975 | 2577169.3292 | 1195358.2353
51 | 2577984.8992 | 1195826.51 | 2577969.0766 | 1195813.5263 | 2577968.2846 | 1195812.9982
52 | 2577893.1928 | 1196174.7534 | 2577870.6432 | 1196198.6204 | 2577855.7181 | 1196218.4532
53 | 2577897.4157 | 1196170.2837 | 2577893.1928 | 1196174.7534
54 | 2577846.5271 | 1196225.5022 | 2577855.7181 | 1196218.4532 | 2577855.7181 | 1196218.4532
55 | 2577897.4157 | 1196170.2837 | 2577922.4165 | 1196143.8222
56 | 2577845.0592 | 1196230.2213 | 2577846.5271 | 1196225.5022
57 | 2577846.5271 | 1196225.5022 | 2577849.7095 | 1196214.818 | 2577857.8426 | 1196187.5398 | 2577863.889 | 1196150.1305 | 2577865.1235 | 1196128.4319
58 | 2577924.298 | 1196141.8308 | 2577922.4165 | 1196143.8222
59 | 2577845.0592 | 1196230.2213 | 2577841.446 | 1196239.7844
60 | 2577845.0592 | 1196230.2213 | 2577871.1773 | 1196247.1255
61 | 2577865.1235 | 1196128.4319 | 2577866.3538 | 1196106.8086
62 | 2577951.9914 | 1196112.5194 | 2577924.298 | 1196141.8308
63 | 2577841.446 | 1196239.7844 | 2577835.9706 | 1196250.0394
64 | 2577836.3478 | 1196237.1686 | 2577841.446 | 1196239.7844
65 | 2577873.1385 | 1196248.3949 | 2577871.1773 | 1196247.1255
66 | 2577867.2315 | 1196091.3823 | 2577866.3538 | 1196106.8086
67 | 2577964.899 | 1196098.8575 | 2577951.9914 | 1196112.5194
68 | 2577818.5782 | 1196282.6136 | 2577835.9706 | 1196250.0394
69 | 2577836.3478 | 1196237.1686 | 2577794.066 | 1196213.4467
70 | 2577836.3478 | 1196237.1686 | 2577829.6675 | 1196251.4304
71 | 2577836.3478 | 1196237.1686 | 2577844.0415 | 1196214.6612 | 2577851.8162 | 1196187.2954 | 2577852.6496 | 1196181.8595
72 | 2577867.2315 | 1196091.3823 | 2577868.5224 | 1196068.6917 | 2577868.8868 | 1196045.7681
73 | 2577956.3673 | 1195909.2425 | 2577974.1551 | 1195924.7108
74 | 2577994.813 | 1195942.6751 | 2577974.1551 | 1195924.7108
75 | 2577994.813 | 1195942.6751 | 2578011.3112 | 1195957.0221
76 | 2578059.447 | 1195998.8812 | 2578011.3112 | 1195957.0221
77 | 2577942.6464 | 1195968.9298 | 2577930.1233 | 1195966.2248
78 | 2577870.2585 | 1195986.9567 | 2577869.6337 | 1195998.7723 | 2577869.4082 | 1196012.9619
79 | 2578034.1021 | 1196025.6112 | 2578059.447 | 1195998.8812
80 | 2577869.2031 | 1196025.8647 | 2577869.4082 | 1196012.9619
81 | 2577869.1097 | 1196031.7389 | 2577869.2031 | 1196025.8647
82 | 2577869.1097 | 1196031.7389 | 2577868.8868 | 1196045.7681
83 | 2577794.066 | 1196213.4467 | 2577781.6851 | 1196205.9738
84 | 2577794.066 | 1196213.4467 | 2577785.5224 | 1196229.6048
85 | 2577817.8581 | 1196274.8586 | 2577823.145 | 1196265.3551 | 2577829.6675 | 1196251.4304
86 | 2577785.5224 | 1196229.6048 | 2577776.64 | 1196246.4035
87 | 2578034.1021 | 1196025.6112 | 2578026.8594 | 1196021.9693 | 2578011.2347 | 1196021.7935 | 2577988.1778 | 1196017.5021
88 | 2577988.1778 | 1196017.5021 | 2577965.2602 | 1196013.2366
89 | 2577967.4843 | 1196004.9239 | 2577965.2602 | 1196013.2366
90 | 2578112.28 | 1195919.0439 | 2578090.9796 | 1195907.5486
91 | 2578151.1211 | 1195862.3042 | 2578144.1768 | 1195869.4335 | 2578112.28 | 1195919.0439
92 | 2578055.6125 | 1195888.4617 | 2578090.9796 | 1195907.5486
93 | 2578151.1211 | 1195862.3042 | 2578215.6914 | 1195918.6334
94 | 2578151.1211 | 1195862.3042 | 2578132.6422 | 1195844.9402
95 | 2578035.2414 | 1195877.3233 | 2578037.8267 | 1195878.8631 | 2578055.6125 | 1195888.4617
96 | 2578122.9089 | 1195827.8535 | 2578132.3007 | 1195844.6193 | 2578132.6422 | 1195844.9402
97 | 2578035.5435 | 1195807.5689 | 2578035.8752 | 1195803.8413
98 | 2578035.5435 | 1195807.5689 | 2578035.5229 | 1195807.8001 | 2578032.0879 | 1195831.4709
99 | 2578032.0879 | 1195831.4709 | 2578028.42 | 1195856.7467
100 | 2578026.2142 | 1195871.9466 | 2578028.42 | 1195856.7467
101 | 2578026.2142 | 1195871.9466 | 2578021.7534 | 1195868.7169 | 2578017.7708 | 1195865.0185
102 | 2578026.2142 | 1195871.9466 | 2578029.683 | 1195874.0126
103 | 2578017.7708 | 1195865.0185 | 2578017.7708 | 1195865.0185 | 2578012.8077 | 1195859.8674 | 2578007.2218 | 1195853.1511
104 | 2578035.2414 | 1195877.3233 | 2578029.683 | 1195874.0126
105 | 2578005.3786 | 1195850.5698 | 2578007.2218 | 1195853.1511 | 2578007.2218 | 1195853.1511
106 | 2577992.8182 | 1195834.2443 | 2577986.1242 | 1195827.5153 | 2577984.8992 | 1195826.51
107 | 2577992.8182 | 1195834.2443 | 2577992.9448 | 1195834.3715 | 2577998.8137 | 1195841.3758 | 2578005.3786 | 1195850.5698
108 | 2578117.3683 | 1195804.9417 | 2578117.3683 | 1195804.9417 | 2578121.9408 | 1195826.1252 | 2578122.9089 | 1195827.8535
109 | 2577145.2728 | 1195332.305 | 2577134.7384 | 1195322.5488
110 | 2577145.2728 | 1195332.305 | 2577152.0109 | 1195339.568
111 | 2577153.6443 | 1195341.3286 | 2577152.0109 | 1195339.568
112 | 2577153.6443 | 1195341.3286 | 2577169.3292 | 1195358.2353
113 | 2577804.5082 | 1196304.2751 | 2577816.7397 | 1196286.0568 | 2577818.5782 | 1196282.6136
114 | 2577769.2935 | 1196260.2976 | 2577776.64 | 1196246.4035
115 | 2577769.2935 | 1196260.2976 | 2577783.3861 | 1196267.73
116 | 2577769.2935 | 1196260.2976 | 2577765.9587 | 1196266.7319
117 | 2577766.2393 | 1196348.0896 | 2577743.2067 | 1196342.6171 | 2577737.4284 | 1196339.4147
118 | 2577766.2393 | 1196348.0896 | 2577772.233 | 1196349.8348
119 | 2577737.9948 | 1196332.5484 | 2577737.1527 | 1196334.9356 | 2577737.4284 | 1196339.4147
120 | 2577772.233 | 1196349.8348 | 2577764.4674 | 1196363.1709 | 2577761.3165 | 1196369.2199
121 | 2577772.233 | 1196349.8348 | 2577774.7794 | 1196346.3116
122 | 2577797.8822 | 1196280.802 | 2577790.6359 | 1196276.1598 | 2577789.1991 | 1196270.7957 | 2577783.3861 | 1196267.73
123 | 2577765.9587 | 1196266.7319 | 2577760.5921 | 1196277.0865
124 | 2577753.7502 | 1196290.2875 | 2577760.5921 | 1196277.0865
125 | 2577753.7502 | 1196290.2875 | 2577751.0971 | 1196295.4067 | 2577744.5703 | 1196313.9083
126 | 2577751.2981 | 1196388.4528 | 2577761.3165 | 1196369.2199
127 | 2577751.2981 | 1196388.4528 | 2577750.567 | 1196389.8562
128 | 2577737.9948 | 1196332.5484 | 2577744.5703 | 1196313.9083
129 | 2577722.4432 | 1196432.5431 | 2577732.7653 | 1196412.8069
130 | 2577722.4432 | 1196432.5431 | 2577690.1434 | 1196413.2521
131 | 2577674.0012 | 1196403.9422 | 2577685.5769 | 1196410.5248 | 2577690.1434 | 1196413.2521

## bus_geodata
| x | y | coords
0 | 2577873.8717 | 1196429.8327
1 | 2577824.1555 | 1196467.0821
2 | 2577806.9956 | 1196485.9117
3 | 2577769.8427 | 1196462.3574
4 | 2577762.0198 | 1196457.3978
5 | 2577726.9624 | 1196435.172
6 | 2577874.7081 | 1195820.3665
7 | 2577870.5575 | 1195819.1528
8 | 2577918.5574 | 1195835.0472
9 | 2577787.8774 | 1195820.0063
10 | 2577926.3766 | 1195837.9531
11 | 2577900.3082 | 1195874.888
12 | 2577929.2854 | 1195824.1024
13 | 2577779.8932 | 1195821.777
14 | 2577908.9668 | 1195868.0227
15 | 2577927.9141 | 1195835.7025
16 | 2577878.9494 | 1195915.1369
17 | 2577730.8405 | 1195832.6559
18 | 2577930.3085 | 1195886.5816
19 | 2577951.2062 | 1195801.6083
20 | 2577865.9251 | 1195972.4941
21 | 2577968.3659 | 1195775.8643
22 | 2577971.7809 | 1195778.5086
23 | 2577976.7918 | 1195767.6879
24 | 2577929.6304 | 1195745.8797
25 | 2577682.9113 | 1195839.7861
26 | 2577873.5868 | 1195953.5444
27 | 2577899.7619 | 1195959.6666
28 | 2577870.986 | 1195973.1979
29 | 2577953.5406 | 1195906.7844
30 | 2577966.4987 | 1195811.8071
31 | 2577846.9746 | 1195967.1106
32 | 2577863.7283 | 1196062.2553
33 | 2577980.9537 | 1195768.0548
34 | 2577999.4001 | 1195745.2847
35 | 2577928.9614 | 1195745.3618
36 | 2577872.7026 | 1195683.2716
37 | 2577821.018 | 1195639.1822
38 | 2577812.1807 | 1195658.1423
39 | 2577647.9044 | 1195459.6329
40 | 2577996.9659 | 1195751.6011
41 | 2577609.8914 | 1195419.9671
42 | 2577189.7971 | 1195380.2975
43 | 2577968.2846 | 1195812.9982
44 | 2578013.3902 | 1195767.6403
45 | 2577893.1928 | 1196174.7534
46 | 2577855.7181 | 1196218.4532
47 | 2577897.4157 | 1196170.2837
48 | 2577846.5271 | 1196225.5022
49 | 2577922.4165 | 1196143.8222
50 | 2577845.0592 | 1196230.2213
51 | 2577865.1235 | 1196128.4319
52 | 2577924.298 | 1196141.8308
53 | 2577841.446 | 1196239.7844
54 | 2577871.1773 | 1196247.1255
55 | 2577866.3538 | 1196106.8086
56 | 2577951.9914 | 1196112.5194
57 | 2577835.9706 | 1196250.0394
58 | 2577836.3478 | 1196237.1686
59 | 2577873.1385 | 1196248.3949
60 | 2577867.2315 | 1196091.3823
61 | 2577964.899 | 1196098.8575
62 | 2577956.3673 | 1195909.2425
63 | 2577974.1551 | 1195924.7108
64 | 2577994.813 | 1195942.6751
65 | 2578011.3112 | 1195957.0221
66 | 2577930.1233 | 1195966.2248
67 | 2577870.2585 | 1195986.9567
68 | 2578059.447 | 1195998.8812
69 | 2577831.5793 | 1195960.2494
70 | 2577863.329 | 1196074.104
71 | 2577869.4082 | 1196012.9619
72 | 2577869.2031 | 1196025.8647
73 | 2577869.1097 | 1196031.7389
74 | 2577868.8868 | 1196045.7681
75 | 2577852.6496 | 1196181.8595
76 | 2577794.066 | 1196213.4467
77 | 2577829.6675 | 1196251.4304
78 | 2577781.6851 | 1196205.9738
79 | 2577785.5224 | 1196229.6048
80 | 2577817.8581 | 1196274.8586
81 | 2578034.1021 | 1196025.6112
82 | 2577988.1778 | 1196017.5021
83 | 2577965.2602 | 1196013.2366
84 | 2578112.28 | 1195919.0439
85 | 2578090.9796 | 1195907.5486
86 | 2578151.1211 | 1195862.3042
87 | 2577967.4843 | 1196004.9239
88 | 2578055.6125 | 1195888.4617
89 | 2578215.6914 | 1195918.6334
90 | 2578132.6422 | 1195844.9402
91 | 2578035.8752 | 1195803.8413
92 | 2578035.5435 | 1195807.5689
93 | 2578032.0879 | 1195831.4709
94 | 2578028.42 | 1195856.7467
95 | 2578026.2142 | 1195871.9466
96 | 2578017.7708 | 1195865.0185
97 | 2578029.683 | 1195874.0126
98 | 2578007.2218 | 1195853.1511
99 | 2578035.2414 | 1195877.3233
100 | 2577984.8992 | 1195826.51
101 | 2577992.8182 | 1195834.2443
102 | 2578005.3786 | 1195850.5698
103 | 2578122.9089 | 1195827.8535
104 | 2577145.2728 | 1195332.305
105 | 2577134.7384 | 1195322.5488
106 | 2577152.0109 | 1195339.568
107 | 2577153.6443 | 1195341.3286
108 | 2577169.3292 | 1195358.2353
109 | 2577942.6464 | 1195968.9298
110 | 2577818.5782 | 1196282.6136
111 | 2577776.64 | 1196246.4035
112 | 2577804.5082 | 1196304.2751
113 | 2577769.2935 | 1196260.2976
114 | 2577766.2393 | 1196348.0896
115 | 2577737.4284 | 1196339.4147
116 | 2577772.233 | 1196349.8348
117 | 2577783.3861 | 1196267.73
118 | 2577765.9587 | 1196266.7319
119 | 2577797.8822 | 1196280.802
120 | 2577760.5921 | 1196277.0865
121 | 2577753.7502 | 1196290.2875
122 | 2577774.7794 | 1196346.3116
123 | 2577761.3165 | 1196369.2199
124 | 2577751.2981 | 1196388.4528
125 | 2577750.567 | 1196389.8562
126 | 2577737.9948 | 1196332.5484
127 | 2577732.7653 | 1196412.8069
128 | 2577722.4432 | 1196432.5431
129 | 2577690.1434 | 1196413.2521
130 | 2577674.0012 | 1196403.9422
131 | 2577744.5703 | 1196313.9083
132 | 2578117.3683 | 1195804.9417
133 | 2577865.9251 | 1195972.4941

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97082 | -0.56407 | 0.010742 | 0.0026923
1 | 0.97149 | -0.55079 | 0 | 0
2 | 0.97174 | -0.54574 | 0 | 0
3 | 0.97218 | -0.53702 | 0.00055661 | 0.0001395
4 | 0.97228 | -0.53509 | 0.0014087 | 0.00035306
5 | 0.97278 | -0.52536 | 0 | 0
6 | 0.98989 | -0.19344 | 0.0067453 | 0.0016905
7 | 0.98983 | -0.19449 | 0.00088725 | 0.00022237
8 | 0.99076 | -0.17658 | 0 | 0
9 | 0.98884 | -0.21376 | 0.006121 | 0.0015341
10 | 0.99042 | -0.18303 | 0 | 0
11 | 0.99289 | -0.13554 | 0.012341 | 0.0030929
12 | 0.9907 | -0.1777 | 0.0041263 | 0.0010341
13 | 0.98879 | -0.21474 | 0.0046717 | 0.0011708
14 | 0.98975 | -0.19607 | 0 | 0
15 | 0.99033 | -0.1848 | 0.0042229 | 0.0010584
16 | 0.99524 | -0.090524 | 0.0014622 | 0.00036647
17 | 0.98869 | -0.2166 | 0 | 0
18 | 0.9892 | -0.20671 | 0.00098973 | 0.00024805
19 | 0.98899 | -0.21064 | 0 | 0
20 | 0.99831 | -0.032078 | 0 | 0
21 | 0.98848 | -0.22053 | 0 | 0
22 | 0.98853 | -0.2195 | 0 | 0
23 | 0.98843 | -0.22147 | 0.0022026 | 0.00055202
24 | 0.98794 | -0.23091 | 0.0014657 | 0.00036734
25 | 0.9886 | -0.21839 | 0.0020662 | 0.00051784
26 | 0.99791 | -0.039583 | 0 | 0
27 | 0.99761 | -0.045475 | 0.0030183 | 0.00075646
28 | 0.99814 | -0.035238 | 0 | 0
29 | 0.98863 | -0.21776 | 0.0057375 | 0.001438
30 | 0.98802 | -0.22942 | 0.002881 | 0.00072205
31 | 1 | 0 | -0.28804 | -0.073322
32 | 0.99803 | -0.037383 | 0.00046338 | 0.00011613
33 | 0.98843 | -0.22152 | 0.0021491 | 0.00053861
34 | 0.98836 | -0.22277 | 0.0022918 | 0.00057437
35 | 0.98793 | -0.23108 | 0.0017092 | 0.00042836
36 | 0.98708 | -0.24745 | 0.0053799 | 0.0013483
37 | 0.98622 | -0.26398 | 0 | 0
38 | 0.9862 | -0.26442 | 0.0011703 | 0.00029331
39 | 0.98022 | -0.38029 | 0 | 0
40 | 0.9883 | -0.22398 | 0 | 0
41 | 0.9789 | -0.40609 | 0.0091494 | 0.0022931
42 | 0.97232 | -0.53515 | 0.0030715 | 0.0007698
43 | 0.98791 | -0.2315 | 0.0016661 | 0.00041756
44 | 0.98817 | -0.22643 | 0.0059885 | 0.0015009
45 | 0.98295 | -0.32628 | 0.0033951 | 0.00085088
46 | 0.98343 | -0.31695 | 0.0030068 | 0.00075357
47 | 0.98292 | -0.3269 | 0.0012653 | 0.00031712
48 | 0.98355 | -0.31445 | 0 | 0
49 | 0.98277 | -0.32973 | 0.001552 | 0.00038896
50 | 0.98322 | -0.32087 | 0 | 0
51 | 0.9913 | -0.16518 | 0.0013366 | 0.00033498
52 | 0.98276 | -0.32987 | 0.00082089 | 0.00020573
53 | 0.98258 | -0.33341 | 0 | 0
54 | 0.9831 | -0.32322 | 0.0028279 | 0.00070874
55 | 0.99301 | -0.1324 | 0.00098678 | 0.00024731
56 | 0.98269 | -0.33128 | 0.0010577 | 0.0002651
57 | 0.98244 | -0.33604 | 0.0024526 | 0.00061469
58 | 0.98228 | -0.33913 | 0 | 0
59 | 0.9831 | -0.32328 | 0.0013531 | 0.00033912
60 | 0.99425 | -0.10882 | 0.00064152 | 0.00016078
61 | 0.98268 | -0.33158 | 0.0008812 | 0.00022085
62 | 0.98858 | -0.21872 | 0.0011817 | 0.00029617
63 | 0.98829 | -0.22428 | 0.0017826 | 0.00044676
64 | 0.98801 | -0.22986 | 0.0012503 | 0.00031336
65 | 0.9878 | -0.23384 | 0.001819 | 0.00045589
66 | 0.99734 | -0.050644 | 0.0033817 | 0.00084754
67 | 0.99774 | -0.042783 | 0.0027532 | 0.00069003
68 | 0.98731 | -0.24337 | 0 | 0
69 | 0.99995 | -0.00097784 | 0.0033261 | 0.00083359
70 | 0.998 | -0.037987 | 0.0029121 | 0.00072985
71 | 0.99701 | -0.056632 | 0.00099574 | 0.00024956
72 | 0.99665 | -0.063431 | 0.00066284 | 0.00016612
73 | 0.99648 | -0.066505 | 0.00033204 | 8.3217e-05
74 | 0.9961 | -0.073824 | 0.0020102 | 0.00050379
75 | 0.98215 | -0.34178 | 0.0025454 | 0.00063793
76 | 0.98009 | -0.38177 | 0 | 0
77 | 0.98222 | -0.34032 | 0.0024057 | 0.00060293
78 | 0.98005 | -0.38259 | 0.0031509 | 0.0007897
79 | 0.97932 | -0.39688 | 0.0018849 | 0.00047239
80 | 0.98218 | -0.34116 | 0.0017769 | 0.00044534
81 | 0.98703 | -0.24887 | 0 | 0
82 | 0.98667 | -0.25593 | 0.0025996 | 0.00065151
83 | 0.98655 | -0.25833 | 0.0031926 | 0.00080013
84 | 0.98268 | -0.33322 | 0 | 0
85 | 0.98306 | -0.32581 | 0.0024336 | 0.00060993
86 | 0.9816 | -0.35433 | 0 | 0
87 | 0.98653 | -0.25873 | 0.0025635 | 0.00064248
88 | 0.98378 | -0.31176 | 0.00083667 | 0.00020969
89 | 0.98104 | -0.36535 | 0.0071064 | 0.001781
90 | 0.98137 | -0.35885 | 0.0006067 | 0.00015205
91 | 0.98376 | -0.31219 | 0.0070024 | 0.001755
92 | 0.98379 | -0.31172 | 0.0019118 | 0.00047914
93 | 0.98399 | -0.30784 | 0.002164 | 0.00054236
94 | 0.98425 | -0.30275 | 0.0025404 | 0.00063669
95 | 0.98444 | -0.29899 | 0 | 0
96 | 0.98482 | -0.29164 | 0.0010214 | 0.00025599
97 | 0.98435 | -0.30071 | 0.0014084 | 0.00035298
98 | 0.98538 | -0.2807 | 0.0047492 | 0.0011903
99 | 0.98422 | -0.3033 | 0.002066 | 0.00051779
100 | 0.98687 | -0.25169 | 0.0041607 | 0.0010428
101 | 0.98637 | -0.26132 | 0.0027652 | 0.00069303
102 | 0.9855 | -0.27824 | 0.0026865 | 0.00067331
103 | 0.98121 | -0.36214 | 0.0044779 | 0.0011223
104 | 0.97168 | -0.54795 | 0 | 0
105 | 0.97166 | -0.54834 | 0.0014572 | 0.00036521
106 | 0.97169 | -0.54768 | 0.00086116 | 0.00021583
107 | 0.97169 | -0.54758 | 0.0091169 | 0.0022849
108 | 0.97194 | -0.54271 | 0.0021865 | 0.00054799
109 | 0.99727 | -0.052017 | 0.0061165 | 0.001533
110 | 0.9821 | -0.34278 | 0.0046837 | 0.0011738
111 | 0.97855 | -0.41196 | 0.0026043 | 0.00065269
112 | 0.98197 | -0.34531 | 0.0054167 | 0.0013575
113 | 0.97795 | -0.42371 | 0 | 0
114 | 0.97469 | -0.48755 | 0 | 0
115 | 0.9754 | -0.47363 | 0.002998 | 0.00075137
116 | 0.97455 | -0.49042 | 0 | 0
117 | 0.9779 | -0.42469 | 0.0021932 | 0.00054967
118 | 0.97769 | -0.42868 | 0.0026563 | 0.00066573
119 | 0.97787 | -0.42513 | 0.0011791 | 0.00029552
120 | 0.97731 | -0.43613 | 0.0018979 | 0.00047566
121 | 0.97685 | -0.44512 | 0.0021533 | 0.00053968
122 | 0.97454 | -0.49053 | 0.0014084 | 0.00035298
123 | 0.97406 | -0.50009 | 0.0043056 | 0.0010791
124 | 0.97366 | -0.50781 | 0.00066469 | 0.00016659
125 | 0.97364 | -0.50836 | 0.00061753 | 0.00015477
126 | 0.97559 | -0.47002 | 0.0010315 | 0.00025852
127 | 0.97271 | -0.52668 | 0.0019441 | 0.00048724
128 | 0.97275 | -0.52588 | 0 | 0
129 | 0.97263 | -0.52825 | 0.00087689 | 0.00021977
130 | 0.97258 | -0.52913 | 0.0025489 | 0.00063882
131 | 0.97612 | -0.45948 | 0.0018382 | 0.00046071
132 | 0.9811 | -0.36418 | 0.0047642 | 0.001194
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010742 | -0.0026923 | 0.010749 | 0.0026958 | 6.7988e-06 | 3.5237e-06 | 0.016465 | 0.016465 | 0.016465 | 0.97082 | -0.56407 | 0.97149 | -0.55079 | 4.5234
1 | -0.010749 | -0.0026958 | 0.010752 | 0.0026971 | 2.5868e-06 | 1.3404e-06 | 0.016465 | 0.016465 | 0.016465 | 0.97149 | -0.55079 | 0.97174 | -0.54574 | 4.5233
2 | -0.010752 | -0.0026971 | 0.010756 | 0.0026994 | 4.4719e-06 | 2.3168e-06 | 0.016465 | 0.016465 | 0.016465 | 0.97174 | -0.54574 | 0.97218 | -0.53702 | 4.5233
3 | -0.011313 | -0.0028389 | 0.011314 | 0.0028395 | 1.0416e-06 | 5.5173e-07 | 0.017316 | 0.017316 | 0.017316 | 0.97218 | -0.53702 | 0.97228 | -0.53509 | 4.7573
4 | -0.012722 | -0.0031926 | 0.012728 | 0.0031958 | 5.9021e-06 | 3.2623e-06 | 0.019472 | 0.019472 | 0.019472 | 0.97228 | -0.53509 | 0.97278 | -0.52536 | 5.3496
5 | 0.0053706 | 0.0013452 | -0.0053705 | -0.0013452 | 1.3203e-07 | 1.9732e-08 | 0.008215 | 0.008215 | 0.008215 | 0.97278 | -0.52536 | 0.97275 | -0.52588 | 2.2569
6 | -0.018099 | -0.0045411 | 0.018114 | 0.0045498 | 1.4688e-05 | 8.7655e-06 | 0.027687 | 0.027687 | 0.027687 | 0.97278 | -0.52536 | 0.97364 | -0.50836 | 7.6064
7 | 0.013759 | 0.003451 | -0.013759 | -0.0034506 | 6.938e-07 | 3.8844e-07 | 0.020684 | 0.020684 | 0.020684 | 0.98989 | -0.19344 | 0.98983 | -0.19449 | 5.6825
8 | -0.020505 | -0.0051416 | 0.020521 | 0.0051515 | 1.6486e-05 | 9.9556e-06 | 0.030824 | 0.030824 | 0.030824 | 0.98989 | -0.19344 | 0.99076 | -0.17658 | 8.4681
9 | 0.012871 | 0.0032283 | -0.01286 | -0.0032218 | 1.181e-05 | 6.4784e-06 | 0.01935 | 0.019351 | 0.019351 | 0.98983 | -0.19449 | 0.98884 | -0.21376 | 5.3162
10 | 0.13167 | 0.033312 | -0.13163 | -0.033286 | 4.0723e-05 | 2.5742e-05 | 0.19787 | 0.19787 | 0.19787 | 0.99076 | -0.17658 | 0.99042 | -0.18303 | 18.1199
11 | -0.15632 | -0.039497 | 0.15663 | 0.039693 | 0.0003082 | 0.00019552 | 0.23489 | 0.23489 | 0.23489 | 0.99076 | -0.17658 | 0.99289 | -0.13554 | 21.5101
12 | 0.0041265 | 0.0010341 | -0.0041263 | -0.0010341 | 2.2116e-07 | -5.6178e-08 | 0.0061975 | 0.0061976 | 0.0061976 | 0.99076 | -0.17658 | 0.9907 | -0.1777 | 1.7026
13 | 0.0067386 | 0.0016877 | -0.0067383 | -0.0016876 | 3.1532e-07 | 9.6903e-08 | 0.01014 | 0.01014 | 0.01014 | 0.98884 | -0.21376 | 0.98879 | -0.21474 | 2.7857
14 | 0.02117 | 0.0053219 | -0.021157 | -0.0053139 | 1.3179e-05 | 7.9881e-06 | 0.031811 | 0.031811 | 0.031811 | 0.99042 | -0.18303 | 0.98975 | -0.19607 | 8.7394
15 | 0.11046 | 0.027964 | -0.11045 | -0.027958 | 9.3949e-06 | 5.9075e-06 | 0.16606 | 0.16606 | 0.16606 | 0.99042 | -0.18303 | 0.99033 | -0.1848 | 15.2068
16 | -0.16897 | -0.042786 | 0.16934 | 0.043018 | 0.00036608 | 0.00023252 | 0.25339 | 0.25338 | 0.25339 | 0.99289 | -0.13554 | 0.99524 | -0.090524 | 23.2038
17 | 0.0020665 | 0.0005168 | -0.0020664 | -0.00051733 | 1.822e-07 | -5.2781e-07 | 0.0031095 | 0.0031097 | 0.0031097 | 0.98879 | -0.21474 | 0.98869 | -0.2166 | 0.85433
18 | 0.021157 | 0.0053139 | -0.021146 | -0.0053074 | 1.0733e-05 | 6.5058e-06 | 0.031811 | 0.031812 | 0.031812 | 0.98975 | -0.19607 | 0.9892 | -0.20671 | 8.7395
19 | 0.10623 | 0.0269 | -0.1061 | -0.026817 | 0.00013166 | 8.267e-05 | 0.15971 | 0.15971 | 0.15971 | 0.99033 | -0.1848 | 0.98899 | -0.21064 | 14.6258
20 | -0.1708 | -0.043385 | 0.17128 | 0.043691 | 0.00048198 | 0.00030616 | 0.25557 | 0.25557 | 0.25557 | 0.99524 | -0.090524 | 0.99831 | -0.032078 | 23.4039
21 | 0.0020664 | 0.00051733 | -0.0020662 | -0.00051784 | 1.762e-07 | -5.1025e-07 | 0.0031097 | 0.00311 | 0.00311 | 0.98869 | -0.2166 | 0.9886 | -0.21839 | 0.85439
22 | 0.020156 | 0.0050593 | -0.020145 | -0.0050529 | 1.0616e-05 | 6.399e-06 | 0.030323 | 0.030323 | 0.030323 | 0.9892 | -0.20671 | 0.98863 | -0.21776 | 8.3305
23 | 0.057518 | 0.014514 | -0.057467 | -0.014481 | 5.1666e-05 | 3.2831e-05 | 0.086576 | 0.086576 | 0.086576 | 0.98899 | -0.21064 | 0.98802 | -0.22942 | 23.7847
24 | 0.04858 | 0.012303 | -0.048559 | -0.012291 | 2.066e-05 | 1.2033e-05 | 0.073138 | 0.073138 | 0.073138 | 0.98899 | -0.21064 | 0.98853 | -0.2195 | 6.6976
25 | -0.28262 | -0.072208 | 0.28306 | 0.072488 | 0.00043911 | 0.00028026 | 0.42175 | 0.42174 | 0.42175 | 0.99831 | -0.032078 | 1 | 0 | 38.6214
26 | 0.10796 | 0.027671 | -0.10795 | -0.027661 | 1.6538e-05 | 1.0384e-05 | 0.16114 | 0.16114 | 0.16114 | 0.99831 | -0.032078 | 0.99814 | -0.035238 | 14.7567
27 | 0.0033765 | 0.00084526 | -0.0033756 | -0.00084589 | 8.5287e-07 | -6.2792e-07 | 0.0050324 | 0.0050328 | 0.0050328 | 0.99831 | -0.032078 | 0.99803 | -0.037383 | 1.3826
28 | -0.040417 | -0.01025 | 0.040419 | 0.010251 | 1.9981e-06 | 1.1129e-06 | 0.060885 | 0.060885 | 0.060885 | 0.98848 | -0.22053 | 0.98853 | -0.2195 | 5.5756
29 | 0.0044947 | 0.0011261 | -0.0044945 | -0.0011261 | 2.0156e-07 | -2.1498e-08 | 0.006766 | 0.0067661 | 0.0067661 | 0.98848 | -0.22053 | 0.98843 | -0.22147 | 1.8588
30 | 0.035922 | 0.0091238 | -0.035905 | -0.0091142 | 1.7934e-05 | 9.5952e-06 | 0.05412 | 0.05412 | 0.05412 | 0.98848 | -0.22053 | 0.98794 | -0.23091 | 4.9561
31 | 0.0081397 | 0.0020401 | -0.008139 | -0.0020398 | 7.8298e-07 | 3.2283e-07 | 0.012253 | 0.012253 | 0.012253 | 0.98853 | -0.2195 | 0.98843 | -0.22152 | 3.3661
32 | 0.0022919 | 0.00057405 | -0.0022918 | -0.00057437 | 1.4209e-07 | -3.17e-07 | 0.0034502 | 0.0034503 | 0.0034503 | 0.98843 | -0.22147 | 0.98836 | -0.22277 | 0.94789
33 | 0.034439 | 0.0087468 | -0.034439 | -0.0087467 | 2.85e-07 | 1.499e-07 | 0.051913 | 0.051913 | 0.051913 | 0.98794 | -0.23091 | 0.98793 | -0.23108 | 4.7539
34 | 0.012523 | 0.00314 | -0.012519 | -0.0031381 | 3.5154e-06 | 1.8987e-06 | 0.018674 | 0.018674 | 0.018674 | 0.99791 | -0.039583 | 0.99761 | -0.045475 | 5.1302
35 | -0.012523 | -0.00314 | 0.012525 | 0.0031414 | 2.5934e-06 | 1.4006e-06 | 0.018674 | 0.018674 | 0.018674 | 0.99791 | -0.039583 | 0.99814 | -0.035238 | 5.1301
36 | 0.009501 | 0.0023817 | -0.0094987 | -0.0023806 | 2.3394e-06 | 1.0918e-06 | 0.014172 | 0.014172 | 0.014172 | 0.99761 | -0.045475 | 0.99734 | -0.050644 | 3.8934
37 | 0.095422 | 0.02452 | -0.095388 | -0.024498 | 3.4958e-05 | 2.1833e-05 | 0.14247 | 0.14247 | 0.14247 | 0.99814 | -0.035238 | 0.99774 | -0.042783 | 13.0467
38 | 0.014408 | 0.003615 | -0.014407 | -0.0036146 | 6.6071e-07 | 3.7482e-07 | 0.021687 | 0.021687 | 0.021687 | 0.98863 | -0.21776 | 0.98858 | -0.21872 | 5.958
39 | 0.054586 | 0.013759 | -0.05458 | -0.013756 | 5.444e-06 | 3.4567e-06 | 0.082237 | 0.082237 | 0.082237 | 0.98802 | -0.22942 | 0.98791 | -0.2315 | 22.5927
40 | 0.0033262 | 0.00083347 | -0.0033261 | -0.00083359 | 1.5493e-07 | -1.2209e-07 | 0.0049494 | 0.0049495 | 0.0049495 | 1 | 0 | 0.99995 | -0.00097784 | 1.3598
41 | 0.0029122 | 0.00072975 | -0.0029121 | -0.00072985 | 8.3826e-08 | -1.0129e-07 | 0.004342 | 0.004342 | 0.004342 | 0.99803 | -0.037383 | 0.998 | -0.037987 | 1.1929
42 | 0.0059899 | 0.0015012 | -0.0059892 | -0.001501 | 7.0039e-07 | 1.5389e-07 | 0.0090174 | 0.0090175 | 0.0090175 | 0.98843 | -0.22152 | 0.9883 | -0.22398 | 2.4773
43 | 0.032729 | 0.0083183 | -0.032704 | -0.0083051 | 2.5783e-05 | 1.3249e-05 | 0.049338 | 0.049339 | 0.049339 | 0.98793 | -0.23108 | 0.98708 | -0.24745 | 4.5183
44 | 0.027324 | 0.0069567 | -0.027302 | -0.0069446 | 2.1758e-05 | 1.2182e-05 | 0.041229 | 0.04123 | 0.04123 | 0.98708 | -0.24745 | 0.98622 | -0.26398 | 5.6634
45 | 0.0011704 | 0.00029306 | -0.0011703 | -0.00029331 | 2.4459e-08 | -2.5126e-07 | 0.0017657 | 0.0017658 | 0.0017658 | 0.98622 | -0.26398 | 0.9862 | -0.26442 | 0.48512
46 | 0.026132 | 0.0066515 | -0.025986 | -0.0065614 | 0.00014567 | 9.0065e-05 | 0.039464 | 0.039465 | 0.039465 | 0.98622 | -0.26398 | 0.98022 | -0.38029 | 10.8421
47 | 0.025986 | 0.0065614 | -0.025954 | -0.0065416 | 3.2089e-05 | 1.9845e-05 | 0.039465 | 0.039466 | 0.039466 | 0.98022 | -0.38029 | 0.9789 | -0.40609 | 10.8422
48 | 0.0059892 | 0.001501 | -0.0059885 | -0.0015009 | 7.0004e-07 | 1.5389e-07 | 0.0090175 | 0.0090176 | 0.0090176 | 0.9883 | -0.22398 | 0.98817 | -0.22643 | 2.4774
49 | 0.016804 | 0.0042485 | -0.016701 | -0.0041876 | 0.00010337 | 6.0885e-05 | 0.025558 | 0.025559 | 0.025559 | 0.9789 | -0.40609 | 0.97232 | -0.53515 | 7.0218
50 | 0.013629 | 0.0034178 | -0.013625 | -0.0034151 | 4.9102e-06 | 2.7694e-06 | 0.020859 | 0.020859 | 0.020859 | 0.97232 | -0.53515 | 0.97194 | -0.54271 | 5.7305
51 | 0.052914 | 0.013338 | -0.052863 | -0.013306 | 5.1058e-05 | 3.2403e-05 | 0.079728 | 0.079728 | 0.079728 | 0.98791 | -0.2315 | 0.98687 | -0.25169 | 21.9033
52 | -0.0089731 | -0.0022479 | 0.0089771 | 0.0022497 | 3.9892e-06 | 1.8219e-06 | 0.013583 | 0.013583 | 0.013583 | 0.98295 | -0.32628 | 0.98343 | -0.31695 | 3.7317
53 | 0.005578 | 0.001397 | -0.0055779 | -0.001397 | 1.6441e-07 | 2.728e-08 | 0.0084439 | 0.0084439 | 0.0084439 | 0.98295 | -0.32628 | 0.98292 | -0.3269 | 2.3198
54 | -0.011984 | -0.0030033 | 0.011985 | 0.0030041 | 1.4281e-06 | 7.6703e-07 | 0.018133 | 0.018133 | 0.018133 | 0.98343 | -0.31695 | 0.98355 | -0.31445 | 4.9815
55 | 0.0043126 | 0.0010799 | -0.004312 | -0.00108 | 5.8184e-07 | -8.8973e-08 | 0.0065284 | 0.0065285 | 0.0065285 | 0.98292 | -0.3269 | 0.98277 | -0.32973 | 1.7936
56 | 0.072549 | 0.018337 | -0.072526 | -0.018323 | 2.2349e-05 | 1.424e-05 | 0.10981 | 0.10981 | 0.10981 | 0.98355 | -0.31445 | 0.98322 | -0.32087 | 30.1687
57 | -0.084534 | -0.021341 | 0.085143 | 0.02173 | 0.00060923 | 0.00038864 | 0.12795 | 0.12795 | 0.12795 | 0.98355 | -0.31445 | 0.9913 | -0.16518 | 35.1502
58 | 0.00276 | 0.000691 | -0.00276 | -0.00069102 | 1.7939e-08 | -2.3233e-08 | 0.0041787 | 0.0041787 | 0.0041787 | 0.98277 | -0.32973 | 0.98276 | -0.32987 | 1.148
59 | 0.068345 | 0.017275 | -0.068304 | -0.017249 | 4.1047e-05 | 2.6141e-05 | 0.10349 | 0.10349 | 0.10349 | 0.98322 | -0.32087 | 0.98258 | -0.33341 | 28.4302
60 | 0.0041815 | 0.0010477 | -0.004181 | -0.0010478 | 4.6722e-07 | -9.5509e-08 | 0.0063282 | 0.0063283 | 0.0063283 | 0.98322 | -0.32087 | 0.9831 | -0.32322 | 1.7386
61 | -0.08648 | -0.022065 | 0.086617 | 0.022152 | 0.00013716 | 8.7502e-05 | 0.12995 | 0.12995 | 0.12995 | 0.9913 | -0.16518 | 0.99301 | -0.1324 | 35.7012
62 | 0.0019391 | 0.00048529 | -0.001939 | -0.00048572 | 1.3034e-07 | -4.275e-07 | 0.0029358 | 0.0029359 | 0.0029359 | 0.98276 | -0.32987 | 0.98269 | -0.33128 | 0.80658
63 | 0.012558 | 0.0031486 | -0.012557 | -0.0031478 | 1.5769e-06 | 8.62e-07 | 0.019019 | 0.019019 | 0.019019 | 0.98258 | -0.33341 | 0.98244 | -0.33604 | 5.225
64 | 0.055745 | 0.0141 | -0.05573 | -0.01409 | 1.5296e-05 | 9.7169e-06 | 0.084467 | 0.084467 | 0.084467 | 0.98258 | -0.33341 | 0.98228 | -0.33913 | 23.2052
65 | 0.0013531 | 0.00033909 | -0.0013531 | -0.00033912 | 3.6745e-09 | -2.7269e-08 | 0.002048 | 0.002048 | 0.002048 | 0.9831 | -0.32322 | 0.9831 | -0.32328 | 0.56265
66 | -0.087604 | -0.022399 | 0.087704 | 0.022463 | 0.00010009 | 6.3857e-05 | 0.13143 | 0.13143 | 0.13143 | 0.99301 | -0.1324 | 0.99425 | -0.10882 | 36.1074
67 | 0.00088121 | 0.00022062 | -0.0008812 | -0.00022085 | 1.2548e-08 | -2.3008e-07 | 0.0013343 | 0.0013344 | 0.0013344 | 0.98269 | -0.33128 | 0.98268 | -0.33158 | 0.36658
68 | 0.010104 | 0.0025331 | -0.010101 | -0.0025315 | 3.2434e-06 | 1.6083e-06 | 0.015304 | 0.015304 | 0.015304 | 0.98244 | -0.33604 | 0.9821 | -0.34278 | 4.2045
69 | 0.049001 | 0.012405 | -0.048901 | -0.012342 | 0.00010008 | 6.3442e-05 | 0.074274 | 0.074275 | 0.074275 | 0.98228 | -0.33913 | 0.98009 | -0.38177 | 20.4051
70 | 0.004183 | 0.0010479 | -0.0041827 | -0.001048 | 2.3712e-07 | -4.7586e-08 | 0.0063364 | 0.0063365 | 0.0063365 | 0.98228 | -0.33913 | 0.98222 | -0.34032 | 1.7408
71 | 0.0025457 | 0.00063741 | -0.0025454 | -0.00063793 | 3.2196e-07 | -5.2468e-07 | 0.0038561 | 0.0038564 | 0.0038564 | 0.98228 | -0.33913 | 0.98215 | -0.34178 | 1.0595
72 | -0.088345 | -0.022624 | 0.088495 | 0.022719 | 0.00015004 | 9.4836e-05 | 0.13239 | 0.13239 | 0.13239 | 0.99425 | -0.10882 | 0.9961 | -0.073824 | 18.1856
73 | 0.013226 | 0.0033184 | -0.013222 | -0.0033165 | 3.5037e-06 | 1.9402e-06 | 0.019908 | 0.019909 | 0.019909 | 0.98858 | -0.21872 | 0.98829 | -0.22428 | 5.4694
74 | 0.011439 | 0.0028697 | -0.011436 | -0.0028681 | 3.0459e-06 | 1.5987e-06 | 0.017225 | 0.017225 | 0.017225 | 0.98829 | -0.22428 | 0.98801 | -0.22986 | 4.7321
75 | 0.010186 | 0.0025547 | -0.010184 | -0.0025538 | 1.9298e-06 | 9.5511e-07 | 0.015342 | 0.015342 | 0.015342 | 0.98801 | -0.22986 | 0.9878 | -0.23384 | 4.2148
76 | 0.0083651 | 0.0020979 | -0.0083613 | -0.0020963 | 3.7989e-06 | 1.6151e-06 | 0.012602 | 0.012602 | 0.012602 | 0.9878 | -0.23384 | 0.98731 | -0.24337 | 3.4621
77 | 0.0061169 | 0.001533 | -0.0061165 | -0.001533 | 4.0017e-07 | 8.8932e-08 | 0.0091264 | 0.0091265 | 0.0091265 | 0.99734 | -0.050644 | 0.99727 | -0.052017 | 2.5073
78 | 0.092634 | 0.023808 | -0.092572 | -0.023769 | 6.2276e-05 | 3.8838e-05 | 0.13836 | 0.13836 | 0.13836 | 0.99774 | -0.042783 | 0.99701 | -0.056632 | 12.6707
79 | 0.0083613 | 0.0020963 | -0.0083592 | -0.0020954 | 2.1909e-06 | 9.3186e-07 | 0.012602 | 0.012602 | 0.012602 | 0.98731 | -0.24337 | 0.98703 | -0.24887 | 3.4621
80 | 0.091576 | 0.023519 | -0.091546 | -0.023501 | 3.0222e-05 | 1.8837e-05 | 0.13688 | 0.13688 | 0.13688 | 0.99701 | -0.056632 | 0.99665 | -0.063431 | 12.5347
81 | 0.090883 | 0.023334 | -0.09087 | -0.023326 | 1.3561e-05 | 8.4493e-06 | 0.13589 | 0.13589 | 0.13589 | 0.99665 | -0.063431 | 0.99648 | -0.066505 | 12.444
82 | 0.090538 | 0.023243 | -0.090505 | -0.023223 | 3.2151e-05 | 2.0028e-05 | 0.13539 | 0.13539 | 0.13539 | 0.99648 | -0.066505 | 0.9961 | -0.073824 | 12.3987
83 | 0.0031511 | 0.0007896 | -0.0031509 | -0.0007897 | 1.2412e-07 | -1.028e-07 | 0.004784 | 0.0047841 | 0.0047841 | 0.98009 | -0.38177 | 0.98005 | -0.38259 | 1.3143
84 | 0.04575 | 0.011552 | -0.045717 | -0.011531 | 3.3098e-05 | 2.0953e-05 | 0.069491 | 0.069491 | 0.069491 | 0.98009 | -0.38177 | 0.97932 | -0.39688 | 19.0908
85 | 0.001777 | 0.00044506 | -0.0017769 | -0.00044534 | 7.1343e-08 | -2.8659e-07 | 0.002692 | 0.0026921 | 0.0026921 | 0.98222 | -0.34032 | 0.98218 | -0.34116 | 0.73959
86 | 0.043832 | 0.011059 | -0.043801 | -0.011039 | 3.1633e-05 | 2.0006e-05 | 0.066627 | 0.066627 | 0.066627 | 0.97932 | -0.39688 | 0.97855 | -0.41196 | 18.3041
87 | 0.0083592 | 0.0020954 | -0.0083563 | -0.0020942 | 2.8102e-06 | 1.1956e-06 | 0.012602 | 0.012602 | 0.012602 | 0.98703 | -0.24887 | 0.98667 | -0.25593 | 3.4622
88 | 0.0057568 | 0.0014427 | -0.0057561 | -0.0014425 | 6.5891e-07 | 1.2402e-07 | 0.0086819 | 0.008682 | 0.008682 | 0.98667 | -0.25593 | 0.98655 | -0.25833 | 2.3852
89 | 0.0025636 | 0.0006424 | -0.0025635 | -0.00064248 | 4.8245e-08 | -7.8996e-08 | 0.0038666 | 0.0038667 | 0.0038667 | 0.98655 | -0.25833 | 0.98653 | -0.25873 | 1.0623
90 | -0.01698 | -0.0042624 | 0.016986 | 0.004266 | 6.0016e-06 | 3.5343e-06 | 0.025714 | 0.025714 | 0.025714 | 0.98268 | -0.33322 | 0.98306 | -0.32581 | 7.0643
91 | 0.01698 | 0.0042624 | -0.016963 | -0.0042524 | 1.7079e-05 | 1.0059e-05 | 0.025714 | 0.025714 | 0.025714 | 0.98268 | -0.33322 | 0.9816 | -0.35433 | 7.0644
92 | -0.01942 | -0.0048759 | 0.019433 | 0.0048837 | 1.3025e-05 | 7.8258e-06 | 0.029398 | 0.029398 | 0.029398 | 0.98306 | -0.32581 | 0.98378 | -0.31176 | 8.0763
93 | 0.0071101 | 0.0017823 | -0.0071064 | -0.001781 | 3.7331e-06 | 1.3066e-06 | 0.010778 | 0.010779 | 0.010779 | 0.9816 | -0.35433 | 0.98104 | -0.36535 | 2.9612
94 | 0.0098528 | 0.00247 | -0.0098507 | -0.002469 | 2.1213e-06 | 1.0372e-06 | 0.014936 | 0.014936 | 0.014936 | 0.9816 | -0.35433 | 0.98137 | -0.35885 | 4.1034
95 | -0.020269 | -0.0050934 | 0.020278 | 0.0050984 | 8.1869e-06 | 4.9446e-06 | 0.030663 | 0.030663 | 0.030663 | 0.98378 | -0.31176 | 0.98422 | -0.3033 | 8.4239
96 | 0.009244 | 0.002317 | -0.0092425 | -0.0023163 | 1.4503e-06 | 6.7949e-07 | 0.014016 | 0.014016 | 0.014016 | 0.98137 | -0.35885 | 0.98121 | -0.36214 | 3.8507
97 | -0.0070024 | -0.001755 | 0.0070025 | 0.001755 | 1.5743e-07 | 5.324e-08 | 0.010592 | 0.010592 | 0.010592 | 0.98376 | -0.31219 | 0.98379 | -0.31172 | 2.9098
98 | -0.0089143 | -0.0022341 | 0.008916 | 0.0022349 | 1.6465e-06 | 7.4702e-07 | 0.013483 | 0.013483 | 0.013483 | 0.98379 | -0.31172 | 0.98399 | -0.30784 | 3.7042
99 | -0.01108 | -0.0027773 | 0.011083 | 0.0027787 | 2.6889e-06 | 1.3964e-06 | 0.016756 | 0.016756 | 0.016756 | 0.98399 | -0.30784 | 0.98425 | -0.30275 | 4.6032
100 | -0.013623 | -0.0034153 | 0.013626 | 0.0034167 | 2.4433e-06 | 1.3685e-06 | 0.020596 | 0.020596 | 0.020596 | 0.98425 | -0.30275 | 0.98444 | -0.29899 | 5.6583
101 | -0.037382 | -0.0093887 | 0.037395 | 0.009397 | 1.3104e-05 | 8.2476e-06 | 0.056512 | 0.056512 | 0.056512 | 0.98444 | -0.29899 | 0.98482 | -0.29164 | 15.5252
102 | 0.023757 | 0.005972 | -0.023755 | -0.0059708 | 1.953e-06 | 1.1986e-06 | 0.035915 | 0.035916 | 0.035916 | 0.98444 | -0.29899 | 0.98435 | -0.30071 | 9.8669
103 | -0.038417 | -0.009653 | 0.038437 | 0.0096656 | 2.0082e-05 | 1.265e-05 | 0.058055 | 0.058055 | 0.058055 | 0.98482 | -0.29164 | 0.98538 | -0.2807 | 15.9492
104 | 0.022346 | 0.0056178 | -0.022344 | -0.0056161 | 2.7695e-06 | 1.6902e-06 | 0.033786 | 0.033786 | 0.033786 | 0.98435 | -0.30071 | 0.98422 | -0.3033 | 9.282
105 | -0.043186 | -0.010856 | 0.043191 | 0.010859 | 5.0604e-06 | 3.1982e-06 | 0.065227 | 0.065227 | 0.065227 | 0.98538 | -0.2807 | 0.9855 | -0.27824 | 17.9194
106 | 0.048702 | 0.012263 | -0.04868 | -0.012249 | 2.2411e-05 | 1.4201e-05 | 0.073454 | 0.073454 | 0.073454 | 0.98687 | -0.25169 | 0.98637 | -0.26132 | 20.1798
107 | 0.045915 | 0.011556 | -0.045878 | -0.011532 | 3.7108e-05 | 2.3486e-05 | 0.069283 | 0.069283 | 0.069283 | 0.98637 | -0.26132 | 0.9855 | -0.27824 | 19.0338
108 | 0.0047646 | 0.001194 | -0.0047642 | -0.001194 | 4.6308e-07 | -2.3443e-09 | 0.0072256 | 0.0072257 | 0.0072257 | 0.98121 | -0.36214 | 0.9811 | -0.36418 | 1.9851
109 | 0.0014572 | 0.00036505 | -0.0014572 | -0.00036521 | 2.6814e-08 | -1.6069e-07 | 0.0022316 | 0.0022316 | 0.0022316 | 0.97168 | -0.54795 | 0.97166 | -0.54834 | 0.61308
110 | -0.0014572 | -0.00036505 | 0.0014573 | 0.00036494 | 1.8501e-08 | -1.1088e-07 | 0.0022316 | 0.0022315 | 0.0022316 | 0.97168 | -0.54795 | 0.97169 | -0.54768 | 0.61306
111 | -0.0023184 | -0.00058077 | 0.0023184 | 0.00058075 | 1.1351e-08 | -2.2483e-08 | 0.0035503 | 0.0035503 | 0.0035503 | 0.97169 | -0.54768 | 0.97169 | -0.54758 | 0.97535
112 | -0.011435 | -0.0028657 | 0.011438 | 0.0028671 | 2.652e-06 | 1.4115e-06 | 0.017512 | 0.017511 | 0.017512 | 0.97169 | -0.54758 | 0.97194 | -0.54271 | 4.8109
113 | 0.0054173 | 0.0013576 | -0.0054167 | -0.0013575 | 6.53e-07 | 9.0903e-08 | 0.0082079 | 0.0082081 | 0.0082081 | 0.9821 | -0.34278 | 0.98197 | -0.34531 | 2.255
114 | 0.041196 | 0.010386 | -0.041173 | -0.010371 | 2.3146e-05 | 1.4616e-05 | 0.062667 | 0.062667 | 0.062667 | 0.97855 | -0.41196 | 0.97795 | -0.42371 | 17.2161
115 | 0.0033725 | 0.00084485 | -0.0033724 | -0.00084495 | 1.5732e-07 | -9.9207e-08 | 0.0051314 | 0.0051315 | 0.0051315 | 0.97795 | -0.42371 | 0.9779 | -0.42469 | 1.4097
116 | 0.037801 | 0.0095266 | -0.037792 | -0.0095209 | 8.9964e-06 | 5.6668e-06 | 0.057535 | 0.057535 | 0.057535 | 0.97795 | -0.42371 | 0.97769 | -0.42868 | 15.8064
117 | -0.025132 | -0.0063166 | 0.025149 | 0.006327 | 1.6721e-05 | 1.0324e-05 | 0.038374 | 0.038374 | 0.038374 | 0.97469 | -0.48755 | 0.9754 | -0.47363 | 10.5423
118 | 0.025132 | 0.0063166 | -0.025128 | -0.0063145 | 3.4381e-06 | 2.1228e-06 | 0.038374 | 0.038374 | 0.038374 | 0.97469 | -0.48755 | 0.97455 | -0.49042 | 10.5424
119 | -0.028147 | -0.0070783 | 0.028152 | 0.0070813 | 4.8549e-06 | 3.0195e-06 | 0.042948 | 0.042948 | 0.042948 | 0.9754 | -0.47363 | 0.97559 | -0.47002 | 11.7988
120 | 0.02372 | 0.0059616 | -0.023709 | -0.0059548 | 1.095e-05 | 6.7307e-06 | 0.036224 | 0.036224 | 0.036224 | 0.97455 | -0.49042 | 0.97406 | -0.50009 | 9.9516
121 | 0.0014084 | 0.00035293 | -0.0014084 | -0.00035298 | 7.5386e-09 | -4.934e-08 | 0.0021504 | 0.0021505 | 0.0021505 | 0.97455 | -0.49042 | 0.97454 | -0.49053 | 0.59078
122 | 0.0011792 | 0.00029527 | -0.0011791 | -0.00029552 | 2.5026e-08 | -2.4406e-07 | 0.0017942 | 0.0017943 | 0.0017943 | 0.9779 | -0.42469 | 0.97787 | -0.42513 | 0.49293
123 | 0.035135 | 0.0088552 | -0.035123 | -0.0088473 | 1.2515e-05 | 7.8631e-06 | 0.053493 | 0.053493 | 0.053493 | 0.97769 | -0.42868 | 0.97731 | -0.43613 | 14.6958
124 | 0.033225 | 0.0083717 | -0.033211 | -0.0083627 | 1.4278e-05 | 8.9515e-06 | 0.050603 | 0.050603 | 0.050603 | 0.97731 | -0.43613 | 0.97685 | -0.44512 | 13.9019
125 | 0.031057 | 0.0078231 | -0.031036 | -0.0078097 | 2.1318e-05 | 1.3326e-05 | 0.047323 | 0.047323 | 0.047323 | 0.97685 | -0.44512 | 0.97612 | -0.45948 | 13.0008
126 | 0.019404 | 0.0048758 | -0.019396 | -0.0048715 | 7.1475e-06 | 4.3046e-06 | 0.029646 | 0.029647 | 0.029647 | 0.97406 | -0.50009 | 0.97366 | -0.50781 | 8.1447
127 | 0.018732 | 0.0047049 | -0.018731 | -0.0047046 | 4.8641e-07 | 2.9163e-07 | 0.028631 | 0.028631 | 0.028631 | 0.97366 | -0.50781 | 0.97364 | -0.50836 | 7.8656
128 | -0.029183 | -0.0073399 | 0.029198 | 0.007349 | 1.4692e-05 | 9.1558e-06 | 0.044521 | 0.044521 | 0.044521 | 0.97559 | -0.47002 | 0.97612 | -0.45948 | 12.231
129 | -0.0019441 | -0.00048724 | 0.0019442 | 0.00048701 | 7.3873e-08 | -2.292e-07 | 0.0029741 | 0.002974 | 0.0029741 | 0.97271 | -0.52668 | 0.97275 | -0.52588 | 0.81705
130 | 0.0034263 | 0.00085821 | -0.0034259 | -0.00085843 | 3.8755e-07 | -2.1895e-07 | 0.0052411 | 0.0052412 | 0.0052412 | 0.97275 | -0.52588 | 0.97263 | -0.52825 | 1.4399
131 | 0.002549 | 0.00063866 | -0.0025489 | -0.00063882 | 1.0628e-07 | -1.6326e-07 | 0.0038997 | 0.0038998 | 0.0038998 | 0.97263 | -0.52825 | 0.97258 | -0.52913 | 1.0714

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29047 | 0.073933

## res_load
| p_mw | q_mvar
0 | 0.010742 | 0.0026923
1 | 0.00055661 | 0.0001395
2 | 0.0014087 | 0.00035306
3 | 0.0067453 | 0.0016905
4 | 0.00088725 | 0.00022237
5 | 0.006121 | 0.0015341
6 | 0.012341 | 0.0030929
7 | 0.0041263 | 0.0010341
8 | 0.0046717 | 0.0011708
9 | 0.0042229 | 0.0010584
10 | 0.0014622 | 0.00036647
11 | 0.00098973 | 0.00024805
12 | 0.0022026 | 0.00055202
13 | 0.0014657 | 0.00036734
14 | 0.0020662 | 0.00051784
15 | 0.0030183 | 0.00075646
16 | 0.0057375 | 0.001438
17 | 0.002881 | 0.00072205
18 | 0.002438 | 0.00061102
19 | 0.00046338 | 0.00011613
20 | 0.0021491 | 0.00053861
21 | 0.0022918 | 0.00057437
22 | 0.0017092 | 0.00042836
23 | 0.0053799 | 0.0013483
24 | 0.0011703 | 0.00029331
25 | 0.0091494 | 0.0022931
26 | 0.0030715 | 0.0007698
27 | 0.0016661 | 0.00041756
28 | 0.0059885 | 0.0015009
29 | 0.0033951 | 0.00085088
30 | 0.0030068 | 0.00075357
31 | 0.0012653 | 0.00031712
32 | 0.001552 | 0.00038896
33 | 0.0013366 | 0.00033498
34 | 0.00082089 | 0.00020573
35 | 0.0028279 | 0.00070874
36 | 0.00098678 | 0.00024731
37 | 0.0010577 | 0.0002651
38 | 0.0024526 | 0.00061469
39 | 0.0013531 | 0.00033912
40 | 0.00064152 | 0.00016078
41 | 0.0008812 | 0.00022085
42 | 0.0011817 | 0.00029617
43 | 0.0017826 | 0.00044676
44 | 0.0012503 | 0.00031336
45 | 0.001819 | 0.00045589
46 | 0.0033817 | 0.00084754
47 | 0.0027532 | 0.00069003
48 | 0.0033261 | 0.00083359
49 | 0.0029121 | 0.00072985
50 | 0.00099574 | 0.00024956
51 | 0.00066284 | 0.00016612
52 | 0.00033204 | 8.3217e-05
53 | 0.0020102 | 0.00050379
54 | 0.0025454 | 0.00063793
55 | 0.0024057 | 0.00060293
56 | 0.0031509 | 0.0007897
57 | 0.0018849 | 0.00047239
58 | 0.0017769 | 0.00044534
59 | 0.0025996 | 0.00065151
60 | 0.0031926 | 0.00080013
61 | 0.0024336 | 0.00060993
62 | 0.0025635 | 0.00064248
63 | 0.00083667 | 0.00020969
64 | 0.0071064 | 0.001781
65 | 0.0006067 | 0.00015205
66 | 0.0070024 | 0.001755
67 | 0.0019118 | 0.00047914
68 | 0.002164 | 0.00054236
69 | 0.0025404 | 0.00063669
70 | 0.0010214 | 0.00025599
71 | 0.0014084 | 0.00035298
72 | 0.0047492 | 0.0011903
73 | 0.002066 | 0.00051779
74 | 0.0041607 | 0.0010428
75 | 0.0027652 | 0.00069303
76 | 0.0026865 | 0.00067331
77 | 0.0044779 | 0.0011223
78 | 0.0014572 | 0.00036521
79 | 0.00086116 | 0.00021583
80 | 0.0091169 | 0.0022849
81 | 0.0021865 | 0.00054799
82 | 0.0061165 | 0.001533
83 | 0.0046837 | 0.0011738
84 | 0.0026043 | 0.00065269
85 | 0.0054167 | 0.0013575
86 | 0.002998 | 0.00075137
87 | 0.0021932 | 0.00054967
88 | 0.0026563 | 0.00066573
89 | 0.0011791 | 0.00029552
90 | 0.0018979 | 0.00047566
91 | 0.0021533 | 0.00053968
92 | 0.0014084 | 0.00035298
93 | 0.0043056 | 0.0010791
94 | 0.00066469 | 0.00016659
95 | 0.00061753 | 0.00015477
96 | 0.0010315 | 0.00025852
97 | 0.0019441 | 0.00048724
98 | 0.00087689 | 0.00021977
99 | 0.0025489 | 0.00063882
100 | 0.0018382 | 0.00046071
101 | 0.0047642 | 0.001194

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1