## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2275-36_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2275-36_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2275-36_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2275-36_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2275-36_0_5_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_2275-36_0_5_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2275-36_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2275-36_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2275-36_0_5_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2275-36_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2275-36_0_5_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_2275-36_0_5_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2275-36_0_5_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_2275-36_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2275-36_0_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_2275-36_0_5_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_2275-36_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2275-36_0_5_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_2275-36_0_5_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_2275-36_0_5_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_2275-36_0_5_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_2275-36_0_5_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_2275-36_0_5_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_2275-36_0_5_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2275-36_0_5_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2275-36_0_5_node_40 | 0.4 | n |  | TRUE
26 | bus_LV_2275-36_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2275-36_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2275-36_0_5_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2275-36_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2275-36_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_2275-36_0_5_node_11 | 0.4 | n |  | TRUE
32 | bus_LV_2275-36_0_5_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_2275-36_0_5_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_2275-36_0_5_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2275-36_0_5_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2275-36_0_5_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2275-36_0_5_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2275-36_0_5_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_2275-36_0_5_node_41 | 0.4 | n |  | TRUE
40 | bus_MV_379_0_node_118 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2275-36_0_5_load_0 | 0 | 0.030269 | 0.0075861 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2275-36_0_5_load_1 | 1 | 0.021767 | 0.0054554 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2275-36_0_5_load_2 | 2 | 0.052861 | 0.013248 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2275-36_0_5_load_14 | 4 | 0.0070678 | 0.0017714 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2275-36_0_5_load_28 | 8 | 0.003908 | 0.00097944 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2275-36_0_5_load_34 | 10 | 0.0068581 | 0.0017188 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2275-36_0_5_load_33 | 11 | 0.010687 | 0.0026783 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2275-36_0_5_load_42 | 12 | 0.0037958 | 0.00095132 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2275-36_0_5_load_36 | 14 | 0.02137 | 0.0053557 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2275-36_0_5_load_35 | 15 | 0.020565 | 0.005154 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2275-36_0_5_load_12 | 16 | 0.0058101 | 0.0014561 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2275-36_0_5_load_32 | 17 | 0.023485 | 0.0058858 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2275-36_0_5_load_30 | 18 | 0.022696 | 0.0056881 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2275-36_0_5_load_38 | 19 | 0.027849 | 0.0069796 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2275-36_0_5_load_37 | 20 | 0.027972 | 0.0070104 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2275-36_0_5_load_29 | 21 | 0.012166 | 0.0030491 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2275-36_0_5_load_23 | 22 | 0.009277 | 0.002325 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2275-36_0_5_load_27 | 23 | 0.0042225 | 0.0010583 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2275-36_0_5_load_18 | 24 | 0.0053999 | 0.0013533 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2275-36_0_5_load_40 | 25 | 0.0034618 | 0.00086762 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2275-36_0_5_load_21 | 26 | 0.004083 | 0.0010233 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2275-36_0_5_load_19 | 27 | 0.0047973 | 0.0012023 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2275-36_0_5_load_25 | 29 | 0.0044699 | 0.0011203 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2275-36_0_5_load_22 | 30 | 0.0036598 | 0.00091724 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2275-36_0_5_load_11 | 31 | 0.018452 | 0.0046245 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2275-36_0_5_load_13 | 32 | 0.0071581 | 0.001794 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2275-36_0_5_load_15 | 33 | 0.014326 | 0.0035904 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2275-36_0_5_load_16 | 34 | 0.013018 | 0.0032627 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2275-36_0_5_load_17 | 35 | 0.0046117 | 0.0011558 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2275-36_0_5_load_20 | 36 | 0.0030575 | 0.00076629 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2275-36_0_5_load_26 | 37 | 0.0048025 | 0.0012036 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2275-36_0_5_load_39 | 38 | 0.0038824 | 0.00097301 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2275-36_0_5_load_41 | 39 | 0.0021287 | 0.0005335 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2275-36_0_5_line_0 |  | 0 | 1 | 0.00093022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2275-36_0_5_line_1 |  | 0 | 2 | 0.00015808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2275-36_0_5_line_2 |  | 2 | 3 | 0.020017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2275-36_0_5_line_3 |  | 3 | 4 | 0.016229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2275-36_0_5_line_4 |  | 3 | 5 | 0.005418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2275-36_0_5_line_5 |  | 4 | 16 | 0.0057039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2275-36_0_5_line_6 |  | 5 | 17 | 0.012551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2275-36_0_5_line_7 |  | 5 | 18 | 0.019802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2275-36_0_5_line_8 |  | 6 | 7 | 0.04856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2275-36_0_5_line_9 |  | 6 | 8 | 0.02483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2275-36_0_5_line_10 |  | 7 | 12 | 0.065189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2275-36_0_5_line_11 |  | 8 | 22 | 0.010853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2275-36_0_5_line_12 |  | 9 | 10 | 0.025801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2275-36_0_5_line_13 |  | 9 | 11 | 0.024604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2275-36_0_5_line_14 |  | 10 | 23 | 6.3392e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2275-36_0_5_line_15 |  | 11 | 24 | 0.0070364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2275-36_0_5_line_16 |  | 12 | 25 | 0.017382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2275-36_0_5_line_17 |  | 13 | 14 | 0.015408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2275-36_0_5_line_18 |  | 13 | 15 | 0.018304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2275-36_0_5_line_19 |  | 14 | 20 | 0.0012325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2275-36_0_5_line_20 |  | 15 | 17 | 0.0080009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2275-36_0_5_line_21 |  | 16 | 31 | 0.0019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2275-36_0_5_line_22 |  | 18 | 21 | 0.0015661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2275-36_0_5_line_23 |  | 19 | 20 | 0.0026386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2275-36_0_5_line_24 |  | 22 | 26 | 0.010704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2275-36_0_5_line_25 |  | 23 | 37 | 0.01965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2275-36_0_5_line_26 |  | 24 | 35 | 0.0057123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2275-36_0_5_line_27 |  | 25 | 38 | 0.017675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2275-36_0_5_line_28 |  | 26 | 27 | 0.0052575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2275-36_0_5_line_29 |  | 27 | 36 | 0.004635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2275-36_0_5_line_30 |  | 28 | 29 | 0.0043328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2275-36_0_5_line_31 |  | 28 | 30 | 0.0086154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2275-36_0_5_line_32 |  | 29 | 37 | 0.0057062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2275-36_0_5_line_33 |  | 30 | 36 | 0.0084989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2275-36_0_5_line_34 |  | 31 | 32 | 0.0051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2275-36_0_5_line_35 |  | 32 | 33 | 0.00047696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2275-36_0_5_line_36 |  | 33 | 34 | 0.0047974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2275-36_0_5_line_37 |  | 34 | 35 | 0.0020609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2275-36_0_5_line_38 |  | 38 | 39 | 0.00059203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2275-36_0_5_trafo_4 | 0.63 MVA 20/0.4 kV | 40 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2575497.4166 | 1197530.5298 | 2575496.7703 | 1197531.1988
1 | 2575497.5265 | 1197530.4161 | 2575497.4166 | 1197530.5298
2 | 2575511.4334 | 1197516.0186 | 2575505.958 | 1197521.6887 | 2575497.5265 | 1197530.4161
3 | 2575511.4334 | 1197516.0186 | 2575498.5328 | 1197506.1727
4 | 2575511.4334 | 1197516.0186 | 2575515.6211 | 1197519.47
5 | 2575498.5328 | 1197506.1727 | 2575493.9986 | 1197502.7122
6 | 2575515.6211 | 1197519.47 | 2575524.9317 | 1197527.886
7 | 2575515.6211 | 1197519.47 | 2575527.9644 | 1197503.9852
8 | 2575554.4298 | 1197470.7842 | 2575568.5919 | 1197451.3489 | 2575572.2937 | 1197447.7652 | 2575579.7427 | 1197451.6145 | 2575581.6586 | 1197450.7951 | 2575581.9154 | 1197450.2826 | 2575584.7238 | 1197451.6719 | 2575585.1016 | 1197450.9255 | 2575582.2703 | 1197449.5252 | 2575582.8143 | 1197448.4668
9 | 2575554.4298 | 1197470.7842 | 2575533.5203 | 1197457.3927
10 | 2575582.8143 | 1197448.4668 | 2575579.5618 | 1197446.4902 | 2575550.1927 | 1197433.0479 | 2575522.94 | 1197423.1544 | 2575522.8494 | 1197423.1462
11 | 2575524.0982 | 1197452.0402 | 2575528.6963 | 1197454.3032 | 2575533.5203 | 1197457.3927
12 | 2575450.2407 | 1197475.6265 | 2575463.599 | 1197458.9958 | 2575466.6598 | 1197455.7389
13 | 2575450.2407 | 1197475.6265 | 2575472.4316 | 1197486.2519
14 | 2575466.6598 | 1197455.7389 | 2575466.7032 | 1197455.6927
15 | 2575478.025 | 1197490.5209 | 2575472.4316 | 1197486.2519 | 2575472.4316 | 1197486.2519
16 | 2575522.8494 | 1197423.1462 | 2575505.5381 | 1197421.5765
17 | 2575544.4401 | 1197545.5323 | 2575541.3741 | 1197548.1797 | 2575534.087 | 1197556.8906
18 | 2575544.4401 | 1197545.5323 | 2575532.4309 | 1197534.6647 | 2575530.8672 | 1197533.2512
19 | 2575534.087 | 1197556.8906 | 2575533.2962 | 1197557.8359
20 | 2575524.9317 | 1197527.886 | 2575530.8672 | 1197533.2512
21 | 2575493.9986 | 1197502.7122 | 2575492.451 | 1197501.531
22 | 2575527.9644 | 1197503.9852 | 2575528.9406 | 1197502.7606
23 | 2575533.2962 | 1197557.8359 | 2575531.6032 | 1197559.8597
24 | 2575514.4942 | 1197447.3133 | 2575524.0982 | 1197452.0402
25 | 2575466.7032 | 1197455.6927 | 2575480.1599 | 1197441.3741
26 | 2575482.5659 | 1197493.9865 | 2575478.025 | 1197490.5209
27 | 2575488.0532 | 1197421.3817 | 2575491.977 | 1197420.3469 | 2575505.5381 | 1197421.5765
28 | 2575514.4942 | 1197447.3133 | 2575509.8132 | 1197444.9199
29 | 2575509.8132 | 1197444.9199 | 2575505.6864 | 1197442.8098
30 | 2575489.4135 | 1197437.7669 | 2575485.3066 | 1197439.1474
31 | 2575489.4135 | 1197437.7669 | 2575497.7661 | 1197439.8784
32 | 2575480.1599 | 1197441.3741 | 2575480.8422 | 1197440.6482 | 2575485.3066 | 1197439.1474
33 | 2575505.6864 | 1197442.8098 | 2575502.0921 | 1197440.972 | 2575497.7661 | 1197439.8784
34 | 2575488.3969 | 1197498.4368 | 2575492.451 | 1197501.531
35 | 2575488.3969 | 1197498.4368 | 2575488.0177 | 1197498.1474
36 | 2575488.0177 | 1197498.1474 | 2575484.2041 | 1197495.2369
37 | 2575482.5659 | 1197493.9865 | 2575484.2041 | 1197495.2369
38 | 2575487.4808 | 1197421.5327 | 2575488.0532 | 1197421.3817

## bus_geodata
| x | y | coords
0 | 2575497.4166 | 1197530.5298
1 | 2575496.7703 | 1197531.1988
2 | 2575497.5265 | 1197530.4161
3 | 2575511.4334 | 1197516.0186
4 | 2575498.5328 | 1197506.1727
5 | 2575515.6211 | 1197519.47
6 | 2575554.4298 | 1197470.7842
7 | 2575582.8143 | 1197448.4668
8 | 2575533.5203 | 1197457.3927
9 | 2575450.2407 | 1197475.6265
10 | 2575466.6598 | 1197455.7389
11 | 2575472.4316 | 1197486.2519
12 | 2575522.8494 | 1197423.1462
13 | 2575544.4401 | 1197545.5323
14 | 2575534.087 | 1197556.8906
15 | 2575530.8672 | 1197533.2512
16 | 2575493.9986 | 1197502.7122
17 | 2575524.9317 | 1197527.886
18 | 2575527.9644 | 1197503.9852
19 | 2575531.6032 | 1197559.8597
20 | 2575533.2962 | 1197557.8359
21 | 2575528.9406 | 1197502.7606
22 | 2575524.0982 | 1197452.0402
23 | 2575466.7032 | 1197455.6927
24 | 2575478.025 | 1197490.5209
25 | 2575505.5381 | 1197421.5765
26 | 2575514.4942 | 1197447.3133
27 | 2575509.8132 | 1197444.9199
28 | 2575489.4135 | 1197437.7669
29 | 2575485.3066 | 1197439.1474
30 | 2575497.7661 | 1197439.8784
31 | 2575492.451 | 1197501.531
32 | 2575488.3969 | 1197498.4368
33 | 2575488.0177 | 1197498.1474
34 | 2575484.2041 | 1197495.2369
35 | 2575482.5659 | 1197493.9865
36 | 2575505.6864 | 1197442.8098
37 | 2575480.1599 | 1197441.3741
38 | 2575488.0532 | 1197421.3817
39 | 2575487.4808 | 1197421.5327
40 | 2575450.2407 | 1197475.6265

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99809 | -0.036812 | 0.030269 | 0.0075861
1 | 0.99807 | -0.037166 | 0.021767 | 0.0054554
2 | 0.99809 | -0.036668 | 0.052861 | 0.013248
3 | 1 | 0 | -0.41293 | -0.10359
4 | 0.9989 | -0.021088 | 0.0070678 | 0.0017714
5 | 0.99962 | -0.0073735 | 0 | 0
6 | 0.99036 | -0.18556 | 0 | 0
7 | 0.98977 | -0.19702 | 0 | 0
8 | 0.99066 | -0.17971 | 0.003908 | 0.00097944
9 | 0.99483 | -0.099189 | 0 | 0
10 | 0.99336 | -0.12759 | 0.0068581 | 0.0017188
11 | 0.99623 | -0.072183 | 0.010687 | 0.0026783
12 | 0.98898 | -0.21243 | 0.0037958 | 0.00095132
13 | 0.99623 | -0.072424 | 0 | 0
14 | 0.99515 | -0.093334 | 0.02137 | 0.0053557
15 | 0.99752 | -0.047643 | 0.020565 | 0.005154
16 | 0.99853 | -0.028159 | 0.0058101 | 0.0014561
17 | 0.99823 | -0.033952 | 0.023485 | 0.0058858
18 | 0.99899 | -0.019423 | 0.022696 | 0.0056881
19 | 0.99502 | -0.095838 | 0.027849 | 0.0069796
20 | 0.99508 | -0.094545 | 0.027972 | 0.0070104
21 | 0.99897 | -0.019756 | 0.012166 | 0.0030491
22 | 0.99083 | -0.1764 | 0.009277 | 0.002325
23 | 0.99335 | -0.12765 | 0.0042225 | 0.0010583
24 | 0.99671 | -0.063155 | 0.0053999 | 0.0013533
25 | 0.98883 | -0.21536 | 0.0034618 | 0.00086762
26 | 0.99109 | -0.17137 | 0.004083 | 0.0010233
27 | 0.99124 | -0.16852 | 0.0047973 | 0.0012023
28 | 0.99202 | -0.15341 | 0 | 0
29 | 0.99219 | -0.15018 | 0.0044699 | 0.0011203
30 | 0.99169 | -0.15983 | 0.0036598 | 0.00091724
31 | 0.99829 | -0.032791 | 0.018452 | 0.0046245
32 | 0.99774 | -0.043287 | 0.0071581 | 0.001794
33 | 0.99769 | -0.04421 | 0.014326 | 0.0035904
34 | 0.99727 | -0.052288 | 0.013018 | 0.0032627
35 | 0.99711 | -0.055291 | 0.0046117 | 0.0011558
36 | 0.99139 | -0.16562 | 0.0030575 | 0.00076629
37 | 0.99243 | -0.14549 | 0.0048025 | 0.0012036
38 | 0.98873 | -0.21726 | 0.0038824 | 0.00097301
39 | 0.98873 | -0.21728 | 0.0021287 | 0.0005335
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.021768 | 0.0054556 | -0.021767 | -0.0054554 | 3.6739e-07 | 2.2297e-07 | 0.032453 | 0.032453 | 0.032453 | 0.99809 | -0.036812 | 0.99807 | -0.037166 | 8.9156
1 | -0.052037 | -0.013042 | 0.052037 | 0.013042 | 3.5679e-07 | 2.2628e-07 | 0.07758 | 0.07758 | 0.07758 | 0.99809 | -0.036812 | 0.99809 | -0.036668 | 21.3132
2 | -0.1049 | -0.02629 | 0.10508 | 0.026408 | 0.00018359 | 0.00011723 | 0.15639 | 0.15639 | 0.15639 | 0.99809 | -0.036668 | 1 | 0 | 42.964
3 | 0.14963 | 0.037767 | -0.14948 | -0.03767 | 0.00015097 | 9.6197e-05 | 0.22274 | 0.22274 | 0.22274 | 1 | 0 | 0.9989 | -0.021088 | 30.5968
4 | 0.15657 | 0.039421 | -0.15651 | -0.039385 | 5.517e-05 | 3.5167e-05 | 0.23304 | 0.23304 | 0.23304 | 1 | 0 | 0.99962 | -0.0073735 | 32.0111
5 | 0.14241 | 0.035899 | -0.14236 | -0.035868 | 4.8165e-05 | 3.0676e-05 | 0.21222 | 0.21222 | 0.21222 | 0.9989 | -0.021088 | 0.99853 | -0.028159 | 29.1506
6 | 0.12163 | 0.030636 | -0.12148 | -0.030537 | 0.00015438 | 9.864e-05 | 0.18111 | 0.18111 | 0.18111 | 0.99962 | -0.0073735 | 0.99823 | -0.033952 | 49.7564
7 | 0.034882 | 0.0087499 | -0.034862 | -0.0087373 | 2.0024e-05 | 1.2556e-05 | 0.051928 | 0.051928 | 0.051928 | 0.99962 | -0.0073735 | 0.99899 | -0.019423 | 14.2659
8 | 0.013288 | 0.0033356 | -0.01328 | -0.0033316 | 7.2597e-06 | 4.0217e-06 | 0.019966 | 0.019967 | 0.019967 | 0.99036 | -0.18556 | 0.98977 | -0.19702 | 5.4854
9 | -0.013288 | -0.0033356 | 0.013291 | 0.0033377 | 3.712e-06 | 2.0561e-06 | 0.019966 | 0.019966 | 0.019966 | 0.99036 | -0.18556 | 0.99066 | -0.17971 | 5.4853
10 | 0.01328 | 0.0033316 | -0.013271 | -0.0033262 | 9.746e-06 | 5.4003e-06 | 0.019967 | 0.019967 | 0.019967 | 0.98977 | -0.19702 | 0.98898 | -0.21243 | 5.4854
11 | -0.017199 | -0.0043171 | 0.017202 | 0.0043187 | 2.7168e-06 | 1.599e-06 | 0.025836 | 0.025836 | 0.025836 | 0.99066 | -0.17971 | 0.99083 | -0.1764 | 7.0979
12 | 0.062614 | 0.015771 | -0.062529 | -0.015717 | 8.4915e-05 | 5.4011e-05 | 0.093683 | 0.093683 | 0.093683 | 0.99483 | -0.099189 | 0.99336 | -0.12759 | 25.7371
13 | -0.062614 | -0.015771 | 0.062695 | 0.015822 | 8.0975e-05 | 5.1504e-05 | 0.093683 | 0.093683 | 0.093683 | 0.99483 | -0.099189 | 0.99623 | -0.072183 | 25.7371
14 | 0.055671 | 0.013998 | -0.055671 | -0.013998 | 1.6539e-07 | 1.0502e-07 | 0.08341 | 0.08341 | 0.08341 | 0.99336 | -0.12759 | 0.99335 | -0.12765 | 22.9148
15 | -0.073382 | -0.018501 | 0.073414 | 0.018521 | 3.1722e-05 | 2.021e-05 | 0.10964 | 0.10964 | 0.10964 | 0.99623 | -0.072183 | 0.99671 | -0.063155 | 30.1222
16 | 0.0094747 | 0.0023749 | -0.0094734 | -0.0023742 | 1.3247e-06 | 6.2481e-07 | 0.014256 | 0.014256 | 0.014256 | 0.98898 | -0.21243 | 0.98883 | -0.21536 | 3.9164
17 | 0.077273 | 0.019398 | -0.077196 | -0.019349 | 7.6984e-05 | 4.9069e-05 | 0.11543 | 0.11543 | 0.11543 | 0.99623 | -0.072424 | 0.99515 | -0.093334 | 31.7113
18 | -0.077273 | -0.019398 | 0.077364 | 0.019456 | 9.1457e-05 | 5.8294e-05 | 0.11543 | 0.11543 | 0.11543 | 0.99623 | -0.072424 | 0.99752 | -0.047643 | 31.7113
19 | 0.055826 | 0.013993 | -0.055823 | -0.013991 | 3.2206e-06 | 2.0452e-06 | 0.083476 | 0.083476 | 0.083476 | 0.99515 | -0.093334 | 0.99508 | -0.094545 | 22.9329
20 | -0.097929 | -0.02461 | 0.097993 | 0.024651 | 6.4048e-05 | 4.0886e-05 | 0.14611 | 0.14611 | 0.14611 | 0.99752 | -0.047643 | 0.99823 | -0.033952 | 40.139
21 | 0.13655 | 0.034412 | -0.13652 | -0.034393 | 3.0251e-05 | 1.9335e-05 | 0.20356 | 0.20356 | 0.20356 | 0.99853 | -0.028159 | 0.99829 | -0.032791 | 55.9226
22 | 0.012166 | 0.0030492 | -0.012166 | -0.0030491 | 1.9286e-07 | 1.0293e-07 | 0.018122 | 0.018122 | 0.018122 | 0.99899 | -0.019423 | 0.99897 | -0.019756 | 4.9785
23 | -0.027849 | -0.0069796 | 0.027851 | 0.0069807 | 1.7162e-06 | 1.0641e-06 | 0.041647 | 0.041647 | 0.041647 | 0.99502 | -0.095838 | 0.99508 | -0.094545 | 11.4416
24 | -0.026479 | -0.0066437 | 0.026485 | 0.0066476 | 6.3484e-06 | 3.925e-06 | 0.039768 | 0.039768 | 0.039768 | 0.99083 | -0.1764 | 0.99109 | -0.17137 | 10.9254
25 | 0.051449 | 0.01294 | -0.051405 | -0.012912 | 4.3785e-05 | 2.7768e-05 | 0.077085 | 0.077085 | 0.077085 | 0.99335 | -0.12765 | 0.99243 | -0.14549 | 21.1771
26 | -0.078813 | -0.019874 | 0.078843 | 0.019893 | 2.9678e-05 | 1.892e-05 | 0.11771 | 0.11771 | 0.11771 | 0.99671 | -0.063155 | 0.99711 | -0.055291 | 32.3369
27 | 0.0060116 | 0.0015066 | -0.006011 | -0.0015065 | 5.4242e-07 | 1.2045e-07 | 0.0090464 | 0.0090465 | 0.0090465 | 0.98883 | -0.21536 | 0.98873 | -0.21726 | 2.4853
28 | -0.030568 | -0.0076709 | 0.030573 | 0.0076735 | 4.1534e-06 | 2.5904e-06 | 0.045898 | 0.045898 | 0.045898 | 0.99109 | -0.17137 | 0.99124 | -0.16852 | 12.6095
29 | -0.03537 | -0.0088758 | 0.035375 | 0.0088789 | 4.9008e-06 | 3.0768e-06 | 0.0531 | 0.0531 | 0.0531 | 0.99124 | -0.16852 | 0.99139 | -0.16562 | 14.5879
30 | -0.042116 | -0.010577 | 0.042122 | 0.010581 | 6.4858e-06 | 4.095e-06 | 0.06318 | 0.06318 | 0.06318 | 0.99202 | -0.15341 | 0.99219 | -0.15018 | 17.3573
31 | 0.042116 | 0.010577 | -0.042103 | -0.010569 | 1.2896e-05 | 8.1425e-06 | 0.06318 | 0.063181 | 0.063181 | 0.99202 | -0.15341 | 0.99169 | -0.15983 | 17.3573
32 | -0.046592 | -0.011702 | 0.046602 | 0.011708 | 1.045e-05 | 6.6145e-06 | 0.069884 | 0.069884 | 0.069884 | 0.99219 | -0.15018 | 0.99243 | -0.14549 | 19.1989
33 | 0.038443 | 0.0096519 | -0.038432 | -0.0096452 | 1.0607e-05 | 6.6787e-06 | 0.057689 | 0.057689 | 0.057689 | 0.99169 | -0.15983 | 0.99139 | -0.16562 | 15.8486
34 | 0.11807 | 0.029768 | -0.11801 | -0.02973 | 5.9278e-05 | 3.7871e-05 | 0.17605 | 0.17605 | 0.17605 | 0.99829 | -0.032791 | 0.99774 | -0.043287 | 48.3665
35 | 0.11085 | 0.027936 | -0.11085 | -0.027933 | 4.8918e-06 | 3.1246e-06 | 0.16538 | 0.16538 | 0.16538 | 0.99774 | -0.043287 | 0.99769 | -0.04421 | 45.4337
36 | 0.096522 | 0.024343 | -0.096485 | -0.024319 | 3.7311e-05 | 2.3816e-05 | 0.14401 | 0.14401 | 0.14401 | 0.99769 | -0.04421 | 0.99727 | -0.052288 | 39.5639
37 | 0.083467 | 0.021057 | -0.083455 | -0.021049 | 1.1996e-05 | 7.6507e-06 | 0.12459 | 0.12459 | 0.12459 | 0.99727 | -0.052288 | 0.99711 | -0.055291 | 34.2276
38 | 0.0021287 | 0.00053349 | -0.0021287 | -0.00053349 | 2.2785e-09 | -6.1345e-09 | 0.0032036 | 0.0032036 | 0.0032036 | 0.98873 | -0.21726 | 0.98873 | -0.21728 | 0.88011

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41293 | 0.10359

## res_load
| p_mw | q_mvar
0 | 0.030269 | 0.0075861
1 | 0.021767 | 0.0054554
2 | 0.052861 | 0.013248
3 | 0.0070678 | 0.0017714
4 | 0.003908 | 0.00097944
5 | 0.0068581 | 0.0017188
6 | 0.010687 | 0.0026783
7 | 0.0037958 | 0.00095132
8 | 0.02137 | 0.0053557
9 | 0.020565 | 0.005154
10 | 0.0058101 | 0.0014561
11 | 0.023485 | 0.0058858
12 | 0.022696 | 0.0056881
13 | 0.027849 | 0.0069796
14 | 0.027972 | 0.0070104
15 | 0.012166 | 0.0030491
16 | 0.009277 | 0.002325
17 | 0.0042225 | 0.0010583
18 | 0.0053999 | 0.0013533
19 | 0.0034618 | 0.00086762
20 | 0.004083 | 0.0010233
21 | 0.0047973 | 0.0012023
22 | 0.0044699 | 0.0011203
23 | 0.0036598 | 0.00091724
24 | 0.018452 | 0.0046245
25 | 0.0071581 | 0.001794
26 | 0.014326 | 0.0035904
27 | 0.013018 | 0.0032627
28 | 0.0046117 | 0.0011558
29 | 0.0030575 | 0.00076629
30 | 0.0048025 | 0.0012036
31 | 0.0038824 | 0.00097301
32 | 0.0021287 | 0.0005335

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1