## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-100_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-100_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-100_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-100_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-100_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-100_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_230-100_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_230-100_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_230-100_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_230-100_0_5_node_56 | 0.4 | n |  | TRUE
10 | bus_LV_230-100_0_5_node_46 | 0.4 | n |  | TRUE
11 | bus_LV_230-100_0_5_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_230-100_0_5_node_50 | 0.4 | n |  | TRUE
13 | bus_LV_230-100_0_5_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_230-100_0_5_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_230-100_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_230-100_0_5_node_54 | 0.4 | n |  | TRUE
17 | bus_LV_230-100_0_5_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_230-100_0_5_node_74 | 0.4 | n |  | TRUE
19 | bus_LV_230-100_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_230-100_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_230-100_0_5_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_230-100_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_230-100_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_230-100_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_230-100_0_5_node_118 | 0.4 | n |  | TRUE
26 | bus_LV_230-100_0_5_node_161 | 0.4 | n |  | TRUE
27 | bus_LV_230-100_0_5_node_120 | 0.4 | n |  | TRUE
28 | bus_LV_230-100_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_230-100_0_5_node_119 | 0.4 | n |  | TRUE
30 | bus_LV_230-100_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_230-100_0_5_node_78 | 0.4 | n |  | TRUE
32 | bus_LV_230-100_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_230-100_0_5_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_230-100_0_5_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_230-100_0_5_node_81 | 0.4 | n |  | TRUE
36 | bus_LV_230-100_0_5_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_230-100_0_5_node_127 | 0.4 | n |  | TRUE
38 | bus_LV_230-100_0_5_node_124 | 0.4 | n |  | TRUE
39 | bus_LV_230-100_0_5_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_230-100_0_5_node_143 | 0.4 | n |  | TRUE
41 | bus_LV_230-100_0_5_node_134 | 0.4 | n |  | TRUE
42 | bus_LV_230-100_0_5_node_138 | 0.4 | n |  | TRUE
43 | bus_LV_230-100_0_5_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_230-100_0_5_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_230-100_0_5_node_75 | 0.4 | n |  | TRUE
46 | bus_LV_230-100_0_5_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_230-100_0_5_node_146 | 0.4 | n |  | TRUE
48 | bus_LV_230-100_0_5_node_145 | 0.4 | n |  | TRUE
49 | bus_LV_230-100_0_5_node_77 | 0.4 | n |  | TRUE
50 | bus_LV_230-100_0_5_node_82 | 0.4 | n |  | TRUE
51 | bus_LV_230-100_0_5_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_230-100_0_5_node_156 | 0.4 | n |  | TRUE
53 | bus_LV_230-100_0_5_node_157 | 0.4 | n |  | TRUE
54 | bus_LV_230-100_0_5_node_154 | 0.4 | n |  | TRUE
55 | bus_LV_230-100_0_5_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_230-100_0_5_node_106 | 0.4 | n |  | TRUE
57 | bus_LV_230-100_0_5_node_151 | 0.4 | n |  | TRUE
58 | bus_LV_230-100_0_5_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_230-100_0_5_node_153 | 0.4 | n |  | TRUE
60 | bus_LV_230-100_0_5_node_31 | 0.4 | n |  | TRUE
61 | bus_LV_230-100_0_5_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_230-100_0_5_node_103 | 0.4 | n |  | TRUE
63 | bus_LV_230-100_0_5_node_32 | 0.4 | n |  | TRUE
64 | bus_LV_230-100_0_5_node_33 | 0.4 | n |  | TRUE
65 | bus_LV_230-100_0_5_node_149 | 0.4 | n |  | TRUE
66 | bus_LV_230-100_0_5_node_147 | 0.4 | n |  | TRUE
67 | bus_LV_230-100_0_5_node_121 | 0.4 | n |  | TRUE
68 | bus_LV_230-100_0_5_node_79 | 0.4 | n |  | TRUE
69 | bus_LV_230-100_0_5_node_85 | 0.4 | n |  | TRUE
70 | bus_LV_230-100_0_5_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_230-100_0_5_node_129 | 0.4 | n |  | TRUE
72 | bus_LV_230-100_0_5_node_125 | 0.4 | n |  | TRUE
73 | bus_LV_230-100_0_5_node_137 | 0.4 | n |  | TRUE
74 | bus_LV_230-100_0_5_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_230-100_0_5_node_144 | 0.4 | n |  | TRUE
76 | bus_LV_230-100_0_5_node_152 | 0.4 | n |  | TRUE
77 | bus_LV_230-100_0_5_node_150 | 0.4 | n |  | TRUE
78 | bus_LV_230-100_0_5_node_48 | 0.4 | n |  | TRUE
79 | bus_LV_230-100_0_5_node_102 | 0.4 | n |  | TRUE
80 | bus_LV_230-100_0_5_node_155 | 0.4 | n |  | TRUE
81 | bus_LV_230-100_0_5_node_135 | 0.4 | n |  | TRUE
82 | bus_LV_230-100_0_5_node_148 | 0.4 | n |  | TRUE
83 | bus_LV_230-100_0_5_node_34 | 0.4 | n |  | TRUE
84 | bus_LV_230-100_0_5_node_35 | 0.4 | n |  | TRUE
85 | bus_LV_230-100_0_5_node_36 | 0.4 | n |  | TRUE
86 | bus_LV_230-100_0_5_node_37 | 0.4 | n |  | TRUE
87 | bus_LV_230-100_0_5_node_38 | 0.4 | n |  | TRUE
88 | bus_LV_230-100_0_5_node_39 | 0.4 | n |  | TRUE
89 | bus_LV_230-100_0_5_node_40 | 0.4 | n |  | TRUE
90 | bus_LV_230-100_0_5_node_41 | 0.4 | n |  | TRUE
91 | bus_LV_230-100_0_5_node_53 | 0.4 | n |  | TRUE
92 | bus_LV_230-100_0_5_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_230-100_0_5_node_63 | 0.4 | n |  | TRUE
94 | bus_LV_230-100_0_5_node_91 | 0.4 | n |  | TRUE
95 | bus_LV_230-100_0_5_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_230-100_0_5_node_42 | 0.4 | n |  | TRUE
97 | bus_LV_230-100_0_5_node_43 | 0.4 | n |  | TRUE
98 | bus_LV_230-100_0_5_node_45 | 0.4 | n |  | TRUE
99 | bus_LV_230-100_0_5_node_55 | 0.4 | n |  | TRUE
100 | bus_LV_230-100_0_5_node_57 | 0.4 | n |  | TRUE
101 | bus_LV_230-100_0_5_node_58 | 0.4 | n |  | TRUE
102 | bus_LV_230-100_0_5_node_59 | 0.4 | n |  | TRUE
103 | bus_LV_230-100_0_5_node_61 | 0.4 | n |  | TRUE
104 | bus_LV_230-100_0_5_node_62 | 0.4 | n |  | TRUE
105 | bus_LV_230-100_0_5_node_64 | 0.4 | n |  | TRUE
106 | bus_LV_230-100_0_5_node_65 | 0.4 | n |  | TRUE
107 | bus_LV_230-100_0_5_node_66 | 0.4 | n |  | TRUE
108 | bus_LV_230-100_0_5_node_67 | 0.4 | n |  | TRUE
109 | bus_LV_230-100_0_5_node_69 | 0.4 | n |  | TRUE
110 | bus_LV_230-100_0_5_node_70 | 0.4 | n |  | TRUE
111 | bus_LV_230-100_0_5_node_72 | 0.4 | n |  | TRUE
112 | bus_LV_230-100_0_5_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_230-100_0_5_node_71 | 0.4 | n |  | TRUE
114 | bus_LV_230-100_0_5_node_87 | 0.4 | n |  | TRUE
115 | bus_LV_230-100_0_5_node_73 | 0.4 | n |  | TRUE
116 | bus_LV_230-100_0_5_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_230-100_0_5_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_230-100_0_5_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_230-100_0_5_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_230-100_0_5_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_230-100_0_5_node_101 | 0.4 | n |  | TRUE
122 | bus_LV_230-100_0_5_node_160 | 0.4 | n |  | TRUE
123 | bus_LV_230-100_0_5_node_88 | 0.4 | n |  | TRUE
124 | bus_LV_230-100_0_5_node_89 | 0.4 | n |  | TRUE
125 | bus_LV_230-100_0_5_node_90 | 0.4 | n |  | TRUE
126 | bus_LV_230-100_0_5_node_92 | 0.4 | n |  | TRUE
127 | bus_LV_230-100_0_5_node_95 | 0.4 | n |  | TRUE
128 | bus_LV_230-100_0_5_node_93 | 0.4 | n |  | TRUE
129 | bus_LV_230-100_0_5_node_97 | 0.4 | n |  | TRUE
130 | bus_LV_230-100_0_5_node_110 | 0.4 | n |  | TRUE
131 | bus_LV_230-100_0_5_node_96 | 0.4 | n |  | TRUE
132 | bus_LV_230-100_0_5_node_107 | 0.4 | n |  | TRUE
133 | bus_LV_230-100_0_5_node_98 | 0.4 | n |  | TRUE
134 | bus_LV_230-100_0_5_node_108 | 0.4 | n |  | TRUE
135 | bus_LV_230-100_0_5_node_105 | 0.4 | n |  | TRUE
136 | bus_LV_230-100_0_5_node_100 | 0.4 | n |  | TRUE
137 | bus_LV_230-100_0_5_node_99 | 0.4 | n |  | TRUE
138 | bus_LV_230-100_0_5_node_114 | 0.4 | n |  | TRUE
139 | bus_LV_230-100_0_5_node_158 | 0.4 | n |  | TRUE
140 | bus_LV_230-100_0_5_node_117 | 0.4 | n |  | TRUE
141 | bus_LV_230-100_0_5_node_104 | 0.4 | n |  | TRUE
142 | bus_LV_230-100_0_5_node_109 | 0.4 | n |  | TRUE
143 | bus_LV_230-100_0_5_node_159 | 0.4 | n |  | TRUE
144 | bus_LV_230-100_0_5_node_139 | 0.4 | n |  | TRUE
145 | bus_LV_230-100_0_5_node_142 | 0.4 | n |  | TRUE
146 | bus_LV_230-100_0_5_node_140 | 0.4 | n |  | TRUE
147 | bus_LV_230-100_0_5_node_141 | 0.4 | n |  | TRUE
148 | bus_LV_230-100_0_5_node_122 | 0.4 | n |  | TRUE
149 | bus_LV_230-100_0_5_node_123 | 0.4 | n |  | TRUE
150 | bus_LV_230-100_0_5_node_126 | 0.4 | n |  | TRUE
151 | bus_LV_230-100_0_5_node_128 | 0.4 | n |  | TRUE
152 | bus_LV_230-100_0_5_node_133 | 0.4 | n |  | TRUE
153 | bus_LV_230-100_0_5_node_130 | 0.4 | n |  | TRUE
154 | bus_LV_230-100_0_5_node_136 | 0.4 | n |  | TRUE
155 | bus_LV_230-100_0_5_node_131 | 0.4 | n |  | TRUE
156 | bus_MV_370_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-100_0_5_load_0 | 0 | 0.003559 | 0.00089196 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-100_0_5_load_1 | 1 | 0.0030127 | 0.00075505 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-100_0_5_load_3 | 3 | 0.0067931 | 0.0017025 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-100_0_5_load_4 | 4 | 0.0049081 | 0.0012301 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-100_0_5_load_5 | 5 | 0.0068029 | 0.001705 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-100_0_5_load_7 | 6 | 0.0031481 | 0.00078899 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-100_0_5_load_8 | 7 | 0.0069241 | 0.0017353 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-100_0_5_load_9 | 8 | 0.0022142 | 0.00055494 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-100_0_5_load_56 | 9 | 0.0034903 | 0.00087475 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-100_0_5_load_49 | 11 | 0.0056459 | 0.001415 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-100_0_5_load_50 | 12 | 0.0035473 | 0.00088903 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-100_0_5_load_52 | 14 | 0.0023221 | 0.00058196 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-100_0_5_load_54 | 16 | 0.0039858 | 0.00099893 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-100_0_5_load_74 | 18 | 0.0031426 | 0.00078762 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-100_0_5_load_11 | 19 | 0.007569 | 0.001897 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-100_0_5_load_118 | 25 | 0.0070664 | 0.001771 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-100_0_5_load_161 | 26 | 0.0070611 | 0.0017697 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-100_0_5_load_120 | 27 | 0.0057389 | 0.0014383 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-100_0_5_load_119 | 29 | 0.0063189 | 0.0015837 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-100_0_5_load_78 | 31 | 0.0029149 | 0.00073054 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-100_0_5_load_83 | 33 | 0.0019522 | 0.00048928 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-100_0_5_load_84 | 34 | 0.012555 | 0.0031467 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-100_0_5_load_81 | 35 | 0.0025037 | 0.00062749 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-100_0_5_load_124 | 38 | 0.0014377 | 0.00036032 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-100_0_5_load_143 | 40 | 0.001775 | 0.00044486 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-100_0_5_load_134 | 41 | 0.0014669 | 0.00036764 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-100_0_5_load_76 | 44 | 0.012426 | 0.0031143 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-100_0_5_load_75 | 45 | 0.0049595 | 0.001243 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-100_0_5_load_146 | 47 | 0.017345 | 0.0043471 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-100_0_5_load_77 | 49 | 0.014697 | 0.0036834 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-100_0_5_load_82 | 50 | 0.0021704 | 0.00054395 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-100_0_5_load_156 | 52 | 0.0013386 | 0.00033548 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-100_0_5_load_157 | 53 | 0.0012588 | 0.00031549 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-100_0_5_load_154 | 54 | 0.0010507 | 0.00026333 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-100_0_5_load_106 | 56 | 0.0023531 | 0.00058973 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-100_0_5_load_151 | 57 | 0.0021194 | 0.00053116 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-100_0_5_load_153 | 59 | 0.0012915 | 0.00032369 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-100_0_5_load_103 | 62 | 0.0026686 | 0.00066881 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-100_0_5_load_149 | 65 | 0.001333 | 0.00033407 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-100_0_5_load_121 | 67 | 0.0015862 | 0.00039754 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-100_0_5_load_79 | 68 | 0.0027064 | 0.00067829 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-100_0_5_load_80 | 70 | 0.0023752 | 0.00059528 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-100_0_5_load_129 | 71 | 0.0014665 | 0.00036755 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-100_0_5_load_125 | 72 | 0.0014679 | 0.00036788 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-100_0_5_load_137 | 73 | 0.0014665 | 0.00036755 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-100_0_5_load_68 | 74 | 0.0096584 | 0.0024206 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-100_0_5_load_144 | 75 | 0.012461 | 0.0031231 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-100_0_5_load_48 | 78 | 0.0034317 | 0.00086006 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-100_0_5_load_102 | 79 | 0.0095966 | 0.0024051 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-100_0_5_load_155 | 80 | 0.002308 | 0.00057844 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-100_0_5_load_148 | 82 | 0.0014895 | 0.0003733 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-100_0_5_load_34 | 83 | 0.0085441 | 0.0021413 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-100_0_5_load_35 | 84 | 0.0028629 | 0.00071752 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-100_0_5_load_36 | 85 | 0.0057537 | 0.001442 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-100_0_5_load_37 | 86 | 0.0065926 | 0.0016523 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-100_0_5_load_39 | 88 | 0.0023498 | 0.00058891 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-100_0_5_load_40 | 89 | 0.0030144 | 0.00075548 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-100_0_5_load_41 | 90 | 0.0064269 | 0.0016107 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-100_0_5_load_53 | 91 | 0.0065958 | 0.0016531 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-100_0_5_load_94 | 92 | 0.0034263 | 0.00085871 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-100_0_5_load_63 | 93 | 0.006546 | 0.0016406 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-100_0_5_load_91 | 94 | 0.0035021 | 0.00087771 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-100_0_5_load_42 | 96 | 0.0033263 | 0.00083365 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-100_0_5_load_43 | 97 | 0.0028412 | 0.00071206 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-100_0_5_load_45 | 98 | 0.0068502 | 0.0017168 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-100_0_5_load_55 | 99 | 0.0023968 | 0.00060071 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-100_0_5_load_57 | 100 | 0.0022129 | 0.0005546 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-100_0_5_load_58 | 101 | 0.0031019 | 0.00077741 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-100_0_5_load_59 | 102 | 0.0021064 | 0.00052791 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-100_0_5_load_61 | 103 | 0.0069452 | 0.0017406 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-100_0_5_load_62 | 104 | 0.0032257 | 0.00080845 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-100_0_5_load_64 | 105 | 0.0036018 | 0.00090269 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-100_0_5_load_67 | 108 | 0.017388 | 0.0043579 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-100_0_5_load_69 | 109 | 0.0038502 | 0.00096494 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-100_0_5_load_70 | 110 | 0.0033292 | 0.00083438 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-100_0_5_load_72 | 111 | 0.0015602 | 0.00039102 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-100_0_5_load_86 | 112 | 0.010063 | 0.0025221 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-100_0_5_load_71 | 113 | 0.0024632 | 0.00061735 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-100_0_5_load_87 | 114 | 0.0020645 | 0.00051742 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-100_0_5_load_73 | 115 | 0.0039606 | 0.00099261 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-100_0_5_load_112 | 116 | 0.0016048 | 0.00040221 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-100_0_5_load_113 | 117 | 0.0062179 | 0.0015584 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-100_0_5_load_115 | 118 | 0.0014661 | 0.00036743 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-100_0_5_load_116 | 119 | 0.0019278 | 0.00048315 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-100_0_5_load_111 | 120 | 0.0053608 | 0.0013435 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-100_0_5_load_160 | 122 | 0.0084754 | 0.0021241 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-100_0_5_load_88 | 123 | 0.0059288 | 0.0014859 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-100_0_5_load_89 | 124 | 0.0034209 | 0.00085735 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-100_0_5_load_95 | 127 | 0.0014202 | 0.00035594 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-100_0_5_load_93 | 128 | 0.0020725 | 0.00051942 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_230-100_0_5_load_110 | 130 | 0.0013305 | 0.00033346 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_230-100_0_5_load_96 | 131 | 0.006889 | 0.0017266 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_230-100_0_5_load_98 | 133 | 0.001894 | 0.00047468 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_230-100_0_5_load_108 | 134 | 0.0021643 | 0.00054243 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_230-100_0_5_load_105 | 135 | 0.0028756 | 0.00072068 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_230-100_0_5_load_100 | 136 | 0.0015036 | 0.00037683 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_230-100_0_5_load_99 | 137 | 0.0016211 | 0.00040628 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_230-100_0_5_load_114 | 138 | 0.0014666 | 0.00036755 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_230-100_0_5_load_158 | 139 | 0.0013035 | 0.00032669 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_230-100_0_5_load_109 | 142 | 0.0011828 | 0.00029643 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_230-100_0_5_load_159 | 143 | 0.0010329 | 0.00025887 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_230-100_0_5_load_142 | 145 | 0.0014666 | 0.00036755 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_230-100_0_5_load_140 | 146 | 0.0027651 | 0.000693 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_230-100_0_5_load_141 | 147 | 0.0014669 | 0.00036764 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_230-100_0_5_load_122 | 148 | 0.0018925 | 0.0004743 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_230-100_0_5_load_123 | 149 | 0.018561 | 0.0046519 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_230-100_0_5_load_126 | 150 | 0.0025441 | 0.00063762 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_230-100_0_5_load_133 | 152 | 0.0010698 | 0.00026811 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_230-100_0_5_load_130 | 153 | 0.0014665 | 0.00036755 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_230-100_0_5_load_136 | 154 | 0.0016619 | 0.0004165 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_230-100_0_5_load_131 | 155 | 0.0014665 | 0.00036755 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 112 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-100_0_5_line_0 |  | 0 | 1 | 0.01253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-100_0_5_line_1 |  | 0 | 2 | 0.012484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-100_0_5_line_2 |  | 1 | 3 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-100_0_5_line_3 |  | 2 | 4 | 0.01343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-100_0_5_line_4 |  | 2 | 5 | 0.030107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-100_0_5_line_5 |  | 3 | 6 | 0.0042818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-100_0_5_line_6 |  | 4 | 7 | 0.0015136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-100_0_5_line_7 |  | 6 | 8 | 0.028259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-100_0_5_line_8 |  | 7 | 9 | 0.031147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-100_0_5_line_9 |  | 8 | 15 | 0.023595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-100_0_5_line_10 |  | 9 | 16 | 0.023163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-100_0_5_line_11 |  | 10 | 11 | 0.017707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-100_0_5_line_12 |  | 10 | 12 | 0.031288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-100_0_5_line_13 |  | 11 | 91 | 0.0045459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-100_0_5_line_14 |  | 12 | 13 | 0.012191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-100_0_5_line_15 |  | 13 | 14 | 0.0052566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-100_0_5_line_16 |  | 15 | 17 | 0.02002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-100_0_5_line_17 |  | 16 | 99 | 0.0056592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-100_0_5_line_18 |  | 17 | 18 | 0.032792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-100_0_5_line_19 |  | 18 | 45 | 0.013978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-100_0_5_line_20 |  | 19 | 20 | 0.018474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-100_0_5_line_21 |  | 20 | 21 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-100_0_5_line_22 |  | 20 | 22 | 0.032792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-100_0_5_line_23 |  | 21 | 49 | 0.02832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-100_0_5_line_24 |  | 21 | 43 | 0.003314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-100_0_5_line_25 |  | 22 | 26 | 0.020244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-100_0_5_line_26 |  | 23 | 24 | 0.035659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-100_0_5_line_27 |  | 23 | 25 | 0.023765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-100_0_5_line_28 |  | 24 | 27 | 0.013291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-100_0_5_line_29 |  | 24 | 28 | 0.026126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-100_0_5_line_30 |  | 24 | 29 | 0.023096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-100_0_5_line_31 |  | 27 | 67 | 0.015429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-100_0_5_line_32 |  | 28 | 30 | 0.011929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-100_0_5_line_33 |  | 28 | 31 | 0.0012793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-100_0_5_line_34 |  | 30 | 50 | 0.010465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-100_0_5_line_35 |  | 30 | 46 | 0.017356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-100_0_5_line_36 |  | 31 | 68 | 0.0097687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-100_0_5_line_37 |  | 32 | 33 | 0.020178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-100_0_5_line_38 |  | 32 | 34 | 0.017985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-100_0_5_line_39 |  | 32 | 35 | 0.014059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-100_0_5_line_40 |  | 33 | 69 | 0.024216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_230-100_0_5_line_41 |  | 35 | 70 | 0.011037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-100_0_5_line_42 |  | 36 | 37 | 0.004495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_230-100_0_5_line_43 |  | 36 | 38 | 0.0081059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_230-100_0_5_line_44 |  | 37 | 71 | 0.0084679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_230-100_0_5_line_45 |  | 38 | 72 | 0.00013472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_230-100_0_5_line_46 |  | 39 | 40 | 0.014428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_230-100_0_5_line_47 |  | 39 | 41 | 0.0078406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-100_0_5_line_48 |  | 39 | 42 | 0.002895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_230-100_0_5_line_49 |  | 40 | 63 | 0.0073667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_230-100_0_5_line_50 |  | 42 | 73 | 0.0085213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_230-100_0_5_line_51 |  | 43 | 44 | 0.017876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-100_0_5_line_52 |  | 43 | 45 | 0.032605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-100_0_5_line_53 |  | 44 | 74 | 0.004534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-100_0_5_line_54 |  | 46 | 47 | 0.039478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-100_0_5_line_55 |  | 46 | 48 | 0.017015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-100_0_5_line_56 |  | 47 | 66 | 0.026745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-100_0_5_line_57 |  | 48 | 75 | 0.0024475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-100_0_5_line_58 |  | 51 | 52 | 0.01404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_230-100_0_5_line_59 |  | 51 | 53 | 0.014168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-100_0_5_line_60 |  | 51 | 54 | 0.0075926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_230-100_0_5_line_61 |  | 52 | 76 | 0.014474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_230-100_0_5_line_62 |  | 53 | 58 | 0.007698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-100_0_5_line_63 |  | 54 | 63 | 0.014338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_230-100_0_5_line_64 |  | 55 | 56 | 0.012964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-100_0_5_line_65 |  | 55 | 57 | 0.0076454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-100_0_5_line_66 |  | 57 | 77 | 0.014068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-100_0_5_line_67 |  | 58 | 59 | 0.015128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-100_0_5_line_68 |  | 59 | 77 | 0.013206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-100_0_5_line_69 |  | 60 | 61 | 0.025922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-100_0_5_line_70 |  | 60 | 62 | 0.017512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-100_0_5_line_71 |  | 61 | 78 | 0.016328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-100_0_5_line_72 |  | 62 | 79 | 0.0085067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-100_0_5_line_73 |  | 64 | 65 | 0.01577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-100_0_5_line_74 |  | 64 | 66 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-100_0_5_line_75 |  | 66 | 82 | 0.015602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-100_0_5_line_76 |  | 67 | 148 | 0.0030238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-100_0_5_line_77 |  | 68 | 70 | 0.015593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-100_0_5_line_78 |  | 69 | 116 | 0.01173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_230-100_0_5_line_79 |  | 69 | 117 | 0.022515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-100_0_5_line_80 |  | 71 | 73 | 0.0066202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_230-100_0_5_line_81 |  | 72 | 150 | 0.011265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_230-100_0_5_line_82 |  | 74 | 107 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_230-100_0_5_line_83 |  | 76 | 143 | 0.0078219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-100_0_5_line_84 |  | 76 | 130 | 0.011987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_230-100_0_5_line_85 |  | 77 | 142 | 0.010186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-100_0_5_line_86 |  | 78 | 98 | 0.0098479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-100_0_5_line_87 |  | 79 | 141 | 0.0064382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-100_0_5_line_88 |  | 80 | 81 | 0.012538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-100_0_5_line_89 |  | 81 | 139 | 0.012736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-100_0_5_line_90 |  | 81 | 136 | 0.010686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-100_0_5_line_91 |  | 83 | 84 | 0.020588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-100_0_5_line_92 |  | 83 | 85 | 0.0023351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-100_0_5_line_93 |  | 84 | 86 | 0.0061962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-100_0_5_line_94 |  | 85 | 87 | 0.014862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-100_0_5_line_95 |  | 86 | 88 | 0.003059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-100_0_5_line_96 |  | 87 | 89 | 0.033193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_230-100_0_5_line_97 |  | 87 | 90 | 0.0054829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_230-100_0_5_line_98 |  | 88 | 91 | 0.013249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-100_0_5_line_99 |  | 89 | 92 | 0.0011294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_230-100_0_5_line_100 |  | 90 | 93 | 0.011723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_230-100_0_5_line_101 |  | 92 | 94 | 0.012986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_230-100_0_5_line_102 |  | 93 | 95 | 0.0055933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_230-100_0_5_line_103 |  | 94 | 124 | 0.00055415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_230-100_0_5_line_104 |  | 95 | 104 | 0.012569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_230-100_0_5_line_105 |  | 95 | 101 | 0.033076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-100_0_5_line_106 |  | 96 | 97 | 0.0058482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-100_0_5_line_107 |  | 97 | 98 | 0.010525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-100_0_5_line_108 |  | 99 | 100 | 0.0042934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-100_0_5_line_109 |  | 101 | 102 | 0.0011901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-100_0_5_line_110 |  | 102 | 103 | 0.0048665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-100_0_5_line_111 |  | 104 | 105 | 0.0034737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_230-100_0_5_line_112 |  | 105 | 106 | 0.02775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_230-100_0_5_line_113 |  | 106 | 107 | 0.014152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-100_0_5_line_114 |  | 106 | 108 | 0.022582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_230-100_0_5_line_115 |  | 107 | 109 | 0.024657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-100_0_5_line_116 |  | 108 | 110 | 0.01603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_230-100_0_5_line_117 |  | 109 | 111 | 0.0094403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-100_0_5_line_118 |  | 110 | 112 | 0.0078476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_230-100_0_5_line_119 |  | 111 | 113 | 0.00040202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-100_0_5_line_120 |  | 112 | 114 | 0.0048464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-100_0_5_line_121 |  | 113 | 115 | 0.003503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-100_0_5_line_122 |  | 114 | 122 | 0.0036959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-100_0_5_line_123 |  | 116 | 118 | 0.00061708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_230-100_0_5_line_124 |  | 117 | 119 | 0.0092914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-100_0_5_line_125 |  | 118 | 144 | 0.0057549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_230-100_0_5_line_126 |  | 120 | 121 | 0.013839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-100_0_5_line_127 |  | 121 | 138 | 0.011947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-100_0_5_line_128 |  | 121 | 137 | 0.005371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_230-100_0_5_line_129 |  | 123 | 124 | 0.0019264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_230-100_0_5_line_130 |  | 123 | 125 | 0.031578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_230-100_0_5_line_131 |  | 125 | 126 | 0.002285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_230-100_0_5_line_132 |  | 126 | 127 | 0.010909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_230-100_0_5_line_133 |  | 127 | 130 | 0.0075327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_230-100_0_5_line_134 |  | 128 | 129 | 0.0069493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-100_0_5_line_135 |  | 129 | 133 | 0.011942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-100_0_5_line_136 |  | 131 | 132 | 0.0053712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_230-100_0_5_line_137 |  | 132 | 134 | 0.012051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_230-100_0_5_line_138 |  | 132 | 135 | 0.012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_230-100_0_5_line_139 |  | 133 | 136 | 0.0078799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_230-100_0_5_line_140 |  | 134 | 142 | 0.008111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_230-100_0_5_line_141 |  | 135 | 141 | 0.0095095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_230-100_0_5_line_142 |  | 138 | 140 | 0.006527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_230-100_0_5_line_143 |  | 139 | 143 | 0.0015184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_230-100_0_5_line_144 |  | 140 | 145 | 0.012028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_230-100_0_5_line_145 |  | 144 | 146 | 0.0056179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_230-100_0_5_line_146 |  | 144 | 147 | 0.012411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_230-100_0_5_line_147 |  | 145 | 147 | 0.0066202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_230-100_0_5_line_148 |  | 146 | 154 | 0.0030942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_230-100_0_5_line_149 |  | 148 | 149 | 0.0056739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_230-100_0_5_line_150 |  | 150 | 151 | 0.0031602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
151 | LV_230-100_0_5_line_151 |  | 151 | 152 | 0.0013643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
152 | LV_230-100_0_5_line_152 |  | 151 | 153 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_230-100_0_5_line_153 |  | 152 | 154 | 0.0095209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_230-100_0_5_line_154 |  | 153 | 155 | 0.0066192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-100_0_5_trafo_86 | 0.63 MVA 20/0.4 kV | 156 | 112 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2695756.5076 | 1260892.4509 | 2695747.7841 | 1260901.4459
1 | 2695765.1985 | 1260883.4894 | 2695756.5076 | 1260892.4509
2 | 2695737.3847 | 1260912.1691 | 2695747.7841 | 1260901.4459
3 | 2695765.1985 | 1260883.4894 | 2695774.8409 | 1260892.838
4 | 2695765.1985 | 1260883.4894 | 2695785.9314 | 1260861.659
5 | 2695737.3847 | 1260912.1691 | 2695734.4037 | 1260915.2429
6 | 2695774.8409 | 1260892.838 | 2695775.9276 | 1260893.8916
7 | 2695715.8259 | 1260936.4772 | 2695723.6625 | 1260926.3185 | 2695734.4037 | 1260915.2429
8 | 2695775.9276 | 1260893.8916 | 2695790.8952 | 1260908.4032 | 2695794.1811 | 1260908.879 | 2695799.3591 | 1260904.1993
9 | 2695701.414 | 1260955.1597 | 2695715.8259 | 1260936.4772
10 | 2695816.5441 | 1260888.6679 | 2695799.3591 | 1260904.1993
11 | 2695891.5346 | 1260883.8247 | 2695884.23 | 1260890.4116 | 2695878.6984 | 1260896.0115
12 | 2695891.5346 | 1260883.8247 | 2695871.4274 | 1260859.8524
13 | 2695875.5037 | 1260899.2456 | 2695878.6984 | 1260896.0115
14 | 2695863.5927 | 1260850.5116 | 2695871.4274 | 1260859.8524
15 | 2695863.5927 | 1260850.5116 | 2695860.0674 | 1260846.6124
16 | 2695701.414 | 1260955.1597 | 2695688.4297 | 1260970.4287
17 | 2695816.5441 | 1260888.6679 | 2695820.7426 | 1260884.8734
18 | 2695688.4297 | 1260970.4287 | 2695712.0806 | 1260993.1431
19 | 2695712.0806 | 1260993.1431 | 2695722.1618 | 1261002.8251
20 | 2695738.2351 | 1261038.2447 | 2695751.5605 | 1261051.04
21 | 2695738.2351 | 1261038.2447 | 2695742.5763 | 1261033.5889 | 2695748.0754 | 1261027.7065
22 | 2695738.2351 | 1261038.2447 | 2695738.1163 | 1261038.1316 | 2695735.206 | 1261036.8056 | 2695733.2772 | 1261035.8403 | 2695730.8799 | 1261035.4123 | 2695728.0254 | 1261035.7553 | 2695723.9991 | 1261037.725 | 2695719.2593 | 1261041.8628 | 2695711.8283 | 1261050.2271
23 | 2695748.0754 | 1261027.7065 | 2695768.5392 | 1261047.2832
24 | 2695745.6782 | 1261025.4103 | 2695748.0754 | 1261027.7065
25 | 2695726.9697 | 1261063.7163 | 2695711.8283 | 1261050.2271
26 | 2695811.6538 | 1261112.9046 | 2695813.2514 | 1261114.3094 | 2695831.338 | 1261131.127 | 2695837.7205 | 1261137.2353
27 | 2695811.6538 | 1261112.9046 | 2695808.589 | 1261117.859 | 2695803.4151 | 1261124.1358 | 2695798.5042 | 1261129.0714 | 2695795.7869 | 1261129.9066
28 | 2695837.7205 | 1261137.2353 | 2695828.3345 | 1261146.6463
29 | 2695843.3273 | 1261118.6667 | 2695837.4322 | 1261124.7984 | 2695831.338 | 1261131.127 | 2695837.7205 | 1261137.2353
30 | 2695837.7205 | 1261137.2353 | 2695854.4698 | 1261153.1381
31 | 2695817.4394 | 1261157.5704 | 2695828.3345 | 1261146.6463
32 | 2695854.586 | 1261118.7269 | 2695851.9524 | 1261119.8629 | 2695848.6043 | 1261120.4425 | 2695845.431 | 1261120.0018 | 2695843.3273 | 1261118.6667
33 | 2695843.3273 | 1261118.6667 | 2695842.4009 | 1261117.7844
34 | 2695854.586 | 1261118.7269 | 2695862.2016 | 1261111.5498
35 | 2695854.586 | 1261118.7269 | 2695860.6714 | 1261124.5635 | 2695867.1131 | 1261130.7396
36 | 2695842.4009 | 1261117.7844 | 2695835.3267 | 1261111.0476
37 | 2695805.8606 | 1261082.9866 | 2695820.2548 | 1261068.8452
38 | 2695805.8606 | 1261082.9866 | 2695792.8645 | 1261070.5539
39 | 2695805.8606 | 1261082.9866 | 2695816.0419 | 1261092.6824
40 | 2695837.5291 | 1261051.8743 | 2695820.2548 | 1261068.8452
41 | 2695824.0346 | 1261100.294 | 2695816.0419 | 1261092.6824
42 | 2695879.8736 | 1261094.8951 | 2695882.8228 | 1261091.4957
43 | 2695879.8736 | 1261094.8951 | 2695874.1857 | 1261089.1199
44 | 2695882.8228 | 1261091.4957 | 2695888.7968 | 1261085.4944
45 | 2695874.1857 | 1261089.1199 | 2695874.0911 | 1261089.0239
46 | 2695901.4132 | 1261072.604 | 2695911.5875 | 1261062.3748
47 | 2695901.4132 | 1261072.604 | 2695895.9222 | 1261067.0072
48 | 2695901.4132 | 1261072.604 | 2695899.4789 | 1261074.7633
49 | 2695916.7825 | 1261057.1517 | 2695911.5875 | 1261062.3748
50 | 2695899.4789 | 1261074.7633 | 2695893.4673 | 1261080.8025
51 | 2695745.6782 | 1261025.4103 | 2695758.7398 | 1261013.2054
52 | 2695745.6782 | 1261025.4103 | 2695722.1618 | 1261002.8251
53 | 2695762.0526 | 1261010.1099 | 2695758.7398 | 1261013.2054
54 | 2695867.1131 | 1261130.7396 | 2695870.9306 | 1261126.3089 | 2695894.4981 | 1261102.3184
55 | 2695867.1131 | 1261130.7396 | 2695868.7713 | 1261136.7713 | 2695871.8346 | 1261141.6694 | 2695875.426 | 1261145.1415
56 | 2695913.2391 | 1261083.2376 | 2695907.6832 | 1261088.8966 | 2695894.4981 | 1261102.3184
57 | 2695875.426 | 1261145.1415 | 2695877.1878 | 1261146.8404
58 | 2695932.1772 | 1261041.5331 | 2695922.3874 | 1261031.4691
59 | 2695932.1772 | 1261041.5331 | 2695942.1656 | 1261031.4855
60 | 2695932.1772 | 1261041.5331 | 2695926.8473 | 1261046.9405
61 | 2695912.2953 | 1261021.0943 | 2695922.3874 | 1261031.4691
62 | 2695947.5928 | 1261026.0261 | 2695942.1656 | 1261031.4855
63 | 2695916.7825 | 1261057.1517 | 2695926.8473 | 1261046.9405
64 | 2695943.2637 | 1260990.4494 | 2695934.1824 | 1260981.198
65 | 2695943.2637 | 1260990.4494 | 2695937.8293 | 1260995.8271
66 | 2695927.8292 | 1261005.7226 | 2695937.8293 | 1260995.8271
67 | 2695947.5928 | 1261026.0261 | 2695937.0405 | 1261015.1855
68 | 2695927.8292 | 1261005.7226 | 2695937.0405 | 1261015.1855
69 | 2695945.2119 | 1260946.1007 | 2695928.264 | 1260926.4434
70 | 2695945.2119 | 1260946.1007 | 2695932.6997 | 1260958.3534
71 | 2695928.264 | 1260926.4434 | 2695915.9196 | 1260937.1313
72 | 2695932.6997 | 1260958.3534 | 2695926.6218 | 1260964.3052
73 | 2695936.271 | 1261082.3214 | 2695924.9947 | 1261071.2629
74 | 2695913.2391 | 1261083.2376 | 2695924.9947 | 1261071.2629
75 | 2695924.3048 | 1261094.2704 | 2695913.2391 | 1261083.2376
76 | 2695817.4394 | 1261157.5704 | 2695815.3041 | 1261159.7114
77 | 2695824.0346 | 1261100.294 | 2695835.3267 | 1261111.0476
78 | 2695837.5291 | 1261051.8743 | 2695845.7544 | 1261060.2365
79 | 2695837.5291 | 1261051.8743 | 2695821.736 | 1261035.8278
80 | 2695888.7968 | 1261085.4944 | 2695893.4673 | 1261080.8025
81 | 2695866.1868 | 1261080.9981 | 2695874.0911 | 1261089.0239
82 | 2695774.9111 | 1260998.0947 | 2695762.0526 | 1261010.1099
83 | 2695912.2953 | 1261021.0943 | 2695906.7344 | 1261026.595
84 | 2695912.2953 | 1261021.0943 | 2695903.9343 | 1261012.504
85 | 2695927.8292 | 1261005.7226 | 2695920.7255 | 1260998.4225
86 | 2695908.8388 | 1260938.1956 | 2695911.3702 | 1260941.0702 | 2695915.9196 | 1260937.1313
87 | 2695922.0219 | 1260968.8097 | 2695926.6218 | 1260964.3052
88 | 2695896.6006 | 1261036.6191 | 2695905.3894 | 1261045.5606
89 | 2695896.6006 | 1261036.6191 | 2695905.6549 | 1261027.6629
90 | 2695896.6006 | 1261036.6191 | 2695889.1162 | 1261028.992
91 | 2695845.2208 | 1260929.9022 | 2695859.689 | 1260915.2554
92 | 2695845.2208 | 1260929.9022 | 2695843.5798 | 1260931.5634
93 | 2695859.689 | 1260915.2554 | 2695864.0435 | 1260910.8472
94 | 2695833.1354 | 1260942.1367 | 2695843.5798 | 1260931.5634
95 | 2695866.1932 | 1260908.671 | 2695864.0435 | 1260910.8472
96 | 2695833.1354 | 1260942.1367 | 2695856.1013 | 1260966.1026
97 | 2695833.1354 | 1260942.1367 | 2695829.2822 | 1260946.0374
98 | 2695875.5037 | 1260899.2456 | 2695866.1932 | 1260908.671
99 | 2695856.1013 | 1260966.1026 | 2695856.8827 | 1260966.918
100 | 2695829.2822 | 1260946.0374 | 2695821.0437 | 1260954.3777
101 | 2695856.8827 | 1260966.918 | 2695865.8677 | 1260976.2943
102 | 2695817.1129 | 1260958.357 | 2695821.0437 | 1260954.3777
103 | 2695865.8677 | 1260976.2943 | 2695866.2511 | 1260976.6945
104 | 2695817.1129 | 1260958.357 | 2695807.9619 | 1260966.9726
105 | 2695817.1129 | 1260958.357 | 2695793.2707 | 1260935.4318
106 | 2695901.8827 | 1260930.2966 | 2695906.2865 | 1260926.4485
107 | 2695908.8388 | 1260938.1956 | 2695901.8827 | 1260930.2966 | 2695901.8827 | 1260930.2966
108 | 2695823.9279 | 1260881.9946 | 2695820.7426 | 1260884.8734
109 | 2695793.2707 | 1260935.4318 | 2695792.4128 | 1260934.6069
110 | 2695788.9049 | 1260931.2339 | 2695792.4128 | 1260934.6069
111 | 2695805.4328 | 1260969.3537 | 2695807.9619 | 1260966.9726
112 | 2695785.2281 | 1260988.3761 | 2695805.4328 | 1260969.3537
113 | 2695785.2281 | 1260988.3761 | 2695774.9111 | 1260998.0947
114 | 2695785.2281 | 1260988.3761 | 2695801.2082 | 1261004.3324
115 | 2695774.9111 | 1260998.0947 | 2695757.6813 | 1260980.4571 | 2695757.6813 | 1260980.4571
116 | 2695801.2082 | 1261004.3324 | 2695805.8764 | 1261008.9937 | 2695812.5627 | 1261002.34
117 | 2695764.5832 | 1260974.0164 | 2695757.6813 | 1260980.4571
118 | 2695818.1253 | 1260996.8044 | 2695818.1253 | 1260996.8044 | 2695812.5627 | 1261002.34
119 | 2695764.8771 | 1260973.7421 | 2695764.5832 | 1260974.0164
120 | 2695818.1253 | 1260996.8044 | 2695814.6959 | 1260993.3799
121 | 2695767.4382 | 1260971.3521 | 2695764.8771 | 1260973.7421
122 | 2695812.0806 | 1260990.7683 | 2695814.6959 | 1260993.3799
123 | 2695845.7544 | 1261060.2365 | 2695846.1871 | 1261060.6765
124 | 2695815.2185 | 1261029.2058 | 2695821.736 | 1261035.8278
125 | 2695850.2227 | 1261064.7793 | 2695846.1871 | 1261060.6765
126 | 2695859.7011 | 1261030.0937 | 2695849.8286 | 1261039.7919
127 | 2695859.7011 | 1261030.0937 | 2695868.0678 | 1261038.6215
128 | 2695859.7011 | 1261030.0937 | 2695863.5336 | 1261026.3308
129 | 2695867.584 | 1260978.0854 | 2695866.2511 | 1260976.6945
130 | 2695889.4325 | 1261000.8852 | 2695867.584 | 1260978.0854
131 | 2695891.0712 | 1260999.2882 | 2695889.4325 | 1261000.8852
132 | 2695891.0712 | 1260999.2882 | 2695898.6803 | 1261007.106
133 | 2695898.6803 | 1261007.106 | 2695903.9343 | 1261012.504
134 | 2695875.2329 | 1261014.8441 | 2695880.1886 | 1261009.9724
135 | 2695875.2329 | 1261014.8441 | 2695883.5971 | 1261023.3677
136 | 2695906.6646 | 1260983.973 | 2695902.8325 | 1260987.7367
137 | 2695906.6646 | 1260983.973 | 2695915.0688 | 1260992.6095
138 | 2695906.6646 | 1260983.973 | 2695914.1168 | 1260976.6435 | 2695915.2672 | 1260975.5034
139 | 2695883.5971 | 1261023.3677 | 2695889.1162 | 1261028.992
140 | 2695915.0688 | 1260992.6095 | 2695920.7255 | 1260998.4225
141 | 2695922.0219 | 1260968.8097 | 2695915.2672 | 1260975.5034
142 | 2695872.6388 | 1261043.2806 | 2695868.0678 | 1261038.6215
143 | 2695905.6549 | 1261027.6629 | 2695906.7344 | 1261026.595
144 | 2695872.6388 | 1261043.2806 | 2695863.9583 | 1261051.6059
145 | 2695850.2227 | 1261064.7793 | 2695854.1634 | 1261068.7832
146 | 2695850.2227 | 1261064.7793 | 2695859.1803 | 1261056.1883
147 | 2695859.1803 | 1261056.1883 | 2695863.9583 | 1261051.6059
148 | 2695856.3338 | 1261070.9885 | 2695854.1634 | 1261068.7832
149 | 2695811.2974 | 1261163.7288 | 2695815.3041 | 1261159.7114
150 | 2695863.9693 | 1261078.7466 | 2695866.1868 | 1261080.9981
151 | 2695863.9693 | 1261078.7466 | 2695863.0123 | 1261077.7742
152 | 2695863.9693 | 1261078.7466 | 2695873.1114 | 1261069.7639
153 | 2695856.3338 | 1261070.9885 | 2695863.0123 | 1261077.7742
154 | 2695873.1114 | 1261069.7639 | 2695877.8328 | 1261065.1248

## bus_geodata
| x | y | coords
0 | 2695756.5076 | 1260892.4509
1 | 2695747.7841 | 1260901.4459
2 | 2695765.1985 | 1260883.4894
3 | 2695737.3847 | 1260912.1691
4 | 2695774.8409 | 1260892.838
5 | 2695785.9314 | 1260861.659
6 | 2695734.4037 | 1260915.2428
7 | 2695775.9276 | 1260893.8916
8 | 2695715.8259 | 1260936.4772
9 | 2695799.3591 | 1260904.1993
10 | 2695891.5346 | 1260883.8247
11 | 2695878.6984 | 1260896.0115
12 | 2695871.4274 | 1260859.8524
13 | 2695863.5927 | 1260850.5116
14 | 2695860.0674 | 1260846.6124
15 | 2695701.414 | 1260955.1597
16 | 2695816.5441 | 1260888.6679
17 | 2695688.4297 | 1260970.4287
18 | 2695712.0806 | 1260993.1431
19 | 2695751.5605 | 1261051.04
20 | 2695738.2351 | 1261038.2447
21 | 2695748.0754 | 1261027.7065
22 | 2695711.8283 | 1261050.2271
23 | 2695811.6538 | 1261112.9046
24 | 2695837.7205 | 1261137.2353
25 | 2695795.7869 | 1261129.9066
26 | 2695726.9697 | 1261063.7163
27 | 2695828.3345 | 1261146.6463
28 | 2695843.3273 | 1261118.6667
29 | 2695854.4698 | 1261153.1381
30 | 2695854.586 | 1261118.7269
31 | 2695842.4009 | 1261117.7844
32 | 2695805.8606 | 1261082.9866
33 | 2695820.2548 | 1261068.8452
34 | 2695792.8645 | 1261070.5539
35 | 2695816.0419 | 1261092.6824
36 | 2695879.8736 | 1261094.8951
37 | 2695882.8228 | 1261091.4957
38 | 2695874.1857 | 1261089.1199
39 | 2695901.4132 | 1261072.604
40 | 2695911.5875 | 1261062.3748
41 | 2695895.9222 | 1261067.0072
42 | 2695899.4789 | 1261074.7633
43 | 2695745.6782 | 1261025.4103
44 | 2695758.7398 | 1261013.2054
45 | 2695722.1618 | 1261002.8251
46 | 2695867.1131 | 1261130.7396
47 | 2695894.4981 | 1261102.3184
48 | 2695875.426 | 1261145.1415
49 | 2695768.5392 | 1261047.2832
50 | 2695862.2016 | 1261111.5498
51 | 2695932.1772 | 1261041.5331
52 | 2695922.3874 | 1261031.4691
53 | 2695942.1656 | 1261031.4855
54 | 2695926.8473 | 1261046.9405
55 | 2695943.2637 | 1260990.4494
56 | 2695934.1824 | 1260981.198
57 | 2695937.8293 | 1260995.8271
58 | 2695947.5928 | 1261026.0261
59 | 2695937.0405 | 1261015.1855
60 | 2695945.2119 | 1260946.1007
61 | 2695928.264 | 1260926.4434
62 | 2695932.6997 | 1260958.3534
63 | 2695916.7825 | 1261057.1517
64 | 2695924.9947 | 1261071.2629
65 | 2695936.271 | 1261082.3214
66 | 2695913.2391 | 1261083.2376
67 | 2695817.4394 | 1261157.5704
68 | 2695835.3267 | 1261111.0476
69 | 2695837.5291 | 1261051.8743
70 | 2695824.0346 | 1261100.294
71 | 2695888.7968 | 1261085.4944
72 | 2695874.0911 | 1261089.0239
73 | 2695893.4673 | 1261080.8025
74 | 2695762.0526 | 1261010.1099
75 | 2695877.1878 | 1261146.8404
76 | 2695912.2953 | 1261021.0943
77 | 2695927.8292 | 1261005.7226
78 | 2695915.9196 | 1260937.1313
79 | 2695926.6218 | 1260964.3052
80 | 2695905.3894 | 1261045.5606
81 | 2695896.6006 | 1261036.6191
82 | 2695924.3048 | 1261094.2704
83 | 2695845.2208 | 1260929.9022
84 | 2695859.689 | 1260915.2554
85 | 2695843.5798 | 1260931.5634
86 | 2695864.0435 | 1260910.8472
87 | 2695833.1354 | 1260942.1367
88 | 2695866.1932 | 1260908.671
89 | 2695856.1013 | 1260966.1026
90 | 2695829.2822 | 1260946.0374
91 | 2695875.5037 | 1260899.2456
92 | 2695856.8827 | 1260966.918
93 | 2695821.0437 | 1260954.3777
94 | 2695865.8677 | 1260976.2943
95 | 2695817.1129 | 1260958.357
96 | 2695906.2865 | 1260926.4485
97 | 2695901.8827 | 1260930.2966
98 | 2695908.8388 | 1260938.1956
99 | 2695820.7426 | 1260884.8734
100 | 2695823.9279 | 1260881.9946
101 | 2695793.2707 | 1260935.4318
102 | 2695792.4128 | 1260934.6069
103 | 2695788.9049 | 1260931.2339
104 | 2695807.9619 | 1260966.9726
105 | 2695805.4328 | 1260969.3537
106 | 2695785.2281 | 1260988.3761
107 | 2695774.9111 | 1260998.0947
108 | 2695801.2082 | 1261004.3324
109 | 2695757.6813 | 1260980.4571
110 | 2695812.5627 | 1261002.34
111 | 2695764.5832 | 1260974.0164
112 | 2695818.1253 | 1260996.8044
113 | 2695764.8771 | 1260973.7421
114 | 2695814.6959 | 1260993.3799
115 | 2695767.4382 | 1260971.3521
116 | 2695845.7544 | 1261060.2365
117 | 2695821.736 | 1261035.8278
118 | 2695846.1871 | 1261060.6765
119 | 2695815.2185 | 1261029.2058
120 | 2695849.8286 | 1261039.7919
121 | 2695859.7011 | 1261030.0937
122 | 2695812.0806 | 1260990.7683
123 | 2695867.584 | 1260978.0854
124 | 2695866.2511 | 1260976.6944
125 | 2695889.4325 | 1261000.8852
126 | 2695891.0712 | 1260999.2882
127 | 2695898.6803 | 1261007.106
128 | 2695880.1886 | 1261009.9724
129 | 2695875.2329 | 1261014.8441
130 | 2695903.9343 | 1261012.504
131 | 2695902.8325 | 1260987.7367
132 | 2695906.6646 | 1260983.973
133 | 2695883.5971 | 1261023.3677
134 | 2695915.0688 | 1260992.6095
135 | 2695915.2672 | 1260975.5034
136 | 2695889.1162 | 1261028.992
137 | 2695863.5336 | 1261026.3308
138 | 2695868.0678 | 1261038.6215
139 | 2695905.6549 | 1261027.6629
140 | 2695872.6388 | 1261043.2806
141 | 2695922.0219 | 1260968.8097
142 | 2695920.7255 | 1260998.4225
143 | 2695906.7344 | 1261026.595
144 | 2695850.2227 | 1261064.7793
145 | 2695863.9583 | 1261051.6059
146 | 2695854.1634 | 1261068.7832
147 | 2695859.1803 | 1261056.1883
148 | 2695815.3041 | 1261159.7114
149 | 2695811.2974 | 1261163.7288
150 | 2695866.1868 | 1261080.9981
151 | 2695863.9693 | 1261078.7466
152 | 2695863.0123 | 1261077.7742
153 | 2695873.1114 | 1261069.7639
154 | 2695856.3338 | 1261070.9885
155 | 2695877.8328 | 1261065.1248
156 | 2695812.0806 | 1260990.7683

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98195 | -0.34733 | 0.003559 | 0.00089196
1 | 0.98235 | -0.33957 | 0.0030127 | 0.00075505
2 | 0.98159 | -0.35427 | 0 | 0
3 | 0.98286 | -0.32951 | 0.0067931 | 0.0017025
4 | 0.9813 | -0.36008 | 0.0049081 | 0.0012301
5 | 0.98141 | -0.35797 | 0.0068029 | 0.001705
6 | 0.98303 | -0.32611 | 0.0031481 | 0.00078899
7 | 0.98127 | -0.3606 | 0.0069241 | 0.0017353
8 | 0.98427 | -0.30206 | 0.0022142 | 0.00055494
9 | 0.98092 | -0.36742 | 0.0034903 | 0.00087475
10 | 0.98901 | -0.2098 | 0 | 0
11 | 0.9891 | -0.20794 | 0.0056459 | 0.001415
12 | 0.98884 | -0.21307 | 0.0035473 | 0.00088903
13 | 0.98882 | -0.21357 | 0 | 0
14 | 0.9888 | -0.21379 | 0.0023221 | 0.00058196
15 | 0.98535 | -0.28109 | 0 | 0
16 | 0.98074 | -0.37103 | 0.0039858 | 0.00099893
17 | 0.98626 | -0.26333 | 0 | 0
18 | 0.98776 | -0.23432 | 0.0031426 | 0.00078762
19 | 0.98976 | -0.19574 | 0.007569 | 0.001897
20 | 0.98989 | -0.19325 | 0 | 0
21 | 0.99008 | -0.1895 | 0 | 0
22 | 0.98967 | -0.19737 | 0 | 0
23 | 0.9714 | -0.55231 | 0 | 0
24 | 0.97163 | -0.54766 | 0 | 0
25 | 0.97124 | -0.55542 | 0.0070664 | 0.001771
26 | 0.98954 | -0.19992 | 0.0070611 | 0.0017697
27 | 0.97129 | -0.55448 | 0.0057389 | 0.0014383
28 | 0.97264 | -0.52782 | 0 | 0
29 | 0.9715 | -0.55035 | 0.0063189 | 0.0015837
30 | 0.97225 | -0.53547 | 0 | 0
31 | 0.97273 | -0.52603 | 0.0029149 | 0.00073054
32 | 0.97664 | -0.44924 | 0 | 0
33 | 0.9785 | -0.41279 | 0.0019522 | 0.00048928
34 | 0.97643 | -0.45337 | 0.012555 | 0.0031467
35 | 0.9755 | -0.47148 | 0.0025037 | 0.00062749
36 | 0.9814 | -0.35639 | 0 | 0
37 | 0.98154 | -0.35359 | 0 | 0
38 | 0.98114 | -0.36143 | 0.0014377 | 0.00036032
39 | 0.9824 | -0.33693 | 0 | 0
40 | 0.98287 | -0.32769 | 0.001775 | 0.00044486
41 | 0.98239 | -0.33714 | 0.0014669 | 0.00036764
42 | 0.9823 | -0.33877 | 0 | 0
43 | 0.99017 | -0.18777 | 0 | 0
44 | 0.9916 | -0.1602 | 0.012426 | 0.0031143
45 | 0.98844 | -0.22119 | 0.0049595 | 0.001243
46 | 0.97172 | -0.54592 | 0 | 0
47 | 0.97098 | -0.56063 | 0.017345 | 0.0043471
48 | 0.97152 | -0.54984 | 0 | 0
49 | 0.9897 | -0.1969 | 0.014697 | 0.0036834
50 | 0.97223 | -0.53589 | 0.0021704 | 0.00054395
51 | 0.98386 | -0.30869 | 0 | 0
52 | 0.98449 | -0.29647 | 0.0013386 | 0.00033548
53 | 0.98322 | -0.32117 | 0.0012588 | 0.00031549
54 | 0.9836 | -0.31364 | 0.0010507 | 0.00026333
55 | 0.98157 | -0.35329 | 0 | 0
56 | 0.98154 | -0.35384 | 0.0023531 | 0.00058973
57 | 0.98159 | -0.35297 | 0.0021194 | 0.00053116
58 | 0.98288 | -0.32777 | 0 | 0
59 | 0.98221 | -0.34077 | 0.0012915 | 0.00032369
60 | 0.97932 | -0.39733 | 0 | 0
61 | 0.97893 | -0.40508 | 0 | 0
62 | 0.97959 | -0.39209 | 0.0026686 | 0.00066881
63 | 0.98312 | -0.32292 | 0 | 0
64 | 0.97089 | -0.56244 | 0 | 0
65 | 0.97087 | -0.56283 | 0.001333 | 0.00033407
66 | 0.97091 | -0.56203 | 0 | 0
67 | 0.97097 | -0.56076 | 0.0015862 | 0.00039754
68 | 0.97345 | -0.51185 | 0.0027064 | 0.00067829
69 | 0.97964 | -0.39056 | 0 | 0
70 | 0.97464 | -0.48847 | 0.0023752 | 0.00059528
71 | 0.98181 | -0.34833 | 0.0014665 | 0.00036755
72 | 0.98113 | -0.36151 | 0.0014679 | 0.00036788
73 | 0.98203 | -0.34417 | 0.0014665 | 0.00036755
74 | 0.99201 | -0.15222 | 0.0096584 | 0.0024206
75 | 0.97149 | -0.5504 | 0.012461 | 0.0031231
76 | 0.98514 | -0.28379 | 0 | 0
77 | 0.98164 | -0.35183 | 0 | 0
78 | 0.97868 | -0.40997 | 0.0034317 | 0.00086006
79 | 0.97974 | -0.38914 | 0.0095966 | 0.0024051
80 | 0.98494 | -0.28776 | 0.002308 | 0.00057844
81 | 0.98497 | -0.28724 | 0 | 0
82 | 0.97089 | -0.56246 | 0.0014895 | 0.0003733
83 | 0.99015 | -0.18768 | 0.0085441 | 0.0021413
84 | 0.98958 | -0.19864 | 0.0028629 | 0.00071752
85 | 0.99023 | -0.18608 | 0.0057537 | 0.001442
86 | 0.98943 | -0.20162 | 0.0065926 | 0.0016523
87 | 0.99083 | -0.17441 | 0 | 0
88 | 0.98937 | -0.20274 | 0.0023498 | 0.00058891
89 | 0.98908 | -0.20792 | 0.0030144 | 0.00075548
90 | 0.99118 | -0.16781 | 0.0064269 | 0.0016107
91 | 0.98915 | -0.20701 | 0.0065958 | 0.0016531
92 | 0.98902 | -0.20905 | 0.0034263 | 0.00085871
93 | 0.99193 | -0.15338 | 0.006546 | 0.0016406
94 | 0.98836 | -0.22182 | 0.0035021 | 0.00087771
95 | 0.9923 | -0.14634 | 0 | 0
96 | 0.97848 | -0.41384 | 0.0033263 | 0.00083365
97 | 0.9785 | -0.41348 | 0.0028412 | 0.00071206
98 | 0.97856 | -0.4123 | 0.0068502 | 0.0017168
99 | 0.98071 | -0.3715 | 0.0023968 | 0.00060071
100 | 0.98071 | -0.37167 | 0.0022129 | 0.0005546
101 | 0.99193 | -0.15346 | 0.0031019 | 0.00077741
102 | 0.99192 | -0.15365 | 0.0021064 | 0.00052791
103 | 0.99189 | -0.15425 | 0.0069452 | 0.0017406
104 | 0.99316 | -0.12987 | 0.0032257 | 0.00080845
105 | 0.9934 | -0.12527 | 0.0036018 | 0.00090269
106 | 0.99535 | -0.088185 | 0 | 0
107 | 0.99378 | -0.11831 | 0 | 0
108 | 0.99756 | -0.046158 | 0.017388 | 0.0043579
109 | 0.99351 | -0.12346 | 0.0038502 | 0.00096494
110 | 0.99919 | -0.015222 | 0.0033292 | 0.00083438
111 | 0.99344 | -0.12479 | 0.0015602 | 0.00039102
112 | 1 | 0 | -0.4638 | -0.11847
113 | 0.99344 | -0.12484 | 0.0024632 | 0.00061735
114 | 0.99995 | -0.00089037 | 0.0020645 | 0.00051742
115 | 0.99343 | -0.12508 | 0.0039606 | 0.00099261
116 | 0.97994 | -0.38475 | 0.0016048 | 0.00040221
117 | 0.97947 | -0.39389 | 0.0062179 | 0.0015584
118 | 0.97995 | -0.38444 | 0.0014661 | 0.00036743
119 | 0.97945 | -0.39422 | 0.0019278 | 0.00048315
120 | 0.97962 | -0.39098 | 0.0053608 | 0.0013435
121 | 0.97969 | -0.38963 | 0 | 0
122 | 0.99993 | -0.0014364 | 0.0084754 | 0.0021241
123 | 0.98824 | -0.2242 | 0.0059288 | 0.0014859
124 | 0.98833 | -0.22236 | 0.0034209 | 0.00085735
125 | 0.98671 | -0.25352 | 0 | 0
126 | 0.9866 | -0.25564 | 0 | 0
127 | 0.98608 | -0.2658 | 0.0014202 | 0.00035594
128 | 0.98485 | -0.28956 | 0.0020725 | 0.00051942
129 | 0.98486 | -0.2893 | 0 | 0
130 | 0.98571 | -0.27276 | 0.0013305 | 0.00033346
131 | 0.98048 | -0.37458 | 0.006889 | 0.0017266
132 | 0.98052 | -0.37391 | 0 | 0
133 | 0.98488 | -0.28885 | 0.001894 | 0.00047468
134 | 0.98094 | -0.36551 | 0.0021643 | 0.00054243
135 | 0.98016 | -0.38083 | 0.0028756 | 0.00072068
136 | 0.98491 | -0.28829 | 0.0015036 | 0.00037683
137 | 0.97968 | -0.38979 | 0.0016211 | 0.00040628
138 | 0.97977 | -0.38811 | 0.0014666 | 0.00036755
139 | 0.98506 | -0.28546 | 0.0013035 | 0.00032669
140 | 0.97982 | -0.38711 | 0 | 0
141 | 0.97991 | -0.38578 | 0 | 0
142 | 0.98125 | -0.35954 | 0.0011828 | 0.00029643
143 | 0.98507 | -0.28521 | 0.0010329 | 0.00025887
144 | 0.98011 | -0.38151 | 0 | 0
145 | 0.97991 | -0.38527 | 0.0014666 | 0.00036755
146 | 0.98027 | -0.37836 | 0.0027651 | 0.000693
147 | 0.97997 | -0.38408 | 0.0014669 | 0.00036764
148 | 0.97091 | -0.56191 | 0.0018925 | 0.0004743
149 | 0.97081 | -0.56385 | 0.018561 | 0.0046519
150 | 0.98078 | -0.36838 | 0.0025441 | 0.00063762
151 | 0.98068 | -0.37027 | 0 | 0
152 | 0.98064 | -0.37107 | 0.0010698 | 0.00026811
153 | 0.98065 | -0.37095 | 0.0014665 | 0.00036755
154 | 0.98036 | -0.37659 | 0.0016619 | 0.0004165
155 | 0.98064 | -0.37112 | 0.0014665 | 0.00036755
156 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034304 | -0.0086052 | 0.034317 | 0.0086131 | 1.2699e-05 | 7.9686e-06 | 0.051986 | 0.051986 | 0.051986 | 0.98195 | -0.34733 | 0.98235 | -0.33957 | 14.2818
1 | 0.030745 | 0.0077132 | -0.030735 | -0.0077068 | 1.0163e-05 | 6.3463e-06 | 0.046593 | 0.046593 | 0.046593 | 0.98195 | -0.34733 | 0.98159 | -0.35427 | 12.8002
2 | -0.037329 | -0.0093682 | 0.037347 | 0.0093794 | 1.7913e-05 | 1.1275e-05 | 0.056549 | 0.056549 | 0.056549 | 0.98235 | -0.33957 | 0.98286 | -0.32951 | 15.5355
3 | 0.023931 | 0.0060015 | -0.023924 | -0.0059974 | 6.6284e-06 | 4.0725e-06 | 0.036278 | 0.036278 | 0.036278 | 0.98159 | -0.35427 | 0.9813 | -0.36008 | 9.9666
4 | 0.0068041 | 0.0017053 | -0.0068029 | -0.001705 | 1.2011e-06 | 3.8822e-07 | 0.010314 | 0.010315 | 0.010315 | 0.98159 | -0.35427 | 0.98141 | -0.35797 | 2.8337
5 | -0.04414 | -0.011082 | 0.044147 | 0.011086 | 7.1722e-06 | 4.5359e-06 | 0.066834 | 0.066834 | 0.066834 | 0.98286 | -0.32951 | 0.98303 | -0.32611 | 18.3609
6 | 0.019016 | 0.0047673 | -0.019015 | -0.0047671 | 4.7196e-07 | 2.8293e-07 | 0.028836 | 0.028836 | 0.028836 | 0.9813 | -0.36008 | 0.98127 | -0.3606 | 7.9219
7 | -0.047296 | -0.011875 | 0.04735 | 0.01191 | 5.4325e-05 | 3.4409e-05 | 0.071599 | 0.071599 | 0.071599 | 0.98303 | -0.32611 | 0.98427 | -0.30206 | 19.67
8 | 0.012091 | 0.0030317 | -0.012087 | -0.0030296 | 3.927e-06 | 2.1199e-06 | 0.018336 | 0.018336 | 0.018336 | 0.98127 | -0.3606 | 0.98092 | -0.36742 | 5.0374
9 | -0.049564 | -0.012465 | 0.049614 | 0.012496 | 4.97e-05 | 3.1508e-05 | 0.074946 | 0.074946 | 0.074946 | 0.98427 | -0.30206 | 0.98535 | -0.28109 | 20.5896
10 | 0.0085971 | 0.0021548 | -0.0085956 | -0.0021542 | 1.4774e-06 | 6.5317e-07 | 0.013041 | 0.013042 | 0.013042 | 0.98092 | -0.36742 | 0.98074 | -0.37103 | 3.5829
11 | -0.0058703 | -0.001471 | 0.0058709 | 0.0014711 | 5.1797e-07 | 1.0425e-07 | 0.0088321 | 0.0088321 | 0.0088321 | 0.98901 | -0.2098 | 0.9891 | -0.20794 | 2.4264
12 | 0.0058703 | 0.001471 | -0.0058694 | -0.0014708 | 9.1528e-07 | 1.8434e-07 | 0.0088321 | 0.0088323 | 0.0088323 | 0.98901 | -0.2098 | 0.98884 | -0.21307 | 2.4265
13 | -0.011517 | -0.0028861 | 0.011517 | 0.0028864 | 5.1172e-07 | 2.6915e-07 | 0.017326 | 0.017326 | 0.017326 | 0.9891 | -0.20794 | 0.98915 | -0.20701 | 4.7598
14 | 0.0023221 | 0.00058179 | -0.0023221 | -0.00058191 | 5.5823e-08 | -1.2066e-07 | 0.0034943 | 0.0034944 | 0.0034944 | 0.98884 | -0.21307 | 0.98882 | -0.21357 | 0.95999
15 | 0.0023221 | 0.00058191 | -0.0023221 | -0.00058196 | 2.407e-08 | -5.2023e-08 | 0.0034944 | 0.0034944 | 0.0034944 | 0.98882 | -0.21357 | 0.9888 | -0.21379 | 0.96
16 | -0.049614 | -0.012496 | 0.049656 | 0.012523 | 4.2169e-05 | 2.6733e-05 | 0.074946 | 0.074946 | 0.074946 | 0.98535 | -0.28109 | 0.98626 | -0.26333 | 20.5896
17 | 0.0046098 | 0.0011553 | -0.0046097 | -0.0011553 | 1.0382e-07 | -4.968e-09 | 0.0069942 | 0.0069942 | 0.0069942 | 0.98074 | -0.37103 | 0.98071 | -0.3715 | 1.9215
18 | -0.049656 | -0.012523 | 0.049725 | 0.012567 | 6.9071e-05 | 4.3786e-05 | 0.074946 | 0.074946 | 0.074946 | 0.98626 | -0.26333 | 0.98776 | -0.23432 | 20.5896
19 | -0.052868 | -0.013354 | 0.052901 | 0.013376 | 3.3278e-05 | 2.1119e-05 | 0.07968 | 0.07968 | 0.07968 | 0.98776 | -0.23432 | 0.98844 | -0.22119 | 21.8902
20 | -0.007569 | -0.001897 | 0.0075699 | 0.0018973 | 8.9705e-07 | 3.3665e-07 | 0.011379 | 0.011379 | 0.011379 | 0.98976 | -0.19574 | 0.98989 | -0.19325 | 3.1262
21 | -0.014633 | -0.0036677 | 0.014636 | 0.0036692 | 2.6162e-06 | 1.489e-06 | 0.021997 | 0.021997 | 0.021997 | 0.98989 | -0.19325 | 0.99008 | -0.1895 | 6.0431
22 | 0.0070633 | 0.0017704 | -0.0070619 | -0.00177 | 1.3863e-06 | 4.658e-07 | 0.010618 | 0.010618 | 0.010618 | 0.98989 | -0.19325 | 0.98967 | -0.19737 | 2.917
23 | 0.014702 | 0.0036864 | -0.014697 | -0.0036834 | 5.1854e-06 | 2.9546e-06 | 0.022097 | 0.022097 | 0.022097 | 0.99008 | -0.1895 | 0.9897 | -0.1969 | 6.0706
24 | -0.029338 | -0.0073556 | 0.02934 | 0.0073571 | 2.4162e-06 | 1.5038e-06 | 0.044094 | 0.044094 | 0.044094 | 0.99008 | -0.1895 | 0.99017 | -0.18777 | 12.1137
25 | 0.0070619 | 0.00177 | -0.0070611 | -0.0017697 | 8.5587e-07 | 2.8766e-07 | 0.010618 | 0.010618 | 0.010618 | 0.98967 | -0.19737 | 0.98954 | -0.19992 | 2.917
26 | -0.0070675 | -0.0017714 | 0.0070691 | 0.001772 | 1.5673e-06 | 5.6152e-07 | 0.010826 | 0.010826 | 0.010826 | 0.9714 | -0.55231 | 0.97163 | -0.54766 | 2.9742
27 | 0.0070675 | 0.0017714 | -0.0070664 | -0.001771 | 1.0446e-06 | 3.7436e-07 | 0.010826 | 0.010826 | 0.010826 | 0.9714 | -0.55231 | 0.97124 | -0.55542 | 2.9743
28 | 0.027797 | 0.0069734 | -0.027788 | -0.0069678 | 9.0338e-06 | 5.6171e-06 | 0.042573 | 0.042573 | 0.042573 | 0.97163 | -0.54766 | 0.97129 | -0.55448 | 11.6958
29 | -0.041186 | -0.010329 | 0.041225 | 0.010354 | 3.8981e-05 | 2.4624e-05 | 0.063077 | 0.063077 | 0.063077 | 0.97163 | -0.54766 | 0.97264 | -0.52782 | 17.3289
30 | 0.0063197 | 0.0015839 | -0.0063189 | -0.0015837 | 8.113e-07 | 2.3321e-07 | 0.0096783 | 0.0096785 | 0.0096785 | 0.97163 | -0.54766 | 0.9715 | -0.55035 | 2.6589
31 | 0.022049 | 0.0055295 | -0.022043 | -0.0055254 | 6.6024e-06 | 4.0346e-06 | 0.033781 | 0.033781 | 0.033781 | 0.97129 | -0.55448 | 0.97097 | -0.56076 | 9.2805
32 | 0.034845 | 0.0087489 | -0.034833 | -0.0087409 | 1.2715e-05 | 7.9899e-06 | 0.053315 | 0.053315 | 0.053315 | 0.97264 | -0.52782 | 0.97225 | -0.53547 | 14.647
33 | -0.07607 | -0.019103 | 0.076077 | 0.019107 | 6.4991e-06 | 4.1435e-06 | 0.11639 | 0.11639 | 0.11639 | 0.97264 | -0.52782 | 0.97273 | -0.52603 | 31.9758
34 | 0.0021704 | 0.00054385 | -0.0021704 | -0.00054395 | 4.3301e-08 | -1.0206e-07 | 0.0033218 | 0.0033218 | 0.0033218 | 0.97225 | -0.53547 | 0.97223 | -0.53589 | 0.91259
35 | 0.032662 | 0.008197 | -0.032646 | -0.0081868 | 1.6267e-05 | 1.0196e-05 | 0.049993 | 0.049993 | 0.049993 | 0.97225 | -0.53547 | 0.97172 | -0.54592 | 13.7344
36 | -0.078992 | -0.019837 | 0.079045 | 0.019872 | 5.3502e-05 | 3.412e-05 | 0.12085 | 0.12085 | 0.12085 | 0.97273 | -0.52603 | 0.97345 | -0.51185 | 33.2008
37 | -0.099441 | -0.025082 | 0.099614 | 0.025193 | 0.00017383 | 0.000111 | 0.15157 | 0.15157 | 0.15157 | 0.97664 | -0.44924 | 0.9785 | -0.41279 | 41.6392
38 | 0.012558 | 0.003148 | -0.012555 | -0.0031467 | 2.4691e-06 | 1.3552e-06 | 0.019133 | 0.019134 | 0.019134 | 0.97664 | -0.44924 | 0.97643 | -0.45337 | 5.2565
39 | 0.086883 | 0.021934 | -0.08679 | -0.021875 | 9.2469e-05 | 5.9004e-05 | 0.13243 | 0.13243 | 0.13243 | 0.97664 | -0.44924 | 0.9755 | -0.47148 | 36.3828
40 | -0.10157 | -0.025682 | 0.10168 | 0.025751 | 0.00010843 | 6.8788e-05 | 0.15454 | 0.15454 | 0.15454 | 0.9785 | -0.41279 | 0.97964 | -0.39056 | 21.2274
41 | 0.084287 | 0.021247 | -0.084218 | -0.021203 | 6.8465e-05 | 4.368e-05 | 0.12861 | 0.12861 | 0.12861 | 0.9755 | -0.47148 | 0.97464 | -0.48847 | 35.3336
42 | -0.13837 | -0.035025 | 0.13838 | 0.035036 | 1.857e-05 | 1.1657e-05 | 0.20992 | 0.20992 | 0.20992 | 0.9814 | -0.35639 | 0.98154 | -0.35359 | 14.4175
43 | 0.13837 | 0.035025 | -0.13833 | -0.035004 | 3.3487e-05 | 2.1022e-05 | 0.20992 | 0.20992 | 0.20992 | 0.9814 | -0.35639 | 0.98114 | -0.36143 | 14.4175
44 | -0.13838 | -0.035036 | 0.13842 | 0.035058 | 3.4982e-05 | 2.196e-05 | 0.20992 | 0.20992 | 0.20992 | 0.98154 | -0.35359 | 0.98181 | -0.34833 | 14.4175
45 | 0.13689 | 0.034643 | -0.13689 | -0.034643 | 5.4504e-07 | 3.4202e-07 | 0.20774 | 0.20774 | 0.20774 | 0.98114 | -0.36143 | 0.98113 | -0.36151 | 14.2677
46 | -0.1429 | -0.036209 | 0.14296 | 0.036249 | 6.3448e-05 | 3.9876e-05 | 0.21658 | 0.21658 | 0.21658 | 0.9824 | -0.33693 | 0.98287 | -0.32769 | 14.8753
47 | 0.0014669 | 0.00036755 | -0.0014669 | -0.00036764 | 1.4515e-08 | -8.9983e-08 | 0.0022219 | 0.0022219 | 0.0022219 | 0.9824 | -0.33693 | 0.98239 | -0.33714 | 0.61041
48 | 0.14143 | 0.035842 | -0.14142 | -0.035834 | 1.2471e-05 | 7.8351e-06 | 0.21436 | 0.21436 | 0.21436 | 0.9824 | -0.33693 | 0.9823 | -0.33877 | 14.7227
49 | -0.14474 | -0.036694 | 0.14477 | 0.036715 | 3.3205e-05 | 2.0878e-05 | 0.21927 | 0.21927 | 0.21927 | 0.98287 | -0.32769 | 0.98312 | -0.32292 | 15.0599
50 | 0.14142 | 0.035834 | -0.14138 | -0.035811 | 3.6709e-05 | 2.3062e-05 | 0.21436 | 0.21436 | 0.21436 | 0.9823 | -0.33877 | 0.98203 | -0.34417 | 14.7227
51 | -0.087294 | -0.022035 | 0.087409 | 0.022108 | 0.00011546 | 7.3666e-05 | 0.13124 | 0.13124 | 0.13124 | 0.99017 | -0.18777 | 0.9916 | -0.1602 | 36.0549
52 | 0.057953 | 0.014678 | -0.05786 | -0.014619 | 9.2858e-05 | 5.901e-05 | 0.087146 | 0.087146 | 0.087146 | 0.99017 | -0.18777 | 0.98844 | -0.22119 | 23.9413
53 | -0.099835 | -0.025223 | 0.099874 | 0.025247 | 3.8198e-05 | 2.4388e-05 | 0.14989 | 0.14989 | 0.14989 | 0.9916 | -0.1602 | 0.99201 | -0.15222 | 41.1777
54 | 0.020182 | 0.0050623 | -0.020168 | -0.0050537 | 1.4142e-05 | 8.5619e-06 | 0.030907 | 0.030907 | 0.030907 | 0.97172 | -0.54592 | 0.97098 | -0.56063 | 8.4909
55 | 0.012464 | 0.0031246 | -0.012462 | -0.0031233 | 2.3245e-06 | 1.2769e-06 | 0.019087 | 0.019087 | 0.019087 | 0.97172 | -0.54592 | 0.97152 | -0.54984 | 5.2436
56 | 0.0028227 | 0.00070662 | -0.0028225 | -0.00070683 | 1.8765e-07 | -2.1068e-07 | 0.0043255 | 0.0043256 | 0.0043256 | 0.97098 | -0.56063 | 0.97091 | -0.56203 | 1.1884
57 | 0.012462 | 0.0031233 | -0.012461 | -0.0031231 | 3.3436e-07 | 1.8368e-07 | 0.019087 | 0.019087 | 0.019087 | 0.97152 | -0.54984 | 0.97149 | -0.5504 | 5.2436
58 | -0.19495 | -0.049397 | 0.19506 | 0.049469 | 0.00011458 | 7.2617e-05 | 0.29504 | 0.29504 | 0.29504 | 0.98386 | -0.30869 | 0.98449 | -0.29647 | 20.2638
59 | 0.049031 | 0.012356 | -0.049002 | -0.012337 | 2.9235e-05 | 1.8531e-05 | 0.07418 | 0.07418 | 0.07418 | 0.98386 | -0.30869 | 0.98322 | -0.32117 | 20.3792
60 | 0.14592 | 0.037041 | -0.14588 | -0.037019 | 3.4721e-05 | 2.1836e-05 | 0.22086 | 0.22086 | 0.22086 | 0.98386 | -0.30869 | 0.9836 | -0.31364 | 15.169
61 | -0.1964 | -0.049805 | 0.19652 | 0.049881 | 0.00011974 | 7.5898e-05 | 0.29706 | 0.29706 | 0.29706 | 0.98449 | -0.29647 | 0.98514 | -0.28379 | 20.4027
62 | 0.047743 | 0.012022 | -0.047728 | -0.012012 | 1.5079e-05 | 9.5533e-06 | 0.072275 | 0.072275 | 0.072275 | 0.98322 | -0.32117 | 0.98288 | -0.32777 | 19.8558
63 | 0.14483 | 0.036756 | -0.14477 | -0.036715 | 6.4627e-05 | 4.0634e-05 | 0.21927 | 0.21927 | 0.21927 | 0.9836 | -0.31364 | 0.98312 | -0.32292 | 15.0599
64 | 0.0023531 | 0.00058961 | -0.0023531 | -0.00058973 | 6.1861e-08 | -1.2427e-07 | 0.0035672 | 0.0035672 | 0.0035672 | 0.98157 | -0.35329 | 0.98154 | -0.35384 | 0.98001
65 | -0.0023531 | -0.00058961 | 0.0023532 | 0.00058953 | 3.6482e-08 | -7.3293e-08 | 0.0035672 | 0.0035671 | 0.0035672 | 0.98157 | -0.35329 | 0.98159 | -0.35297 | 0.97999
66 | -0.0044725 | -0.0011207 | 0.0044728 | 0.0011207 | 2.4251e-07 | -2.2639e-08 | 0.0067799 | 0.0067799 | 0.0067799 | 0.98159 | -0.35297 | 0.98164 | -0.35183 | 1.8626
67 | 0.047728 | 0.012012 | -0.047698 | -0.011994 | 2.9635e-05 | 1.8775e-05 | 0.072275 | 0.072275 | 0.072275 | 0.98288 | -0.32777 | 0.98221 | -0.34077 | 19.8558
68 | 0.046407 | 0.01167 | -0.046382 | -0.011654 | 2.4487e-05 | 1.5505e-05 | 0.070318 | 0.070319 | 0.070319 | 0.98221 | -0.34077 | 0.98164 | -0.35183 | 19.3183
69 | 0.016461 | 0.0041293 | -0.016455 | -0.0041257 | 6.0818e-06 | 3.5663e-06 | 0.025013 | 0.025013 | 0.025013 | 0.97932 | -0.39733 | 0.97893 | -0.40508 | 6.8717
70 | -0.016461 | -0.0041293 | 0.016465 | 0.0041317 | 4.1087e-06 | 2.4092e-06 | 0.025013 | 0.025013 | 0.025013 | 0.97932 | -0.39733 | 0.97959 | -0.39209 | 6.8717
71 | 0.016455 | 0.0041257 | -0.016451 | -0.0041235 | 3.831e-06 | 2.2466e-06 | 0.025013 | 0.025013 | 0.025013 | 0.97893 | -0.40508 | 0.97868 | -0.40997 | 6.8718
72 | -0.019134 | -0.0048005 | 0.019137 | 0.0048021 | 2.6951e-06 | 1.6178e-06 | 0.029067 | 0.029067 | 0.029067 | 0.97959 | -0.39209 | 0.97974 | -0.38914 | 7.9853
73 | 0.001333 | 0.00033389 | -0.001333 | -0.00033407 | 2.4682e-08 | -1.7922e-07 | 0.0020429 | 0.002043 | 0.002043 | 0.97089 | -0.56244 | 0.97087 | -0.56283 | 0.56126
74 | -0.001333 | -0.00033389 | 0.001333 | 0.0003337 | 2.6225e-08 | -1.9045e-07 | 0.0020429 | 0.0020428 | 0.0020429 | 0.97089 | -0.56244 | 0.97091 | -0.56203 | 0.56124
75 | 0.0014895 | 0.00037313 | -0.0014895 | -0.0003733 | 3.049e-08 | -1.7343e-07 | 0.0022828 | 0.0022828 | 0.0022828 | 0.97091 | -0.56203 | 0.97089 | -0.56246 | 0.62716
76 | 0.020457 | 0.0051279 | -0.020455 | -0.0051272 | 1.1145e-06 | 6.7586e-07 | 0.03135 | 0.03135 | 0.03135 | 0.97097 | -0.56076 | 0.97091 | -0.56191 | 8.6127
77 | -0.081752 | -0.02055 | 0.081843 | 0.020608 | 9.135e-05 | 5.827e-05 | 0.12499 | 0.12499 | 0.12499 | 0.97345 | -0.51185 | 0.97464 | -0.48847 | 34.3374
78 | -0.10982 | -0.027793 | 0.10985 | 0.027812 | 3.0635e-05 | 1.9015e-05 | 0.16691 | 0.16691 | 0.16691 | 0.97964 | -0.39056 | 0.97994 | -0.38475 | 11.4636
79 | 0.008147 | 0.0020419 | -0.0081457 | -0.0020414 | 1.293e-06 | 5.4407e-07 | 0.012375 | 0.012375 | 0.012375 | 0.97964 | -0.39056 | 0.97947 | -0.39389 | 3.3997
80 | -0.13989 | -0.035426 | 0.13991 | 0.035443 | 2.7931e-05 | 1.7541e-05 | 0.21214 | 0.21214 | 0.21214 | 0.98181 | -0.34833 | 0.98203 | -0.34417 | 14.5701
81 | 0.13543 | 0.034275 | -0.13538 | -0.034247 | 4.4603e-05 | 2.7977e-05 | 0.20551 | 0.20551 | 0.20551 | 0.98113 | -0.36151 | 0.98078 | -0.36838 | 14.1148
82 | -0.10953 | -0.027668 | 0.10971 | 0.027782 | 0.00017831 | 0.00011389 | 0.16437 | 0.16437 | 0.16437 | 0.99201 | -0.15222 | 0.99378 | -0.11831 | 45.1578
83 | 0.010116 | 0.0025353 | -0.010116 | -0.0025349 | 6.8488e-07 | 3.3874e-07 | 0.01528 | 0.01528 | 0.01528 | 0.98514 | -0.28379 | 0.98507 | -0.28521 | 4.1979
84 | -0.20664 | -0.052416 | 0.20675 | 0.052486 | 0.00010964 | 6.9558e-05 | 0.31234 | 0.31234 | 0.31234 | 0.98514 | -0.28379 | 0.98571 | -0.27276 | 21.4522
85 | 0.041909 | 0.010534 | -0.041894 | -0.010524 | 1.5421e-05 | 9.7407e-06 | 0.063539 | 0.063539 | 0.063539 | 0.98164 | -0.35183 | 0.98125 | -0.35954 | 17.4557
86 | 0.01302 | 0.0032634 | -0.013018 | -0.0032626 | 1.4471e-06 | 8.0244e-07 | 0.019796 | 0.019796 | 0.019796 | 0.97868 | -0.40997 | 0.97856 | -0.4123 | 5.4383
87 | -0.028733 | -0.0072072 | 0.028738 | 0.0072101 | 4.5983e-06 | 2.8618e-06 | 0.043642 | 0.043642 | 0.043642 | 0.97974 | -0.38914 | 0.97991 | -0.38578 | 11.9895
88 | -0.002308 | -0.00057844 | 0.0023081 | 0.00057832 | 5.7163e-08 | -1.2299e-07 | 0.0034869 | 0.0034868 | 0.0034869 | 0.98494 | -0.28776 | 0.98497 | -0.28724 | 0.95793
89 | -0.0077786 | -0.0019491 | 0.0077793 | 0.0019493 | 6.5949e-07 | 2.5997e-07 | 0.011751 | 0.011751 | 0.011751 | 0.98497 | -0.28724 | 0.98506 | -0.28546 | 3.2284
90 | 0.0054705 | 0.0013707 | -0.0054703 | -0.0013707 | 2.737e-07 | 3.9164e-08 | 0.0082644 | 0.0082644 | 0.0082644 | 0.98497 | -0.28724 | 0.98491 | -0.28829 | 2.2704
91 | 0.029943 | 0.0075131 | -0.029927 | -0.0075033 | 1.5635e-05 | 9.7417e-06 | 0.045001 | 0.045002 | 0.045002 | 0.99015 | -0.18768 | 0.98958 | -0.19864 | 12.3631
92 | -0.038487 | -0.0096544 | 0.03849 | 0.0096563 | 2.9296e-06 | 1.8449e-06 | 0.057842 | 0.057842 | 0.057842 | 0.99015 | -0.18768 | 0.99023 | -0.18608 | 15.8906
93 | 0.027064 | 0.0067858 | -0.02706 | -0.0067834 | 3.8483e-06 | 2.3833e-06 | 0.040697 | 0.040697 | 0.040697 | 0.98958 | -0.19864 | 0.98943 | -0.20162 | 11.1804
94 | -0.044243 | -0.011098 | 0.044268 | 0.011114 | 2.4637e-05 | 1.5577e-05 | 0.066488 | 0.066488 | 0.066488 | 0.99023 | -0.18608 | 0.99083 | -0.17441 | 18.2659
95 | 0.020468 | 0.0051312 | -0.020466 | -0.0051305 | 1.0869e-06 | 6.5636e-07 | 0.030782 | 0.030782 | 0.030782 | 0.98943 | -0.20162 | 0.98937 | -0.20274 | 8.4566
96 | 0.22983 | 0.058668 | -0.22946 | -0.058432 | 0.00037154 | 0.00023608 | 0.34553 | 0.34553 | 0.34553 | 0.99083 | -0.17441 | 0.98908 | -0.20792 | 23.7317
97 | -0.2741 | -0.069782 | 0.27418 | 0.069837 | 8.7261e-05 | 5.5565e-05 | 0.41202 | 0.41202 | 0.41202 | 0.99083 | -0.17441 | 0.99118 | -0.16781 | 28.2981
98 | 0.018117 | 0.0045416 | -0.018113 | -0.0045394 | 3.6886e-06 | 2.1906e-06 | 0.027248 | 0.027248 | 0.027248 | 0.98937 | -0.20274 | 0.98915 | -0.20701 | 7.4857
99 | 0.22644 | 0.057676 | -0.22643 | -0.057669 | 1.2312e-05 | 7.8214e-06 | 0.341 | 0.341 | 0.341 | 0.98908 | -0.20792 | 0.98902 | -0.20905 | 23.4202
100 | -0.28061 | -0.071448 | 0.28081 | 0.071573 | 0.00019542 | 0.00012446 | 0.42167 | 0.42167 | 0.42167 | 0.99118 | -0.16781 | 0.99193 | -0.15338 | 28.9607
101 | 0.223 | 0.05681 | -0.22287 | -0.056723 | 0.00013732 | 8.7219e-05 | 0.33584 | 0.33584 | 0.33584 | 0.98902 | -0.20905 | 0.98836 | -0.22182 | 23.0662
102 | -0.28735 | -0.073213 | 0.28745 | 0.073275 | 9.7629e-05 | 6.2194e-05 | 0.43149 | 0.43149 | 0.43149 | 0.99193 | -0.15338 | 0.9923 | -0.14634 | 29.6352
103 | 0.21936 | 0.055845 | -0.21936 | -0.055841 | 5.6772e-06 | 3.605e-06 | 0.33057 | 0.33057 | 0.33057 | 0.98836 | -0.22182 | 0.98833 | -0.22236 | 22.7041
104 | -0.29961 | -0.076324 | 0.29984 | 0.076476 | 0.00023831 | 0.00015187 | 0.44972 | 0.44972 | 0.44972 | 0.9923 | -0.14634 | 0.99316 | -0.12987 | 30.8873
105 | 0.012158 | 0.0030482 | -0.012154 | -0.003046 | 4.123e-06 | 2.2116e-06 | 0.018232 | 0.018232 | 0.018232 | 0.9923 | -0.14634 | 0.99193 | -0.15346 | 5.0088
106 | -0.0033263 | -0.00083365 | 0.0033263 | 0.00083361 | 5.6116e-08 | -3.7545e-08 | 0.0050584 | 0.0050584 | 0.0050584 | 0.97848 | -0.41384 | 0.9785 | -0.41348 | 1.3897
107 | -0.0061675 | -0.0015457 | 0.0061679 | 0.0015458 | 3.472e-07 | 8.9989e-08 | 0.009379 | 0.009379 | 0.009379 | 0.9785 | -0.41348 | 0.97856 | -0.4123 | 2.5767
108 | 0.0022129 | 0.00055456 | -0.0022129 | -0.0005546 | 1.815e-08 | -4.2558e-08 | 0.0033576 | 0.0033576 | 0.0033576 | 0.98071 | -0.3715 | 0.98071 | -0.37167 | 0.92241
109 | 0.0090518 | 0.0022686 | -0.0090517 | -0.0022686 | 8.2288e-08 | 3.7302e-08 | 0.013579 | 0.013579 | 0.013579 | 0.99193 | -0.15346 | 0.99192 | -0.15365 | 3.7304
110 | 0.0069454 | 0.0017407 | -0.0069452 | -0.0017406 | 1.9811e-07 | 6.3973e-08 | 0.010419 | 0.010419 | 0.010419 | 0.99192 | -0.15365 | 0.99189 | -0.15425 | 2.8624
111 | -0.30307 | -0.077284 | 0.30314 | 0.077327 | 6.7286e-05 | 4.2883e-05 | 0.45455 | 0.45455 | 0.45455 | 0.99316 | -0.12987 | 0.9934 | -0.12527 | 31.2193
112 | -0.30674 | -0.07823 | 0.30729 | 0.07858 | 0.00055037 | 0.0003508 | 0.45995 | 0.45995 | 0.45995 | 0.9934 | -0.12527 | 0.99535 | -0.088185 | 31.5898
113 | 0.12172 | 0.030862 | -0.12155 | -0.030749 | 0.00017598 | 0.00011244 | 0.1821 | 0.1821 | 0.1821 | 0.99535 | -0.088185 | 0.99378 | -0.11831 | 50.0273
114 | -0.42901 | -0.10944 | 0.42989 | 0.11 | 0.00087272 | 0.00055736 | 0.64205 | 0.64205 | 0.64205 | 0.99535 | -0.088185 | 0.99756 | -0.046158 | 44.0966
115 | 0.011838 | 0.0029676 | -0.011835 | -0.0029661 | 2.905e-06 | 1.5398e-06 | 0.017725 | 0.017725 | 0.017725 | 0.99378 | -0.11831 | 0.99351 | -0.12346 | 4.8696
116 | -0.44728 | -0.11436 | 0.44795 | 0.11479 | 0.00067055 | 0.00042831 | 0.66798 | 0.66798 | 0.66798 | 0.99756 | -0.046158 | 0.99919 | -0.015222 | 45.8779
117 | 0.0079846 | 0.0020012 | -0.0079841 | -0.002001 | 5.0628e-07 | 2.0178e-07 | 0.011959 | 0.011959 | 0.011959 | 0.99351 | -0.12346 | 0.99344 | -0.12479 | 3.2854
118 | -0.45127 | -0.11562 | 0.45161 | 0.11583 | 0.00033317 | 0.00021282 | 0.67294 | 0.67294 | 0.67294 | 0.99919 | -0.015222 | 1 | 0 | 46.2184
119 | 0.0064239 | 0.0016099 | -0.0064239 | -0.0016099 | 1.3957e-08 | 3.7275e-09 | 0.0096219 | 0.0096219 | 0.0096219 | 0.99344 | -0.12479 | 0.99344 | -0.12484 | 2.6434
120 | 0.010541 | 0.0026419 | -0.01054 | -0.0026416 | 4.471e-07 | 2.2256e-07 | 0.015685 | 0.015685 | 0.015685 | 1 | 0 | 0.99995 | -0.00089037 | 4.309
121 | 0.0039606 | 0.0009926 | -0.0039606 | -0.00099261 | 4.623e-08 | -1.5768e-08 | 0.0059324 | 0.0059324 | 0.0059324 | 0.99344 | -0.12484 | 0.99343 | -0.12508 | 1.6298
122 | 0.0084756 | 0.0021242 | -0.0084754 | -0.0021241 | 2.2047e-07 | 9.262e-08 | 0.012612 | 0.012612 | 0.012612 | 0.99995 | -0.00089037 | 0.99993 | -0.0014364 | 3.465
123 | -0.11146 | -0.028214 | 0.11146 | 0.028215 | 1.6591e-06 | 1.0307e-06 | 0.16935 | 0.16935 | 0.16935 | 0.97994 | -0.38475 | 0.97995 | -0.38444 | 11.631
124 | 0.0019278 | 0.00048305 | -0.0019278 | -0.00048315 | 2.9886e-08 | -9.7813e-08 | 0.0029287 | 0.0029288 | 0.0029288 | 0.97947 | -0.39389 | 0.97945 | -0.39422 | 0.80461
125 | -0.11293 | -0.028582 | 0.11294 | 0.028592 | 1.5882e-05 | 9.8745e-06 | 0.17157 | 0.17157 | 0.17157 | 0.97995 | -0.38444 | 0.98011 | -0.38151 | 11.7838
126 | -0.0053608 | -0.0013435 | 0.0053611 | 0.0013436 | 3.441e-07 | 4.5978e-08 | 0.0081428 | 0.0081428 | 0.0081428 | 0.97962 | -0.39098 | 0.97969 | -0.38963 | 2.237
127 | -0.0069822 | -0.0017498 | 0.0069827 | 0.00175 | 5.0385e-07 | 1.7202e-07 | 0.010605 | 0.010605 | 0.010605 | 0.97969 | -0.38963 | 0.97977 | -0.38811 | 2.9135
128 | 0.0016211 | 0.00040622 | -0.0016211 | -0.00040628 | 1.2211e-08 | -5.9815e-08 | 0.0024622 | 0.0024622 | 0.0024622 | 0.97969 | -0.38963 | 0.97968 | -0.38979 | 0.67644
129 | -0.21592 | -0.054972 | 0.21594 | 0.054984 | 1.9126e-05 | 1.2142e-05 | 0.32542 | 0.32542 | 0.32542 | 0.98824 | -0.2242 | 0.98833 | -0.22236 | 22.3503
130 | 0.20999 | 0.053486 | -0.20969 | -0.053298 | 0.00029655 | 0.00018817 | 0.31649 | 0.31649 | 0.31649 | 0.98824 | -0.2242 | 0.98671 | -0.25352 | 21.7373
131 | 0.20969 | 0.053298 | -0.20967 | -0.053284 | 2.1458e-05 | 1.3616e-05 | 0.31649 | 0.31649 | 0.31649 | 0.98671 | -0.25352 | 0.9866 | -0.25564 | 21.7373
132 | 0.20967 | 0.053284 | -0.20957 | -0.053219 | 0.00010245 | 6.501e-05 | 0.31649 | 0.31649 | 0.31649 | 0.9866 | -0.25564 | 0.98608 | -0.2658 | 21.7373
133 | 0.20815 | 0.052863 | -0.20808 | -0.052819 | 6.9784e-05 | 4.4278e-05 | 0.31435 | 0.31435 | 0.31435 | 0.98608 | -0.2658 | 0.98571 | -0.27276 | 21.5901
134 | -0.0020725 | -0.00051942 | 0.0020725 | 0.00051935 | 2.5553e-08 | -7.2075e-08 | 0.0031314 | 0.0031314 | 0.0031314 | 0.98485 | -0.28956 | 0.98486 | -0.2893 | 0.86027
135 | -0.0020725 | -0.00051935 | 0.0020726 | 0.00051923 | 4.391e-08 | -1.2386e-07 | 0.0031314 | 0.0031313 | 0.0031314 | 0.98486 | -0.2893 | 0.98488 | -0.28885 | 0.86026
136 | -0.006889 | -0.0017266 | 0.0068893 | 0.0017266 | 2.2017e-07 | 7.3164e-08 | 0.010455 | 0.010455 | 0.010455 | 0.98048 | -0.37458 | 0.98052 | -0.37391 | 2.8723
137 | -0.03852 | -0.0096682 | 0.038535 | 0.0096779 | 1.5445e-05 | 9.7329e-06 | 0.058462 | 0.058462 | 0.058462 | 0.98052 | -0.37391 | 0.98094 | -0.36551 | 16.061
138 | 0.03163 | 0.0079415 | -0.03162 | -0.007935 | 1.0434e-05 | 6.5253e-06 | 0.048007 | 0.048007 | 0.048007 | 0.98052 | -0.37391 | 0.98016 | -0.38083 | 13.1888
139 | -0.0039666 | -0.0009939 | 0.0039667 | 0.00099387 | 1.0612e-07 | -3.236e-08 | 0.0059928 | 0.0059928 | 0.0059928 | 0.98488 | -0.28885 | 0.98491 | -0.28829 | 1.6464
140 | -0.0407 | -0.01022 | 0.040711 | 0.010228 | 1.1596e-05 | 7.3191e-06 | 0.061745 | 0.061745 | 0.061745 | 0.98094 | -0.36551 | 0.98125 | -0.35954 | 16.9629
141 | 0.028744 | 0.0072143 | -0.028738 | -0.0072101 | 6.7919e-06 | 4.227e-06 | 0.043642 | 0.043642 | 0.043642 | 0.98016 | -0.38083 | 0.97991 | -0.38578 | 11.9895
142 | -0.0084493 | -0.0021175 | 0.0084497 | 0.0021177 | 4.0304e-07 | 1.7574e-07 | 0.012832 | 0.012832 | 0.012832 | 0.97977 | -0.38811 | 0.97982 | -0.38711 | 3.5253
143 | -0.0090828 | -0.002276 | 0.0090829 | 0.0022761 | 1.0719e-07 | 4.927e-08 | 0.01372 | 0.01372 | 0.01372 | 0.98506 | -0.28546 | 0.98507 | -0.28521 | 3.7693
144 | -0.0084497 | -0.0021177 | 0.0084504 | 0.002118 | 7.427e-07 | 3.2382e-07 | 0.012832 | 0.012832 | 0.012832 | 0.97982 | -0.38711 | 0.97991 | -0.38527 | 3.5253
145 | -0.12433 | -0.031446 | 0.12435 | 0.031458 | 1.8785e-05 | 1.1739e-05 | 0.18886 | 0.18886 | 0.18886 | 0.98011 | -0.38151 | 0.98027 | -0.37836 | 12.9711
146 | 0.011386 | 0.0028542 | -0.011384 | -0.0028535 | 1.3908e-06 | 7.3372e-07 | 0.017286 | 0.017287 | 0.017287 | 0.98011 | -0.38151 | 0.97997 | -0.38408 | 4.749
147 | -0.009917 | -0.0024856 | 0.0099175 | 0.0024859 | 5.6299e-07 | 2.7691e-07 | 0.015059 | 0.015059 | 0.015059 | 0.97991 | -0.38527 | 0.97997 | -0.38408 | 4.1371
148 | -0.12711 | -0.032151 | 0.12712 | 0.032158 | 1.0812e-05 | 6.7633e-06 | 0.19306 | 0.19306 | 0.19306 | 0.98027 | -0.37836 | 0.98036 | -0.37659 | 13.2594
149 | 0.018563 | 0.0046529 | -0.018561 | -0.0046519 | 1.7221e-06 | 1.032e-06 | 0.02845 | 0.02845 | 0.02845 | 0.97091 | -0.56191 | 0.97081 | -0.56385 | 7.8159
150 | 0.13284 | 0.033609 | -0.13283 | -0.033602 | 1.2047e-05 | 7.5508e-06 | 0.20165 | 0.20165 | 0.20165 | 0.98078 | -0.36838 | 0.98068 | -0.37027 | 13.8497
151 | 0.12989 | 0.032867 | -0.12989 | -0.032864 | 4.9741e-06 | 3.1146e-06 | 0.1972 | 0.1972 | 0.1972 | 0.98068 | -0.37027 | 0.98064 | -0.37107 | 13.5441
152 | 0.0029332 | 0.00073493 | -0.0029331 | -0.00073503 | 9.52e-08 | -1.0078e-07 | 0.0044506 | 0.0044506 | 0.0044506 | 0.98068 | -0.37027 | 0.98065 | -0.37095 | 1.2227
153 | 0.12882 | 0.032596 | -0.12878 | -0.032574 | 3.4142e-05 | 2.1371e-05 | 0.19558 | 0.19558 | 0.19558 | 0.98064 | -0.37107 | 0.98036 | -0.37659 | 13.4326
154 | 0.0014666 | 0.00036748 | -0.0014665 | -0.00036755 | 1.2292e-08 | -7.5643e-08 | 0.0022253 | 0.0022253 | 0.0022253 | 0.98065 | -0.37095 | 0.98064 | -0.37112 | 0.61136

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47386 | 0.121

## res_load
| p_mw | q_mvar
0 | 0.003559 | 0.00089196
1 | 0.0030127 | 0.00075505
2 | 0.0067931 | 0.0017025
3 | 0.0049081 | 0.0012301
4 | 0.0068029 | 0.001705
5 | 0.0031481 | 0.00078899
6 | 0.0069241 | 0.0017353
7 | 0.0022142 | 0.00055494
8 | 0.0034903 | 0.00087475
9 | 0.0056459 | 0.001415
10 | 0.0035473 | 0.00088903
11 | 0.0023221 | 0.00058196
12 | 0.0039858 | 0.00099893
13 | 0.0031426 | 0.00078762
14 | 0.007569 | 0.001897
15 | 0.0070664 | 0.001771
16 | 0.0070611 | 0.0017697
17 | 0.0057389 | 0.0014383
18 | 0.0063189 | 0.0015837
19 | 0.0029149 | 0.00073054
20 | 0.0019522 | 0.00048928
21 | 0.012555 | 0.0031467
22 | 0.0025037 | 0.00062749
23 | 0.0014377 | 0.00036032
24 | 0.001775 | 0.00044486
25 | 0.0014669 | 0.00036764
26 | 0.012426 | 0.0031143
27 | 0.0049595 | 0.001243
28 | 0.017345 | 0.0043471
29 | 0.014697 | 0.0036834
30 | 0.0021704 | 0.00054395
31 | 0.0013386 | 0.00033548
32 | 0.0012588 | 0.00031549
33 | 0.0010507 | 0.00026333
34 | 0.0023531 | 0.00058973
35 | 0.0021194 | 0.00053116
36 | 0.0012915 | 0.00032369
37 | 0.0026686 | 0.00066881
38 | 0.001333 | 0.00033407
39 | 0.0015862 | 0.00039754
40 | 0.0027064 | 0.00067829
41 | 0.0023752 | 0.00059528
42 | 0.0014665 | 0.00036755
43 | 0.0014679 | 0.00036788
44 | 0.0014665 | 0.00036755
45 | 0.0096584 | 0.0024206
46 | 0.012461 | 0.0031231
47 | 0.0034317 | 0.00086006
48 | 0.0095966 | 0.0024051
49 | 0.002308 | 0.00057844
50 | 0.0014895 | 0.0003733
51 | 0.0085441 | 0.0021413
52 | 0.0028629 | 0.00071752
53 | 0.0057537 | 0.001442
54 | 0.0065926 | 0.0016523
55 | 0.0023498 | 0.00058891
56 | 0.0030144 | 0.00075548
57 | 0.0064269 | 0.0016107
58 | 0.0065958 | 0.0016531
59 | 0.0034263 | 0.00085871
60 | 0.006546 | 0.0016406
61 | 0.0035021 | 0.00087771
62 | 0.0033263 | 0.00083365
63 | 0.0028412 | 0.00071206
64 | 0.0068502 | 0.0017168
65 | 0.0023968 | 0.00060071
66 | 0.0022129 | 0.0005546
67 | 0.0031019 | 0.00077741
68 | 0.0021064 | 0.00052791
69 | 0.0069452 | 0.0017406
70 | 0.0032257 | 0.00080845
71 | 0.0036018 | 0.00090269
72 | 0.017388 | 0.0043579
73 | 0.0038502 | 0.00096494
74 | 0.0033292 | 0.00083438
75 | 0.0015602 | 0.00039102
76 | 0.010063 | 0.0025221
77 | 0.0024632 | 0.00061735
78 | 0.0020645 | 0.00051742
79 | 0.0039606 | 0.00099261
80 | 0.0016048 | 0.00040221
81 | 0.0062179 | 0.0015584
82 | 0.0014661 | 0.00036743
83 | 0.0019278 | 0.00048315
84 | 0.0053608 | 0.0013435
85 | 0.0084754 | 0.0021241
86 | 0.0059288 | 0.0014859
87 | 0.0034209 | 0.00085735
88 | 0.0014202 | 0.00035594
89 | 0.0020725 | 0.00051942
90 | 0.0013305 | 0.00033346
91 | 0.006889 | 0.0017266
92 | 0.001894 | 0.00047468
93 | 0.0021643 | 0.00054243
94 | 0.0028756 | 0.00072068
95 | 0.0015036 | 0.00037683
96 | 0.0016211 | 0.00040628
97 | 0.0014666 | 0.00036755
98 | 0.0013035 | 0.00032669
99 | 0.0011828 | 0.00029643
100 | 0.0010329 | 0.00025887
101 | 0.0014666 | 0.00036755
102 | 0.0027651 | 0.000693
103 | 0.0014669 | 0.00036764
104 | 0.0018925 | 0.0004743
105 | 0.018561 | 0.0046519
106 | 0.0025441 | 0.00063762
107 | 0.0010698 | 0.00026811
108 | 0.0014665 | 0.00036755
109 | 0.0016619 | 0.0004165
110 | 0.0014665 | 0.00036755

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1