## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-132_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-132_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-132_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-132_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_230-132_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_230-132_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_230-132_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_230-132_0_4_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_230-132_0_4_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_230-132_0_4_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_230-132_0_4_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_230-132_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_230-132_0_4_node_65 | 0.4 | n |  | TRUE
13 | bus_LV_230-132_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_230-132_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_230-132_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_230-132_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_230-132_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_230-132_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_230-132_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_230-132_0_4_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_230-132_0_4_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_230-132_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_230-132_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_230-132_0_4_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_230-132_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_230-132_0_4_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_230-132_0_4_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_230-132_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_230-132_0_4_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_230-132_0_4_node_47 | 0.4 | n |  | TRUE
31 | bus_LV_230-132_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_230-132_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_230-132_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_230-132_0_4_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_230-132_0_4_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_230-132_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_230-132_0_4_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_230-132_0_4_node_62 | 0.4 | n |  | TRUE
39 | bus_LV_230-132_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_230-132_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_230-132_0_4_node_51 | 0.4 | n |  | TRUE
42 | bus_LV_230-132_0_4_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_230-132_0_4_node_56 | 0.4 | n |  | TRUE
44 | bus_LV_230-132_0_4_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_230-132_0_4_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_230-132_0_4_node_61 | 0.4 | n |  | TRUE
47 | bus_LV_230-132_0_4_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_230-132_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_230-132_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_230-132_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_230-132_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_230-132_0_4_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_230-132_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_230-132_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_230-132_0_4_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_230-132_0_4_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_230-132_0_4_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_230-132_0_4_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_230-132_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_MV_370_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-132_0_4_load_0 | 0 | 0.0023155 | 0.00058032 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-132_0_4_load_23 | 6 | 0.00031778 | 7.9643e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-132_0_4_load_28 | 8 | 0.014703 | 0.0036848 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-132_0_4_load_27 | 9 | 0.0011376 | 0.00028511 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-132_0_4_load_24 | 10 | 0.0011263 | 0.00028228 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-132_0_4_load_65 | 12 | 0.0027015 | 0.00067706 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-132_0_4_load_29 | 16 | 0.0014074 | 0.00035273 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-132_0_4_load_60 | 20 | 0.01445 | 0.0036214 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-132_0_4_load_34 | 21 | 0.033903 | 0.0084969 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-132_0_4_load_50 | 24 | 0.037196 | 0.0093223 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-132_0_4_load_36 | 26 | 0.0076188 | 0.0019095 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-132_0_4_load_33 | 27 | 0.036995 | 0.0092719 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-132_0_4_load_49 | 29 | 0.0051459 | 0.0012897 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-132_0_4_load_47 | 30 | 0.0067225 | 0.0016848 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-132_0_4_load_31 | 33 | 0.0071524 | 0.0017926 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-132_0_4_load_48 | 34 | 0.0068553 | 0.0017181 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-132_0_4_load_66 | 35 | 0.0080171 | 0.0020093 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-132_0_4_load_62 | 38 | 0.0014428 | 0.00036159 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-132_0_4_load_30 | 39 | 0.00015708 | 3.9367e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-132_0_4_load_51 | 41 | 0.03096 | 0.0077593 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-132_0_4_load_53 | 44 | 0.0077665 | 0.0019465 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-132_0_4_load_43 | 45 | 0.0087372 | 0.0021898 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-132_0_4_load_61 | 46 | 0.0012042 | 0.00030179 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-132_0_4_load_54 | 47 | 0.0057873 | 0.0014504 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-132_0_4_load_37 | 48 | 0.030967 | 0.007761 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-132_0_4_load_38 | 49 | 0.023198 | 0.0058139 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-132_0_4_load_39 | 50 | 0.031922 | 0.0080005 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-132_0_4_load_40 | 51 | 0.023497 | 0.0058888 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-132_0_4_load_42 | 54 | 0.047041 | 0.01179 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-132_0_4_load_44 | 55 | 0.0064075 | 0.0016059 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-132_0_4_load_46 | 56 | 0.011269 | 0.0028243 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-132_0_4_load_58 | 57 | 0.0085783 | 0.0021499 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-132_0_4_load_59 | 58 | 0.046693 | 0.011702 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-132_0_4_load_55 | 59 | 0.007929 | 0.0019872 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-132_0_4_line_0 |  | 0 | 1 | 0.10143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-132_0_4_line_1 |  | 0 | 2 | 0.025933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-132_0_4_line_2 |  | 1 | 3 | 0.056804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-132_0_4_line_3 |  | 1 | 4 | 0.076355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-132_0_4_line_4 |  | 2 | 5 | 0.004351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-132_0_4_line_5 |  | 2 | 6 | 0.010744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-132_0_4_line_6 |  | 3 | 10 | 0.11349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-132_0_4_line_7 |  | 4 | 11 | 0.093125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_230-132_0_4_line_8 |  | 4 | 12 | 0.10459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_230-132_0_4_line_9 |  | 5 | 9 | 0.013822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-132_0_4_line_10 |  | 5 | 7 | 0.017441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-132_0_4_line_11 |  | 7 | 8 | 0.033186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-132_0_4_line_12 |  | 8 | 13 | 0.029892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-132_0_4_line_13 |  | 11 | 25 | 0.052534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_230-132_0_4_line_14 |  | 11 | 26 | 0.023813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_230-132_0_4_line_15 |  | 12 | 35 | 0.023175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_230-132_0_4_line_16 |  | 13 | 14 | 0.006503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-132_0_4_line_17 |  | 14 | 15 | 0.13215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-132_0_4_line_18 |  | 15 | 16 | 0.097801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-132_0_4_line_19 |  | 16 | 39 | 0.073552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-132_0_4_line_20 |  | 17 | 18 | 0.023816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_230-132_0_4_line_21 |  | 17 | 19 | 0.038803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_230-132_0_4_line_22 |  | 17 | 20 | 0.017251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-132_0_4_line_23 |  | 18 | 21 | 0.021292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_230-132_0_4_line_24 |  | 19 | 24 | 0.017935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_230-132_0_4_line_25 |  | 21 | 40 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_230-132_0_4_line_26 |  | 22 | 23 | 0.031865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_230-132_0_4_line_27 |  | 22 | 24 | 0.0065839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_230-132_0_4_line_28 |  | 23 | 34 | 0.02922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_230-132_0_4_line_29 |  | 25 | 27 | 0.010749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-132_0_4_line_30 |  | 26 | 40 | 0.018849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_230-132_0_4_line_31 |  | 28 | 29 | 0.015692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_230-132_0_4_line_32 |  | 28 | 30 | 0.00088356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_230-132_0_4_line_33 |  | 29 | 43 | 0.00922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_230-132_0_4_line_34 |  | 30 | 34 | 0.021622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_230-132_0_4_line_35 |  | 31 | 32 | 0.030708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-132_0_4_line_36 |  | 31 | 33 | 0.013697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-132_0_4_line_37 |  | 32 | 43 | 0.017873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-132_0_4_line_38 |  | 32 | 44 | 0.014073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-132_0_4_line_39 |  | 35 | 56 | 0.02 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_230-132_0_4_line_40 |  | 36 | 37 | 0.10539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_230-132_0_4_line_41 |  | 36 | 38 | 0.073015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_230-132_0_4_line_42 |  | 37 | 45 | 0.08727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_230-132_0_4_line_43 |  | 38 | 46 | 0.020433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_230-132_0_4_line_44 |  | 41 | 42 | 0.0042335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-132_0_4_line_45 |  | 42 | 43 | 0.027272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_230-132_0_4_line_46 |  | 42 | 50 | 0.018196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_230-132_0_4_line_47 |  | 44 | 47 | 0.018005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-132_0_4_line_48 |  | 45 | 54 | 0.072997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_230-132_0_4_line_49 |  | 47 | 59 | 0.025798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-132_0_4_line_50 |  | 48 | 49 | 0.017952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-132_0_4_line_51 |  | 48 | 50 | 0.020342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-132_0_4_line_52 |  | 49 | 51 | 0.017756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-132_0_4_line_53 |  | 51 | 52 | 0.010962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-132_0_4_line_54 |  | 52 | 53 | 0.029018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-132_0_4_line_55 |  | 53 | 57 | 0.030492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-132_0_4_line_56 |  | 54 | 55 | 0.031308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_230-132_0_4_line_57 |  | 55 | 56 | 0.014879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_230-132_0_4_line_58 |  | 57 | 58 | 0.023501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-132_0_4_trafo_39 | 0.63 MVA 20/0.4 kV | 60 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2695476.2866 | 1260061.9254 | 2695476.6583 | 1260052.913 | 2695480.4738 | 1259994.9502 | 2695484.6224 | 1259960.8789
1 | 2695487.4329 | 1259935.1033 | 2695486.8266 | 1259942.7774 | 2695484.6224 | 1259960.8789
2 | 2695476.2866 | 1260061.9254 | 2695476.1095 | 1260065.4253 | 2695477.1941 | 1260068.2784 | 2695479.3955 | 1260070.5936 | 2695482.922 | 1260072.541 | 2695492.4955 | 1260077.1881 | 2695494.3113 | 1260074.4374 | 2695506.2876 | 1260047.9316
3 | 2695476.2866 | 1260061.9254 | 2695476.1095 | 1260065.4253 | 2695477.1941 | 1260068.2784 | 2695479.3955 | 1260070.5936 | 2695482.922 | 1260072.541 | 2695492.4955 | 1260077.1881 | 2695495.6025 | 1260078.5059 | 2695539.2125 | 1260096.9803 | 2695540.3208 | 1260097.4318
4 | 2695487.4329 | 1259935.1033 | 2695483.1248 | 1259934.411
5 | 2695487.4329 | 1259935.1033 | 2695498.044 | 1259936.7898
6 | 2695506.2876 | 1260047.9316 | 2695530.6472 | 1259982.8057 | 2695546.0599 | 1259941.6357
7 | 2695540.3208 | 1260097.4318 | 2695548.8984 | 1260100.2615 | 2695557.9959 | 1260102.6437 | 2695567.0698 | 1260106.0151 | 2695571.9117 | 1260096.9972 | 2695587.2348 | 1260063.5177 | 2695592.7893 | 1260057.5137 | 2695599.2112 | 1260055.2156 | 2695598.322 | 1260052.399
8 | 2695540.3208 | 1260097.4318 | 2695572.3434 | 1260012.9254 | 2695577.4695 | 1259999.6669
9 | 2695483.1248 | 1259934.411 | 2695483.9066 | 1259920.6108
10 | 2695474.6218 | 1259940.4787 | 2695482.6187 | 1259943.3433 | 2695483.1248 | 1259934.411
11 | 2695474.6218 | 1259940.4787 | 2695469.5478 | 1259938.662 | 2695470.4516 | 1259910.8803
12 | 2695477.9921 | 1259885.3443 | 2695471.1791 | 1259888.5147 | 2695470.4516 | 1259910.8803
13 | 2695598.322 | 1260052.399 | 2695599.2112 | 1260055.2156 | 2695602.8937 | 1260057.7661 | 2695607.6564 | 1260060.6453 | 2695615.3993 | 1260065.6856 | 2695619.0287 | 1260067.7904 | 2695619.7008 | 1260068.1793 | 2695639.2298 | 1260067.828 | 2695642.286 | 1260072.748
14 | 2695598.322 | 1260052.399 | 2695609.3631 | 1260031.2998
15 | 2695577.4695 | 1259999.6669 | 2695585.8268 | 1259978.0513
16 | 2695477.9921 | 1259885.3443 | 2695483.9012 | 1259882.593
17 | 2695391.0476 | 1259803.9768 | 2695394.6265 | 1259809.2276 | 2695401.5664 | 1259810.8074 | 2695413.3242 | 1259815.1338 | 2695418.8621 | 1259817.1691 | 2695421.9046 | 1259818.2858 | 2695428.4018 | 1259820.6702 | 2695435.0038 | 1259823.1009 | 2695439.5676 | 1259824.7758 | 2695449.4442 | 1259828.4158 | 2695452.8517 | 1259830.2722 | 2695461.566 | 1259836.3399 | 2695469.0911 | 1259842.7553 | 2695475.3582 | 1259850.9853 | 2695481.5784 | 1259867.2543 | 2695483.9012 | 1259882.593
18 | 2695391.0476 | 1259803.9768 | 2695394.4975 | 1259789.1872 | 2695399.0459 | 1259772.1913 | 2695403.9744 | 1259754.5344 | 2695409.4974 | 1259736.9426 | 2695417.5125 | 1259714.8763 | 2695419.291 | 1259710.4464
19 | 2695446.7715 | 1259642.2457 | 2695444.5109 | 1259649.2813 | 2695426.3797 | 1259692.7905 | 2695419.291 | 1259710.4464
20 | 2695639.7876 | 1260039.403 | 2695646.6462 | 1260032.0079 | 2695654.7559 | 1260020.8967
21 | 2695654.7559 | 1260020.8967 | 2695658.0365 | 1260021.7282 | 2695664.4028 | 1260023.3324 | 2695693.1976 | 1260021.4965
22 | 2695654.7559 | 1260020.8967 | 2695658.3211 | 1260013.9265 | 2695659.1814 | 1260004.544 | 2695659.1814 | 1260004.544
23 | 2695639.7876 | 1260039.403 | 2695637.4235 | 1260030.8357 | 2695633.0266 | 1260023.9813 | 2695629.8387 | 1260021.154
24 | 2695693.1976 | 1260021.4965 | 2695694.2533 | 1260039.4004
25 | 2695618.1023 | 1260014.5993 | 2695626.2195 | 1260017.9442 | 2695629.8387 | 1260021.154
26 | 2695694.6408 | 1260045.9728 | 2695718.5877 | 1260046.5161 | 2695723.4831 | 1260052.8337
27 | 2695694.6408 | 1260045.9728 | 2695694.2533 | 1260039.4004
28 | 2695723.4831 | 1260052.8337 | 2695721.6004 | 1260023.6746
29 | 2695642.286 | 1260072.748 | 2695652.9955 | 1260071.8268
30 | 2695618.1023 | 1260014.5993 | 2695609.3631 | 1260031.2998
31 | 2695720.1502 | 1260001.2161 | 2695719.0314 | 1259985.5639
32 | 2695720.2072 | 1260002.0978 | 2695720.1502 | 1260001.2161
33 | 2695718.374 | 1259976.3673 | 2695719.0314 | 1259985.5639
34 | 2695720.2072 | 1260002.0978 | 2695721.6004 | 1260023.6746
35 | 2695736.2528 | 1259975.0666 | 2695766.9816 | 1259972.9844
36 | 2695766.9816 | 1259972.9844 | 2695768.1796 | 1259986.6288
37 | 2695718.374 | 1259976.3673 | 2695736.2528 | 1259975.0666
38 | 2695736.2528 | 1259975.0666 | 2695735.054 | 1259961.0446
39 | 2695585.8268 | 1259978.0513 | 2695593.0391 | 1259959.397
40 | 2695766.7407 | 1259713.2382 | 2695757.2424 | 1259718.3553 | 2695751.1666 | 1259724.8622 | 2695736.8253 | 1259728.7889 | 2695725.1557 | 1259734.8495 | 2695709.278 | 1259748.4703 | 2695701.4559 | 1259763.2112 | 2695690.1215 | 1259779.7746
41 | 2695766.7407 | 1259713.2382 | 2695772.7184 | 1259742.5808 | 2695777.3441 | 1259758.5796 | 2695787.9303 | 1259782.781
42 | 2695690.1215 | 1259779.7746 | 2695677.9473 | 1259791.4093 | 2695666.2601 | 1259805.098 | 2695653.4635 | 1259822.1271 | 2695647.1277 | 1259831.6768 | 2695638.0744 | 1259848.444 | 2695637.7982 | 1259848.9924
43 | 2695796.1191 | 1259801.5013 | 2695787.9303 | 1259782.781
44 | 2695691.0919 | 1259978.3388 | 2695691.2982 | 1259982.5673
45 | 2695718.374 | 1259976.3673 | 2695691.0919 | 1259978.3388
46 | 2695691.0919 | 1259978.3388 | 2695689.8089 | 1259960.1885
47 | 2695735.054 | 1259961.0446 | 2695733.5203 | 1259943.1051
48 | 2695610.1796 | 1259916.5152 | 2695626.9318 | 1259872.7501 | 2695633.526 | 1259857.4777 | 2695637.7982 | 1259848.9924
49 | 2695724.8047 | 1259920.1157 | 2695732.3106 | 1259928.9546 | 2695733.5203 | 1259943.1051
50 | 2695694.5284 | 1259923.0325 | 2695689.7708 | 1259936.0723 | 2695688.3746 | 1259939.8973 | 2695688.3746 | 1259939.8973
51 | 2695689.8089 | 1259960.1885 | 2695688.3746 | 1259939.8973
52 | 2695694.5284 | 1259923.0325 | 2695700.6144 | 1259906.3517
53 | 2695704.3716 | 1259896.054 | 2695700.6144 | 1259906.3517
54 | 2695704.3716 | 1259896.054 | 2695685.2316 | 1259874.1936
55 | 2695685.2316 | 1259874.1936 | 2695674.0892 | 1259870.5216 | 2695667.1182 | 1259887.9383
56 | 2695610.1796 | 1259916.5152 | 2695605.7676 | 1259928.0415 | 2695598.509 | 1259945.2492 | 2695598.4045 | 1259945.5195
57 | 2695598.4045 | 1259945.5195 | 2695593.0391 | 1259959.397
58 | 2695667.1182 | 1259887.9383 | 2695658.3855 | 1259909.7565

## bus_geodata
| x | y | coords
0 | 2695484.6224 | 1259960.8789
1 | 2695476.2866 | 1260061.9254
2 | 2695487.4329 | 1259935.1033
3 | 2695506.2876 | 1260047.9316
4 | 2695540.3208 | 1260097.4318
5 | 2695483.1248 | 1259934.411
6 | 2695498.044 | 1259936.7898
7 | 2695474.6218 | 1259940.4787
8 | 2695470.4516 | 1259910.8803
9 | 2695483.9066 | 1259920.6108
10 | 2695546.0599 | 1259941.6357
11 | 2695598.322 | 1260052.399
12 | 2695577.4695 | 1259999.6669
13 | 2695477.9921 | 1259885.3443
14 | 2695483.9012 | 1259882.593
15 | 2695391.0476 | 1259803.9768
16 | 2695419.291 | 1259710.4464
17 | 2695654.7559 | 1260020.8967
18 | 2695639.7876 | 1260039.403
19 | 2695693.1976 | 1260021.4965
20 | 2695659.1814 | 1260004.544
21 | 2695629.8387 | 1260021.154
22 | 2695694.6408 | 1260045.9728
23 | 2695723.4831 | 1260052.8337
24 | 2695694.2533 | 1260039.4004
25 | 2695642.286 | 1260072.748
26 | 2695609.3631 | 1260031.2998
27 | 2695652.9955 | 1260071.8268
28 | 2695720.1502 | 1260001.2161
29 | 2695719.0314 | 1259985.5639
30 | 2695720.2072 | 1260002.0978
31 | 2695766.9816 | 1259972.9844
32 | 2695736.2528 | 1259975.0666
33 | 2695768.1796 | 1259986.6288
34 | 2695721.6004 | 1260023.6746
35 | 2695585.8268 | 1259978.0513
36 | 2695766.7407 | 1259713.2382
37 | 2695690.1215 | 1259779.7746
38 | 2695787.9303 | 1259782.781
39 | 2695446.7715 | 1259642.2457
40 | 2695618.1023 | 1260014.5993
41 | 2695691.2982 | 1259982.5673
42 | 2695691.0919 | 1259978.3388
43 | 2695718.374 | 1259976.3673
44 | 2695735.054 | 1259961.0446
45 | 2695637.7982 | 1259848.9924
46 | 2695796.1191 | 1259801.5013
47 | 2695733.5203 | 1259943.1051
48 | 2695688.3746 | 1259939.8973
49 | 2695694.5284 | 1259923.0325
50 | 2695689.8089 | 1259960.1885
51 | 2695700.6144 | 1259906.3517
52 | 2695704.3716 | 1259896.054
53 | 2695685.2316 | 1259874.1936
54 | 2695610.1796 | 1259916.5152
55 | 2695598.4045 | 1259945.5195
56 | 2695593.0391 | 1259959.397
57 | 2695667.1182 | 1259887.9383
58 | 2695658.3855 | 1259909.7565
59 | 2695724.8047 | 1259920.1157
60 | 2695691.0919 | 1259978.3388

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97186 | -0.54262 | 0.0023155 | 0.00058032
1 | 0.97376 | -0.50516 | 0 | 0
2 | 0.97143 | -0.55111 | 0 | 0
3 | 0.9737 | -0.50634 | 0 | 0
4 | 0.97526 | -0.47547 | 0 | 0
5 | 0.97136 | -0.55251 | 0 | 0
6 | 0.97142 | -0.55118 | 0.00031778 | 7.9643e-05
7 | 0.97109 | -0.55776 | 0 | 0
8 | 0.97059 | -0.56775 | 0.014703 | 0.0036848
9 | 0.97134 | -0.5528 | 0.0011376 | 0.00028511
10 | 0.97358 | -0.50869 | 0.0011263 | 0.00028228
11 | 0.9784 | -0.41419 | 0 | 0
12 | 0.97244 | -0.53112 | 0.0027015 | 0.00067706
13 | 0.97054 | -0.56862 | 0 | 0
14 | 0.97053 | -0.56881 | 0 | 0
15 | 0.97034 | -0.57265 | 0 | 0
16 | 0.9702 | -0.57549 | 0.0014074 | 0.00035273
17 | 0.98362 | -0.31259 | 0 | 0
18 | 0.98224 | -0.33932 | 0 | 0
19 | 0.98604 | -0.26586 | 0 | 0
20 | 0.98339 | -0.31709 | 0.01445 | 0.0036214
21 | 0.98101 | -0.36327 | 0.033903 | 0.0084969
22 | 0.98764 | -0.23499 | 0 | 0
23 | 0.99 | -0.18988 | 0 | 0
24 | 0.98716 | -0.24434 | 0.037196 | 0.0093223
25 | 0.97749 | -0.4319 | 0 | 0
26 | 0.97947 | -0.39325 | 0.0076188 | 0.0019095
27 | 0.97713 | -0.43916 | 0.036995 | 0.0092719
28 | 0.99386 | -0.11616 | 0 | 0
29 | 0.99508 | -0.092947 | 0.0051459 | 0.0012897
30 | 0.99379 | -0.11747 | 0.0067225 | 0.0016848
31 | 0.99515 | -0.091921 | 0 | 0
32 | 0.99535 | -0.088056 | 0 | 0
33 | 0.99506 | -0.093645 | 0.0071524 | 0.0017926
34 | 0.99215 | -0.1487 | 0.0068553 | 0.0017181
35 | 0.97183 | -0.54311 | 0.0080171 | 0.0020093
36 | 0.97007 | -0.57802 | 0 | 0
37 | 0.97016 | -0.57629 | 0 | 0
38 | 0.97001 | -0.57922 | 0.0014428 | 0.00036159
39 | 0.97019 | -0.57571 | 0.00015708 | 3.9367e-05
40 | 0.98036 | -0.37583 | 0 | 0
41 | 0.9981 | -0.03582 | 0.03096 | 0.0077593
42 | 0.99822 | -0.033527 | 0 | 0
43 | 0.99582 | -0.079055 | 0 | 0
44 | 0.99508 | -0.093376 | 0.0077665 | 0.0019465
45 | 0.97023 | -0.57485 | 0.0087372 | 0.0021898
46 | 0.97 | -0.57937 | 0.0012042 | 0.00030179
47 | 0.99485 | -0.097725 | 0.0057873 | 0.0014504
48 | 0.99753 | -0.047249 | 0.030967 | 0.007761
49 | 0.99586 | -0.079368 | 0.023198 | 0.0058139
50 | 1 | 0 | -0.4573 | -0.11658
51 | 0.99458 | -0.10398 | 0.023497 | 0.0058888
52 | 0.99402 | -0.11466 | 0 | 0
53 | 0.99256 | -0.143 | 0 | 0
54 | 0.97049 | -0.56971 | 0.047041 | 0.01179
55 | 0.97106 | -0.55843 | 0.0064075 | 0.0016059
56 | 0.97136 | -0.55248 | 0.011269 | 0.0028243
57 | 0.99101 | -0.17286 | 0.0085783 | 0.0021499
58 | 0.99001 | -0.19236 | 0.046693 | 0.011702
59 | 0.99466 | -0.10133 | 0.007929 | 0.0019872
60 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.020059 | -0.0050297 | 0.020094 | 0.0050514 | 3.5879e-05 | 2.1703e-05 | 0.030713 | 0.030712 | 0.030713 | 0.97186 | -0.54262 | 0.97376 | -0.50516 | 8.4376
1 | 0.017743 | 0.0044494 | -0.017736 | -0.0044451 | 7.1778e-06 | 4.2726e-06 | 0.027168 | 0.027168 | 0.027168 | 0.97186 | -0.54262 | 0.97143 | -0.55111 | 7.4636
2 | 0.0011265 | 0.00028028 | -0.0011264 | -0.00028095 | 6.3076e-08 | -6.6621e-07 | 0.0017207 | 0.0017209 | 0.0017209 | 0.97376 | -0.50516 | 0.9737 | -0.50634 | 0.47278
3 | -0.021221 | -0.0053317 | 0.021251 | 0.00535 | 3.0119e-05 | 1.8325e-05 | 0.032433 | 0.032433 | 0.032433 | 0.97376 | -0.50516 | 0.97526 | -0.47547 | 8.9102
4 | 0.017418 | 0.0043656 | -0.017417 | -0.0043649 | 1.1615e-06 | 6.895e-07 | 0.026681 | 0.026681 | 0.026681 | 0.97143 | -0.55111 | 0.97136 | -0.55251 | 7.3299
5 | 0.00031778 | 7.9511e-05 | -0.00031778 | -7.9643e-05 | 9.5458e-10 | -1.3241e-07 | 0.00048672 | 0.00048677 | 0.00048677 | 0.97143 | -0.55111 | 0.97142 | -0.55118 | 0.13373
6 | 0.0011264 | 0.00028095 | -0.0011263 | -0.00028228 | 1.2608e-07 | -1.3308e-06 | 0.0017209 | 0.0017214 | 0.0017214 | 0.9737 | -0.50634 | 0.97358 | -0.50869 | 0.47292
7 | -0.10844 | -0.027324 | 0.10876 | 0.027524 | 0.00031885 | 0.00020057 | 0.1655 | 0.1655 | 0.1655 | 0.97526 | -0.47547 | 0.9784 | -0.41419 | 15.156
8 | 0.087188 | 0.021974 | -0.086956 | -0.021829 | 0.0002315 | 0.00014426 | 0.13307 | 0.13307 | 0.13307 | 0.97526 | -0.47547 | 0.97244 | -0.53112 | 12.1861
9 | 0.0011376 | 0.00028494 | -0.0011376 | -0.00028511 | 1.5741e-08 | -1.6102e-07 | 0.0017426 | 0.0017427 | 0.0017427 | 0.97136 | -0.55251 | 0.97134 | -0.5528 | 0.47876
10 | 0.016279 | 0.00408 | -0.016275 | -0.0040776 | 4.0676e-06 | 2.3874e-06 | 0.024938 | 0.024938 | 0.024938 | 0.97136 | -0.55251 | 0.97109 | -0.55776 | 6.8512
11 | 0.016275 | 0.0040776 | -0.016268 | -0.0040731 | 7.7397e-06 | 4.543e-06 | 0.024938 | 0.024939 | 0.024939 | 0.97109 | -0.55776 | 0.97059 | -0.56775 | 6.8512
12 | 0.0015651 | 0.00038827 | -0.001565 | -0.00038859 | 6.4461e-08 | -3.2816e-07 | 0.002398 | 0.0023981 | 0.0023981 | 0.97059 | -0.56775 | 0.97054 | -0.56862 | 0.65882
13 | 0.037039 | 0.0092986 | -0.037008 | -0.00928 | 3.1264e-05 | 1.8691e-05 | 0.056338 | 0.056338 | 0.056338 | 0.9784 | -0.41419 | 0.97749 | -0.4319 | 7.7388
14 | -0.1458 | -0.036823 | 0.14594 | 0.036916 | 0.00014649 | 9.2856e-05 | 0.22184 | 0.22184 | 0.22184 | 0.9784 | -0.41419 | 0.97947 | -0.39325 | 20.315
15 | 0.084255 | 0.021152 | -0.084206 | -0.021122 | 4.8161e-05 | 2.9961e-05 | 0.12894 | 0.12894 | 0.12894 | 0.97244 | -0.53112 | 0.97183 | -0.54311 | 11.8076
16 | 0.001565 | 0.00038859 | -0.001565 | -0.00038867 | 1.4024e-08 | -7.1386e-08 | 0.0023981 | 0.0023981 | 0.0023981 | 0.97054 | -0.56862 | 0.97053 | -0.56881 | 0.65883
17 | 0.001565 | 0.00038867 | -0.0015647 | -0.00039012 | 2.8507e-07 | -1.4503e-06 | 0.0023981 | 0.0023987 | 0.0023987 | 0.97053 | -0.56881 | 0.97034 | -0.57265 | 0.65899
18 | 0.0015647 | 0.00039012 | -0.0015645 | -0.00039119 | 2.1106e-07 | -1.0728e-06 | 0.0023987 | 0.0023992 | 0.0023992 | 0.97034 | -0.57265 | 0.9702 | -0.57549 | 0.65911
19 | 0.00015708 | 3.846e-05 | -0.00015708 | -3.9367e-05 | 1.5987e-09 | -9.0725e-07 | 0.00024059 | 0.00024092 | 0.00024092 | 0.9702 | -0.57549 | 0.97019 | -0.57571 | 0.066186
20 | 0.18814 | 0.047753 | -0.1879 | -0.0476 | 0.00024153 | 0.00015368 | 0.28484 | 0.28484 | 0.28484 | 0.98362 | -0.31259 | 0.98224 | -0.33932 | 26.0841
21 | -0.2026 | -0.051377 | 0.20305 | 0.051667 | 0.00045626 | 0.00029052 | 0.3067 | 0.3067 | 0.3067 | 0.98362 | -0.31259 | 0.98604 | -0.26586 | 28.0863
22 | 0.014453 | 0.0036232 | -0.01445 | -0.0036214 | 3.0926e-06 | 1.7603e-06 | 0.021864 | 0.021865 | 0.021865 | 0.98362 | -0.31259 | 0.98339 | -0.31709 | 6.0067
23 | 0.1879 | 0.0476 | -0.18769 | -0.047462 | 0.00021594 | 0.00013739 | 0.28484 | 0.28484 | 0.28484 | 0.98224 | -0.33932 | 0.98101 | -0.36327 | 26.0842
24 | -0.20305 | -0.051667 | 0.20326 | 0.051801 | 0.00021088 | 0.00013428 | 0.3067 | 0.3067 | 0.3067 | 0.98604 | -0.26586 | 0.98716 | -0.24434 | 28.0863
25 | 0.15378 | 0.038965 | -0.15369 | -0.038907 | 9.2734e-05 | 5.8834e-05 | 0.23341 | 0.23341 | 0.23341 | 0.98101 | -0.36327 | 0.98036 | -0.37583 | 21.3749
26 | -0.24057 | -0.061193 | 0.24109 | 0.061527 | 0.00052419 | 0.00033425 | 0.36277 | 0.36277 | 0.36277 | 0.98764 | -0.23499 | 0.99 | -0.18988 | 33.2207
27 | 0.24057 | 0.061193 | -0.24046 | -0.061124 | 0.00010831 | 6.9063e-05 | 0.36277 | 0.36277 | 0.36277 | 0.98764 | -0.23499 | 0.98716 | -0.24434 | 33.2207
28 | -0.24109 | -0.061527 | 0.24157 | 0.061834 | 0.00048067 | 0.0003065 | 0.36277 | 0.36277 | 0.36277 | 0.99 | -0.18988 | 0.99215 | -0.1487 | 33.2207
29 | 0.037008 | 0.00928 | -0.036995 | -0.0092719 | 1.2794e-05 | 8.0535e-06 | 0.056338 | 0.056338 | 0.056338 | 0.97749 | -0.4319 | 0.97713 | -0.43916 | 15.4776
30 | -0.15356 | -0.038825 | 0.15369 | 0.038907 | 0.00012837 | 8.1442e-05 | 0.23341 | 0.23341 | 0.23341 | 0.97947 | -0.39325 | 0.98036 | -0.37583 | 21.375
31 | -0.25554 | -0.065487 | 0.25583 | 0.06567 | 0.00028791 | 0.00018365 | 0.38312 | 0.38312 | 0.38312 | 0.99386 | -0.11616 | 0.99508 | -0.092947 | 35.0839
32 | 0.25554 | 0.065487 | -0.25553 | -0.065476 | 1.6211e-05 | 1.0341e-05 | 0.38312 | 0.38312 | 0.38312 | 0.99386 | -0.11616 | 0.99379 | -0.11747 | 35.0839
33 | -0.26098 | -0.06696 | 0.26115 | 0.067072 | 0.00017602 | 0.0001123 | 0.39081 | 0.39081 | 0.39081 | 0.99508 | -0.092947 | 0.99582 | -0.079055 | 35.7885
34 | 0.2488 | 0.063791 | -0.24843 | -0.063552 | 0.00037613 | 0.00023988 | 0.37305 | 0.37305 | 0.37305 | 0.99379 | -0.11747 | 0.99215 | -0.1487 | 34.1622
35 | -0.007153 | -0.0017928 | 0.0071543 | 0.0017932 | 1.3173e-06 | 4.4404e-07 | 0.010696 | 0.010696 | 0.010696 | 0.99515 | -0.091921 | 0.99535 | -0.088056 | 2.9384
36 | 0.007153 | 0.0017928 | -0.0071524 | -0.0017926 | 5.8759e-07 | 1.9812e-07 | 0.010696 | 0.010696 | 0.010696 | 0.99515 | -0.091921 | 0.99506 | -0.093645 | 2.9384
37 | -0.028647 | -0.0071827 | 0.028659 | 0.0071903 | 1.2293e-05 | 7.6352e-06 | 0.042827 | 0.042827 | 0.042827 | 0.99535 | -0.088056 | 0.99582 | -0.079055 | 11.7657
38 | 0.021492 | 0.0053895 | -0.021487 | -0.0053862 | 5.4486e-06 | 3.3042e-06 | 0.032131 | 0.032132 | 0.032132 | 0.99535 | -0.088056 | 0.99508 | -0.093376 | 8.8273
39 | 0.076189 | 0.019113 | -0.076155 | -0.019092 | 3.4026e-05 | 2.1034e-05 | 0.11666 | 0.11666 | 0.11666 | 0.97183 | -0.54311 | 0.97136 | -0.55248 | 10.6835
40 | -0.0026471 | -0.00066003 | 0.0026473 | 0.00065627 | 2.1699e-07 | -3.7647e-06 | 0.0040593 | 0.0040579 | 0.0040593 | 0.97007 | -0.57802 | 0.97016 | -0.57629 | 0.37173
41 | 0.0026471 | 0.00066003 | -0.002647 | -0.00066264 | 1.5042e-07 | -2.6078e-06 | 0.0040593 | 0.0040602 | 0.0040602 | 0.97007 | -0.57802 | 0.97001 | -0.57922 | 0.37182
42 | -0.0026473 | -0.00065627 | 0.0026475 | 0.00065315 | 1.7957e-07 | -3.1181e-06 | 0.0040579 | 0.0040567 | 0.0040579 | 0.97016 | -0.57629 | 0.97023 | -0.57485 | 0.3716
43 | 0.0012042 | 0.00030104 | -0.0012042 | -0.00030179 | 8.7142e-09 | -7.511e-07 | 0.001847 | 0.0018472 | 0.0018472 | 0.97001 | -0.57922 | 0.97 | -0.57937 | 0.16916
44 | -0.03096 | -0.0077593 | 0.030963 | 0.0077614 | 3.3822e-06 | 2.1093e-06 | 0.046157 | 0.046157 | 0.046157 | 0.9981 | -0.03582 | 0.99822 | -0.033527 | 12.6804
45 | 0.29045 | 0.074672 | -0.28981 | -0.074263 | 0.00064103 | 0.00040919 | 0.43364 | 0.43364 | 0.43364 | 0.99822 | -0.033527 | 0.99582 | -0.079055 | 39.7103
46 | -0.32142 | -0.082433 | 0.32194 | 0.082768 | 0.00052358 | 0.00033438 | 0.47979 | 0.47979 | 0.47979 | 0.99822 | -0.033527 | 1 | 0 | 43.937
47 | 0.01372 | 0.0034397 | -0.013718 | -0.0034382 | 2.8424e-06 | 1.5853e-06 | 0.020518 | 0.020518 | 0.020518 | 0.99508 | -0.093376 | 0.99485 | -0.097725 | 5.6368
48 | -0.011385 | -0.0028429 | 0.011388 | 0.002842 | 2.7805e-06 | -9.257e-07 | 0.017457 | 0.017456 | 0.017457 | 0.97023 | -0.57485 | 0.97049 | -0.56971 | 1.5986
49 | 0.0079304 | 0.0019877 | -0.007929 | -0.0019872 | 1.3612e-06 | 5.3624e-07 | 0.011862 | 0.011862 | 0.011862 | 0.99485 | -0.097725 | 0.99466 | -0.10133 | 3.2587
50 | 0.10244 | 0.025858 | -0.10229 | -0.025758 | 0.00015734 | 0.00010046 | 0.15288 | 0.15288 | 0.15288 | 0.99753 | -0.047249 | 0.99586 | -0.079368 | 41.9995
51 | -0.13341 | -0.033619 | 0.13371 | 0.033812 | 0.0003023 | 0.00019321 | 0.19907 | 0.19907 | 0.19907 | 0.99753 | -0.047249 | 1 | 0 | 54.6897
52 | 0.079087 | 0.019944 | -0.078994 | -0.019884 | 9.3054e-05 | 5.9324e-05 | 0.11822 | 0.11822 | 0.11822 | 0.99586 | -0.079368 | 0.99458 | -0.10398 | 32.4769
53 | 0.055497 | 0.013996 | -0.055469 | -0.013978 | 2.836e-05 | 1.8008e-05 | 0.083062 | 0.083062 | 0.083062 | 0.99458 | -0.10398 | 0.99402 | -0.11466 | 22.8192
54 | 0.055469 | 0.013978 | -0.055394 | -0.01393 | 7.5076e-05 | 4.7673e-05 | 0.083062 | 0.083062 | 0.083062 | 0.99402 | -0.11466 | 0.99256 | -0.143 | 22.8192
55 | 0.055394 | 0.01393 | -0.055315 | -0.01388 | 7.8889e-05 | 5.0096e-05 | 0.083062 | 0.083062 | 0.083062 | 0.99256 | -0.143 | 0.99101 | -0.17286 | 22.8193
56 | -0.058429 | -0.014632 | 0.05846 | 0.014651 | 3.1406e-05 | 1.8938e-05 | 0.089583 | 0.089582 | 0.089583 | 0.97049 | -0.56971 | 0.97106 | -0.55843 | 8.2035
57 | -0.064868 | -0.016256 | 0.064886 | 0.016268 | 1.8376e-05 | 1.1208e-05 | 0.099401 | 0.099401 | 0.099401 | 0.97106 | -0.55843 | 0.97136 | -0.55248 | 9.1026
58 | 0.046737 | 0.01173 | -0.046693 | -0.011702 | 4.3408e-05 | 2.7478e-05 | 0.070182 | 0.070182 | 0.070182 | 0.99101 | -0.17286 | 0.99001 | -0.19236 | 19.2807

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48922 | 0.12458

## res_load
| p_mw | q_mvar
0 | 0.0023155 | 0.00058032
1 | 0.00031778 | 7.9643e-05
2 | 0.014703 | 0.0036848
3 | 0.0011376 | 0.00028511
4 | 0.0011263 | 0.00028228
5 | 0.0027015 | 0.00067706
6 | 0.0014074 | 0.00035273
7 | 0.01445 | 0.0036214
8 | 0.033903 | 0.0084969
9 | 0.037196 | 0.0093223
10 | 0.0076188 | 0.0019095
11 | 0.036995 | 0.0092719
12 | 0.0051459 | 0.0012897
13 | 0.0067225 | 0.0016848
14 | 0.0071524 | 0.0017926
15 | 0.0068553 | 0.0017181
16 | 0.0080171 | 0.0020093
17 | 0.0014428 | 0.00036159
18 | 0.00015708 | 3.9367e-05
19 | 0.03096 | 0.0077593
20 | 0.0077665 | 0.0019465
21 | 0.0087372 | 0.0021898
22 | 0.0012042 | 0.00030179
23 | 0.0057873 | 0.0014504
24 | 0.030967 | 0.007761
25 | 0.023198 | 0.0058139
26 | 0.031922 | 0.0080005
27 | 0.023497 | 0.0058888
28 | 0.047041 | 0.01179
29 | 0.0064075 | 0.0016059
30 | 0.011269 | 0.0028243
31 | 0.0085783 | 0.0021499
32 | 0.046693 | 0.011702
33 | 0.007929 | 0.0019872

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1