## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-143_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-143_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-143_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_230-143_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_230-143_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_230-143_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_230-143_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_230-143_0_4_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_230-143_0_4_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_230-143_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_230-143_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_230-143_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_230-143_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_230-143_0_4_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_230-143_0_4_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_230-143_0_4_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_230-143_0_4_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_230-143_0_4_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_230-143_0_4_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_230-143_0_4_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_230-143_0_4_node_55 | 0.4 | n |  | TRUE
21 | bus_LV_230-143_0_4_node_56 | 0.4 | n |  | TRUE
22 | bus_LV_230-143_0_4_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_230-143_0_4_node_59 | 0.4 | n |  | TRUE
24 | bus_LV_230-143_0_4_node_66 | 0.4 | n |  | TRUE
25 | bus_LV_230-143_0_4_node_67 | 0.4 | n |  | TRUE
26 | bus_LV_230-143_0_4_node_68 | 0.4 | n |  | TRUE
27 | bus_LV_230-143_0_4_node_71 | 0.4 | n |  | TRUE
28 | bus_LV_230-143_0_4_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_230-143_0_4_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_230-143_0_4_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_230-143_0_4_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_230-143_0_4_node_74 | 0.4 | n |  | TRUE
33 | bus_LV_230-143_0_4_node_82 | 0.4 | n |  | TRUE
34 | bus_LV_230-143_0_4_node_80 | 0.4 | n |  | TRUE
35 | bus_MV_371_0_node_163 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-143_0_4_load_0 | 0 | 0.0093677 | 0.0023478 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-143_0_4_load_3 | 2 | 0.0017466 | 0.00043774 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-143_0_4_load_4 | 3 | 0.00085973 | 0.00021547 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-143_0_4_load_57 | 8 | 0.0092904 | 0.0023284 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-143_0_4_load_9 | 9 | 0.012546 | 0.0031443 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-143_0_4_load_7 | 10 | 0.0033033 | 0.00082789 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-143_0_4_load_54 | 14 | 0.015911 | 0.0039877 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-143_0_4_load_38 | 16 | 0.017517 | 0.0043902 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-143_0_4_load_39 | 17 | 0.017611 | 0.0044136 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-143_0_4_load_63 | 19 | 0.015969 | 0.0040021 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-143_0_4_load_56 | 21 | 0.014818 | 0.0037137 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-143_0_4_load_58 | 22 | 0.00064167 | 0.00016082 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-143_0_4_load_59 | 23 | 0.00064395 | 0.00016139 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-143_0_4_load_66 | 24 | 0.0079098 | 0.0019824 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-143_0_4_load_72 | 28 | 0.010326 | 0.0025878 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-143_0_4_load_69 | 29 | 0.017725 | 0.0044422 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-143_0_4_load_70 | 30 | 0.017708 | 0.004438 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-143_0_4_load_73 | 31 | 0.011676 | 0.0029264 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-143_0_4_load_82 | 33 | 0.0054954 | 0.0013773 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-143_0_4_load_80 | 34 | 0.0050331 | 0.0012614 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-143_0_4_line_0 |  | 0 | 1 | 0.035083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-143_0_4_line_1 |  | 1 | 2 | 0.016123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-143_0_4_line_2 |  | 1 | 3 | 0.022615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-143_0_4_line_3 |  | 3 | 4 | 0.026176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-143_0_4_line_4 |  | 4 | 9 | 0.015642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-143_0_4_line_5 |  | 5 | 6 | 0.22666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-143_0_4_line_6 |  | 5 | 7 | 0.20249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-143_0_4_line_7 |  | 5 | 8 | 0.049358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-143_0_4_line_8 |  | 6 | 14 | 0.033406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-143_0_4_line_9 |  | 7 | 15 | 0.034533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-143_0_4_line_10 |  | 7 | 16 | 0.085175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-143_0_4_line_11 |  | 8 | 22 | 0.022903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-143_0_4_line_12 |  | 9 | 12 | 0.022536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-143_0_4_line_13 |  | 10 | 11 | 0.0083376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-143_0_4_line_14 |  | 11 | 13 | 0.022384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-143_0_4_line_15 |  | 11 | 12 | 0.0243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-143_0_4_line_16 |  | 13 | 17 | 0.032841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-143_0_4_line_17 |  | 13 | 16 | 0.070326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-143_0_4_line_18 |  | 14 | 20 | 0.0057299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-143_0_4_line_19 |  | 15 | 18 | 0.0321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-143_0_4_line_20 |  | 15 | 19 | 0.013013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-143_0_4_line_21 |  | 18 | 24 | 0.013628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-143_0_4_line_22 |  | 18 | 25 | 0.021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-143_0_4_line_23 |  | 18 | 26 | 0.024588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_230-143_0_4_line_24 |  | 20 | 21 | 0.051329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-143_0_4_line_25 |  | 22 | 23 | 0.022522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-143_0_4_line_26 |  | 25 | 27 | 0.020146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-143_0_4_line_27 |  | 25 | 28 | 0.015137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-143_0_4_line_28 |  | 26 | 29 | 0.01562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-143_0_4_line_29 |  | 26 | 30 | 0.007966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-143_0_4_line_30 |  | 27 | 31 | 0.015097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-143_0_4_line_31 |  | 27 | 32 | 0.026058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-143_0_4_line_32 |  | 32 | 33 | 0.012275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-143_0_4_line_33 |  | 33 | 34 | 0.017824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-143_0_4_trafo_68 | 0.63 MVA 20/0.4 kV | 35 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2693823.6465 | 1262773.8614 | 2693818.6376 | 1262766.1758 | 2693816.884 | 1262740.3256
1 | 2693823.6465 | 1262773.8614 | 2693821.4942 | 1262789.8402
2 | 2693823.6465 | 1262773.8614 | 2693829.0391 | 1262778.2616 | 2693838.0364 | 1262791.0724
3 | 2693853.0804 | 1262812.4929 | 2693838.0364 | 1262791.0724
4 | 2693853.0804 | 1262812.4929 | 2693841.5507 | 1262823.063
5 | 2694133.722 | 1262800.1648 | 2694170.8218 | 1262807.7059 | 2694192.1758 | 1262811.3933 | 2694209.4343 | 1262813.9369 | 2694208.9857 | 1262820.3349 | 2694208.6445 | 1262825.2001 | 2694207.9355 | 1262832.339 | 2694206.0528 | 1262843.1511 | 2694204.1878 | 1262851.4392 | 2694199.8256 | 1262867.0268 | 2694192.2716 | 1262886.222 | 2694185.6312 | 1262899.1601 | 2694178.2592 | 1262911.1969 | 2694172.2637 | 1262920.5424 | 2694163.9828 | 1262914.4389 | 2694152.3853 | 1262906.0697 | 2694143.7738 | 1262899.9055
6 | 2694133.722 | 1262800.1648 | 2694132.8361 | 1262805.1658 | 2694129.25 | 1262821.2329 | 2694127.5775 | 1262827.3779 | 2694085.1065 | 1262815.5259 | 2694076.4684 | 1262811.4964 | 2694051.3425 | 1262797.2075 | 2694019.1579 | 1262784.7413 | 2694013.4192 | 1262783.1599 | 2693998.4629 | 1262780.8203 | 2693980.2909 | 1262781.2319 | 2693962.2187 | 1262783.8914
7 | 2694133.722 | 1262800.1648 | 2694135.1121 | 1262793.3036 | 2694113.1811 | 1262785.6261 | 2694112.9529 | 1262766.5062
8 | 2694143.7738 | 1262899.9055 | 2694116.9251 | 1262880.0288
9 | 2693971.9991 | 1262817.018 | 2693962.2187 | 1262783.8914
10 | 2693962.2187 | 1262783.8914 | 2693941.1766 | 1262791.3743 | 2693891.1819 | 1262829.4484
11 | 2694112.9529 | 1262766.5062 | 2694112.9454 | 1262765.8842 | 2694111.444 | 1262759.8666 | 2694111.4457 | 1262743.7879
12 | 2693820.4133 | 1262830.8784 | 2693841.5507 | 1262823.063
13 | 2693821.4757 | 1262854.6034 | 2693814.3259 | 1262858.8924
14 | 2693835.3458 | 1262872.2043 | 2693831.3335 | 1262867.2366 | 2693822.8566 | 1262856.3711 | 2693821.4757 | 1262854.6034
15 | 2693820.4133 | 1262830.8784 | 2693818.9753 | 1262848.8479 | 2693821.4757 | 1262854.6034
16 | 2693835.3458 | 1262872.2043 | 2693837.1016 | 1262874.5563 | 2693855.0146 | 1262898.5043
17 | 2693835.3458 | 1262872.2043 | 2693882.5046 | 1262836.0567 | 2693891.1819 | 1262829.4484
18 | 2694112.3198 | 1262876.6194 | 2694116.9251 | 1262880.0288
19 | 2693971.9991 | 1262817.018 | 2693979.5347 | 1262842.525 | 2693978.3792 | 1262847.911
20 | 2693984.3616 | 1262812.8444 | 2693971.9991 | 1262817.018
21 | 2693991.357 | 1262847.6837 | 2693983.6515 | 1262849.9186 | 2693978.3792 | 1262847.911
22 | 2693981.8963 | 1262868.8505 | 2693977.6376 | 1262853.3258 | 2693978.3792 | 1262847.911
23 | 2693955.3968 | 1262850.448 | 2693958.8974 | 1262846.834 | 2693973.5532 | 1262846.7445 | 2693978.3792 | 1262847.911
24 | 2694112.3198 | 1262876.6194 | 2694104.6409 | 1262850.2092 | 2694101.0487 | 1262847.7389 | 2694092.8246 | 1262847.9972 | 2694082.0424 | 1262851.1643
25 | 2694111.4457 | 1262743.7879 | 2694111.4481 | 1262721.2655
26 | 2693981.8963 | 1262868.8505 | 2693987.7679 | 1262888.1261
27 | 2693996.4746 | 1262864.6232 | 2693981.8963 | 1262868.8505
28 | 2693955.3968 | 1262850.448 | 2693954.1329 | 1262845.5906 | 2693953.9624 | 1262834.9905
29 | 2693955.3968 | 1262850.448 | 2693958.2745 | 1262854.2634 | 2693958.1409 | 1262857.4528
30 | 2694002.2152 | 1262883.6075 | 2693987.7679 | 1262888.1261
31 | 2693987.7679 | 1262888.1261 | 2693995.3728 | 1262913.056
32 | 2694007.0883 | 1262909.2835 | 2693995.3728 | 1262913.056
33 | 2694007.0883 | 1262909.2835 | 2694012.2416 | 1262926.3459

## bus_geodata
| x | y | coords
0 | 2693816.884 | 1262740.3256
1 | 2693823.6465 | 1262773.8614
2 | 2693821.4942 | 1262789.8402
3 | 2693838.0364 | 1262791.0724
4 | 2693853.0804 | 1262812.4929
5 | 2694133.722 | 1262800.1648
6 | 2694143.7738 | 1262899.9055
7 | 2693962.2187 | 1262783.8914
8 | 2694112.9529 | 1262766.5062
9 | 2693841.5507 | 1262823.063
10 | 2693814.3259 | 1262858.8924
11 | 2693821.4757 | 1262854.6034
12 | 2693820.4133 | 1262830.8784
13 | 2693835.3458 | 1262872.2043
14 | 2694116.9251 | 1262880.0288
15 | 2693971.9991 | 1262817.018
16 | 2693891.1819 | 1262829.4484
17 | 2693855.0146 | 1262898.5043
18 | 2693978.3792 | 1262847.911
19 | 2693984.3616 | 1262812.8444
20 | 2694112.3198 | 1262876.6194
21 | 2694082.0424 | 1262851.1643
22 | 2694111.4457 | 1262743.7879
23 | 2694111.4481 | 1262721.2655
24 | 2693991.357 | 1262847.6837
25 | 2693981.8963 | 1262868.8505
26 | 2693955.3968 | 1262850.448
27 | 2693987.7679 | 1262888.1261
28 | 2693996.4746 | 1262864.6232
29 | 2693953.9624 | 1262834.9905
30 | 2693958.1409 | 1262857.4528
31 | 2694002.2152 | 1262883.6075
32 | 2693995.3728 | 1262913.056
33 | 2694007.0883 | 1262909.2835
34 | 2694012.2416 | 1262926.3459
35 | 2693958.1409 | 1262857.4528

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98075 | -0.37051 | 0.0093677 | 0.0023478
1 | 0.98106 | -0.36455 | 0 | 0
2 | 0.98103 | -0.36506 | 0.0017466 | 0.00043774
3 | 0.98129 | -0.36 | 0.00085973 | 0.00021547
4 | 0.98158 | -0.35433 | 0 | 0
5 | 0.98352 | -0.31552 | 0 | 0
6 | 0.97705 | -0.44187 | 0 | 0
7 | 0.99129 | -0.16593 | 0 | 0
8 | 0.98304 | -0.32493 | 0.0092904 | 0.0023284
9 | 0.98175 | -0.35094 | 0.012546 | 0.0031443
10 | 0.98279 | -0.33069 | 0.0033033 | 0.00082789
11 | 0.98281 | -0.33019 | 0 | 0
12 | 0.98226 | -0.34095 | 0 | 0
13 | 0.98339 | -0.31896 | 0 | 0
14 | 0.97609 | -0.46064 | 0.015911 | 0.0039877
15 | 0.99462 | -0.10227 | 0 | 0
16 | 0.98634 | -0.26153 | 0.017517 | 0.0043902
17 | 0.98285 | -0.32939 | 0.017611 | 0.0044136
18 | 0.99818 | -0.034498 | 0 | 0
19 | 0.99443 | -0.10593 | 0.015969 | 0.0040021
20 | 0.97601 | -0.46219 | 0 | 0
21 | 0.97531 | -0.47612 | 0.014818 | 0.0037137
22 | 0.98301 | -0.32546 | 0.00064167 | 0.00016082
23 | 0.983 | -0.32572 | 0.00064395 | 0.00016139
24 | 0.99808 | -0.036384 | 0.0079098 | 0.0019824
25 | 0.99754 | -0.046777 | 0 | 0
26 | 1 | 0 | -0.19979 | -0.050436
27 | 0.99714 | -0.054616 | 0 | 0
28 | 0.9974 | -0.049515 | 0.010326 | 0.0025878
29 | 0.99975 | -0.0048268 | 0.017725 | 0.0044422
30 | 0.99987 | -0.0024589 | 0.017708 | 0.004438
31 | 0.99698 | -0.057707 | 0.011676 | 0.0029264
32 | 0.99689 | -0.059427 | 0 | 0
33 | 0.99677 | -0.061694 | 0.0054954 | 0.0013773
34 | 0.99669 | -0.063268 | 0.0050331 | 0.0012614
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0093677 | -0.0023478 | 0.0093703 | 0.002349 | 2.6576e-06 | 1.258e-06 | 0.014213 | 0.014213 | 0.014213 | 0.98075 | -0.37051 | 0.98106 | -0.36455 | 3.9046
1 | 0.0017466 | 0.00043756 | -0.0017466 | -0.00043774 | 4.2433e-08 | -1.7642e-07 | 0.0026492 | 0.0026492 | 0.0026492 | 0.98106 | -0.36455 | 0.98103 | -0.36506 | 0.72781
2 | -0.011117 | -0.0027866 | 0.011119 | 0.0027878 | 2.4112e-06 | 1.2575e-06 | 0.016862 | 0.016862 | 0.016862 | 0.98106 | -0.36455 | 0.98129 | -0.36 | 4.6324
3 | -0.011979 | -0.0030033 | 0.011982 | 0.0030051 | 3.239e-06 | 1.7422e-06 | 0.018165 | 0.018165 | 0.018165 | 0.98129 | -0.36 | 0.98158 | -0.35433 | 4.9905
4 | -0.011982 | -0.0030051 | 0.011984 | 0.0030061 | 1.9355e-06 | 1.041e-06 | 0.018165 | 0.018165 | 0.018165 | 0.98158 | -0.35433 | 0.98175 | -0.35094 | 4.9905
5 | 0.030954 | 0.0078415 | -0.030767 | -0.0077249 | 0.00018667 | 0.00011661 | 0.046862 | 0.046863 | 0.046863 | 0.98352 | -0.31552 | 0.97705 | -0.44187 | 12.8744
6 | -0.041535 | -0.010494 | 0.041835 | 0.010683 | 0.00030014 | 0.0001895 | 0.06287 | 0.062869 | 0.06287 | 0.98352 | -0.31552 | 0.99129 | -0.16593 | 17.2721
7 | 0.010581 | 0.0026524 | -0.010576 | -0.00265 | 4.7434e-06 | 2.4097e-06 | 0.016008 | 0.016009 | 0.016009 | 0.98352 | -0.31552 | 0.98304 | -0.32493 | 4.398
8 | 0.030767 | 0.0077249 | -0.03074 | -0.0077077 | 2.7511e-05 | 1.7189e-05 | 0.046863 | 0.046863 | 0.046863 | 0.97705 | -0.44187 | 0.97609 | -0.46064 | 12.8745
9 | -0.10526 | -0.026759 | 0.10558 | 0.026965 | 0.00032385 | 0.00020682 | 0.15814 | 0.15814 | 0.15814 | 0.99129 | -0.16593 | 0.99462 | -0.10227 | 43.4449
10 | 0.063424 | 0.016075 | -0.063135 | -0.015891 | 0.00028991 | 0.00018445 | 0.09527 | 0.09527 | 0.09527 | 0.99129 | -0.16593 | 0.98634 | -0.26153 | 26.1732
11 | 0.0012857 | 0.00032166 | -0.0012856 | -0.00032193 | 3.2522e-08 | -2.6954e-07 | 0.0019459 | 0.001946 | 0.001946 | 0.98304 | -0.32493 | 0.98301 | -0.32546 | 0.53461
12 | -0.02453 | -0.0061504 | 0.024542 | 0.0061576 | 1.1683e-05 | 7.1918e-06 | 0.037181 | 0.037181 | 0.037181 | 0.98175 | -0.35094 | 0.98226 | -0.34095 | 10.2145
13 | -0.0033033 | -0.00082789 | 0.0033034 | 0.00082784 | 7.8211e-08 | -5.5598e-08 | 0.0050015 | 0.0050015 | 0.0050015 | 0.98279 | -0.33069 | 0.98281 | -0.33019 | 1.374
14 | -0.027858 | -0.0069932 | 0.027873 | 0.0070025 | 1.4936e-05 | 9.275e-06 | 0.042182 | 0.042182 | 0.042182 | 0.98281 | -0.33019 | 0.98339 | -0.31896 | 11.5885
15 | 0.024555 | 0.0061654 | -0.024542 | -0.0061576 | 1.2597e-05 | 7.7544e-06 | 0.037181 | 0.037181 | 0.037181 | 0.98281 | -0.33019 | 0.98226 | -0.34095 | 10.2145
16 | 0.017619 | 0.0044188 | -0.017611 | -0.0044136 | 8.7546e-06 | 5.1865e-06 | 0.026662 | 0.026662 | 0.026662 | 0.98339 | -0.31896 | 0.98285 | -0.32939 | 7.3247
17 | -0.045492 | -0.011421 | 0.045617 | 0.0115 | 0.00012499 | 7.9099e-05 | 0.068844 | 0.068843 | 0.068844 | 0.98339 | -0.31896 | 0.98634 | -0.26153 | 18.9131
18 | 0.014829 | 0.00372 | -0.014828 | -0.0037193 | 1.0982e-06 | 6.3122e-07 | 0.022607 | 0.022607 | 0.022607 | 0.97609 | -0.46064 | 0.97601 | -0.46219 | 6.2108
19 | -0.12155 | -0.030969 | 0.12195 | 0.031224 | 0.00039888 | 0.00025486 | 0.18203 | 0.18203 | 0.18203 | 0.99462 | -0.10227 | 0.99818 | -0.034498 | 50.0093
20 | 0.015971 | 0.0040037 | -0.015969 | -0.0040021 | 2.7862e-06 | 1.6143e-06 | 0.023895 | 0.023895 | 0.023895 | 0.99462 | -0.10227 | 0.99443 | -0.10593 | 6.5645
21 | 0.0079105 | 0.0019827 | -0.0079098 | -0.0019824 | 7.1068e-07 | 2.7671e-07 | 0.011792 | 0.011792 | 0.011792 | 0.99818 | -0.034498 | 0.99808 | -0.036384 | 3.2397
22 | 0.032565 | 0.0081732 | -0.032546 | -0.0081613 | 1.9057e-05 | 1.1915e-05 | 0.048549 | 0.048549 | 0.048549 | 0.99818 | -0.034498 | 0.99754 | -0.046777 | 13.3377
23 | -0.16243 | -0.04138 | 0.1627 | 0.041552 | 0.00027083 | 0.00017269 | 0.24237 | 0.24237 | 0.24237 | 0.99818 | -0.034498 | 1 | 0 | 33.2932
24 | 0.014828 | 0.0037193 | -0.014818 | -0.0037137 | 9.8377e-06 | 5.6551e-06 | 0.022607 | 0.022607 | 0.022607 | 0.97601 | -0.46219 | 0.97531 | -0.47612 | 6.2108
25 | 0.00064396 | 0.00016111 | -0.00064395 | -0.00016139 | 8.0244e-09 | -2.8038e-07 | 0.00097468 | 0.00097478 | 0.00097478 | 0.98301 | -0.32546 | 0.983 | -0.32572 | 0.2678
26 | 0.022219 | 0.0055728 | -0.02221 | -0.0055677 | 8.2995e-06 | 5.0488e-06 | 0.033145 | 0.033145 | 0.033145 | 0.99754 | -0.046777 | 0.99714 | -0.054616 | 9.1057
27 | 0.010327 | 0.0025885 | -0.010326 | -0.0025878 | 1.347e-06 | 6.645e-07 | 0.015405 | 0.015405 | 0.015405 | 0.99754 | -0.046777 | 0.9974 | -0.049515 | 4.232
28 | 0.017729 | 0.0044446 | -0.017725 | -0.0044422 | 4.0766e-06 | 2.4042e-06 | 0.026381 | 0.026381 | 0.026381 | 1 | 0 | 0.99975 | -0.0048268 | 7.2476
29 | 0.01771 | 0.0044392 | -0.017708 | -0.004438 | 2.0746e-06 | 1.2232e-06 | 0.026353 | 0.026353 | 0.026353 | 1 | 0 | 0.99987 | -0.0024589 | 7.2398
30 | 0.011678 | 0.0029273 | -0.011676 | -0.0029264 | 1.7194e-06 | 9.0352e-07 | 0.017427 | 0.017427 | 0.017427 | 0.99714 | -0.054616 | 0.99698 | -0.057707 | 4.7877
31 | 0.010532 | 0.0026405 | -0.01053 | -0.0026393 | 2.4141e-06 | 1.2052e-06 | 0.015718 | 0.015718 | 0.015718 | 0.99714 | -0.054616 | 0.99689 | -0.059427 | 4.3181
32 | 0.01053 | 0.0026393 | -0.010529 | -0.0026387 | 1.1372e-06 | 5.6778e-07 | 0.015718 | 0.015718 | 0.015718 | 0.99689 | -0.059427 | 0.99677 | -0.061694 | 4.3181
33 | 0.0050335 | 0.0012614 | -0.0050331 | -0.0012614 | 3.7739e-07 | 9.2213e-09 | 0.0075141 | 0.0075142 | 0.0075142 | 0.99677 | -0.061694 | 0.99669 | -0.063268 | 2.0643

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.19979 | 0.050436

## res_load
| p_mw | q_mvar
0 | 0.0093677 | 0.0023478
1 | 0.0017466 | 0.00043774
2 | 0.00085973 | 0.00021547
3 | 0.0092904 | 0.0023284
4 | 0.012546 | 0.0031443
5 | 0.0033033 | 0.00082789
6 | 0.015911 | 0.0039877
7 | 0.017517 | 0.0043902
8 | 0.017611 | 0.0044136
9 | 0.015969 | 0.0040021
10 | 0.014818 | 0.0037137
11 | 0.00064167 | 0.00016082
12 | 0.00064395 | 0.00016139
13 | 0.0079098 | 0.0019824
14 | 0.010326 | 0.0025878
15 | 0.017725 | 0.0044422
16 | 0.017708 | 0.004438
17 | 0.011676 | 0.0029264
18 | 0.0054954 | 0.0013773
19 | 0.0050331 | 0.0012614

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1