## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-180_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-180_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-180_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-180_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-180_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-180_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_230-180_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_230-180_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_230-180_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_230-180_0_4_node_78 | 0.4 | n |  | TRUE
10 | bus_LV_230-180_0_4_node_149 | 0.4 | n |  | TRUE
11 | bus_LV_230-180_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_230-180_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_230-180_0_4_node_140 | 0.4 | n |  | TRUE
14 | bus_LV_230-180_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_230-180_0_4_node_138 | 0.4 | n |  | TRUE
16 | bus_LV_230-180_0_4_node_106 | 0.4 | n |  | TRUE
17 | bus_LV_230-180_0_4_node_66 | 0.4 | n |  | TRUE
18 | bus_LV_230-180_0_4_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_230-180_0_4_node_75 | 0.4 | n |  | TRUE
20 | bus_LV_230-180_0_4_node_76 | 0.4 | n |  | TRUE
21 | bus_LV_230-180_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_230-180_0_4_node_65 | 0.4 | n |  | TRUE
23 | bus_LV_230-180_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_230-180_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_230-180_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_230-180_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_230-180_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_230-180_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_230-180_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_230-180_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_230-180_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_230-180_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_230-180_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_230-180_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_230-180_0_4_node_102 | 0.4 | n |  | TRUE
36 | bus_LV_230-180_0_4_node_125 | 0.4 | n |  | TRUE
37 | bus_LV_230-180_0_4_node_85 | 0.4 | n |  | TRUE
38 | bus_LV_230-180_0_4_node_109 | 0.4 | n |  | TRUE
39 | bus_LV_230-180_0_4_node_127 | 0.4 | n |  | TRUE
40 | bus_LV_230-180_0_4_node_100 | 0.4 | n |  | TRUE
41 | bus_LV_230-180_0_4_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_230-180_0_4_node_126 | 0.4 | n |  | TRUE
43 | bus_LV_230-180_0_4_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_230-180_0_4_node_72 | 0.4 | n |  | TRUE
45 | bus_LV_230-180_0_4_node_83 | 0.4 | n |  | TRUE
46 | bus_LV_230-180_0_4_node_128 | 0.4 | n |  | TRUE
47 | bus_LV_230-180_0_4_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_230-180_0_4_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_230-180_0_4_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_230-180_0_4_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_230-180_0_4_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_230-180_0_4_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_230-180_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_230-180_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_230-180_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_230-180_0_4_node_69 | 0.4 | n |  | TRUE
57 | bus_LV_230-180_0_4_node_146 | 0.4 | n |  | TRUE
58 | bus_LV_230-180_0_4_node_71 | 0.4 | n |  | TRUE
59 | bus_LV_230-180_0_4_node_67 | 0.4 | n |  | TRUE
60 | bus_LV_230-180_0_4_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_230-180_0_4_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_230-180_0_4_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_230-180_0_4_node_95 | 0.4 | n |  | TRUE
64 | bus_LV_230-180_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_230-180_0_4_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_230-180_0_4_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_230-180_0_4_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_230-180_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_230-180_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_230-180_0_4_node_42 | 0.4 | n |  | TRUE
71 | bus_LV_230-180_0_4_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_230-180_0_4_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_230-180_0_4_node_105 | 0.4 | n |  | TRUE
74 | bus_LV_230-180_0_4_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_230-180_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_230-180_0_4_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_230-180_0_4_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_230-180_0_4_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_230-180_0_4_node_46 | 0.4 | n |  | TRUE
80 | bus_LV_230-180_0_4_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_230-180_0_4_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_230-180_0_4_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_230-180_0_4_node_134 | 0.4 | n |  | TRUE
84 | bus_LV_230-180_0_4_node_97 | 0.4 | n |  | TRUE
85 | bus_LV_230-180_0_4_node_135 | 0.4 | n |  | TRUE
86 | bus_LV_230-180_0_4_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_230-180_0_4_node_55 | 0.4 | n |  | TRUE
88 | bus_LV_230-180_0_4_node_56 | 0.4 | n |  | TRUE
89 | bus_LV_230-180_0_4_node_130 | 0.4 | n |  | TRUE
90 | bus_LV_230-180_0_4_node_122 | 0.4 | n |  | TRUE
91 | bus_LV_230-180_0_4_node_119 | 0.4 | n |  | TRUE
92 | bus_LV_230-180_0_4_node_121 | 0.4 | n |  | TRUE
93 | bus_LV_230-180_0_4_node_123 | 0.4 | n |  | TRUE
94 | bus_LV_230-180_0_4_node_124 | 0.4 | n |  | TRUE
95 | bus_LV_230-180_0_4_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_230-180_0_4_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_230-180_0_4_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_230-180_0_4_node_60 | 0.4 | n |  | TRUE
99 | bus_LV_230-180_0_4_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_230-180_0_4_node_63 | 0.4 | n |  | TRUE
101 | bus_LV_230-180_0_4_node_98 | 0.4 | n |  | TRUE
102 | bus_LV_230-180_0_4_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_230-180_0_4_node_157 | 0.4 | n |  | TRUE
104 | bus_LV_230-180_0_4_node_68 | 0.4 | n |  | TRUE
105 | bus_LV_230-180_0_4_node_70 | 0.4 | n |  | TRUE
106 | bus_LV_230-180_0_4_node_73 | 0.4 | n |  | TRUE
107 | bus_LV_230-180_0_4_node_148 | 0.4 | n |  | TRUE
108 | bus_LV_230-180_0_4_node_144 | 0.4 | n |  | TRUE
109 | bus_LV_230-180_0_4_node_147 | 0.4 | n |  | TRUE
110 | bus_LV_230-180_0_4_node_113 | 0.4 | n |  | TRUE
111 | bus_LV_230-180_0_4_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_230-180_0_4_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_230-180_0_4_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_230-180_0_4_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_230-180_0_4_node_150 | 0.4 | n |  | TRUE
116 | bus_LV_230-180_0_4_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_230-180_0_4_node_96 | 0.4 | n |  | TRUE
118 | bus_LV_230-180_0_4_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_230-180_0_4_node_145 | 0.4 | n |  | TRUE
120 | bus_LV_230-180_0_4_node_155 | 0.4 | n |  | TRUE
121 | bus_LV_230-180_0_4_node_94 | 0.4 | n |  | TRUE
122 | bus_LV_230-180_0_4_node_141 | 0.4 | n |  | TRUE
123 | bus_LV_230-180_0_4_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_230-180_0_4_node_104 | 0.4 | n |  | TRUE
125 | bus_LV_230-180_0_4_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_230-180_0_4_node_152 | 0.4 | n |  | TRUE
127 | bus_LV_230-180_0_4_node_153 | 0.4 | n |  | TRUE
128 | bus_LV_230-180_0_4_node_154 | 0.4 | n |  | TRUE
129 | bus_LV_230-180_0_4_node_151 | 0.4 | n |  | TRUE
130 | bus_LV_230-180_0_4_node_156 | 0.4 | n |  | TRUE
131 | bus_LV_230-180_0_4_node_142 | 0.4 | n |  | TRUE
132 | bus_LV_230-180_0_4_node_111 | 0.4 | n |  | TRUE
133 | bus_LV_230-180_0_4_node_101 | 0.4 | n |  | TRUE
134 | bus_LV_230-180_0_4_node_103 | 0.4 | n |  | TRUE
135 | bus_LV_230-180_0_4_node_108 | 0.4 | n |  | TRUE
136 | bus_LV_230-180_0_4_node_114 | 0.4 | n |  | TRUE
137 | bus_LV_230-180_0_4_node_115 | 0.4 | n |  | TRUE
138 | bus_LV_230-180_0_4_node_117 | 0.4 | n |  | TRUE
139 | bus_LV_230-180_0_4_node_118 | 0.4 | n |  | TRUE
140 | bus_LV_230-180_0_4_node_120 | 0.4 | n |  | TRUE
141 | bus_LV_230-180_0_4_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_230-180_0_4_node_129 | 0.4 | n |  | TRUE
143 | bus_LV_230-180_0_4_node_131 | 0.4 | n |  | TRUE
144 | bus_LV_230-180_0_4_node_139 | 0.4 | n |  | TRUE
145 | bus_LV_230-180_0_4_node_136 | 0.4 | n |  | TRUE
146 | bus_LV_230-180_0_4_node_137 | 0.4 | n |  | TRUE
147 | bus_LV_230-180_0_4_node_133 | 0.4 | n |  | TRUE
148 | bus_LV_230-180_0_4_node_143 | 0.4 | n |  | TRUE
149 | bus_MV_369_0_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-180_0_4_load_0 | 0 | 0.00072285 | 0.00018116 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-180_0_4_load_4 | 4 | 0.00065659 | 0.00016456 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-180_0_4_load_7 | 5 | 0.0001763 | 4.4185e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-180_0_4_load_149 | 10 | 0.0019168 | 0.00048039 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-180_0_4_load_12 | 11 | 0.0022082 | 0.00055343 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-180_0_4_load_140 | 13 | 0.00048831 | 0.00012238 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-180_0_4_load_138 | 15 | 0.00041948 | 0.00010513 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-180_0_4_load_106 | 16 | 0.0021787 | 0.00054604 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-180_0_4_load_75 | 19 | 0.00066408 | 0.00016643 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-180_0_4_load_76 | 20 | 0.0015702 | 0.00039353 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-180_0_4_load_13 | 21 | 0.00050599 | 0.00012681 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-180_0_4_load_65 | 22 | 0.00035239 | 8.8316e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-180_0_4_load_14 | 23 | 0.0014954 | 0.00037479 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-180_0_4_load_17 | 26 | 0.0010267 | 0.00025733 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-180_0_4_load_19 | 28 | 0.00030603 | 7.6697e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-180_0_4_load_20 | 29 | 0.00038108 | 9.5507e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-180_0_4_load_21 | 30 | 0.0045619 | 0.0011433 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-180_0_4_load_24 | 32 | 0.0024879 | 0.00062352 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-180_0_4_load_25 | 33 | 0.00034134 | 8.5549e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-180_0_4_load_26 | 34 | 0.00034405 | 8.6227e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-180_0_4_load_102 | 35 | 0.0053315 | 0.0013362 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-180_0_4_load_125 | 36 | 0.0026119 | 0.00065461 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-180_0_4_load_85 | 37 | 0.0016245 | 0.00040714 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-180_0_4_load_109 | 38 | 0.00060685 | 0.00015209 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-180_0_4_load_127 | 39 | 0.0015763 | 0.00039506 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-180_0_4_load_100 | 40 | 0.0015466 | 0.00038762 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-180_0_4_load_126 | 42 | 0.00057038 | 0.00014295 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-180_0_4_load_72 | 44 | 0.0010568 | 0.00026487 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-180_0_4_load_83 | 45 | 0.00070401 | 0.00017644 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-180_0_4_load_128 | 46 | 0.00089477 | 0.00022425 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-180_0_4_load_27 | 47 | 0.001147 | 0.00028748 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-180_0_4_load_28 | 48 | 0.0014029 | 0.0003516 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-180_0_4_load_30 | 50 | 0.00077162 | 0.00019339 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-180_0_4_load_31 | 51 | 0.00049751 | 0.00012469 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-180_0_4_load_32 | 52 | 0.0012015 | 0.00030111 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-180_0_4_load_33 | 53 | 0.00057707 | 0.00014463 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-180_0_4_load_34 | 54 | 0.001798 | 0.00045061 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-180_0_4_load_35 | 55 | 0.0021872 | 0.00054816 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-180_0_4_load_146 | 57 | 0.0015823 | 0.00039657 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-180_0_4_load_71 | 58 | 0.0015664 | 0.00039257 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-180_0_4_load_67 | 59 | 0.00213 | 0.00053382 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-180_0_4_load_52 | 61 | 0.0031946 | 0.00080065 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-180_0_4_load_53 | 62 | 0.00060656 | 0.00015202 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-180_0_4_load_36 | 64 | 0.0010235 | 0.00025652 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-180_0_4_load_37 | 65 | 0.0028639 | 0.00071777 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-180_0_4_load_38 | 66 | 0.001332 | 0.00033382 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-180_0_4_load_39 | 67 | 0.001316 | 0.00032982 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-180_0_4_load_40 | 68 | 0.0015814 | 0.00039634 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-180_0_4_load_41 | 69 | 0.0014842 | 0.00037198 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-180_0_4_load_42 | 70 | 0.002183 | 0.00054711 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-180_0_4_load_64 | 72 | 0.00069033 | 0.00017301 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-180_0_4_load_105 | 73 | 0.0012549 | 0.00031451 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-180_0_4_load_61 | 75 | 0.0041226 | 0.0010332 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-180_0_4_load_43 | 76 | 0.0012879 | 0.00032278 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-180_0_4_load_44 | 77 | 0.0039083 | 0.0009795 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-180_0_4_load_45 | 78 | 0.00060562 | 0.00015178 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-180_0_4_load_46 | 79 | 0.0012156 | 0.00030465 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-180_0_4_load_47 | 80 | 0.0004978 | 0.00012476 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-180_0_4_load_48 | 81 | 0.00095156 | 0.00023848 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-180_0_4_load_49 | 82 | 0.0053797 | 0.0013483 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-180_0_4_load_134 | 83 | 0.0024506 | 0.00061418 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-180_0_4_load_97 | 84 | 0.0026446 | 0.0006628 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-180_0_4_load_135 | 85 | 0.00080791 | 0.00020248 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-180_0_4_load_55 | 87 | 0.0018376 | 0.00046056 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-180_0_4_load_56 | 88 | 0.00032242 | 8.0805e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-180_0_4_load_130 | 89 | 0.0015406 | 0.00038611 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-180_0_4_load_119 | 91 | 0.0011589 | 0.00029046 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-180_0_4_load_121 | 92 | 0.0018633 | 0.00046699 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-180_0_4_load_123 | 93 | 0.0057057 | 0.00143 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-180_0_4_load_124 | 94 | 0.00016365 | 4.1015e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-180_0_4_load_58 | 96 | 0.0012861 | 0.00032234 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-180_0_4_load_59 | 97 | 0.00073388 | 0.00018393 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-180_0_4_load_62 | 99 | 0.00048977 | 0.00012275 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-180_0_4_load_63 | 100 | 0.00016319 | 4.0899e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-180_0_4_load_98 | 101 | 0.0012219 | 0.00030623 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-180_0_4_load_157 | 103 | 0.0023676 | 0.00059337 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-180_0_4_load_68 | 104 | 0.0006906 | 0.00017308 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-180_0_4_load_70 | 105 | 0.00025504 | 6.3918e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-180_0_4_load_73 | 106 | 0.00051196 | 0.00012831 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-180_0_4_load_148 | 107 | 0.0033528 | 0.0008403 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-180_0_4_load_144 | 108 | 0.0004071 | 0.00010203 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-180_0_4_load_147 | 109 | 0.0060615 | 0.0015192 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-180_0_4_load_113 | 110 | 0.00076336 | 0.00019132 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-180_0_4_load_82 | 111 | 0.0056912 | 0.0014263 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-180_0_4_load_89 | 113 | 0.00096821 | 0.00024266 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-180_0_4_load_150 | 115 | 0.00045885 | 0.000115 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-180_0_4_load_96 | 117 | 0.00018317 | 4.5906e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-180_0_4_load_145 | 119 | 0.0013188 | 0.00033051 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-180_0_4_load_155 | 120 | 0.00018268 | 4.5783e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-180_0_4_load_94 | 121 | 0.0071017 | 0.0017799 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_230-180_0_4_load_141 | 122 | 0.001083 | 0.00027143 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_230-180_0_4_load_107 | 123 | 0.0010033 | 0.00025144 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_230-180_0_4_load_153 | 127 | 0.00093964 | 0.0002355 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_230-180_0_4_load_151 | 129 | 0.0013504 | 0.00033844 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_230-180_0_4_load_156 | 130 | 0.0051615 | 0.0012936 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_230-180_0_4_load_101 | 133 | 0.001557 | 0.00039022 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_230-180_0_4_load_103 | 134 | 0.0012822 | 0.00032135 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_230-180_0_4_load_108 | 135 | 0.0035006 | 0.00087734 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_230-180_0_4_load_114 | 136 | 0.00090788 | 0.00022754 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_230-180_0_4_load_115 | 137 | 0.00067255 | 0.00016856 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_230-180_0_4_load_117 | 138 | 0.00080136 | 0.00020084 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_230-180_0_4_load_118 | 139 | 0.00065189 | 0.00016338 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_230-180_0_4_load_120 | 140 | 0.0027443 | 0.00068778 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_230-180_0_4_load_129 | 142 | 0.0011439 | 0.00028668 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_230-180_0_4_load_131 | 143 | 0.0020424 | 0.00051186 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_230-180_0_4_load_139 | 144 | 0.010076 | 0.0025254 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_230-180_0_4_load_136 | 145 | 0.000924 | 0.00023158 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_230-180_0_4_load_137 | 146 | 0.00063749 | 0.00015977 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_230-180_0_4_load_133 | 147 | 0.00073254 | 0.00018359 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_230-180_0_4_load_143 | 148 | 0.00034254 | 8.5848e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-180_0_4_line_0 |  | 0 | 1 | 0.094872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-180_0_4_line_1 |  | 1 | 2 | 0.073081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-180_0_4_line_2 |  | 1 | 3 | 0.009612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-180_0_4_line_3 |  | 2 | 4 | 0.11108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-180_0_4_line_4 |  | 3 | 5 | 0.008404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-180_0_4_line_5 |  | 4 | 6 | 0.14743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-180_0_4_line_6 |  | 5 | 9 | 0.0037449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-180_0_4_line_7 |  | 6 | 7 | 0.44964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-180_0_4_line_8 |  | 7 | 11 | 0.082211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-180_0_4_line_9 |  | 8 | 9 | 0.082053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-180_0_4_line_10 |  | 8 | 10 | 0.21606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-180_0_4_line_11 |  | 9 | 17 | 0.21741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-180_0_4_line_12 |  | 10 | 18 | 0.077506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-180_0_4_line_13 |  | 11 | 21 | 0.0073094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-180_0_4_line_14 |  | 12 | 13 | 0.023043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-180_0_4_line_15 |  | 12 | 14 | 0.018012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-180_0_4_line_16 |  | 12 | 15 | 0.0097162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-180_0_4_line_17 |  | 14 | 16 | 0.045082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-180_0_4_line_18 |  | 16 | 22 | 0.054781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-180_0_4_line_19 |  | 17 | 20 | 0.017131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-180_0_4_line_20 |  | 17 | 100 | 0.084138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-180_0_4_line_21 |  | 18 | 102 | 0.23286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-180_0_4_line_22 |  | 19 | 20 | 0.031969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-180_0_4_line_23 |  | 22 | 99 | 0.00387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-180_0_4_line_24 |  | 23 | 24 | 0.013926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-180_0_4_line_25 |  | 23 | 25 | 0.0054659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-180_0_4_line_26 |  | 24 | 26 | 0.017397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-180_0_4_line_27 |  | 24 | 27 | 0.005997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-180_0_4_line_28 |  | 25 | 28 | 0.020309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-180_0_4_line_29 |  | 25 | 29 | 0.0095044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-180_0_4_line_30 |  | 26 | 30 | 0.015067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-180_0_4_line_31 |  | 27 | 31 | 0.027324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-180_0_4_line_32 |  | 27 | 32 | 0.021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-180_0_4_line_33 |  | 28 | 33 | 0.0070492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-180_0_4_line_34 |  | 29 | 34 | 0.0006148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-180_0_4_line_35 |  | 30 | 35 | 0.0038494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-180_0_4_line_36 |  | 31 | 36 | 0.0098732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-180_0_4_line_37 |  | 32 | 37 | 0.0029816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-180_0_4_line_38 |  | 33 | 38 | 0.0287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-180_0_4_line_39 |  | 34 | 39 | 0.0054022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-180_0_4_line_40 |  | 35 | 40 | 0.015635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-180_0_4_line_41 |  | 36 | 41 | 0.0056978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-180_0_4_line_42 |  | 37 | 45 | 0.031874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-180_0_4_line_43 |  | 39 | 46 | 0.015023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-180_0_4_line_44 |  | 40 | 133 | 0.012606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-180_0_4_line_45 |  | 41 | 44 | 0.01755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-180_0_4_line_46 |  | 42 | 43 | 0.0080852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-180_0_4_line_47 |  | 43 | 91 | 0.01428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_230-180_0_4_line_48 |  | 43 | 62 | 0.010987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-180_0_4_line_49 |  | 44 | 105 | 0.0033741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-180_0_4_line_50 |  | 45 | 111 | 0.015286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-180_0_4_line_51 |  | 46 | 142 | 0.0011999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-180_0_4_line_52 |  | 47 | 48 | 0.017654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-180_0_4_line_53 |  | 47 | 49 | 0.014529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-180_0_4_line_54 |  | 48 | 50 | 0.0082619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-180_0_4_line_55 |  | 49 | 51 | 0.010818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-180_0_4_line_56 |  | 49 | 52 | 0.009781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-180_0_4_line_57 |  | 50 | 53 | 0.010405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-180_0_4_line_58 |  | 51 | 54 | 0.016727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-180_0_4_line_59 |  | 52 | 55 | 0.028375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-180_0_4_line_60 |  | 53 | 56 | 0.0070552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-180_0_4_line_61 |  | 55 | 57 | 0.0016158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-180_0_4_line_62 |  | 56 | 58 | 0.014672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-180_0_4_line_63 |  | 56 | 59 | 0.015816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-180_0_4_line_64 |  | 57 | 63 | 0.037102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-180_0_4_line_65 |  | 58 | 106 | 0.014963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-180_0_4_line_66 |  | 59 | 104 | 0.0023895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-180_0_4_line_67 |  | 60 | 61 | 0.02116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-180_0_4_line_68 |  | 60 | 62 | 0.0369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-180_0_4_line_69 |  | 61 | 88 | 0.038038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-180_0_4_line_70 |  | 63 | 109 | 0.040298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-180_0_4_line_71 |  | 64 | 65 | 0.0061216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-180_0_4_line_72 |  | 64 | 66 | 0.0054426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-180_0_4_line_73 |  | 65 | 67 | 0.005021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-180_0_4_line_74 |  | 66 | 68 | 0.0026241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-180_0_4_line_75 |  | 67 | 69 | 0.014626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-180_0_4_line_76 |  | 68 | 70 | 0.0096582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-180_0_4_line_77 |  | 69 | 71 | 0.013562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-180_0_4_line_78 |  | 70 | 72 | 0.01197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-180_0_4_line_79 |  | 71 | 73 | 0.011805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-180_0_4_line_80 |  | 71 | 74 | 0.030002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-180_0_4_line_81 |  | 72 | 75 | 0.00089968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-180_0_4_line_82 |  | 73 | 85 | 0.0047206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_230-180_0_4_line_83 |  | 74 | 87 | 0.0097489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-180_0_4_line_84 |  | 75 | 97 | 0.022941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-180_0_4_line_85 |  | 76 | 77 | 0.008403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-180_0_4_line_86 |  | 76 | 78 | 0.003033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-180_0_4_line_87 |  | 77 | 79 | 0.010889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-180_0_4_line_88 |  | 78 | 80 | 0.00028094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-180_0_4_line_89 |  | 79 | 81 | 0.0057389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-180_0_4_line_90 |  | 80 | 82 | 0.0092298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-180_0_4_line_91 |  | 81 | 83 | 0.00026902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-180_0_4_line_92 |  | 82 | 84 | 0.0091907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-180_0_4_line_93 |  | 83 | 85 | 0.0012666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-180_0_4_line_94 |  | 84 | 86 | 0.015617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-180_0_4_line_95 |  | 86 | 101 | 0.027387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-180_0_4_line_96 |  | 87 | 89 | 0.012311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_230-180_0_4_line_97 |  | 88 | 90 | 0.04436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_230-180_0_4_line_98 |  | 89 | 92 | 0.0084572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-180_0_4_line_99 |  | 90 | 93 | 0.051487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-180_0_4_line_100 |  | 90 | 94 | 0.020159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_230-180_0_4_line_101 |  | 91 | 95 | 0.0087673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_230-180_0_4_line_102 |  | 92 | 139 | 0.0076154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-180_0_4_line_103 |  | 93 | 144 | 0.023584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-180_0_4_line_104 |  | 94 | 145 | 0.0093448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-180_0_4_line_105 |  | 95 | 139 | 0.01599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-180_0_4_line_106 |  | 95 | 136 | 0.0021069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-180_0_4_line_107 |  | 96 | 97 | 0.0083151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-180_0_4_line_108 |  | 96 | 98 | 0.014502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-180_0_4_line_109 |  | 98 | 99 | 0.024391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-180_0_4_line_110 |  | 98 | 100 | 0.0031808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-180_0_4_line_111 |  | 101 | 110 | 0.053342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_230-180_0_4_line_112 |  | 102 | 103 | 0.019585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_230-180_0_4_line_113 |  | 104 | 105 | 0.0086345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-180_0_4_line_114 |  | 106 | 107 | 0.012363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-180_0_4_line_115 |  | 107 | 108 | 0.0053484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-180_0_4_line_116 |  | 108 | 131 | 0.019551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-180_0_4_line_117 |  | 112 | 113 | 0.15865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-180_0_4_line_118 |  | 112 | 114 | 0.069399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_230-180_0_4_line_119 |  | 113 | 115 | 0.037496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-180_0_4_line_120 |  | 114 | 119 | 0.02498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-180_0_4_line_121 |  | 115 | 116 | 0.15432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-180_0_4_line_122 |  | 116 | 117 | 0.19674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-180_0_4_line_123 |  | 116 | 118 | 0.27578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-180_0_4_line_124 |  | 118 | 120 | 0.02409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-180_0_4_line_125 |  | 119 | 125 | 0.051743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_230-180_0_4_line_126 |  | 120 | 127 | 0.031329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-180_0_4_line_127 |  | 121 | 122 | 0.0080099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-180_0_4_line_128 |  | 122 | 131 | 0.053393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_230-180_0_4_line_129 |  | 123 | 124 | 0.051018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_230-180_0_4_line_130 |  | 124 | 135 | 0.032659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_230-180_0_4_line_131 |  | 124 | 134 | 0.0066932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_230-180_0_4_line_132 |  | 125 | 132 | 0.071679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_230-180_0_4_line_133 |  | 126 | 127 | 0.050048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_230-180_0_4_line_134 |  | 126 | 128 | 0.10488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-180_0_4_line_135 |  | 126 | 129 | 0.048927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-180_0_4_line_136 |  | 128 | 130 | 0.0419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_230-180_0_4_line_137 |  | 131 | 148 | 0.011692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_230-180_0_4_line_138 |  | 132 | 135 | 0.0077898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_230-180_0_4_line_139 |  | 133 | 134 | 0.02262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_230-180_0_4_line_140 |  | 136 | 137 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_230-180_0_4_line_141 |  | 137 | 138 | 0.0094791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_230-180_0_4_line_142 |  | 138 | 140 | 0.023577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_230-180_0_4_line_143 |  | 140 | 141 | 0.0061446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_230-180_0_4_line_144 |  | 141 | 142 | 0.032491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_230-180_0_4_line_145 |  | 141 | 143 | 0.018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_230-180_0_4_line_146 |  | 143 | 147 | 0.038422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_230-180_0_4_line_147 |  | 145 | 146 | 0.0096527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-180_0_4_trafo_57 | 0.63 MVA 20/0.4 kV | 149 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2699236.0932 | 1265982.5362 | 2699195.4279 | 1265959.2343 | 2699177.9706 | 1265957.0729 | 2699148.2888 | 1265950.4465
1 | 2699175.4342 | 1266019.7826 | 2699190.3132 | 1266015.373 | 2699205.4116 | 1266009.566 | 2699217.8551 | 1266002.6579 | 2699229.3978 | 1265991.9983 | 2699236.0932 | 1265982.5362
2 | 2699241.4611 | 1265974.553 | 2699236.0932 | 1265982.5362
3 | 2699175.4342 | 1266019.7826 | 2699155.0549 | 1266019.8853 | 2699144.9803 | 1266020.7059 | 2699129.1751 | 1266022.42 | 2699106.6609 | 1266028.581 | 2699097.7887 | 1266028.6546 | 2699091.1504 | 1266027.0976 | 2699085.1182 | 1266023.0709 | 2699079.4286 | 1266016.5812 | 2699076.1812 | 1266007.3551
4 | 2699241.4611 | 1265974.553 | 2699245.5126 | 1265967.19
5 | 2698938.4681 | 1265965.1331 | 2698957.7382 | 1265969.2146 | 2698995.4748 | 1265982.1906 | 2699058.4485 | 1265991.8868 | 2699069.7376 | 1265998.5705 | 2699075.5542 | 1266005.5738 | 2699076.1812 | 1266007.3551
6 | 2699247.318 | 1265963.9091 | 2699245.5126 | 1265967.19
7 | 2698871.2182 | 1265766.376 | 2698911.5051 | 1265733.278 | 2698961.6844 | 1265701.7471 | 2698969.0599 | 1265688.1036 | 2698988.112 | 1265745.2479 | 2698999.2288 | 1265785.6121 | 2698997.059 | 1265809.9293 | 2698992.6078 | 1265824.7893 | 2698981.7038 | 1265861.1592 | 2698977.3883 | 1265875.5657 | 2698968.094 | 1265894.081 | 2698926.1835 | 1265944.1323 | 2698915.7395 | 1265958.9143 | 2698925.6776 | 1265962.1944 | 2698938.4681 | 1265965.1331
8 | 2698871.2182 | 1265766.376 | 2698872.1585 | 1265770.94 | 2698875.8668 | 1265779.7538 | 2698884.8852 | 1265784.9089 | 2698907.008 | 1265796.7666 | 2698910.6406 | 1265806.0462 | 2698910.5646 | 1265828.5822
9 | 2699294.1037 | 1266029.4271 | 2699284.4761 | 1266003.655 | 2699275.4823 | 1265990.8044 | 2699247.318 | 1265963.9091
10 | 2699294.1037 | 1266029.4271 | 2699303.9932 | 1266032.8961 | 2699309.6093 | 1266032.1009 | 2699323.1019 | 1266024.6102 | 2699333.1868 | 1266017.3514 | 2699381.0082 | 1265980.5022 | 2699391.8388 | 1265975.0353 | 2699405.3813 | 1265973.0947 | 2699425.2366 | 1265976.398 | 2699487.0728 | 1265998.7189
11 | 2699247.318 | 1265963.9091 | 2699246.9925 | 1265957.287 | 2699248.2663 | 1265948.2564 | 2699253.9864 | 1265931.4162 | 2699262.9055 | 1265912.4279 | 2699270.9015 | 1265901.7644 | 2699296.8464 | 1265878.3695 | 2699322.0358 | 1265860.5 | 2699380.1339 | 1265833.7318 | 2699387.2414 | 1265831.138 | 2699397.2252 | 1265824.1
12 | 2699559.6042 | 1266026.0341 | 2699502.0484 | 1266004.1246 | 2699487.0728 | 1265998.7189
13 | 2698910.54 | 1265835.8916 | 2698910.5646 | 1265828.5822
14 | 2699390.1568 | 1265681.1399 | 2699403.3582 | 1265662.253
15 | 2699378.7912 | 1265690.1786 | 2699384.4001 | 1265679.5307 | 2699390.1568 | 1265681.1399
16 | 2699390.1568 | 1265681.1399 | 2699399.5204 | 1265683.7338
17 | 2699378.7912 | 1265690.1786 | 2699376.5275 | 1265703.4182 | 2699378.8917 | 1265711.954 | 2699395.6366 | 1265727.4177
18 | 2699439.2386 | 1265759.8515 | 2699430.2437 | 1265756.3321 | 2699406.2185 | 1265737.19 | 2699395.6366 | 1265727.4177
19 | 2699397.2252 | 1265824.1 | 2699381.2469 | 1265817.9234
20 | 2699397.2252 | 1265824.1 | 2699402.9258 | 1265820.0814 | 2699416.4429 | 1265808.0431 | 2699431.7111 | 1265793.5322 | 2699443.508 | 1265784.3675 | 2699454.2149 | 1265777.7754 | 2699462.9172 | 1265771.9237
21 | 2699559.6042 | 1266026.0341 | 2699580.3835 | 1265966.0229 | 2699591.1619 | 1265974.3892 | 2699643.7197 | 1266003.7438 | 2699705.9899 | 1266037.6554 | 2699716.1605 | 1266044.9775 | 2699723.1179 | 1266054.8364
22 | 2699350.6621 | 1265809.1323 | 2699365.254 | 1265811.7412 | 2699381.2469 | 1265817.9234
23 | 2699439.2386 | 1265759.8515 | 2699442.8425 | 1265761.2616
24 | 2699728.0652 | 1265680.6188 | 2699730.321 | 1265694.3607
25 | 2699731.2064 | 1265699.7544 | 2699730.321 | 1265694.3607
26 | 2699728.0652 | 1265680.6188 | 2699745.171 | 1265677.4478
27 | 2699728.0652 | 1265680.6188 | 2699722.15 | 1265681.7088
28 | 2699731.2064 | 1265699.7544 | 2699734.3303 | 1265705.1894 | 2699746.1454 | 1265712.7741
29 | 2699731.2064 | 1265699.7544 | 2699726.3286 | 1265707.9117
30 | 2699759.9857 | 1265674.7016 | 2699745.171 | 1265677.4478
31 | 2699702.0544 | 1265663.1433 | 2699716.9296 | 1265676.4386 | 2699722.15 | 1265681.7088
32 | 2699722.15 | 1265681.7088 | 2699724.9419 | 1265673.36 | 2699728.0416 | 1265661.3088
33 | 2699746.1454 | 1265712.7741 | 2699752.0776 | 1265716.5822
34 | 2699726.3286 | 1265707.9117 | 2699726.0131 | 1265708.4394
35 | 2699759.9857 | 1265674.7016 | 2699763.7707 | 1265673.9999
36 | 2699702.0544 | 1265663.1433 | 2699694.6776 | 1265656.581
37 | 2699728.0416 | 1265661.3088 | 2699728.6898 | 1265658.7889 | 2699728.8008 | 1265658.4257
38 | 2699774.8133 | 1265734.0609 | 2699773.9929 | 1265733.4489 | 2699756.2487 | 1265719.2598 | 2699752.0776 | 1265716.5822
39 | 2699726.0131 | 1265708.4394 | 2699723.2406 | 1265713.0759
40 | 2699778.8529 | 1265669.9891 | 2699778.8529 | 1265669.9891 | 2699769.6308 | 1265672.9137 | 2699763.7707 | 1265673.9999
41 | 2699690.4205 | 1265652.794 | 2699694.6776 | 1265656.581
42 | 2699739.5152 | 1265628.507 | 2699735.5848 | 1265636.242 | 2699728.8008 | 1265658.4257
43 | 2699710.6744 | 1265714.5906 | 2699720.9302 | 1265716.9398 | 2699723.2406 | 1265713.0759
44 | 2699778.8529 | 1265669.9891 | 2699789.4108 | 1265664.6739 | 2699790.0939 | 1265664.2863
45 | 2699690.4205 | 1265652.794 | 2699684.7131 | 1265647.8159 | 2699675.7108 | 1265643.516
46 | 2699643.2825 | 1265696.18 | 2699646.1386 | 1265695.6276 | 2699651.2322 | 1265694.7066
47 | 2699643.2825 | 1265696.18 | 2699644.6292 | 1265710.3963
48 | 2699643.2825 | 1265696.18 | 2699632.4948 | 1265698.2637
49 | 2699672.3844 | 1265642.9512 | 2699675.7108 | 1265643.516
50 | 2699746.4398 | 1265614.8797 | 2699739.5152 | 1265628.507
51 | 2699709.5048 | 1265714.3227 | 2699710.6744 | 1265714.5906
52 | 2699602.4187 | 1265638.8574 | 2699620.0713 | 1265639.1042
53 | 2699587.8907 | 1265638.6542 | 2699602.4187 | 1265638.8574
54 | 2699620.0713 | 1265639.1042 | 2699628.3323 | 1265639.2197
55 | 2699587.8907 | 1265638.6542 | 2699589.2044 | 1265649.3923
56 | 2699587.8907 | 1265638.6542 | 2699579.7288 | 1265633.2643
57 | 2699638.7361 | 1265639.3652 | 2699628.3323 | 1265639.2197
58 | 2699591.2357 | 1265665.9955 | 2699589.2044 | 1265649.3923
59 | 2699579.7288 | 1265633.2643 | 2699576.9867 | 1265631.4535 | 2699566.9402 | 1265619.8413 | 2699562.6919 | 1265611.0836
60 | 2699645.7906 | 1265639.4638 | 2699638.7361 | 1265639.3652
61 | 2699562.6919 | 1265611.0836 | 2699561.9867 | 1265609.6299
62 | 2699645.7906 | 1265639.4638 | 2699646.9494 | 1265631.9327 | 2699648.3337 | 1265625.0172
63 | 2699645.7906 | 1265639.4638 | 2699659.4227 | 1265640.7503 | 2699661.5159 | 1265641.1057
64 | 2699555.6749 | 1265573.3017 | 2699557.3854 | 1265590.2223 | 2699559.9022 | 1265605.3329 | 2699561.9867 | 1265609.6299
65 | 2699651.2709 | 1265610.3457 | 2699650.823 | 1265612.5818 | 2699648.3337 | 1265625.0172
66 | 2699661.5159 | 1265641.1057 | 2699663.8717 | 1265641.5057
67 | 2699596.2643 | 1265705.2619 | 2699575.3753 | 1265708.6408
68 | 2699596.2643 | 1265705.2619 | 2699632.4948 | 1265698.2637
69 | 2699575.3753 | 1265708.6408 | 2699561.3989 | 1265710.9016 | 2699544.562 | 1265712.1079 | 2699537.5802 | 1265712.6048
70 | 2699555.6749 | 1265573.3017 | 2699579.2101 | 1265561.655 | 2699593.1872 | 1265562.9701
71 | 2699540.9136 | 1265776.4597 | 2699542.1549 | 1265776.7435 | 2699546.9965 | 1265776.4904
72 | 2699535.6079 | 1265775.2468 | 2699540.9136 | 1265776.4597
73 | 2699551.9527 | 1265775.8586 | 2699550.1974 | 1265776.323 | 2699546.9965 | 1265776.4904
74 | 2699535.6079 | 1265775.2468 | 2699533.0498 | 1265774.662
75 | 2699551.9527 | 1265775.8586 | 2699566.0922 | 1265772.1176
76 | 2699533.0498 | 1265774.662 | 2699527.7136 | 1265773.4421 | 2699523.6006 | 1265772.6729
77 | 2699578.7994 | 1265767.3973 | 2699567.3463 | 1265771.7858 | 2699566.0922 | 1265772.1176
78 | 2699523.6006 | 1265772.6729 | 2699511.8348 | 1265770.4727
79 | 2699578.7994 | 1265767.3973 | 2699584.9732 | 1265777.4592
80 | 2699597.4249 | 1265744.0694 | 2699591.6413 | 1265753.8912 | 2699578.7994 | 1265767.3973
81 | 2699511.8348 | 1265770.4727 | 2699510.9505 | 1265770.3073
82 | 2699584.9732 | 1265777.4592 | 2699585.887 | 1265778.9485 | 2699588.3257 | 1265780.6496
83 | 2699597.4249 | 1265744.0694 | 2699606.0766 | 1265739.5761
84 | 2699488.2356 | 1265768.0292 | 2699497.9776 | 1265767.8813 | 2699510.9505 | 1265770.3073
85 | 2699610.1149 | 1265795.8485 | 2699610.1149 | 1265795.8485 | 2699603.2229 | 1265791.0411
86 | 2699612.8368 | 1265797.1866 | 2699610.1149 | 1265795.8485
87 | 2699594.292 | 1265784.8114 | 2699603.2229 | 1265791.0411
88 | 2699613.0889 | 1265797.3106 | 2699612.8368 | 1265797.1866
89 | 2699594.292 | 1265784.8114 | 2699589.5851 | 1265781.5281
90 | 2699621.372 | 1265801.3825 | 2699613.0889 | 1265797.3106
91 | 2699589.5851 | 1265781.5281 | 2699589.3645 | 1265781.3742
92 | 2699621.372 | 1265801.3825 | 2699629.6199 | 1265805.4372
93 | 2699589.3645 | 1265781.3742 | 2699588.3257 | 1265780.6496
94 | 2699643.6353 | 1265812.3272 | 2699629.6199 | 1265805.4372
95 | 2699643.6353 | 1265812.3272 | 2699662.7507 | 1265815.3185 | 2699670.5783 | 1265817.1474
96 | 2699617.0019 | 1265733.9021 | 2699606.0766 | 1265739.5761
97 | 2699493.4921 | 1265708.6899 | 2699510.0278 | 1265711.5038 | 2699535.7176 | 1265712.7373 | 2699537.5802 | 1265712.6048
98 | 2699617.0019 | 1265733.9021 | 2699624.5073 | 1265730.0042
99 | 2699493.4921 | 1265708.6899 | 2699489.4352 | 1265732.6971 | 2699496.2954 | 1265736.3045 | 2699515.1997 | 1265740.6118
100 | 2699493.4921 | 1265708.6899 | 2699483.4594 | 1265706.9863 | 2699473.8391 | 1265704.3213
101 | 2699645.456 | 1265719.1246 | 2699644.6292 | 1265710.3963
102 | 2699631.2656 | 1265726.4943 | 2699624.5073 | 1265730.0042
103 | 2699538.1946 | 1265745.8511 | 2699515.1997 | 1265740.6118
104 | 2699473.8391 | 1265704.3213 | 2699464.8334 | 1265701.8266
105 | 2699645.456 | 1265719.1246 | 2699631.2656 | 1265726.4943
106 | 2699645.456 | 1265719.1246 | 2699645.797 | 1265721.2037
107 | 2699488.2356 | 1265768.0292 | 2699479.9215 | 1265768.1555 | 2699479.9215 | 1265768.1555
108 | 2699465.5567 | 1265770.1488 | 2699479.9215 | 1265768.1555
109 | 2699465.5567 | 1265770.1488 | 2699442.8425 | 1265761.2616
110 | 2699465.5567 | 1265770.1488 | 2699462.9172 | 1265771.9237
111 | 2699670.5783 | 1265817.1474 | 2699685.682 | 1265820.6763 | 2699689.6601 | 1265821.4551 | 2699721.8625 | 1265831.6498
112 | 2699704.4379 | 1266060.893 | 2699723.1179 | 1266054.8364
113 | 2699672.3844 | 1265642.9512 | 2699663.8717 | 1265641.5057
114 | 2699651.2709 | 1265610.3457 | 2699653.699 | 1265598.224
115 | 2699654.7495 | 1265592.9798 | 2699653.699 | 1265598.224
116 | 2699657.8579 | 1265573.6902 | 2699656.5796 | 1265583.8438 | 2699654.7495 | 1265592.9798
117 | 2699900.6438 | 1265531.0744 | 2699902.631 | 1265528.9062 | 2699942.2746 | 1265487.9866 | 2699983.9758 | 1265447.4467 | 2699998.307 | 1265409.4826
118 | 2699900.6438 | 1265531.0744 | 2699902.9597 | 1265532.1812 | 2699905.9855 | 1265533.6224 | 2699914.5189 | 1265538.9266 | 2699919.5177 | 1265544.8271 | 2699928.3413 | 1265555.2404 | 2699930.6175 | 1265570.2692 | 2699927.6408 | 1265586.855
119 | 2700019.2542 | 1265381.7908 | 2700012.9648 | 1265382.8832 | 2700005.9747 | 1265389.1702 | 2699998.307 | 1265409.4826
120 | 2699927.6408 | 1265586.855 | 2699922.4517 | 1265611.2897
121 | 2700149.5221 | 1265312.7808 | 2700065.5526 | 1265379.9929 | 2700056.5969 | 1265382.7102 | 2700021.5985 | 1265381.3836 | 2700019.2542 | 1265381.7908
122 | 2700149.5221 | 1265312.7808 | 2700016.7327 | 1265259.0883 | 2700005.4821 | 1265254.5497 | 2699967.1256 | 1265239.0367
123 | 2700149.5221 | 1265312.7808 | 2700244.4445 | 1265234.9134 | 2700282.4304 | 1265204.9437 | 2700289.2755 | 1265202.3466 | 2700298.976 | 1265194.8159 | 2700306.2481 | 1265188.3673 | 2700336.0226 | 1265163.8632 | 2700342.1106 | 1265158.8401 | 2700316.5258 | 1265145.517
124 | 2700316.5258 | 1265145.517 | 2700294.4571 | 1265135.8584
125 | 2699921.7216 | 1265662.0843 | 2699917.761 | 1265646.4599 | 2699918.0397 | 1265632.6531 | 2699921.6591 | 1265615.0218 | 2699922.4517 | 1265611.2897
126 | 2700266.7745 | 1265121.1999 | 2700292.8938 | 1265135.1742 | 2700294.4571 | 1265135.8584
127 | 2699663.819 | 1265520.78 | 2699667.4025 | 1265513.6163
128 | 2699657.8579 | 1265573.6902 | 2699660.7513 | 1265561.5511 | 2699662.157 | 1265551.4442 | 2699663.819 | 1265520.78
129 | 2699812.4309 | 1265645.6356 | 2699839.8495 | 1265612.3263 | 2699844.9047 | 1265606.2877
130 | 2699812.4309 | 1265645.6356 | 2699821.4795 | 1265651.6489 | 2699825.1651 | 1265652.3673 | 2699837.8695 | 1265651.9481 | 2699843.1956 | 1265652.0788
131 | 2699812.4309 | 1265645.6356 | 2699807.8016 | 1265650.4696
132 | 2699850.9831 | 1265652.2699 | 2699882.62 | 1265656.7747 | 2699912.4282 | 1265663.4284 | 2699921.7216 | 1265662.0843
133 | 2700222.6663 | 1265097.552 | 2700235.5023 | 1265104.5421 | 2700245.9904 | 1265110.0801 | 2700266.7745 | 1265121.1999
134 | 2700222.6663 | 1265097.552 | 2700223.3698 | 1265089.3793 | 2700213.7311 | 1265044.4229 | 2700214.6651 | 1265038.2003 | 2700221.2939 | 1265044.3733 | 2700224.8583 | 1265046.4799 | 2700228.8761 | 1265047.1708 | 2700237.5226 | 1265046.2833 | 2700255.411 | 1265041.8274
135 | 2700222.6663 | 1265097.552 | 2700178.8528 | 1265075.7747
136 | 2700255.411 | 1265041.8274 | 2700257.1353 | 1265046.7385 | 2700274.1643 | 1265060.5165 | 2700278.1839 | 1265074.7499
137 | 2699657.8579 | 1265573.6902 | 2699646.3877 | 1265571.4246
138 | 2699850.9831 | 1265652.2699 | 2699843.1956 | 1265652.0788
139 | 2699790.0939 | 1265664.2863 | 2699796.1858 | 1265660.8295 | 2699802.2654 | 1265656.2506 | 2699807.8016 | 1265650.4696
140 | 2699645.797 | 1265721.2037 | 2699646.89 | 1265727.8672 | 2699660.8605 | 1265732.865
141 | 2699660.8605 | 1265732.865 | 2699669.7857 | 1265736.058
142 | 2699669.7857 | 1265736.058 | 2699679.8721 | 1265739.6663 | 2699692.5233 | 1265742.0021
143 | 2699698.5658 | 1265743.1178 | 2699692.5233 | 1265742.0021
144 | 2699698.5658 | 1265743.1178 | 2699701.0607 | 1265739.8682 | 2699701.151 | 1265725.1464 | 2699709.5048 | 1265714.3227 | 2699709.5048 | 1265714.3227
145 | 2699698.5658 | 1265743.1178 | 2699704.9711 | 1265744.2156 | 2699711.1491 | 1265745.3986 | 2699714.8359 | 1265749.6087
146 | 2699686.4762 | 1265763.7978 | 2699702.2724 | 1265764.4536 | 2699709.3388 | 1265762.9716 | 2699713.843 | 1265758.466 | 2699715.0129 | 1265754.2934 | 2699714.8359 | 1265749.6087
147 | 2699455.5311 | 1265699.2497 | 2699464.8334 | 1265701.8266

## bus_geodata
| x | y | coords
0 | 2699148.2888 | 1265950.4465
1 | 2699236.0932 | 1265982.5362
2 | 2699175.4342 | 1266019.7826
3 | 2699241.4611 | 1265974.553
4 | 2699076.1812 | 1266007.3551
5 | 2699245.5126 | 1265967.19
6 | 2698938.4681 | 1265965.1331
7 | 2698871.2182 | 1265766.376
8 | 2699294.1037 | 1266029.4271
9 | 2699247.318 | 1265963.9091
10 | 2699487.0728 | 1265998.7189
11 | 2698910.5646 | 1265828.5822
12 | 2699390.1568 | 1265681.1399
13 | 2699403.3582 | 1265662.253
14 | 2699378.7912 | 1265690.1786
15 | 2699399.5204 | 1265683.7338
16 | 2699395.6366 | 1265727.4177
17 | 2699397.2252 | 1265824.1
18 | 2699559.6042 | 1266026.0341
19 | 2699350.6621 | 1265809.1323
20 | 2699381.2469 | 1265817.9234
21 | 2698910.54 | 1265835.8916
22 | 2699439.2386 | 1265759.8515
23 | 2699730.321 | 1265694.3607
24 | 2699728.0652 | 1265680.6188
25 | 2699731.2064 | 1265699.7544
26 | 2699745.171 | 1265677.4478
27 | 2699722.15 | 1265681.7088
28 | 2699746.1454 | 1265712.7741
29 | 2699726.3286 | 1265707.9117
30 | 2699759.9857 | 1265674.7016
31 | 2699702.0544 | 1265663.1433
32 | 2699728.0416 | 1265661.3088
33 | 2699752.0776 | 1265716.5822
34 | 2699726.0131 | 1265708.4394
35 | 2699763.7707 | 1265673.9999
36 | 2699694.6776 | 1265656.581
37 | 2699728.8008 | 1265658.4257
38 | 2699774.8133 | 1265734.0609
39 | 2699723.2406 | 1265713.0759
40 | 2699778.8529 | 1265669.9891
41 | 2699690.4205 | 1265652.794
42 | 2699651.2322 | 1265694.7066
43 | 2699643.2825 | 1265696.1799
44 | 2699675.7108 | 1265643.516
45 | 2699739.5152 | 1265628.507
46 | 2699710.6744 | 1265714.5906
47 | 2699602.4187 | 1265638.8574
48 | 2699620.0713 | 1265639.1042
49 | 2699587.8907 | 1265638.6542
50 | 2699628.3323 | 1265639.2197
51 | 2699589.2044 | 1265649.3923
52 | 2699579.7288 | 1265633.2643
53 | 2699638.7361 | 1265639.3652
54 | 2699591.2357 | 1265665.9955
55 | 2699562.6919 | 1265611.0836
56 | 2699645.7906 | 1265639.4638
57 | 2699561.9867 | 1265609.6299
58 | 2699648.3337 | 1265625.0172
59 | 2699661.5159 | 1265641.1057
60 | 2699596.2643 | 1265705.2619
61 | 2699575.3753 | 1265708.6408
62 | 2699632.4948 | 1265698.2637
63 | 2699555.6749 | 1265573.3017
64 | 2699540.9136 | 1265776.4597
65 | 2699546.9965 | 1265776.4904
66 | 2699535.6079 | 1265775.2468
67 | 2699551.9527 | 1265775.8586
68 | 2699533.0498 | 1265774.662
69 | 2699566.0922 | 1265772.1176
70 | 2699523.6006 | 1265772.6729
71 | 2699578.7994 | 1265767.3973
72 | 2699511.8348 | 1265770.4727
73 | 2699584.9732 | 1265777.4592
74 | 2699597.4249 | 1265744.0694
75 | 2699510.9505 | 1265770.3073
76 | 2699610.1149 | 1265795.8485
77 | 2699603.2229 | 1265791.0411
78 | 2699612.8368 | 1265797.1866
79 | 2699594.292 | 1265784.8114
80 | 2699613.0889 | 1265797.3106
81 | 2699589.5851 | 1265781.5281
82 | 2699621.3719 | 1265801.3825
83 | 2699589.3645 | 1265781.3742
84 | 2699629.6199 | 1265805.4372
85 | 2699588.3257 | 1265780.6496
86 | 2699643.6353 | 1265812.3272
87 | 2699606.0766 | 1265739.5761
88 | 2699537.5802 | 1265712.6048
89 | 2699617.0019 | 1265733.9021
90 | 2699493.4921 | 1265708.6899
91 | 2699644.6292 | 1265710.3963
92 | 2699624.5073 | 1265730.0042
93 | 2699515.1997 | 1265740.6118
94 | 2699473.8391 | 1265704.3213
95 | 2699645.456 | 1265719.1246
96 | 2699479.9215 | 1265768.1555
97 | 2699488.2356 | 1265768.0292
98 | 2699465.5567 | 1265770.1488
99 | 2699442.8425 | 1265761.2616
100 | 2699462.9172 | 1265771.9237
101 | 2699670.5783 | 1265817.1474
102 | 2699723.1179 | 1266054.8364
103 | 2699704.4379 | 1266060.893
104 | 2699663.8717 | 1265641.5057
105 | 2699672.3844 | 1265642.9512
106 | 2699651.2709 | 1265610.3457
107 | 2699653.699 | 1265598.224
108 | 2699654.7495 | 1265592.9798
109 | 2699593.1872 | 1265562.9701
110 | 2699721.8625 | 1265831.6498
111 | 2699746.4398 | 1265614.8797
112 | 2699900.6438 | 1265531.0744
113 | 2699998.307 | 1265409.4826
114 | 2699927.6408 | 1265586.855
115 | 2700019.2542 | 1265381.7908
116 | 2700149.5221 | 1265312.7808
117 | 2699967.1256 | 1265239.0367
118 | 2700316.5258 | 1265145.517
119 | 2699922.4517 | 1265611.2897
120 | 2700294.4571 | 1265135.8584
121 | 2699667.4025 | 1265513.6163
122 | 2699663.819 | 1265520.78
123 | 2699844.9047 | 1265606.2877
124 | 2699812.4309 | 1265645.6356
125 | 2699921.7216 | 1265662.0843
126 | 2700222.6663 | 1265097.552
127 | 2700266.7745 | 1265121.1999
128 | 2700255.411 | 1265041.8274
129 | 2700178.8528 | 1265075.7747
130 | 2700278.1839 | 1265074.7499
131 | 2699657.8579 | 1265573.6902
132 | 2699850.9831 | 1265652.2699
133 | 2699790.0939 | 1265664.2863
134 | 2699807.8016 | 1265650.4696
135 | 2699843.1956 | 1265652.0788
136 | 2699645.797 | 1265721.2037
137 | 2699660.8605 | 1265732.865
138 | 2699669.7857 | 1265736.058
139 | 2699631.2656 | 1265726.4943
140 | 2699692.5233 | 1265742.0021
141 | 2699698.5658 | 1265743.1178
142 | 2699709.5048 | 1265714.3227
143 | 2699714.8359 | 1265749.6087
144 | 2699538.1946 | 1265745.8511
145 | 2699464.8334 | 1265701.8266
146 | 2699455.5311 | 1265699.2497
147 | 2699686.4762 | 1265763.7978
148 | 2699646.3877 | 1265571.4246
149 | 2699645.456 | 1265719.1246

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98863 | -0.21956 | 0.00072285 | 0.00018116
1 | 0.98869 | -0.21834 | 0 | 0
2 | 0.98846 | -0.22277 | 0 | 0
3 | 0.98873 | -0.21763 | 0 | 0
4 | 0.98812 | -0.2295 | 0.00065659 | 0.00016456
5 | 0.98876 | -0.21701 | 0.0001763 | 4.4185e-05
6 | 0.98775 | -0.2367 | 0 | 0
7 | 0.98663 | -0.2586 | 0 | 0
8 | 0.98845 | -0.22302 | 0 | 0
9 | 0.98877 | -0.21672 | 0 | 0
10 | 0.9876 | -0.23961 | 0.0019168 | 0.00048039
11 | 0.98643 | -0.2626 | 0.0022082 | 0.00055343
12 | 0.99104 | -0.17254 | 0 | 0
13 | 0.99103 | -0.17274 | 0.00048831 | 0.00012238
14 | 0.99105 | -0.17225 | 0 | 0
15 | 0.99103 | -0.17261 | 0.00041948 | 0.00010513
16 | 0.99109 | -0.17152 | 0.0021787 | 0.00054604
17 | 0.99048 | -0.18341 | 0 | 0
18 | 0.98743 | -0.2429 | 0 | 0
19 | 0.99042 | -0.18447 | 0.00066408 | 0.00016643
20 | 0.99044 | -0.18409 | 0.0015702 | 0.00039353
21 | 0.98642 | -0.26267 | 0.00050599 | 0.00012681
22 | 0.99124 | -0.16852 | 0.00035239 | 8.8316e-05
23 | 0.98755 | -0.23857 | 0.0014954 | 0.00037479
24 | 0.98653 | -0.25832 | 0 | 0
25 | 0.98796 | -0.23068 | 0 | 0
26 | 0.98604 | -0.2678 | 0.0010267 | 0.00025733
27 | 0.98626 | -0.26357 | 0 | 0
28 | 0.98793 | -0.23113 | 0.00030603 | 7.6697e-05
29 | 0.98867 | -0.21677 | 0.00038108 | 9.5507e-05
30 | 0.98564 | -0.27574 | 0.0045619 | 0.0011433
31 | 0.98529 | -0.28236 | 0 | 0
32 | 0.98606 | -0.26757 | 0.0024879 | 0.00062352
33 | 0.98793 | -0.23125 | 0.00034134 | 8.5549e-05
34 | 0.98872 | -0.21586 | 0.00034405 | 8.6227e-05
35 | 0.98555 | -0.27746 | 0.0053315 | 0.0013362
36 | 0.98495 | -0.28916 | 0.0026119 | 0.00065461
37 | 0.98603 | -0.268 | 0.0016245 | 0.00040714
38 | 0.98791 | -0.23157 | 0.00060685 | 0.00015209
39 | 0.98913 | -0.20789 | 0.0015763 | 0.00039506
40 | 0.98527 | -0.28293 | 0.0015466 | 0.00038762
41 | 0.98476 | -0.29282 | 0 | 0
42 | 1 | -8.0397e-05 | 0.00057038 | 0.00014295
43 | 1 | 0 | -0.18347 | -0.046234
44 | 0.98418 | -0.3041 | 0.0010568 | 0.00026487
45 | 0.98585 | -0.27165 | 0.00070401 | 0.00017644
46 | 0.9903 | -0.18535 | 0.00089477 | 0.00022425
47 | 0.98263 | -0.33431 | 0.001147 | 0.00028748
48 | 0.98287 | -0.3297 | 0.0014029 | 0.0003516
49 | 0.98245 | -0.33781 | 0 | 0
50 | 0.98299 | -0.32733 | 0.00077162 | 0.00019339
51 | 0.98243 | -0.33826 | 0.00049751 | 0.00012469
52 | 0.98235 | -0.33976 | 0.0012015 | 0.00030111
53 | 0.98315 | -0.32421 | 0.00057707 | 0.00014463
54 | 0.9824 | -0.3388 | 0.001798 | 0.00045061
55 | 0.9821 | -0.3448 | 0.0021872 | 0.00054816
56 | 0.98326 | -0.32202 | 0 | 0
57 | 0.98208 | -0.34503 | 0.0015823 | 0.00039657
58 | 0.98307 | -0.32582 | 0.0015664 | 0.00039257
59 | 0.98372 | -0.31301 | 0.00213 | 0.00053382
60 | 0.99908 | -0.017687 | 0 | 0
61 | 0.99867 | -0.025461 | 0.0031946 | 0.00080065
62 | 0.99978 | -0.0041448 | 0.00060656 | 0.00015202
63 | 0.98188 | -0.34909 | 0 | 0
64 | 0.99268 | -0.14062 | 0.0010235 | 0.00025652
65 | 0.99284 | -0.1376 | 0.0028639 | 0.00071777
66 | 0.99255 | -0.1432 | 0.001332 | 0.00033382
67 | 0.99298 | -0.13486 | 0.001316 | 0.00032982
68 | 0.99249 | -0.14439 | 0.0015814 | 0.00039634
69 | 0.99341 | -0.12657 | 0.0014842 | 0.00037198
70 | 0.99227 | -0.14849 | 0.002183 | 0.00054711
71 | 0.99382 | -0.11853 | 0 | 0
72 | 0.99204 | -0.15311 | 0.00069033 | 0.00017301
73 | 0.99357 | -0.12332 | 0.0012549 | 0.00031451
74 | 0.99537 | -0.088631 | 0 | 0
75 | 0.99202 | -0.15344 | 0.0041226 | 0.0010332
76 | 0.9931 | -0.13245 | 0.0012879 | 0.00032278
77 | 0.9932 | -0.13061 | 0.0039083 | 0.0009795
78 | 0.99307 | -0.13305 | 0.00060562 | 0.00015178
79 | 0.99336 | -0.12747 | 0.0012156 | 0.00030465
80 | 0.99307 | -0.1331 | 0.0004978 | 0.00012476
81 | 0.99345 | -0.12569 | 0.00095156 | 0.00023848
82 | 0.99298 | -0.13473 | 0.0053797 | 0.0013483
83 | 0.99346 | -0.12561 | 0.0024506 | 0.00061418
84 | 0.99295 | -0.13548 | 0.0026446 | 0.0006628
85 | 0.99348 | -0.12514 | 0.00080791 | 0.00020248
86 | 0.99292 | -0.13603 | 0 | 0
87 | 0.99587 | -0.078934 | 0.0018376 | 0.00046056
88 | 0.99806 | -0.037324 | 0.00032242 | 8.0805e-05
89 | 0.99653 | -0.066306 | 0.0015406 | 0.00038611
90 | 0.99735 | -0.050926 | 0 | 0
91 | 0.99896 | -0.019671 | 0.0011589 | 0.00029046
92 | 0.99699 | -0.057412 | 0.0018633 | 0.00046699
93 | 0.99661 | -0.065176 | 0.0057057 | 0.00143
94 | 0.99732 | -0.051536 | 0.00016365 | 4.1015e-05
95 | 0.99833 | -0.03168 | 0 | 0
96 | 0.99154 | -0.16273 | 0.0012861 | 0.00032234
97 | 0.99166 | -0.16034 | 0.00073388 | 0.00018393
98 | 0.99134 | -0.16658 | 0 | 0
99 | 0.99126 | -0.16828 | 0.00048977 | 0.00012275
100 | 0.99131 | -0.1672 | 0.00016319 | 4.0899e-05
101 | 0.99287 | -0.137 | 0.0012219 | 0.00030623
102 | 0.98693 | -0.25278 | 0 | 0
103 | 0.98688 | -0.25361 | 0.0023676 | 0.00059337
104 | 0.9838 | -0.31156 | 0.0006906 | 0.00017308
105 | 0.98407 | -0.30621 | 0.00025504 | 6.3918e-05
106 | 0.98289 | -0.32927 | 0.00051196 | 0.00012831
107 | 0.98275 | -0.33202 | 0.0033528 | 0.0008403
108 | 0.98271 | -0.33288 | 0.0004071 | 0.00010203
109 | 0.98165 | -0.35351 | 0.0060615 | 0.0015192
110 | 0.99283 | -0.13772 | 0.00076336 | 0.00019132
111 | 0.98577 | -0.27321 | 0.0056912 | 0.0014263
112 | 0.9821 | -0.34465 | 0 | 0
113 | 0.98074 | -0.37129 | 0.00096821 | 0.00024266
114 | 0.9827 | -0.33302 | 0 | 0
115 | 0.98045 | -0.37694 | 0.00045885 | 0.000115
116 | 0.97934 | -0.39891 | 0 | 0
117 | 0.9793 | -0.39958 | 0.00018317 | 4.5906e-05
118 | 0.97738 | -0.43732 | 0 | 0
119 | 0.98291 | -0.32884 | 0.0013188 | 0.00033051
120 | 0.97721 | -0.44068 | 0.00018268 | 4.5783e-05
121 | 0.9821 | -0.34481 | 0.0071017 | 0.0017799
122 | 0.98215 | -0.34378 | 0.001083 | 0.00027143
123 | 0.98458 | -0.2964 | 0.0010033 | 0.00025144
124 | 0.98462 | -0.29548 | 0 | 0
125 | 0.98342 | -0.31894 | 0 | 0
126 | 0.97669 | -0.4509 | 0 | 0
127 | 0.97699 | -0.44494 | 0.00093964 | 0.0002355
128 | 0.97619 | -0.46081 | 0 | 0
129 | 0.97663 | -0.45211 | 0.0013504 | 0.00033844
130 | 0.97599 | -0.46476 | 0.0051615 | 0.0012936
131 | 0.98255 | -0.33589 | 0 | 0
132 | 0.98412 | -0.30525 | 0 | 0
133 | 0.98506 | -0.287 | 0.001557 | 0.00039022
134 | 0.98472 | -0.29366 | 0.0012822 | 0.00032135
135 | 0.9842 | -0.30377 | 0.0035006 | 0.00087734
136 | 0.99815 | -0.035154 | 0.00090788 | 0.00022754
137 | 0.99629 | -0.070487 | 0.00067255 | 0.00016856
138 | 0.99548 | -0.085929 | 0.00080136 | 0.00020084
139 | 0.99742 | -0.049162 | 0.00065189 | 0.00016338
140 | 0.99349 | -0.12411 | 0.0027443 | 0.00068778
141 | 0.99298 | -0.13379 | 0 | 0
142 | 0.9904 | -0.18353 | 0.0011439 | 0.00028668
143 | 0.99294 | -0.1347 | 0.0020424 | 0.00051186
144 | 0.99639 | -0.069347 | 0.010076 | 0.0025254
145 | 0.99731 | -0.051792 | 0.000924 | 0.00023158
146 | 0.9973 | -0.0519 | 0.00063749 | 0.00015977
147 | 0.99291 | -0.13519 | 0.00073254 | 0.00018359
148 | 0.98255 | -0.33596 | 0.00034254 | 8.5848e-05
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00072285 | -0.00018116 | 0.0007229 | 0.00017997 | 4.2097e-08 | -1.1896e-06 | 0.001088 | 0.0010876 | 0.001088 | 0.98863 | -0.21956 | 0.98869 | -0.21834 | 0.2989
1 | 0.0033768 | 0.00083753 | -0.0033761 | -0.00083802 | 7.0705e-07 | -4.8448e-07 | 0.0050792 | 0.0050795 | 0.0050795 | 0.98869 | -0.21834 | 0.98846 | -0.22277 | 1.3955
2 | -0.0040997 | -0.0010175 | 0.0040999 | 0.0010175 | 1.3707e-07 | -3.5544e-08 | 0.0061667 | 0.0061667 | 0.0061667 | 0.98869 | -0.21834 | 0.98873 | -0.21763 | 1.6942
3 | 0.0033761 | 0.00083802 | -0.0033751 | -0.00083875 | 1.0749e-06 | -7.3547e-07 | 0.0050795 | 0.00508 | 0.00508 | 0.98846 | -0.22277 | 0.98812 | -0.2295 | 1.3956
4 | -0.0040999 | -0.0010175 | 0.0041 | 0.0010174 | 1.1985e-07 | -3.1085e-08 | 0.0061667 | 0.0061667 | 0.0061667 | 0.98873 | -0.21763 | 0.98876 | -0.21701 | 1.6941
5 | 0.0027185 | 0.0006742 | -0.0027175 | -0.00067549 | 9.2555e-07 | -1.2954e-06 | 0.0040912 | 0.0040919 | 0.0040919 | 0.98812 | -0.2295 | 0.98775 | -0.2367 | 1.1242
6 | -0.0042763 | -0.0010616 | 0.0042764 | 0.0010616 | 5.8097e-08 | -1.085e-08 | 0.006432 | 0.006432 | 0.006432 | 0.98876 | -0.21701 | 0.98877 | -0.21672 | 1.767
7 | 0.0027175 | 0.00067549 | -0.0027147 | -0.00067943 | 2.8246e-06 | -3.941e-06 | 0.0040919 | 0.0040939 | 0.0040939 | 0.98775 | -0.2367 | 0.98663 | -0.2586 | 1.1247
8 | 0.0027147 | 0.00067943 | -0.0027142 | -0.00068015 | 5.1676e-07 | -7.1897e-07 | 0.0040939 | 0.0040943 | 0.0040943 | 0.98663 | -0.2586 | 0.98643 | -0.2626 | 1.1248
9 | -0.0042893 | -0.00107 | 0.0042906 | 0.0010697 | 1.2822e-06 | -2.3151e-07 | 0.0064554 | 0.006455 | 0.0064554 | 0.98845 | -0.22302 | 0.98877 | -0.21672 | 1.7735
10 | 0.0042893 | 0.00107 | -0.004286 | -0.0010706 | 3.377e-06 | -6.0588e-07 | 0.0064554 | 0.0064564 | 0.0064564 | 0.98845 | -0.22302 | 0.9876 | -0.23961 | 1.7737
11 | -0.008567 | -0.0021313 | 0.0085805 | 0.0021372 | 1.3539e-05 | 5.8715e-06 | 0.012887 | 0.012886 | 0.012887 | 0.98877 | -0.21672 | 0.99048 | -0.18341 | 3.5404
12 | 0.0023692 | 0.00059016 | -0.0023688 | -0.00059092 | 3.7012e-07 | -7.5472e-07 | 0.0035683 | 0.0035687 | 0.0035687 | 0.9876 | -0.23961 | 0.98743 | -0.2429 | 0.98041
13 | 0.00050599 | 0.00012672 | -0.00050599 | -0.00012681 | 1.5969e-09 | -9.2287e-08 | 0.00076325 | 0.00076329 | 0.00076329 | 0.98643 | -0.2626 | 0.98642 | -0.26267 | 0.20969
14 | 0.00048831 | 0.00012209 | -0.00048831 | -0.00012238 | 4.6446e-09 | -2.9394e-07 | 0.00073309 | 0.00073319 | 0.00073319 | 0.99104 | -0.17254 | 0.99103 | -0.17274 | 0.20143
15 | -0.0009078 | -0.0002271 | 0.00090781 | 0.00022687 | 1.2546e-08 | -2.2407e-07 | 0.0013629 | 0.0013628 | 0.0013629 | 0.99104 | -0.17254 | 0.99105 | -0.17225 | 0.37442
16 | 0.00041948 | 0.00010501 | -0.00041948 | -0.00010513 | 1.4453e-09 | -1.2427e-07 | 0.0006298 | 0.00062984 | 0.00062984 | 0.99104 | -0.17254 | 0.99103 | -0.17261 | 0.17303
17 | -0.00090781 | -0.00022687 | 0.00090784 | 0.00022631 | 3.1393e-08 | -5.6083e-07 | 0.0013628 | 0.0013626 | 0.0013628 | 0.99105 | -0.17225 | 0.99109 | -0.17152 | 0.3744
18 | -0.0030866 | -0.00077235 | 0.003087 | 0.00077193 | 4.4107e-07 | -4.2377e-07 | 0.0046337 | 0.0046335 | 0.0046337 | 0.99109 | -0.17152 | 0.99124 | -0.16852 | 1.273
19 | 0.0022344 | 0.00055938 | -0.0022343 | -0.00055956 | 7.2375e-08 | -1.7415e-07 | 0.0033565 | 0.0033566 | 0.0033566 | 0.99048 | -0.18341 | 0.99044 | -0.18409 | 0.92214
20 | -0.010815 | -0.0026966 | 0.010823 | 0.0027008 | 8.3237e-06 | 4.2434e-06 | 0.016242 | 0.016242 | 0.016242 | 0.99048 | -0.18341 | 0.99131 | -0.1672 | 4.4622
21 | 0.0023688 | 0.00059092 | -0.0023677 | -0.00059318 | 1.1124e-06 | -2.2651e-06 | 0.0035687 | 0.0035697 | 0.0035697 | 0.98743 | -0.2429 | 0.98693 | -0.25278 | 0.9807
22 | -0.00066408 | -0.00016643 | 0.00066409 | 0.00016603 | 1.1932e-08 | -4.0379e-07 | 0.00099771 | 0.00099757 | 0.00099771 | 0.99042 | -0.18447 | 0.99044 | -0.18409 | 0.2741
23 | -0.0034394 | -0.00086024 | 0.0034394 | 0.00086022 | 3.8677e-08 | -2.5133e-08 | 0.0051625 | 0.0051625 | 0.0051625 | 0.99124 | -0.16852 | 0.99126 | -0.16828 | 1.4183
24 | 0.079549 | 0.020041 | -0.079474 | -0.019993 | 7.5074e-05 | 4.787e-05 | 0.1199 | 0.1199 | 0.1199 | 0.98755 | -0.23857 | 0.98653 | -0.25832 | 32.9396
25 | -0.081045 | -0.020415 | 0.081075 | 0.020435 | 3.0585e-05 | 1.9504e-05 | 0.12215 | 0.12215 | 0.12215 | 0.98755 | -0.23857 | 0.98796 | -0.23068 | 33.5586
26 | 0.030485 | 0.0076645 | -0.030471 | -0.0076559 | 1.3799e-05 | 8.6091e-06 | 0.04599 | 0.04599 | 0.04599 | 0.98653 | -0.25832 | 0.98604 | -0.2678 | 12.6346
27 | 0.04899 | 0.012328 | -0.048977 | -0.01232 | 1.2285e-05 | 7.7859e-06 | 0.07391 | 0.07391 | 0.07391 | 0.98653 | -0.25832 | 0.98626 | -0.26357 | 20.3051
28 | 0.0012543 | 0.00031365 | -0.0012542 | -0.00031389 | 2.7173e-08 | -2.4266e-07 | 0.0018889 | 0.001889 | 0.001889 | 0.98796 | -0.23068 | 0.98793 | -0.23113 | 0.51895
29 | -0.08233 | -0.020748 | 0.082385 | 0.020783 | 5.484e-05 | 3.4976e-05 | 0.12404 | 0.12404 | 0.12404 | 0.98796 | -0.23068 | 0.98867 | -0.21677 | 34.0775
30 | 0.029444 | 0.0073986 | -0.029433 | -0.0073916 | 1.1159e-05 | 6.9496e-06 | 0.04444 | 0.044441 | 0.044441 | 0.98604 | -0.2678 | 0.98564 | -0.27574 | 12.2089
31 | 0.038466 | 0.0096855 | -0.038431 | -0.0096637 | 3.453e-05 | 2.1751e-05 | 0.058051 | 0.058052 | 0.058052 | 0.98626 | -0.26357 | 0.98529 | -0.28236 | 15.9482
32 | 0.010511 | 0.0026349 | -0.010509 | -0.0026339 | 2.0039e-06 | 1.0114e-06 | 0.015859 | 0.015859 | 0.015859 | 0.98626 | -0.26357 | 0.98606 | -0.26757 | 4.3569
33 | 0.00094821 | 0.00023719 | -0.0009482 | -0.00023728 | 5.3908e-09 | -8.6812e-08 | 0.001428 | 0.0014281 | 0.0014281 | 0.98793 | -0.23113 | 0.98793 | -0.23125 | 0.39232
34 | -0.082766 | -0.020879 | 0.082769 | 0.020881 | 3.5802e-06 | 2.2835e-06 | 0.12462 | 0.12462 | 0.12462 | 0.98867 | -0.21677 | 0.98872 | -0.21586 | 34.2351
35 | 0.024871 | 0.0062483 | -0.024869 | -0.006247 | 2.0358e-06 | 1.2538e-06 | 0.037553 | 0.037553 | 0.037553 | 0.98564 | -0.27574 | 0.98555 | -0.27746 | 10.3169
36 | 0.038431 | 0.0096637 | -0.038419 | -0.0096558 | 1.2477e-05 | 7.8597e-06 | 0.058052 | 0.058052 | 0.058052 | 0.98529 | -0.28236 | 0.98495 | -0.28916 | 15.9482
37 | 0.0080214 | 0.0020104 | -0.0080212 | -0.0020103 | 1.6383e-07 | 6.682e-08 | 0.012105 | 0.012105 | 0.012105 | 0.98606 | -0.26757 | 0.98603 | -0.268 | 3.3255
38 | 0.00060686 | 0.00015173 | -0.00060685 | -0.00015209 | 8.9907e-09 | -3.6172e-07 | 0.00091393 | 0.00091406 | 0.00091406 | 0.98793 | -0.23125 | 0.98791 | -0.23157 | 0.25111
39 | -0.083113 | -0.020967 | 0.083145 | 0.020988 | 3.1721e-05 | 2.0232e-05 | 0.12513 | 0.12513 | 0.12513 | 0.98872 | -0.21586 | 0.98913 | -0.20789 | 34.3773
40 | 0.019538 | 0.0049108 | -0.019533 | -0.0049078 | 5.1036e-06 | 3.0671e-06 | 0.029504 | 0.029504 | 0.029504 | 0.98555 | -0.27746 | 0.98527 | -0.28293 | 8.1054
41 | 0.035807 | 0.0090012 | -0.035801 | -0.0089973 | 6.2549e-06 | 3.9306e-06 | 0.054106 | 0.054106 | 0.054106 | 0.98495 | -0.28916 | 0.98476 | -0.29282 | 14.8642
42 | 0.0063967 | 0.0016032 | -0.0063956 | -0.0016029 | 1.1138e-06 | 3.0636e-07 | 0.0096532 | 0.0096534 | 0.0096534 | 0.98603 | -0.268 | 0.98585 | -0.27165 | 2.652
43 | -0.084721 | -0.021383 | 0.084813 | 0.021441 | 9.1591e-05 | 5.8425e-05 | 0.1275 | 0.1275 | 0.1275 | 0.98913 | -0.20789 | 0.9903 | -0.18535 | 35.0288
44 | 0.017986 | 0.0045201 | -0.017982 | -0.0045181 | 3.4891e-06 | 2.0725e-06 | 0.027168 | 0.027168 | 0.027168 | 0.98527 | -0.28293 | 0.98506 | -0.287 | 7.4638
45 | 0.035801 | 0.0089973 | -0.035782 | -0.0089852 | 1.9266e-05 | 1.2107e-05 | 0.054106 | 0.054106 | 0.054106 | 0.98476 | -0.29282 | 0.98418 | -0.3041 | 14.8642
46 | -0.00057038 | -0.00014295 | 0.00057038 | 0.00014284 | 2.184e-09 | -1.0467e-07 | 0.00084873 | 0.00084869 | 0.00084873 | 1 | -8.0397e-05 | 1 | 0 | 0.23317
47 | 0.15956 | 0.040635 | -0.15941 | -0.040538 | 0.00015123 | 9.6413e-05 | 0.23766 | 0.23766 | 0.23766 | 1 | 0 | 0.99896 | -0.019671 | 32.6455
48 | 0.021691 | 0.0054561 | -0.021686 | -0.0054535 | 4.2941e-06 | 2.6041e-06 | 0.032283 | 0.032283 | 0.032283 | 1 | 0 | 0.99978 | -0.0041448 | 8.869
49 | 0.034725 | 0.0087203 | -0.034721 | -0.0087181 | 3.4885e-06 | 2.1897e-06 | 0.052508 | 0.052508 | 0.052508 | 0.98418 | -0.3041 | 0.98407 | -0.30621 | 14.4252
50 | 0.0056916 | 0.0014264 | -0.0056912 | -0.0014263 | 4.2304e-07 | 7.5861e-08 | 0.0085907 | 0.0085908 | 0.0085908 | 0.98585 | -0.27165 | 0.98577 | -0.27321 | 2.3601
51 | -0.085708 | -0.021665 | 0.085715 | 0.02167 | 7.4704e-06 | 4.7656e-06 | 0.12885 | 0.12885 | 0.12885 | 0.9903 | -0.18535 | 0.9904 | -0.18353 | 35.3981
52 | -0.014483 | -0.003631 | 0.014486 | 0.0036328 | 3.1846e-06 | 1.8145e-06 | 0.021933 | 0.021932 | 0.021933 | 0.98263 | -0.33431 | 0.98287 | -0.3297 | 6.0254
53 | 0.013336 | 0.0033435 | -0.013334 | -0.0033423 | 2.2223e-06 | 1.2382e-06 | 0.020196 | 0.020196 | 0.020196 | 0.98263 | -0.33431 | 0.98245 | -0.33781 | 5.5482
54 | -0.015889 | -0.0039844 | 0.015891 | 0.0039855 | 1.793e-06 | 1.0428e-06 | 0.024056 | 0.024056 | 0.024056 | 0.98287 | -0.3297 | 0.98299 | -0.32733 | 6.6089
55 | 0.0022956 | 0.00057501 | -0.0022955 | -0.00057512 | 4.9038e-08 | -1.056e-07 | 0.0034767 | 0.0034768 | 0.0034768 | 0.98245 | -0.33781 | 0.98243 | -0.33826 | 0.95516
56 | 0.011038 | 0.0027673 | -0.011037 | -0.0027668 | 1.0252e-06 | 5.3232e-07 | 0.016719 | 0.016719 | 0.016719 | 0.98245 | -0.33781 | 0.98235 | -0.33976 | 4.5931
57 | -0.016663 | -0.0041789 | 0.016665 | 0.0041803 | 2.4826e-06 | 1.4569e-06 | 0.025224 | 0.025224 | 0.025224 | 0.98299 | -0.32733 | 0.98315 | -0.32421 | 6.9298
58 | 0.001798 | 0.00045043 | -0.001798 | -0.00045061 | 4.6519e-08 | -1.8203e-07 | 0.0027232 | 0.0027233 | 0.0027233 | 0.98243 | -0.33826 | 0.9824 | -0.3388 | 0.74816
59 | 0.0098359 | 0.0024656 | -0.0098335 | -0.0024645 | 2.362e-06 | 1.1526e-06 | 0.014899 | 0.014899 | 0.014899 | 0.98235 | -0.33976 | 0.9821 | -0.3448 | 4.0932
60 | -0.017242 | -0.0043249 | 0.017244 | 0.004326 | 1.802e-06 | 1.0638e-06 | 0.026098 | 0.026098 | 0.026098 | 0.98315 | -0.32421 | 0.98326 | -0.32202 | 7.1697
61 | 0.0076463 | 0.0019163 | -0.0076463 | -0.0019163 | 8.1325e-08 | 3.1603e-08 | 0.011585 | 0.011585 | 0.011585 | 0.9821 | -0.3448 | 0.98208 | -0.34503 | 3.1828
62 | 0.014377 | 0.0036058 | -0.014374 | -0.0036044 | 2.6048e-06 | 1.481e-06 | 0.021758 | 0.021758 | 0.021758 | 0.98326 | -0.32202 | 0.98307 | -0.32582 | 5.9775
63 | -0.031621 | -0.0079318 | 0.031635 | 0.0079403 | 1.3583e-05 | 8.4924e-06 | 0.047856 | 0.047856 | 0.047856 | 0.98326 | -0.32202 | 0.98372 | -0.31301 | 13.1472
64 | 0.0060639 | 0.0015197 | -0.0060628 | -0.0015195 | 1.1745e-06 | 2.8232e-07 | 0.0091878 | 0.009188 | 0.009188 | 0.98208 | -0.34503 | 0.98188 | -0.34909 | 2.5242
65 | 0.012808 | 0.0032118 | -0.012806 | -0.0032106 | 2.109e-06 | 1.1601e-06 | 0.019387 | 0.019387 | 0.019387 | 0.98307 | -0.32582 | 0.98289 | -0.32927 | 5.3262
66 | -0.033764 | -0.0084742 | 0.033767 | 0.0084756 | 2.3378e-06 | 1.4658e-06 | 0.051078 | 0.051078 | 0.051078 | 0.98372 | -0.31301 | 0.9838 | -0.31156 | 14.0323
67 | 0.021066 | 0.0052932 | -0.021058 | -0.0052885 | 7.8141e-06 | 4.7241e-06 | 0.031381 | 0.031381 | 0.031381 | 0.99908 | -0.017687 | 0.99867 | -0.025461 | 8.6211
68 | -0.021066 | -0.0052932 | 0.02108 | 0.0053015 | 1.3626e-05 | 8.2373e-06 | 0.031381 | 0.03138 | 0.031381 | 0.99908 | -0.017687 | 0.99978 | -0.0041448 | 8.621
69 | 0.017864 | 0.0044879 | -0.017854 | -0.0044819 | 1.0109e-05 | 5.9721e-06 | 0.026621 | 0.026621 | 0.026621 | 0.99867 | -0.025461 | 0.99806 | -0.037324 | 7.3134
70 | 0.0060628 | 0.0015195 | -0.0060615 | -0.0015192 | 1.2758e-06 | 3.069e-07 | 0.009188 | 0.0091882 | 0.0091882 | 0.98188 | -0.34909 | 0.98165 | -0.35351 | 2.5242
71 | -0.027894 | -0.0069859 | 0.027898 | 0.0069883 | 4.013e-06 | 2.4892e-06 | 0.041811 | 0.041811 | 0.041811 | 0.99268 | -0.14062 | 0.99284 | -0.1376 | 11.4865
72 | 0.02687 | 0.0067293 | -0.026867 | -0.0067273 | 3.3108e-06 | 2.0486e-06 | 0.040276 | 0.040276 | 0.040276 | 0.99268 | -0.14062 | 0.99255 | -0.1432 | 11.065
73 | -0.030762 | -0.0077061 | 0.030766 | 0.0077086 | 4.002e-06 | 2.4963e-06 | 0.046103 | 0.046103 | 0.046103 | 0.99284 | -0.1376 | 0.99298 | -0.13486 | 12.6657
74 | 0.025535 | 0.0063935 | -0.025534 | -0.0063926 | 1.4419e-06 | 8.8891e-07 | 0.03828 | 0.03828 | 0.03828 | 0.99255 | -0.1432 | 0.99249 | -0.14439 | 10.5164
75 | -0.032082 | -0.0080384 | 0.032094 | 0.0080463 | 1.2676e-05 | 7.9236e-06 | 0.048075 | 0.048075 | 0.048075 | 0.99298 | -0.13486 | 0.99341 | -0.12657 | 13.2074
76 | 0.023952 | 0.0059962 | -0.023947 | -0.0059934 | 4.6701e-06 | 2.8641e-06 | 0.035909 | 0.035909 | 0.035909 | 0.99249 | -0.14439 | 0.99227 | -0.14849 | 9.865
77 | -0.033579 | -0.0084183 | 0.033591 | 0.0084264 | 1.2867e-05 | 8.0591e-06 | 0.050298 | 0.050298 | 0.050298 | 0.99341 | -0.12657 | 0.99382 | -0.11853 | 13.8182
78 | 0.021764 | 0.0054463 | -0.02176 | -0.0054434 | 4.7806e-06 | 2.905e-06 | 0.032635 | 0.032635 | 0.032635 | 0.99227 | -0.14849 | 0.99204 | -0.15311 | 8.9657
79 | 0.023004 | 0.0057687 | -0.022999 | -0.0057655 | 5.2521e-06 | 3.2084e-06 | 0.034444 | 0.034444 | 0.034444 | 0.99382 | -0.11853 | 0.99357 | -0.12332 | 9.4627
80 | -0.056595 | -0.014195 | 0.056676 | 0.014246 | 8.0794e-05 | 5.1319e-05 | 0.084742 | 0.084742 | 0.084742 | 0.99382 | -0.11853 | 0.99537 | -0.088631 | 23.2808
81 | 0.021069 | 0.0052703 | -0.021069 | -0.0052701 | 3.3688e-07 | 2.0399e-07 | 0.0316 | 0.0316 | 0.0316 | 0.99204 | -0.15311 | 0.99202 | -0.15344 | 8.6812
82 | 0.021744 | 0.005451 | -0.021742 | -0.0054499 | 1.8773e-06 | 1.1403e-06 | 0.032565 | 0.032565 | 0.032565 | 0.99357 | -0.12332 | 0.99348 | -0.12514 | 8.9464
83 | -0.056676 | -0.014246 | 0.056702 | 0.014263 | 2.6253e-05 | 1.6675e-05 | 0.084742 | 0.084742 | 0.084742 | 0.99537 | -0.088631 | 0.99587 | -0.078934 | 23.2808
84 | 0.016946 | 0.0042369 | -0.016941 | -0.0042337 | 5.5571e-06 | 3.2605e-06 | 0.025416 | 0.025416 | 0.025416 | 0.99202 | -0.15344 | 0.99166 | -0.16034 | 6.9824
85 | -0.012402 | -0.0031074 | 0.012403 | 0.0031079 | 1.0881e-06 | 5.8767e-07 | 0.018583 | 0.018583 | 0.018583 | 0.9931 | -0.13245 | 0.9932 | -0.13061 | 5.1052
86 | 0.011114 | 0.0027846 | -0.011114 | -0.0027844 | 3.1542e-07 | 1.6263e-07 | 0.016653 | 0.016653 | 0.016653 | 0.9931 | -0.13245 | 0.99307 | -0.13305 | 4.575
87 | -0.016312 | -0.0040875 | 0.016314 | 0.0040889 | 2.4387e-06 | 1.4198e-06 | 0.024438 | 0.024438 | 0.024438 | 0.9932 | -0.13061 | 0.99336 | -0.12747 | 6.7138
88 | 0.010508 | 0.0026326 | -0.010508 | -0.0026326 | 2.612e-08 | 1.3081e-08 | 0.015746 | 0.015746 | 0.015746 | 0.99307 | -0.13305 | 0.99307 | -0.1331 | 4.3257
89 | -0.01753 | -0.0043935 | 0.017531 | 0.0043944 | 1.4839e-06 | 8.7541e-07 | 0.026259 | 0.026259 | 0.026259 | 0.99336 | -0.12747 | 0.99345 | -0.12569 | 7.214
90 | 0.010011 | 0.0025079 | -0.01001 | -0.0025075 | 7.7873e-07 | 3.7898e-07 | 0.015 | 0.015 | 0.015 | 0.99307 | -0.1331 | 0.99298 | -0.13473 | 4.1208
91 | -0.018483 | -0.0046329 | 0.018483 | 0.0046329 | 7.7317e-08 | 4.5999e-08 | 0.027684 | 0.027684 | 0.027684 | 0.99345 | -0.12569 | 0.99346 | -0.12561 | 7.6055
92 | 0.0046302 | 0.0011592 | -0.00463 | -0.0011592 | 1.659e-07 | -1.2708e-08 | 0.006938 | 0.006938 | 0.006938 | 0.99298 | -0.13473 | 0.99295 | -0.13548 | 1.9061
93 | -0.020933 | -0.0052471 | 0.020934 | 0.0052474 | 4.6696e-07 | 2.8245e-07 | 0.031355 | 0.031355 | 0.031355 | 0.99346 | -0.12561 | 0.99348 | -0.12514 | 8.6139
94 | 0.0019854 | 0.00049641 | -0.0019854 | -0.00049658 | 5.1831e-08 | -1.6883e-07 | 0.0029749 | 0.002975 | 0.002975 | 0.99295 | -0.13548 | 0.99292 | -0.13603 | 0.8173
95 | 0.0019854 | 0.00049658 | -0.0019853 | -0.00049687 | 9.0897e-08 | -2.9603e-07 | 0.002975 | 0.0029751 | 0.0029751 | 0.99292 | -0.13603 | 0.99287 | -0.137 | 0.81733
96 | -0.05854 | -0.014724 | 0.058575 | 0.014746 | 3.5336e-05 | 2.2455e-05 | 0.087488 | 0.087488 | 0.087488 | 0.99587 | -0.078934 | 0.99653 | -0.066306 | 24.0351
97 | 0.017531 | 0.0044011 | -0.01752 | -0.0043944 | 1.1367e-05 | 6.6956e-06 | 0.02614 | 0.02614 | 0.02614 | 0.99806 | -0.037324 | 0.99735 | -0.050926 | 7.1814
98 | -0.060116 | -0.015132 | 0.060142 | 0.015148 | 2.5568e-05 | 1.6253e-05 | 0.089788 | 0.089788 | 0.089788 | 0.99653 | -0.066306 | 0.99699 | -0.057412 | 24.6671
99 | 0.015795 | 0.0039625 | -0.015784 | -0.0039563 | 1.0723e-05 | 6.1915e-06 | 0.023567 | 0.023567 | 0.023567 | 0.99735 | -0.050926 | 0.99661 | -0.065176 | 6.4744
100 | 0.0017252 | 0.0004319 | -0.0017252 | -0.00043213 | 5.008e-08 | -2.3101e-07 | 0.0025738 | 0.0025739 | 0.0025739 | 0.99735 | -0.050926 | 0.99732 | -0.051536 | 0.70711
101 | 0.15825 | 0.040248 | -0.15816 | -0.04019 | 9.1505e-05 | 5.8334e-05 | 0.23593 | 0.23593 | 0.23593 | 0.99896 | -0.019671 | 0.99833 | -0.03168 | 32.4084
102 | -0.062005 | -0.015615 | 0.062029 | 0.015631 | 2.4471e-05 | 1.5562e-05 | 0.092569 | 0.092569 | 0.092569 | 0.99699 | -0.057412 | 0.99742 | -0.049162 | 25.4311
103 | 0.010078 | 0.0025263 | -0.010076 | -0.0025254 | 2.0027e-06 | 9.7445e-07 | 0.015048 | 0.015048 | 0.015048 | 0.99661 | -0.065176 | 0.99639 | -0.069347 | 4.1341
104 | 0.0015615 | 0.00039111 | -0.0015615 | -0.00039122 | 1.902e-08 | -1.0977e-07 | 0.0023297 | 0.0023298 | 0.0023298 | 0.99732 | -0.051536 | 0.99731 | -0.051792 | 0.64005
105 | 0.062734 | 0.015828 | -0.062681 | -0.015794 | 5.2467e-05 | 3.337e-05 | 0.093542 | 0.093542 | 0.093542 | 0.99833 | -0.03168 | 0.99742 | -0.049162 | 25.6983
106 | 0.095427 | 0.024362 | -0.095411 | -0.024352 | 1.6019e-05 | 1.0225e-05 | 0.14239 | 0.14239 | 0.14239 | 0.99833 | -0.03168 | 0.99815 | -0.035154 | 39.1186
107 | -0.016205 | -0.0040487 | 0.016207 | 0.0040497 | 1.8435e-06 | 1.0726e-06 | 0.024315 | 0.024315 | 0.024315 | 0.99154 | -0.16273 | 0.99166 | -0.16034 | 6.6799
108 | 0.014919 | 0.0037263 | -0.014916 | -0.0037248 | 2.725e-06 | 1.557e-06 | 0.022385 | 0.022385 | 0.022385 | 0.99154 | -0.16273 | 0.99134 | -0.16658 | 6.1496
109 | 0.0039295 | 0.00098286 | -0.0039292 | -0.00098297 | 3.1814e-07 | -1.1084e-07 | 0.0058976 | 0.0058977 | 0.0058977 | 0.99134 | -0.16658 | 0.99126 | -0.16828 | 1.6202
110 | 0.010987 | 0.0027419 | -0.010986 | -0.0027417 | 3.2423e-07 | 1.665e-07 | 0.016487 | 0.016487 | 0.016487 | 0.99134 | -0.16658 | 0.99131 | -0.1672 | 4.5294
111 | 0.00076339 | 0.00019064 | -0.00076336 | -0.00019132 | 2.6178e-08 | -6.7308e-07 | 0.0011439 | 0.0011441 | 0.0011441 | 0.99287 | -0.137 | 0.99283 | -0.13772 | 0.31431
112 | 0.0023677 | 0.00059318 | -0.0023676 | -0.00059337 | 9.3592e-08 | -1.9036e-07 | 0.0035697 | 0.0035698 | 0.0035698 | 0.98693 | -0.25278 | 0.98688 | -0.25361 | 0.98072
113 | -0.034457 | -0.0086487 | 0.034466 | 0.0086542 | 8.7966e-06 | 5.5202e-06 | 0.052122 | 0.052122 | 0.052122 | 0.9838 | -0.31156 | 0.98407 | -0.30621 | 14.3193
114 | 0.012294 | 0.0030823 | -0.012292 | -0.0030814 | 1.606e-06 | 8.7117e-07 | 0.018612 | 0.018612 | 0.018612 | 0.98289 | -0.32927 | 0.98275 | -0.33202 | 5.1133
115 | 0.0089394 | 0.0022411 | -0.008939 | -0.002241 | 3.6746e-07 | 1.6741e-07 | 0.013536 | 0.013536 | 0.013536 | 0.98275 | -0.33202 | 0.98271 | -0.33288 | 3.7186
116 | 0.0085319 | 0.0021389 | -0.0085307 | -0.0021384 | 1.2237e-06 | 5.3552e-07 | 0.012919 | 0.012919 | 0.012919 | 0.98271 | -0.33288 | 0.98255 | -0.33589 | 3.5493
117 | 0.0092887 | 0.0023311 | -0.0092769 | -0.0023256 | 1.1786e-05 | 5.5385e-06 | 0.014075 | 0.014075 | 0.014075 | 0.9821 | -0.34465 | 0.98074 | -0.37129 | 3.8669
118 | -0.0092887 | -0.0023311 | 0.0092939 | 0.0023335 | 5.1553e-06 | 2.4207e-06 | 0.014075 | 0.014074 | 0.014075 | 0.9821 | -0.34465 | 0.9827 | -0.33302 | 3.8667
119 | 0.0083087 | 0.0020829 | -0.0083065 | -0.0020819 | 2.2347e-06 | 9.5717e-07 | 0.012606 | 0.012607 | 0.012607 | 0.98074 | -0.37129 | 0.98045 | -0.37694 | 3.4634
120 | -0.0092939 | -0.0023335 | 0.0092957 | 0.0023344 | 1.8556e-06 | 8.7102e-07 | 0.014074 | 0.014074 | 0.014074 | 0.9827 | -0.33302 | 0.98291 | -0.32884 | 3.8666
121 | 0.0078476 | 0.0019669 | -0.0078394 | -0.0019636 | 8.2095e-06 | 3.3101e-06 | 0.01191 | 0.011911 | 0.011911 | 0.98045 | -0.37694 | 0.97934 | -0.39891 | 3.2722
122 | 0.00018317 | 4.3434e-05 | -0.00018317 | -4.5906e-05 | 5.6968e-09 | -2.4718e-06 | 0.00027745 | 0.00027832 | 0.00027832 | 0.97934 | -0.39891 | 0.9793 | -0.39958 | 0.07646
123 | 0.0076563 | 0.0019202 | -0.0076423 | -0.0019147 | 1.3998e-05 | 5.4955e-06 | 0.011634 | 0.011635 | 0.011635 | 0.97934 | -0.39891 | 0.97738 | -0.43732 | 3.1964
124 | 0.0076423 | 0.0019147 | -0.007641 | -0.0019142 | 1.2229e-06 | 4.8079e-07 | 0.011635 | 0.011635 | 0.011635 | 0.97738 | -0.43732 | 0.97721 | -0.44068 | 3.1964
125 | -0.010614 | -0.0026649 | 0.01062 | 0.0026675 | 5.0113e-06 | 2.551e-06 | 0.016071 | 0.016071 | 0.016071 | 0.98291 | -0.32884 | 0.98342 | -0.31894 | 4.415
126 | 0.0074584 | 0.0018684 | -0.0074568 | -0.0018679 | 1.5153e-06 | 5.7736e-07 | 0.011357 | 0.011357 | 0.011357 | 0.97721 | -0.44068 | 0.97699 | -0.44494 | 3.12
127 | -0.0071017 | -0.0017799 | 0.0071021 | 0.00178 | 3.4777e-07 | 1.2121e-07 | 0.01076 | 0.01076 | 0.01076 | 0.9821 | -0.34481 | 0.98215 | -0.34378 | 2.9561
128 | -0.0081851 | -0.0020514 | 0.0081882 | 0.0020527 | 3.079e-06 | 1.2946e-06 | 0.012401 | 0.012401 | 0.012401 | 0.98215 | -0.34378 | 0.98255 | -0.33589 | 3.4069
129 | -0.0010033 | -0.00025144 | 0.0010033 | 0.00025082 | 4.3977e-08 | -6.2072e-07 | 0.0015162 | 0.001516 | 0.0015162 | 0.98458 | -0.2964 | 0.98462 | -0.29548 | 0.41655
130 | 0.014133 | 0.0035519 | -0.014128 | -0.0035487 | 5.5891e-06 | 3.1618e-06 | 0.021363 | 0.021363 | 0.021363 | 0.98462 | -0.29548 | 0.9842 | -0.30377 | 5.8689
131 | -0.015137 | -0.0038027 | 0.015138 | 0.0038034 | 1.3138e-06 | 7.5569e-07 | 0.022879 | 0.022879 | 0.022879 | 0.98462 | -0.29548 | 0.98472 | -0.29366 | 6.2854
132 | -0.01062 | -0.0026675 | 0.010626 | 0.002671 | 6.9419e-06 | 3.5327e-06 | 0.016071 | 0.01607 | 0.016071 | 0.98342 | -0.31894 | 0.98412 | -0.30525 | 4.415
133 | -0.0065153 | -0.0016318 | 0.0065172 | 0.0016324 | 1.8491e-06 | 5.5686e-07 | 0.0099259 | 0.0099257 | 0.0099259 | 0.97669 | -0.4509 | 0.97699 | -0.44494 | 2.7269
134 | 0.0051649 | 0.0012939 | -0.0051624 | -0.0012937 | 2.4352e-06 | 2.467e-07 | 0.0078686 | 0.0078691 | 0.0078691 | 0.97669 | -0.4509 | 0.97619 | -0.46081 | 2.1618
135 | 0.0013505 | 0.00033788 | -0.0013504 | -0.00033844 | 7.7664e-08 | -5.6257e-07 | 0.0020573 | 0.0020575 | 0.0020575 | 0.97669 | -0.4509 | 0.97663 | -0.45211 | 0.56525
136 | 0.0051624 | 0.0012937 | -0.0051615 | -0.0012936 | 9.7299e-07 | 9.899e-08 | 0.0078691 | 0.0078693 | 0.0078693 | 0.97619 | -0.46081 | 0.97599 | -0.46476 | 2.1619
137 | 0.00034254 | 8.57e-05 | -0.00034254 | -8.5848e-05 | 1.1797e-09 | -1.4733e-07 | 0.0005187 | 0.00051875 | 0.00051875 | 0.98255 | -0.33589 | 0.98255 | -0.33596 | 0.14251
138 | -0.010626 | -0.002671 | 0.010627 | 0.0026714 | 7.5439e-07 | 3.8383e-07 | 0.01607 | 0.01607 | 0.01607 | 0.98412 | -0.30525 | 0.9842 | -0.30377 | 4.4149
139 | 0.016425 | 0.0041279 | -0.01642 | -0.0041248 | 5.2238e-06 | 3.0554e-06 | 0.024816 | 0.024816 | 0.024816 | 0.98506 | -0.287 | 0.98472 | -0.29366 | 6.8177
140 | 0.094503 | 0.024124 | -0.094342 | -0.024021 | 0.00016105 | 0.00010279 | 0.14104 | 0.14104 | 0.14104 | 0.99815 | -0.035154 | 0.99629 | -0.070487 | 38.7468
141 | 0.093669 | 0.023853 | -0.0936 | -0.023808 | 6.9705e-05 | 4.4488e-05 | 0.14003 | 0.14003 | 0.14003 | 0.99629 | -0.070487 | 0.99548 | -0.085929 | 38.4708
142 | 0.092798 | 0.023607 | -0.092628 | -0.023499 | 0.00017042 | 0.00010877 | 0.13884 | 0.13884 | 0.13884 | 0.99548 | -0.085929 | 0.99349 | -0.12411 | 38.1418
143 | 0.089884 | 0.022811 | -0.089842 | -0.022784 | 4.1824e-05 | 2.6688e-05 | 0.13473 | 0.13473 | 0.13473 | 0.99349 | -0.12411 | 0.99298 | -0.13379 | 37.0126
144 | 0.087067 | 0.022089 | -0.086859 | -0.021957 | 0.00020772 | 0.00013252 | 0.13057 | 0.13057 | 0.13057 | 0.99298 | -0.13379 | 0.9904 | -0.18353 | 35.8703
145 | 0.002775 | 0.00069481 | -0.0027749 | -0.00069497 | 1.1921e-07 | -1.6152e-07 | 0.0041582 | 0.0041583 | 0.0041583 | 0.99298 | -0.13379 | 0.99294 | -0.1347 | 1.1424
146 | 0.00073256 | 0.00018311 | -0.00073254 | -0.00018359 | 1.7362e-08 | -4.8585e-07 | 0.0010976 | 0.0010978 | 0.0010978 | 0.99294 | -0.1347 | 0.99291 | -0.13519 | 0.3016
147 | 0.0006375 | 0.00015965 | -0.00063749 | -0.00015977 | 3.2747e-09 | -1.2386e-07 | 0.00095112 | 0.00095117 | 0.00095117 | 0.99731 | -0.051792 | 0.9973 | -0.0519 | 0.26131

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18347 | 0.046234

## res_load
| p_mw | q_mvar
0 | 0.00072285 | 0.00018116
1 | 0.00065659 | 0.00016456
2 | 0.0001763 | 4.4185e-05
3 | 0.0019168 | 0.00048039
4 | 0.0022082 | 0.00055343
5 | 0.00048831 | 0.00012238
6 | 0.00041948 | 0.00010513
7 | 0.0021787 | 0.00054604
8 | 0.00066408 | 0.00016643
9 | 0.0015702 | 0.00039353
10 | 0.00050599 | 0.00012681
11 | 0.00035239 | 8.8316e-05
12 | 0.0014954 | 0.00037479
13 | 0.0010267 | 0.00025733
14 | 0.00030603 | 7.6697e-05
15 | 0.00038108 | 9.5507e-05
16 | 0.0045619 | 0.0011433
17 | 0.0024879 | 0.00062352
18 | 0.00034134 | 8.5549e-05
19 | 0.00034405 | 8.6227e-05
20 | 0.0053315 | 0.0013362
21 | 0.0026119 | 0.00065461
22 | 0.0016245 | 0.00040714
23 | 0.00060685 | 0.00015209
24 | 0.0015763 | 0.00039506
25 | 0.0015466 | 0.00038762
26 | 0.00057038 | 0.00014295
27 | 0.0010568 | 0.00026487
28 | 0.00070401 | 0.00017644
29 | 0.00089477 | 0.00022425
30 | 0.001147 | 0.00028748
31 | 0.0014029 | 0.0003516
32 | 0.00077162 | 0.00019339
33 | 0.00049751 | 0.00012469
34 | 0.0012015 | 0.00030111
35 | 0.00057707 | 0.00014463
36 | 0.001798 | 0.00045061
37 | 0.0021872 | 0.00054816
38 | 0.0015823 | 0.00039657
39 | 0.0015664 | 0.00039257
40 | 0.00213 | 0.00053382
41 | 0.0031946 | 0.00080065
42 | 0.00060656 | 0.00015202
43 | 0.0010235 | 0.00025652
44 | 0.0028639 | 0.00071777
45 | 0.001332 | 0.00033382
46 | 0.001316 | 0.00032982
47 | 0.0015814 | 0.00039634
48 | 0.0014842 | 0.00037198
49 | 0.002183 | 0.00054711
50 | 0.00069033 | 0.00017301
51 | 0.0012549 | 0.00031451
52 | 0.0041226 | 0.0010332
53 | 0.0012879 | 0.00032278
54 | 0.0039083 | 0.0009795
55 | 0.00060562 | 0.00015178
56 | 0.0012156 | 0.00030465
57 | 0.0004978 | 0.00012476
58 | 0.00095156 | 0.00023848
59 | 0.0053797 | 0.0013483
60 | 0.0024506 | 0.00061418
61 | 0.0026446 | 0.0006628
62 | 0.00080791 | 0.00020248
63 | 0.0018376 | 0.00046056
64 | 0.00032242 | 8.0805e-05
65 | 0.0015406 | 0.00038611
66 | 0.0011589 | 0.00029046
67 | 0.0018633 | 0.00046699
68 | 0.0057057 | 0.00143
69 | 0.00016365 | 4.1015e-05
70 | 0.0012861 | 0.00032234
71 | 0.00073388 | 0.00018393
72 | 0.00048977 | 0.00012275
73 | 0.00016319 | 4.0899e-05
74 | 0.0012219 | 0.00030623
75 | 0.0023676 | 0.00059337
76 | 0.0006906 | 0.00017308
77 | 0.00025504 | 6.3918e-05
78 | 0.00051196 | 0.00012831
79 | 0.0033528 | 0.0008403
80 | 0.0004071 | 0.00010203
81 | 0.0060615 | 0.0015192
82 | 0.00076336 | 0.00019132
83 | 0.0056912 | 0.0014263
84 | 0.00096821 | 0.00024266
85 | 0.00045885 | 0.000115
86 | 0.00018317 | 4.5906e-05
87 | 0.0013188 | 0.00033051
88 | 0.00018268 | 4.5783e-05
89 | 0.0071017 | 0.0017799
90 | 0.001083 | 0.00027143
91 | 0.0010033 | 0.00025144
92 | 0.00093964 | 0.0002355
93 | 0.0013504 | 0.00033844
94 | 0.0051615 | 0.0012936
95 | 0.001557 | 0.00039022
96 | 0.0012822 | 0.00032135
97 | 0.0035006 | 0.00087734
98 | 0.00090788 | 0.00022754
99 | 0.00067255 | 0.00016856
100 | 0.00080136 | 0.00020084
101 | 0.00065189 | 0.00016338
102 | 0.0027443 | 0.00068778
103 | 0.0011439 | 0.00028668
104 | 0.0020424 | 0.00051186
105 | 0.010076 | 0.0025254
106 | 0.000924 | 0.00023158
107 | 0.00063749 | 0.00015977
108 | 0.00073254 | 0.00018359
109 | 0.00034254 | 8.5848e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1