## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-184_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-184_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-184_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-184_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-184_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-184_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_230-184_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_230-184_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_230-184_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_230-184_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_230-184_0_4_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_230-184_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_230-184_0_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_230-184_0_4_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_230-184_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_230-184_0_4_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_230-184_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_230-184_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_230-184_0_4_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_230-184_0_4_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_230-184_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_230-184_0_4_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_230-184_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_230-184_0_4_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_230-184_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_230-184_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_230-184_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_230-184_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_MV_513_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-184_0_4_load_0 | 0 | 0.0021489 | 0.00053857 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-184_0_4_load_1 | 1 | 0.0016796 | 0.00042094 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-184_0_4_load_2 | 2 | 0.0022793 | 0.00057125 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-184_0_4_load_3 | 3 | 0.001991 | 0.00049898 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-184_0_4_load_4 | 4 | 0.0022808 | 0.00057162 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-184_0_4_load_6 | 6 | 0.0027596 | 0.00069161 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-184_0_4_load_16 | 8 | 0.0025023 | 0.00062713 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-184_0_4_load_20 | 9 | 0.077175 | 0.019342 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-184_0_4_load_21 | 10 | 0.028581 | 0.0071632 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-184_0_4_load_17 | 11 | 0.0084544 | 0.0021189 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-184_0_4_load_28 | 13 | 0.027246 | 0.0068285 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-184_0_4_load_29 | 14 | 0.054675 | 0.013703 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-184_0_4_load_25 | 15 | 0.0089001 | 0.0022306 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-184_0_4_load_15 | 16 | 0.0023992 | 0.00060129 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-184_0_4_load_22 | 17 | 0.010552 | 0.0026445 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-184_0_4_load_33 | 18 | 0.022455 | 0.0056277 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-184_0_4_load_18 | 19 | 0.010691 | 0.0026795 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-184_0_4_load_30 | 20 | 0.017764 | 0.004452 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-184_0_4_load_27 | 21 | 0.013436 | 0.0033674 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-184_0_4_load_26 | 22 | 0.0093349 | 0.0023396 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-184_0_4_load_31 | 23 | 0.022569 | 0.0056562 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-184_0_4_load_24 | 24 | 0.0094615 | 0.0023713 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-184_0_4_load_19 | 25 | 0.0091881 | 0.0023027 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-184_0_4_load_23 | 26 | 0.054538 | 0.013669 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-184_0_4_load_32 | 27 | 0.011929 | 0.0029898 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-184_0_4_line_0 |  | 0 | 1 | 0.0056601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-184_0_4_line_1 |  | 0 | 2 | 0.0053567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-184_0_4_line_2 |  | 1 | 3 | 0.0051174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-184_0_4_line_3 |  | 2 | 4 | 0.0062705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-184_0_4_line_4 |  | 4 | 5 | 0.023495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-184_0_4_line_5 |  | 5 | 6 | 0.019914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-184_0_4_line_6 |  | 5 | 7 | 0.048028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-184_0_4_line_7 |  | 6 | 8 | 0.00022466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-184_0_4_line_8 |  | 7 | 9 | 0.011977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-184_0_4_line_9 |  | 7 | 10 | 0.01967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-184_0_4_line_10 |  | 7 | 11 | 0.016209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-184_0_4_line_11 |  | 8 | 16 | 0.00091167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-184_0_4_line_12 |  | 9 | 17 | 0.001351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_230-184_0_4_line_13 |  | 10 | 18 | 0.0056236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-184_0_4_line_14 |  | 11 | 19 | 0.0065165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-184_0_4_line_15 |  | 12 | 13 | 0.016801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-184_0_4_line_16 |  | 12 | 14 | 0.012682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-184_0_4_line_17 |  | 12 | 15 | 0.016521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-184_0_4_line_18 |  | 13 | 20 | 0.0049613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-184_0_4_line_19 |  | 14 | 23 | 0.00089265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-184_0_4_line_20 |  | 15 | 22 | 0.0066473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-184_0_4_line_21 |  | 17 | 26 | 0.011063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_230-184_0_4_line_22 |  | 19 | 25 | 0.0073068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-184_0_4_line_23 |  | 21 | 22 | 0.0075534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-184_0_4_line_24 |  | 23 | 27 | 0.0024235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_230-184_0_4_line_25 |  | 24 | 25 | 0.0064155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-184_0_4_line_26 |  | 26 | 27 | 0.0095121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-184_0_4_trafo_23 | 0.63 MVA 20/0.4 kV | 28 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2697392.0021 | 1261714.0131 | 2697391.9266 | 1261708.3535
1 | 2697392.0021 | 1261714.0131 | 2697392.0737 | 1261719.3694
2 | 2697391.8583 | 1261703.2365 | 2697391.9266 | 1261708.3535
3 | 2697392.1574 | 1261725.6393 | 2697392.0737 | 1261719.3694
4 | 2697392.4711 | 1261749.1326 | 2697392.1574 | 1261725.6393
5 | 2697392.4711 | 1261749.1326 | 2697412.3165 | 1261747.487
6 | 2697376.4422 | 1261703.843 | 2697392.4711 | 1261749.1326
7 | 2697412.5404 | 1261747.4685 | 2697412.3165 | 1261747.487
8 | 2697376.4422 | 1261703.843 | 2697372.7082 | 1261704.0706 | 2697364.4976 | 1261704.7128
9 | 2697376.4422 | 1261703.843 | 2697375.9093 | 1261723.5054
10 | 2697376.4422 | 1261703.843 | 2697375.9127 | 1261687.6423
11 | 2697413.4489 | 1261747.3931 | 2697412.5404 | 1261747.4685
12 | 2697363.1507 | 1261704.8181 | 2697364.4976 | 1261704.7128
13 | 2697375.9093 | 1261723.5054 | 2697375.757 | 1261729.127
14 | 2697375.6998 | 1261681.1293 | 2697375.9127 | 1261687.6423
15 | 2697326.7008 | 1261707.761 | 2697326.9523 | 1261724.5601
16 | 2697326.7008 | 1261707.761 | 2697331.7461 | 1261707.5327 | 2697339.3518 | 1261706.9044
17 | 2697326.7008 | 1261707.761 | 2697325.4932 | 1261691.2839
18 | 2697327.0266 | 1261729.5209 | 2697326.9523 | 1261724.5601
19 | 2697340.2414 | 1261706.8309 | 2697339.3518 | 1261706.9044
20 | 2697325.4932 | 1261691.2839 | 2697325.0073 | 1261684.6545
21 | 2697363.1507 | 1261704.8181 | 2697357.3226 | 1261705.2739 | 2697352.1306 | 1261705.7824
22 | 2697375.4611 | 1261673.8264 | 2697375.6998 | 1261681.1293
23 | 2697325.0073 | 1261684.6545 | 2697324.4552 | 1261677.1212
24 | 2697342.6568 | 1261706.6314 | 2697340.2414 | 1261706.8309
25 | 2697375.4611 | 1261673.8264 | 2697375.2516 | 1261667.4144
26 | 2697342.6568 | 1261706.6314 | 2697347.7968 | 1261706.2068 | 2697352.1306 | 1261705.7824

## bus_geodata
| x | y | coords
0 | 2697392.0021 | 1261714.0131
1 | 2697391.9266 | 1261708.3535
2 | 2697392.0737 | 1261719.3693
3 | 2697391.8583 | 1261703.2365
4 | 2697392.1574 | 1261725.6393
5 | 2697392.4711 | 1261749.1326
6 | 2697412.3165 | 1261747.487
7 | 2697376.4422 | 1261703.843
8 | 2697412.5404 | 1261747.4685
9 | 2697364.4976 | 1261704.7128
10 | 2697375.9093 | 1261723.5054
11 | 2697375.9127 | 1261687.6423
12 | 2697326.7008 | 1261707.761
13 | 2697326.9523 | 1261724.5601
14 | 2697339.3518 | 1261706.9044
15 | 2697325.4932 | 1261691.2839
16 | 2697413.4489 | 1261747.3931
17 | 2697363.1507 | 1261704.8181
18 | 2697375.757 | 1261729.127
19 | 2697375.6998 | 1261681.1293
20 | 2697327.0266 | 1261729.5209
21 | 2697324.4552 | 1261677.1212
22 | 2697325.0073 | 1261684.6545
23 | 2697340.2414 | 1261706.8309
24 | 2697375.2516 | 1261667.4144
25 | 2697375.4611 | 1261673.8264
26 | 2697352.1306 | 1261705.7824
27 | 2697342.6568 | 1261706.6314
28 | 2697376.4422 | 1261703.843

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99666 | -0.064237 | 0.0021489 | 0.00053857
1 | 0.99664 | -0.064602 | 0.0016796 | 0.00042094
2 | 0.99669 | -0.06369 | 0.0022793 | 0.00057125
3 | 0.99663 | -0.064781 | 0.001991 | 0.00049898
4 | 0.99673 | -0.062799 | 0.0022808 | 0.00057162
5 | 0.99696 | -0.058521 | 0 | 0
6 | 0.99682 | -0.061197 | 0.0027596 | 0.00069161
7 | 0.99774 | -0.043337 | 0 | 0
8 | 0.99682 | -0.061216 | 0.0025023 | 0.00062713
9 | 0.99891 | -0.020951 | 0.077175 | 0.019342
10 | 0.99683 | -0.060929 | 0.028581 | 0.0071632
11 | 0.99719 | -0.054069 | 0.0084544 | 0.0021189
12 | 0.99812 | -0.036061 | 0 | 0
13 | 0.99744 | -0.0493 | 0.027246 | 0.0068285
14 | 0.99901 | -0.019062 | 0.054675 | 0.013703
15 | 0.99765 | -0.04522 | 0.0089001 | 0.0022306
16 | 0.99681 | -0.061255 | 0.0023992 | 0.00060129
17 | 0.99902 | -0.01878 | 0.010552 | 0.0026445
18 | 0.99672 | -0.063144 | 0.022455 | 0.0056277
19 | 0.99701 | -0.057421 | 0.010691 | 0.0026795
20 | 0.99736 | -0.050844 | 0.017764 | 0.004452
21 | 0.99742 | -0.049649 | 0.013436 | 0.0033674
22 | 0.99751 | -0.047871 | 0.0093349 | 0.0023396
23 | 0.99911 | -0.017015 | 0.022569 | 0.0056562
24 | 0.99683 | -0.060875 | 0.0094615 | 0.0023713
25 | 0.99689 | -0.059811 | 0.0091881 | 0.0023027
26 | 1 | 0 | -0.36275 | -0.090751
27 | 0.99928 | -0.013759 | 0.011929 | 0.0029898
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0036706 | 0.00091983 | -0.0036705 | -0.00091987 | 6.3746e-08 | -3.2963e-08 | 0.0054802 | 0.0054802 | 0.0054802 | 0.99666 | -0.064237 | 0.99664 | -0.064602 | 1.5056
1 | -0.0058195 | -0.0014584 | 0.0058197 | 0.0014584 | 1.5164e-07 | 2.7242e-08 | 0.0086885 | 0.0086885 | 0.0086885 | 0.99666 | -0.064237 | 0.99669 | -0.06369 | 2.387
2 | 0.001991 | 0.00049892 | -0.001991 | -0.00049898 | 1.6957e-08 | -5.5834e-08 | 0.0029726 | 0.0029726 | 0.0029726 | 0.99664 | -0.064602 | 0.99663 | -0.064781 | 0.81664
3 | -0.008099 | -0.0020297 | 0.0080994 | 0.0020298 | 3.4379e-07 | 1.383e-07 | 0.012091 | 0.012091 | 0.012091 | 0.99669 | -0.06369 | 0.99673 | -0.062799 | 3.3218
4 | -0.01038 | -0.0026014 | 0.010382 | 0.0026025 | 2.1158e-06 | 1.0478e-06 | 0.015496 | 0.015496 | 0.015496 | 0.99673 | -0.062799 | 0.99696 | -0.058521 | 4.2573
5 | 0.007662 | 0.0019204 | -0.007661 | -0.00192 | 9.7663e-07 | 3.6542e-07 | 0.011436 | 0.011436 | 0.011436 | 0.99696 | -0.058521 | 0.99682 | -0.061197 | 3.1418
6 | -0.018044 | -0.0045229 | 0.018057 | 0.0045306 | 1.3064e-05 | 7.7341e-06 | 0.026932 | 0.026932 | 0.026932 | 0.99696 | -0.058521 | 0.99774 | -0.043337 | 7.399
7 | 0.0049015 | 0.0012284 | -0.0049015 | -0.0012284 | 4.5098e-09 | -4.2244e-11 | 0.0073167 | 0.0073167 | 0.0073167 | 0.99682 | -0.061197 | 0.99682 | -0.061216 | 2.0101
8 | -0.10696 | -0.026839 | 0.10707 | 0.026912 | 0.0001143 | 7.2996e-05 | 0.15953 | 0.15953 | 0.15953 | 0.99774 | -0.043337 | 0.99891 | -0.020951 | 43.8269
9 | 0.051081 | 0.012819 | -0.051039 | -0.012792 | 4.2815e-05 | 2.7145e-05 | 0.076188 | 0.076188 | 0.076188 | 0.99774 | -0.043337 | 0.99683 | -0.060929 | 20.9307
10 | 0.037822 | 0.0094889 | -0.037803 | -0.0094768 | 1.9343e-05 | 1.2168e-05 | 0.05641 | 0.05641 | 0.05641 | 0.99774 | -0.043337 | 0.99719 | -0.054069 | 15.4973
11 | 0.0023992 | 0.00060128 | -0.0023992 | -0.00060129 | 4.3851e-09 | -9.0781e-09 | 0.0035814 | 0.0035814 | 0.0035814 | 0.99682 | -0.061216 | 0.99681 | -0.061255 | 0.98391
12 | -0.18425 | -0.046254 | 0.18427 | 0.046266 | 1.9086e-05 | 1.218e-05 | 0.27449 | 0.27449 | 0.27449 | 0.99891 | -0.020951 | 0.99902 | -0.01878 | 37.7051
13 | 0.022457 | 0.0056291 | -0.022455 | -0.0056277 | 2.3699e-06 | 1.4434e-06 | 0.033523 | 0.033523 | 0.033523 | 0.99683 | -0.060929 | 0.99672 | -0.063144 | 9.2096
14 | 0.029348 | 0.0073579 | -0.029343 | -0.007355 | 4.6869e-06 | 2.9146e-06 | 0.043795 | 0.043795 | 0.043795 | 0.99719 | -0.054069 | 0.99701 | -0.057421 | 12.0315
15 | 0.04504 | 0.011299 | -0.045011 | -0.011281 | 2.8409e-05 | 1.7962e-05 | 0.06715 | 0.06715 | 0.06715 | 0.99812 | -0.036061 | 0.99744 | -0.0493 | 18.4477
16 | -0.076729 | -0.019248 | 0.076791 | 0.019288 | 6.2235e-05 | 3.9664e-05 | 0.11439 | 0.11439 | 0.11439 | 0.99812 | -0.036061 | 0.99901 | -0.019062 | 31.427
17 | 0.031689 | 0.0079486 | -0.031675 | -0.0079399 | 1.3829e-05 | 8.6345e-06 | 0.047245 | 0.047245 | 0.047245 | 0.99812 | -0.036061 | 0.99765 | -0.04522 | 12.9793
18 | 0.017765 | 0.0044528 | -0.017764 | -0.004452 | 1.3068e-06 | 7.716e-07 | 0.026503 | 0.026503 | 0.026503 | 0.99744 | -0.0493 | 0.99736 | -0.050844 | 7.281
19 | -0.13147 | -0.03299 | 0.13148 | 0.032999 | 1.2838e-05 | 8.2043e-06 | 0.19583 | 0.19583 | 0.19583 | 0.99901 | -0.019062 | 0.99911 | -0.017015 | 53.8
20 | 0.022775 | 0.0057093 | -0.022772 | -0.0057076 | 2.8765e-06 | 1.7542e-06 | 0.03397 | 0.03397 | 0.03397 | 0.99765 | -0.04522 | 0.99751 | -0.047871 | 9.3324
21 | -0.19482 | -0.048911 | 0.195 | 0.049022 | 0.0001747 | 0.00011152 | 0.29021 | 0.29021 | 0.29021 | 0.99902 | -0.01878 | 1 | 0 | 39.864
22 | 0.018652 | 0.0046755 | -0.01865 | -0.0046743 | 2.1235e-06 | 1.2637e-06 | 0.027838 | 0.027838 | 0.027838 | 0.99701 | -0.057421 | 0.99689 | -0.059811 | 7.6479
23 | -0.013436 | -0.0033674 | 0.013437 | 0.003368 | 1.1381e-06 | 6.2979e-07 | 0.020045 | 0.020045 | 0.020045 | 0.99742 | -0.049649 | 0.99751 | -0.047871 | 5.5068
24 | -0.15405 | -0.038655 | 0.15407 | 0.03867 | 2.3922e-05 | 1.5247e-05 | 0.22944 | 0.22944 | 0.22944 | 0.99911 | -0.017015 | 0.99928 | -0.013759 | 31.5171
25 | -0.0094615 | -0.0023713 | 0.009462 | 0.0023715 | 4.799e-07 | 2.235e-07 | 0.014124 | 0.014124 | 0.014124 | 0.99683 | -0.060875 | 0.99689 | -0.059811 | 3.8801
26 | 0.16611 | 0.041729 | -0.166 | -0.04166 | 0.00010899 | 6.9507e-05 | 0.24721 | 0.24721 | 0.24721 | 1 | 0 | 0.99928 | -0.013759 | 33.9572

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41729 | 0.10442

## res_load
| p_mw | q_mvar
0 | 0.0021489 | 0.00053857
1 | 0.0016796 | 0.00042094
2 | 0.0022793 | 0.00057125
3 | 0.001991 | 0.00049898
4 | 0.0022808 | 0.00057162
5 | 0.0027596 | 0.00069161
6 | 0.0025023 | 0.00062713
7 | 0.077175 | 0.019342
8 | 0.028581 | 0.0071632
9 | 0.0084544 | 0.0021189
10 | 0.027246 | 0.0068285
11 | 0.054675 | 0.013703
12 | 0.0089001 | 0.0022306
13 | 0.0023992 | 0.00060129
14 | 0.010552 | 0.0026445
15 | 0.022455 | 0.0056277
16 | 0.010691 | 0.0026795
17 | 0.017764 | 0.004452
18 | 0.013436 | 0.0033674
19 | 0.0093349 | 0.0023396
20 | 0.022569 | 0.0056562
21 | 0.0094615 | 0.0023713
22 | 0.0091881 | 0.0023027
23 | 0.054538 | 0.013669
24 | 0.011929 | 0.0029898

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1