## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-196_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_230-196_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_230-196_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_230-196_1_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_230-196_1_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_230-196_1_3_node_59 | 0.4 | n |  | TRUE
6 | bus_LV_230-196_1_3_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_230-196_1_3_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_230-196_1_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_230-196_1_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_230-196_1_3_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_230-196_1_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_230-196_1_3_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_230-196_1_3_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_230-196_1_3_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_230-196_1_3_node_42 | 0.4 | n |  | TRUE
16 | bus_LV_230-196_1_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_230-196_1_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_230-196_1_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_230-196_1_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_230-196_1_3_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_230-196_1_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_230-196_1_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_230-196_1_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_230-196_1_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_230-196_1_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_230-196_1_3_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_230-196_1_3_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_230-196_1_3_node_270 | 0.4 | n |  | TRUE
29 | bus_LV_230-196_1_3_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_230-196_1_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_230-196_1_3_node_316 | 0.4 | n |  | TRUE
32 | bus_LV_230-196_1_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_230-196_1_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_230-196_1_3_node_272 | 0.4 | n |  | TRUE
35 | bus_LV_230-196_1_3_node_78 | 0.4 | n |  | TRUE
36 | bus_LV_230-196_1_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_230-196_1_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_230-196_1_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_230-196_1_3_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_230-196_1_3_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_230-196_1_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_230-196_1_3_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_230-196_1_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_230-196_1_3_node_267 | 0.4 | n |  | TRUE
45 | bus_LV_230-196_1_3_node_311 | 0.4 | n |  | TRUE
46 | bus_LV_230-196_1_3_node_251 | 0.4 | n |  | TRUE
47 | bus_LV_230-196_1_3_node_250 | 0.4 | n |  | TRUE
48 | bus_LV_230-196_1_3_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_230-196_1_3_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_230-196_1_3_node_280 | 0.4 | n |  | TRUE
51 | bus_LV_230-196_1_3_node_263 | 0.4 | n |  | TRUE
52 | bus_LV_230-196_1_3_node_283 | 0.4 | n |  | TRUE
53 | bus_LV_230-196_1_3_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_230-196_1_3_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_230-196_1_3_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_230-196_1_3_node_84 | 0.4 | n |  | TRUE
57 | bus_LV_230-196_1_3_node_312 | 0.4 | n |  | TRUE
58 | bus_LV_230-196_1_3_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_230-196_1_3_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_230-196_1_3_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_230-196_1_3_node_262 | 0.4 | n |  | TRUE
62 | bus_LV_230-196_1_3_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_230-196_1_3_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_230-196_1_3_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_230-196_1_3_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_230-196_1_3_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_230-196_1_3_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_230-196_1_3_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_230-196_1_3_node_87 | 0.4 | n |  | TRUE
70 | bus_LV_230-196_1_3_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_230-196_1_3_node_293 | 0.4 | n |  | TRUE
72 | bus_LV_230-196_1_3_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_230-196_1_3_node_82 | 0.4 | n |  | TRUE
74 | bus_LV_230-196_1_3_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_230-196_1_3_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_230-196_1_3_node_302 | 0.4 | n |  | TRUE
77 | bus_LV_230-196_1_3_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_230-196_1_3_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_230-196_1_3_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_230-196_1_3_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_230-196_1_3_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_230-196_1_3_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_230-196_1_3_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_230-196_1_3_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_230-196_1_3_node_265 | 0.4 | n |  | TRUE
86 | bus_LV_230-196_1_3_node_269 | 0.4 | n |  | TRUE
87 | bus_LV_230-196_1_3_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_230-196_1_3_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_230-196_1_3_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_230-196_1_3_node_85 | 0.4 | n |  | TRUE
91 | bus_LV_230-196_1_3_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_230-196_1_3_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_230-196_1_3_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_230-196_1_3_node_275 | 0.4 | n |  | TRUE
95 | bus_LV_230-196_1_3_node_143 | 0.4 | n |  | TRUE
96 | bus_LV_230-196_1_3_node_144 | 0.4 | n |  | TRUE
97 | bus_LV_230-196_1_3_node_145 | 0.4 | n |  | TRUE
98 | bus_LV_230-196_1_3_node_146 | 0.4 | n |  | TRUE
99 | bus_LV_230-196_1_3_node_147 | 0.4 | n |  | TRUE
100 | bus_LV_230-196_1_3_node_281 | 0.4 | n |  | TRUE
101 | bus_LV_230-196_1_3_node_292 | 0.4 | n |  | TRUE
102 | bus_LV_230-196_1_3_node_252 | 0.4 | n |  | TRUE
103 | bus_LV_230-196_1_3_node_253 | 0.4 | n |  | TRUE
104 | bus_LV_230-196_1_3_node_256 | 0.4 | n |  | TRUE
105 | bus_LV_230-196_1_3_node_254 | 0.4 | n |  | TRUE
106 | bus_LV_230-196_1_3_node_276 | 0.4 | n |  | TRUE
107 | bus_LV_230-196_1_3_node_255 | 0.4 | n |  | TRUE
108 | bus_LV_230-196_1_3_node_260 | 0.4 | n |  | TRUE
109 | bus_LV_230-196_1_3_node_257 | 0.4 | n |  | TRUE
110 | bus_LV_230-196_1_3_node_258 | 0.4 | n |  | TRUE
111 | bus_LV_230-196_1_3_node_259 | 0.4 | n |  | TRUE
112 | bus_LV_230-196_1_3_node_261 | 0.4 | n |  | TRUE
113 | bus_LV_230-196_1_3_node_264 | 0.4 | n |  | TRUE
114 | bus_LV_230-196_1_3_node_266 | 0.4 | n |  | TRUE
115 | bus_LV_230-196_1_3_node_268 | 0.4 | n |  | TRUE
116 | bus_LV_230-196_1_3_node_298 | 0.4 | n |  | TRUE
117 | bus_LV_230-196_1_3_node_284 | 0.4 | n |  | TRUE
118 | bus_LV_230-196_1_3_node_271 | 0.4 | n |  | TRUE
119 | bus_LV_230-196_1_3_node_277 | 0.4 | n |  | TRUE
120 | bus_LV_230-196_1_3_node_278 | 0.4 | n |  | TRUE
121 | bus_LV_230-196_1_3_node_279 | 0.4 | n |  | TRUE
122 | bus_LV_230-196_1_3_node_288 | 0.4 | n |  | TRUE
123 | bus_LV_230-196_1_3_node_285 | 0.4 | n |  | TRUE
124 | bus_LV_230-196_1_3_node_286 | 0.4 | n |  | TRUE
125 | bus_LV_230-196_1_3_node_287 | 0.4 | n |  | TRUE
126 | bus_LV_230-196_1_3_node_290 | 0.4 | n |  | TRUE
127 | bus_LV_230-196_1_3_node_289 | 0.4 | n |  | TRUE
128 | bus_LV_230-196_1_3_node_291 | 0.4 | n |  | TRUE
129 | bus_LV_230-196_1_3_node_294 | 0.4 | n |  | TRUE
130 | bus_LV_230-196_1_3_node_295 | 0.4 | n |  | TRUE
131 | bus_LV_230-196_1_3_node_296 | 0.4 | n |  | TRUE
132 | bus_LV_230-196_1_3_node_297 | 0.4 | n |  | TRUE
133 | bus_LV_230-196_1_3_node_299 | 0.4 | n |  | TRUE
134 | bus_LV_230-196_1_3_node_300 | 0.4 | n |  | TRUE
135 | bus_LV_230-196_1_3_node_301 | 0.4 | n |  | TRUE
136 | bus_LV_230-196_1_3_node_303 | 0.4 | n |  | TRUE
137 | bus_LV_230-196_1_3_node_308 | 0.4 | n |  | TRUE
138 | bus_LV_230-196_1_3_node_304 | 0.4 | n |  | TRUE
139 | bus_LV_230-196_1_3_node_305 | 0.4 | n |  | TRUE
140 | bus_LV_230-196_1_3_node_306 | 0.4 | n |  | TRUE
141 | bus_LV_230-196_1_3_node_307 | 0.4 | n |  | TRUE
142 | bus_LV_230-196_1_3_node_309 | 0.4 | n |  | TRUE
143 | bus_LV_230-196_1_3_node_310 | 0.4 | n |  | TRUE
144 | bus_LV_230-196_1_3_node_313 | 0.4 | n |  | TRUE
145 | bus_MV_511_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-196_1_3_load_5 | 0 | 0.01532 | 0.0038397 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-196_1_3_load_6 | 1 | 0.0040382 | 0.0010121 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-196_1_3_load_8 | 3 | 0.0048295 | 0.0012104 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-196_1_3_load_41 | 6 | 0.0018825 | 0.0004718 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-196_1_3_load_38 | 7 | 0.013323 | 0.0033391 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-196_1_3_load_25 | 10 | 0.0062364 | 0.001563 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-196_1_3_load_23 | 13 | 0.0025218 | 0.00063201 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-196_1_3_load_42 | 15 | 0.00224 | 0.00056139 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-196_1_3_load_13 | 16 | 0.0010318 | 0.0002586 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-196_1_3_load_14 | 17 | 0.0009932 | 0.00024892 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-196_1_3_load_15 | 18 | 0.0010631 | 0.00026645 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-196_1_3_load_16 | 19 | 0.0010282 | 0.00025768 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-196_1_3_load_60 | 20 | 0.0011784 | 0.00029534 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-196_1_3_load_17 | 21 | 0.0026649 | 0.00066788 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-196_1_3_load_18 | 22 | 0.0037566 | 0.0009415 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-196_1_3_load_20 | 24 | 0.0038678 | 0.00096935 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-196_1_3_load_22 | 26 | 0.0017314 | 0.00043392 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-196_1_3_load_58 | 27 | 0.0028288 | 0.00070897 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-196_1_3_load_270 | 28 | 0.0017305 | 0.0004337 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-196_1_3_load_33 | 29 | 0.0017307 | 0.00043375 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-196_1_3_load_24 | 30 | 0.019767 | 0.0049541 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-196_1_3_load_316 | 31 | 0.0041883 | 0.0010497 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-196_1_3_load_272 | 34 | 0.0055871 | 0.0014002 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-196_1_3_load_78 | 35 | 0.015245 | 0.0038207 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-196_1_3_load_29 | 36 | 0.0008503 | 0.00021311 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-196_1_3_load_37 | 41 | 0.00056772 | 0.00014228 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-196_1_3_load_32 | 42 | 0.0017307 | 0.00043375 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-196_1_3_load_311 | 45 | 0.0010719 | 0.00026864 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-196_1_3_load_251 | 46 | 0.00050258 | 0.00012596 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-196_1_3_load_250 | 47 | 0.00052726 | 0.00013214 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-196_1_3_load_39 | 48 | 0.0018829 | 0.0004719 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-196_1_3_load_280 | 50 | 0.0013637 | 0.00034178 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-196_1_3_load_263 | 51 | 0.0013586 | 0.0003405 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-196_1_3_load_283 | 52 | 0.0010103 | 0.0002532 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-196_1_3_load_43 | 54 | 0.0046881 | 0.001175 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-196_1_3_load_84 | 56 | 0.0090445 | 0.0022668 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-196_1_3_load_312 | 57 | 0.0052009 | 0.0013035 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-196_1_3_load_47 | 58 | 0.0011212 | 0.00028101 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-196_1_3_load_48 | 59 | 0.0010292 | 0.00025793 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-196_1_3_load_50 | 60 | 0.00095765 | 0.00024001 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-196_1_3_load_262 | 61 | 0.0011527 | 0.0002889 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-196_1_3_load_53 | 62 | 0.001036 | 0.00025965 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-196_1_3_load_54 | 63 | 0.0012509 | 0.00031352 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-196_1_3_load_55 | 64 | 0.001035 | 0.00025939 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-196_1_3_load_87 | 69 | 0.0028289 | 0.000709 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-196_1_3_load_293 | 71 | 0.0010124 | 0.00025374 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-196_1_3_load_302 | 76 | 0.0010123 | 0.00025371 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-196_1_3_load_66 | 77 | 0.00061138 | 0.00015323 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-196_1_3_load_67 | 78 | 0.00052707 | 0.0001321 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-196_1_3_load_69 | 79 | 0.00052741 | 0.00013218 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-196_1_3_load_72 | 80 | 0.001495 | 0.00037467 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-196_1_3_load_75 | 83 | 0.0017315 | 0.00043396 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-196_1_3_load_76 | 84 | 0.0017296 | 0.00043347 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-196_1_3_load_265 | 85 | 0.0017315 | 0.00043396 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-196_1_3_load_269 | 86 | 0.0017313 | 0.0004339 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-196_1_3_load_79 | 87 | 0.0011295 | 0.00028308 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-196_1_3_load_80 | 88 | 0.0012123 | 0.00030383 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-196_1_3_load_81 | 89 | 0.0014773 | 0.00037026 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-196_1_3_load_85 | 90 | 0.00087942 | 0.0002204 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-196_1_3_load_86 | 91 | 0.0027485 | 0.00068885 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-196_1_3_load_88 | 92 | 0.0028288 | 0.00070897 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-196_1_3_load_89 | 93 | 0.0028314 | 0.00070961 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-196_1_3_load_275 | 94 | 0.0028328 | 0.00070997 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-196_1_3_load_143 | 95 | 0.0033862 | 0.00084866 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-196_1_3_load_146 | 98 | 0.0010607 | 0.00026584 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-196_1_3_load_147 | 99 | 0.0010589 | 0.00026539 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-196_1_3_load_281 | 100 | 0.0010602 | 0.00026571 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-196_1_3_load_292 | 101 | 0.0010583 | 0.00026523 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-196_1_3_load_252 | 102 | 0.00054705 | 0.0001371 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-196_1_3_load_253 | 103 | 0.00055974 | 0.00014028 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-196_1_3_load_256 | 104 | 0.00058313 | 0.00014615 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-196_1_3_load_276 | 106 | 0.0028286 | 0.00070891 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-196_1_3_load_257 | 109 | 0.00050245 | 0.00012593 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-196_1_3_load_258 | 110 | 0.00041778 | 0.00010471 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-196_1_3_load_259 | 111 | 0.00044909 | 0.00011255 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-196_1_3_load_261 | 112 | 0.00058363 | 0.00014627 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-196_1_3_load_264 | 113 | 0.0017313 | 0.00043391 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-196_1_3_load_298 | 116 | 0.0010584 | 0.00026527 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-196_1_3_load_284 | 117 | 0.0010584 | 0.00026526 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-196_1_3_load_271 | 118 | 0.0055698 | 0.0013959 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-196_1_3_load_277 | 119 | 0.0028286 | 0.00070891 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-196_1_3_load_278 | 120 | 0.0013594 | 0.00034071 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-196_1_3_load_279 | 121 | 0.0013593 | 0.00034067 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-196_1_3_load_288 | 122 | 0.0010121 | 0.00025365 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-196_1_3_load_285 | 123 | 0.0010584 | 0.00026526 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-196_1_3_load_286 | 124 | 0.0010577 | 0.00026508 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-196_1_3_load_287 | 125 | 0.0010583 | 0.00026522 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-196_1_3_load_290 | 126 | 0.0010584 | 0.00026525 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-196_1_3_load_289 | 127 | 0.0010101 | 0.00025316 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-196_1_3_load_294 | 129 | 0.0010107 | 0.0002533 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_230-196_1_3_load_295 | 130 | 0.0010107 | 0.0002533 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_230-196_1_3_load_296 | 131 | 0.0010114 | 0.00025348 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_230-196_1_3_load_297 | 132 | 0.0010104 | 0.00025324 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_230-196_1_3_load_300 | 134 | 0.0010584 | 0.00026527 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_230-196_1_3_load_301 | 135 | 0.0010724 | 0.00026876 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_230-196_1_3_load_303 | 136 | 0.0010583 | 0.00026523 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_230-196_1_3_load_308 | 137 | 0.0010718 | 0.00026863 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_230-196_1_3_load_304 | 138 | 0.0010583 | 0.00026525 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_230-196_1_3_load_305 | 139 | 0.0010582 | 0.00026522 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_230-196_1_3_load_306 | 140 | 0.0010577 | 0.00026508 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_230-196_1_3_load_307 | 141 | 0.0010583 | 0.00026525 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_230-196_1_3_load_309 | 142 | 0.0010736 | 0.00026907 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_230-196_1_3_load_310 | 143 | 0.0010718 | 0.00026863 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_230-196_1_3_load_313 | 144 | 0.0062315 | 0.0015618 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 93 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-196_1_3_line_0 |  | 0 | 1 | 0.017117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-196_1_3_line_1 |  | 0 | 2 | 0.020408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-196_1_3_line_2 |  | 1 | 3 | 0.023528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-196_1_3_line_3 |  | 2 | 4 | 0.02158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-196_1_3_line_4 |  | 3 | 5 | 0.020542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-196_1_3_line_5 |  | 4 | 6 | 0.017553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-196_1_3_line_6 |  | 4 | 7 | 0.013396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-196_1_3_line_7 |  | 5 | 32 | 0.006863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-196_1_3_line_8 |  | 6 | 53 | 0.0054916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-196_1_3_line_9 |  | 8 | 9 | 0.029285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-196_1_3_line_10 |  | 8 | 10 | 0.020106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-196_1_3_line_11 |  | 9 | 14 | 0.027593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-196_1_3_line_12 |  | 9 | 15 | 0.0082026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-196_1_3_line_13 |  | 11 | 12 | 0.032594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-196_1_3_line_14 |  | 11 | 13 | 0.010342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-196_1_3_line_15 |  | 12 | 31 | 0.002324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-196_1_3_line_16 |  | 12 | 32 | 0.047247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-196_1_3_line_17 |  | 13 | 30 | 0.024111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-196_1_3_line_18 |  | 14 | 55 | 0.030451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-196_1_3_line_19 |  | 14 | 56 | 0.019019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_230-196_1_3_line_20 |  | 15 | 54 | 0.019441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-196_1_3_line_21 |  | 16 | 17 | 0.0052885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-196_1_3_line_22 |  | 16 | 18 | 0.0064683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-196_1_3_line_23 |  | 17 | 19 | 0.004125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-196_1_3_line_24 |  | 19 | 20 | 0.0091694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-196_1_3_line_25 |  | 20 | 70 | 0.0068885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-196_1_3_line_26 |  | 21 | 22 | 0.00037705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-196_1_3_line_27 |  | 21 | 23 | 0.017764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-196_1_3_line_28 |  | 22 | 24 | 0.00018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-196_1_3_line_29 |  | 23 | 25 | 0.012088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-196_1_3_line_30 |  | 23 | 26 | 0.0053682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-196_1_3_line_31 |  | 24 | 27 | 0.019009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-196_1_3_line_32 |  | 25 | 28 | 0.010834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-196_1_3_line_33 |  | 26 | 29 | 0.0075593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-196_1_3_line_34 |  | 27 | 69 | 0.0062391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-196_1_3_line_35 |  | 29 | 37 | 0.016873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-196_1_3_line_36 |  | 32 | 33 | 0.031637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-196_1_3_line_37 |  | 32 | 34 | 0.0097828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-196_1_3_line_38 |  | 33 | 35 | 0.0054071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-196_1_3_line_39 |  | 34 | 118 | 0.021893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-196_1_3_line_40 |  | 35 | 87 | 0.01096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-196_1_3_line_41 |  | 36 | 37 | 0.022157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-196_1_3_line_42 |  | 36 | 38 | 0.0066006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-196_1_3_line_43 |  | 37 | 39 | 0.024731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-196_1_3_line_44 |  | 38 | 40 | 0.02388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-196_1_3_line_45 |  | 38 | 41 | 0.011336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-196_1_3_line_46 |  | 39 | 45 | 0.0098793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-196_1_3_line_47 |  | 40 | 46 | 0.010143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-196_1_3_line_48 |  | 41 | 47 | 0.0083108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-196_1_3_line_49 |  | 42 | 43 | 0.005008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-196_1_3_line_50 |  | 43 | 44 | 0.005329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-196_1_3_line_51 |  | 44 | 116 | 0.011169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-196_1_3_line_52 |  | 44 | 114 | 0.012419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-196_1_3_line_53 |  | 45 | 143 | 0.0070705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-196_1_3_line_54 |  | 46 | 102 | 0.018256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-196_1_3_line_55 |  | 47 | 79 | 0.0081722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-196_1_3_line_56 |  | 48 | 49 | 0.0044273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-196_1_3_line_57 |  | 49 | 50 | 0.0091297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_230-196_1_3_line_58 |  | 49 | 51 | 0.0071116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-196_1_3_line_59 |  | 49 | 52 | 0.012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_230-196_1_3_line_60 |  | 50 | 121 | 0.00625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_230-196_1_3_line_61 |  | 51 | 108 | 0.024005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-196_1_3_line_62 |  | 52 | 122 | 0.0062448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_230-196_1_3_line_63 |  | 53 | 54 | 0.012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-196_1_3_line_64 |  | 55 | 57 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-196_1_3_line_65 |  | 56 | 90 | 0.0011046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_230-196_1_3_line_66 |  | 57 | 144 | 0.013743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-196_1_3_line_67 |  | 58 | 59 | 0.008115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-196_1_3_line_68 |  | 59 | 60 | 0.0067412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-196_1_3_line_69 |  | 60 | 61 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-196_1_3_line_70 |  | 61 | 108 | 0.0086627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-196_1_3_line_71 |  | 62 | 63 | 0.017746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-196_1_3_line_72 |  | 62 | 64 | 0.0069521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-196_1_3_line_73 |  | 63 | 65 | 0.0083899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-196_1_3_line_74 |  | 64 | 66 | 0.012592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-196_1_3_line_75 |  | 65 | 67 | 0.010632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-196_1_3_line_76 |  | 66 | 68 | 0.004727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-196_1_3_line_77 |  | 67 | 71 | 0.023872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-196_1_3_line_78 |  | 67 | 70 | 0.017885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-196_1_3_line_79 |  | 68 | 72 | 0.058109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-196_1_3_line_80 |  | 69 | 91 | 0.0019663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-196_1_3_line_81 |  | 71 | 128 | 0.0067463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-196_1_3_line_82 |  | 72 | 73 | 0.019718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_230-196_1_3_line_83 |  | 73 | 88 | 0.012142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-196_1_3_line_84 |  | 74 | 75 | 0.008563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_230-196_1_3_line_85 |  | 74 | 76 | 0.0090873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_230-196_1_3_line_86 |  | 75 | 90 | 0.017724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_230-196_1_3_line_87 |  | 76 | 132 | 0.0062464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_230-196_1_3_line_88 |  | 77 | 78 | 0.0071137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-196_1_3_line_89 |  | 78 | 79 | 0.0081756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-196_1_3_line_90 |  | 80 | 81 | 0.0047518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-196_1_3_line_91 |  | 80 | 82 | 4.8027e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-196_1_3_line_92 |  | 81 | 83 | 0.010432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-196_1_3_line_93 |  | 82 | 84 | 0.017146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-196_1_3_line_94 |  | 83 | 85 | 0.0075642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-196_1_3_line_95 |  | 84 | 86 | 0.00089799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-196_1_3_line_96 |  | 85 | 113 | 0.0075658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_230-196_1_3_line_97 |  | 88 | 89 | 0.0067749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_230-196_1_3_line_98 |  | 91 | 92 | 0.0042728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-196_1_3_line_99 |  | 92 | 93 | 0.0062416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-196_1_3_line_100 |  | 93 | 94 | 0.0062467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_230-196_1_3_line_101 |  | 94 | 105 | 0.0091764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_230-196_1_3_line_102 |  | 95 | 96 | 0.0036434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-196_1_3_line_103 |  | 95 | 97 | 0.028502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-196_1_3_line_104 |  | 96 | 98 | 0.014709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-196_1_3_line_105 |  | 97 | 99 | 0.013541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-196_1_3_line_106 |  | 98 | 100 | 0.0073758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-196_1_3_line_107 |  | 99 | 101 | 0.0074121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-196_1_3_line_108 |  | 101 | 126 | 0.0074103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-196_1_3_line_109 |  | 102 | 103 | 0.0087124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-196_1_3_line_110 |  | 103 | 104 | 0.0087714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-196_1_3_line_111 |  | 105 | 106 | 0.0073093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_230-196_1_3_line_112 |  | 106 | 119 | 0.0062412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_230-196_1_3_line_113 |  | 107 | 108 | 0.028083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-196_1_3_line_114 |  | 107 | 109 | 0.0080921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-196_1_3_line_115 |  | 109 | 110 | 0.017858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-196_1_3_line_116 |  | 110 | 111 | 0.0068546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-196_1_3_line_117 |  | 111 | 112 | 0.008383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-196_1_3_line_118 |  | 113 | 114 | 0.010849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_230-196_1_3_line_119 |  | 114 | 115 | 0.021337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-196_1_3_line_120 |  | 115 | 117 | 0.012048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-196_1_3_line_121 |  | 116 | 133 | 0.0042746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-196_1_3_line_122 |  | 117 | 123 | 0.0074245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-196_1_3_line_123 |  | 119 | 120 | 0.0062414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
124 | LV_230-196_1_3_line_124 |  | 120 | 121 | 0.0062409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
125 | LV_230-196_1_3_line_125 |  | 122 | 127 | 0.0062443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_230-196_1_3_line_126 |  | 123 | 124 | 0.0074099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-196_1_3_line_127 |  | 124 | 125 | 0.0074135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-196_1_3_line_128 |  | 125 | 126 | 0.0074115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_230-196_1_3_line_129 |  | 127 | 128 | 0.012895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
130 | LV_230-196_1_3_line_130 |  | 128 | 129 | 0.0097387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_230-196_1_3_line_131 |  | 129 | 130 | 0.0062389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
132 | LV_230-196_1_3_line_132 |  | 130 | 131 | 0.0062429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
133 | LV_230-196_1_3_line_133 |  | 131 | 132 | 0.0062428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
134 | LV_230-196_1_3_line_134 |  | 133 | 134 | 0.0034798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-196_1_3_line_135 |  | 133 | 135 | 0.019234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-196_1_3_line_136 |  | 134 | 136 | 0.0074112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_230-196_1_3_line_137 |  | 135 | 137 | 0.0069714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_230-196_1_3_line_138 |  | 136 | 138 | 0.0074111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_230-196_1_3_line_139 |  | 137 | 142 | 0.0069746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_230-196_1_3_line_140 |  | 138 | 139 | 0.0074123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_230-196_1_3_line_141 |  | 139 | 140 | 0.0074144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_230-196_1_3_line_142 |  | 140 | 141 | 0.0074105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_230-196_1_3_line_143 |  | 142 | 143 | 0.0069746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-196_1_3_trafo_89 | 0.63 MVA 20/0.4 kV | 145 | 93 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2699355.2405 | 1263355.4213 | 2699353.8079 | 1263372.4779
1 | 2699352.0998 | 1263392.8146 | 2699353.8079 | 1263372.4779
2 | 2699357.2097 | 1263331.9761 | 2699355.2405 | 1263355.4213
3 | 2699349.7953 | 1263414.2714 | 2699351.107 | 1263402.1278 | 2699352.0998 | 1263392.8146
4 | 2699358.9289 | 1263311.5067 | 2699357.2097 | 1263331.9761
5 | 2699349.7953 | 1263414.2714 | 2699347.9009 | 1263431.7223
6 | 2699349.7953 | 1263414.2714 | 2699336.4785 | 1263412.8173
7 | 2699359.4659 | 1263304.6656 | 2699358.9289 | 1263311.5067
8 | 2699347.3082 | 1263437.1818 | 2699347.9009 | 1263431.7223
9 | 2699343.0531 | 1263476.9765 | 2699349.3818 | 1263469.788 | 2699350.7207 | 1263457.3669 | 2699357.9043 | 1263458.0326
10 | 2699357.9043 | 1263458.0326 | 2699360.1149 | 1263438.0486
11 | 2699340.5947 | 1263504.4579 | 2699343.0531 | 1263476.9765
12 | 2699343.0531 | 1263476.9765 | 2699343.893 | 1263468.817
13 | 2699368.6809 | 1263340.0051 | 2699368.2192 | 1263345.9578 | 2699366.1832 | 1263372.5011
14 | 2699366.1832 | 1263372.5011 | 2699376.4905 | 1263373.3416
15 | 2699368.6809 | 1263340.0051 | 2699371.0062 | 1263340.1665
16 | 2699359.4659 | 1263304.6656 | 2699364.5987 | 1263304.9854 | 2699371.9594 | 1263305.4317 | 2699369.1052 | 1263334.4855 | 2699368.6809 | 1263340.0051
17 | 2699374.1495 | 1263397.3387 | 2699376.4905 | 1263373.3416 | 2699376.4905 | 1263373.3416
18 | 2699340.5947 | 1263504.4579 | 2699340.2313 | 1263507.6989 | 2699345.3677 | 1263508.2412 | 2699352.279 | 1263508.969 | 2699367.2665 | 1263510.5888
19 | 2699340.5947 | 1263504.4579 | 2699321.5913 | 1263503.6915
20 | 2699345.8836 | 1263449.4782 | 2699343.893 | 1263468.817
21 | 2699254.4397 | 1263482.8763 | 2699253.9664 | 1263486.3885 | 2699253.9888 | 1263488.133
22 | 2699254.0718 | 1263494.6008 | 2699253.9888 | 1263488.133
23 | 2699254.9906 | 1263478.7883 | 2699254.4397 | 1263482.8763
24 | 2699262.3139 | 1263474.0301 | 2699260.786 | 1263474.6377 | 2699258.374 | 1263477.8443 | 2699254.9906 | 1263478.7883 | 2699254.9906 | 1263478.7883
25 | 2699269.0956 | 1263474.6439 | 2699262.9324 | 1263473.7842 | 2699262.3139 | 1263474.0301
26 | 2699316.7527 | 1263328.3794 | 2699316.78 | 1263328.0033
27 | 2699318.0625 | 1263310.2859 | 2699316.78 | 1263328.0033
28 | 2699316.7391 | 1263328.5676 | 2699316.7527 | 1263328.3794
29 | 2699318.0625 | 1263310.2859 | 2699330.1764 | 1263310.7787
30 | 2699318.0625 | 1263310.2859 | 2699312.6986 | 1263310.0716
31 | 2699316.7391 | 1263328.5676 | 2699315.3667 | 1263347.5266
32 | 2699330.1764 | 1263310.7787 | 2699330.9815 | 1263299.9743
33 | 2699305.1453 | 1263309.7698 | 2699312.6986 | 1263310.0716
34 | 2699315.3667 | 1263347.5266 | 2699314.9162 | 1263353.7494
35 | 2699288.2856 | 1263309.0961 | 2699305.1453 | 1263309.7698
36 | 2699359.4659 | 1263304.6656 | 2699364.5987 | 1263304.9854 | 2699371.9594 | 1263305.4317 | 2699390.7832 | 1263308.7841
37 | 2699359.4659 | 1263304.6656 | 2699360.2302 | 1263294.9127
38 | 2699390.7832 | 1263308.7841 | 2699396.1371 | 1263309.5412
39 | 2699361.9408 | 1263273.0869 | 2699360.2302 | 1263294.9127
40 | 2699396.1371 | 1263309.5412 | 2699400.7796 | 1263310.1977 | 2699407.0458 | 1263309.9355
41 | 2699288.2856 | 1263309.0961 | 2699282.3133 | 1263315.2454 | 2699281.7861 | 1263328.8199
42 | 2699281.53 | 1263335.4155 | 2699281.7861 | 1263328.8199
43 | 2699263.56 | 1263308.5918 | 2699281.0946 | 1263308.8641 | 2699288.2856 | 1263309.0961
44 | 2699281.53 | 1263335.4155 | 2699281.438 | 1263337.7492 | 2699280.6093 | 1263359.2753
45 | 2699281.53 | 1263335.4155 | 2699270.2283 | 1263334.5398
46 | 2699263.56 | 1263308.5918 | 2699264.2679 | 1263298.7378
47 | 2699280.6093 | 1263359.2753 | 2699274.0063 | 1263359.0198 | 2699270.5441 | 1263359.7355
48 | 2699261.9424 | 1263333.8977 | 2699270.2283 | 1263334.5398
49 | 2699296.8362 | 1263264.7364 | 2699296.3952 | 1263269.7249
50 | 2699297.3096 | 1263259.4289 | 2699296.8362 | 1263264.7364
51 | 2699297.3096 | 1263259.4289 | 2699286.1448 | 1263259.1367
52 | 2699298.4065 | 1263247.0593 | 2699297.3096 | 1263259.4289
53 | 2699265.3522 | 1263291.8146 | 2699265.0207 | 1263296.5397 | 2699264.2877 | 1263298.4623 | 2699264.2679 | 1263298.7378
54 | 2699270.5441 | 1263359.7355 | 2699264.7527 | 1263360.9327 | 2699259.144 | 1263366.9658 | 2699255.0505 | 1263366.6637
55 | 2699261.9424 | 1263333.8977 | 2699253.7946 | 1263333.2663
56 | 2699308.6758 | 1263422.7767 | 2699313.1006 | 1263422.6286
57 | 2699308.6758 | 1263422.7767 | 2699309.6074 | 1263413.6946
58 | 2699308.6758 | 1263422.7767 | 2699301.6333 | 1263421.7872
59 | 2699308.6758 | 1263422.7767 | 2699306.8428 | 1263434.9458
60 | 2699310.2451 | 1263407.4772 | 2699309.6074 | 1263413.6946
61 | 2699278.3846 | 1263416.8076 | 2699285.5914 | 1263417.4402 | 2699292.7642 | 1263420.541 | 2699301.6333 | 1263421.7872
62 | 2699306.8428 | 1263434.9458 | 2699305.9127 | 1263441.1209
63 | 2699347.3082 | 1263437.1818 | 2699346.2137 | 1263446.2709 | 2699345.8836 | 1263449.4782
64 | 2699367.2665 | 1263510.5888 | 2699368.5126 | 1263499.1539
65 | 2699320.4876 | 1263503.6469 | 2699321.5913 | 1263503.6915
66 | 2699370.0014 | 1263485.4918 | 2699368.5126 | 1263499.1539
67 | 2699246.4706 | 1263421.7761 | 2699243.451 | 1263423.4824 | 2699238.8352 | 1263422.9481
68 | 2699253.1837 | 1263422.3918 | 2699246.4706 | 1263421.7761 | 2699246.4706 | 1263421.7761
69 | 2699269.7467 | 1263416.151 | 2699260.463 | 1263421.6553 | 2699257.4531 | 1263422.7835 | 2699253.1837 | 1263422.3918
70 | 2699278.3846 | 1263416.8076 | 2699269.7467 | 1263416.151 | 2699269.7467 | 1263416.151
71 | 2699250.0139 | 1263449.9497 | 2699254.2434 | 1263450.1633 | 2699266.5348 | 1263444.5538
72 | 2699250.0139 | 1263449.9497 | 2699243.0707 | 1263449.599
73 | 2699274.6507 | 1263446.6807 | 2699266.5348 | 1263444.5538 | 2699266.5348 | 1263444.5538
74 | 2699230.4944 | 1263448.9638 | 2699243.0707 | 1263449.599
75 | 2699274.6507 | 1263446.6807 | 2699272.9138 | 1263455.4477 | 2699272.5845 | 1263457.1102
76 | 2699230.4944 | 1263448.9638 | 2699231.2145 | 1263453.6353
77 | 2699272.5845 | 1263457.1102 | 2699296.3468 | 1263459.3995
78 | 2699272.5845 | 1263457.1102 | 2699272.3966 | 1263458.8752 | 2699269.0956 | 1263474.6439
79 | 2699231.2145 | 1263453.6353 | 2699234.1528 | 1263478.3049 | 2699235.2742 | 1263503.0442 | 2699235.3512 | 1263506.982 | 2699235.4479 | 1263511.543
80 | 2699314.9162 | 1263353.7494 | 2699314.7742 | 1263355.7105
81 | 2699303.0621 | 1263460.0465 | 2699296.3468 | 1263459.3995
82 | 2699235.4483 | 1263531.2593 | 2699235.4479 | 1263511.543
83 | 2699235.4483 | 1263531.2593 | 2699247.5621 | 1263532.0908
84 | 2699294.1899 | 1263502.9329 | 2699302.7784 | 1263502.9327
85 | 2699294.1899 | 1263502.9329 | 2699294.9649 | 1263498.509 | 2699295.9117 | 1263494.0116
86 | 2699302.7784 | 1263502.9327 | 2699320.4876 | 1263503.6469
87 | 2699297.1985 | 1263487.8992 | 2699295.9117 | 1263494.0116
88 | 2699245.6434 | 1263332.6347 | 2699245.0679 | 1263332.5901 | 2699238.6163 | 1263333.6403
89 | 2699245.6434 | 1263332.6347 | 2699253.7946 | 1263333.2663
90 | 2699334.7116 | 1263249.8379 | 2699334.3635 | 1263254.5769
91 | 2699334.3635 | 1263254.5769 | 2699334.3599 | 1263254.6248
92 | 2699334.7116 | 1263249.8379 | 2699332.349 | 1263249.6536 | 2699324.3101 | 1263249.0392
93 | 2699334.3599 | 1263254.6248 | 2699333.9317 | 1263260.3779 | 2699333.0864 | 1263271.723
94 | 2699316.768 | 1263248.4627 | 2699324.3101 | 1263249.0392
95 | 2699333.0864 | 1263271.723 | 2699333.0197 | 1263272.6185
96 | 2699309.2241 | 1263247.8861 | 2699316.768 | 1263248.4627
97 | 2699247.5621 | 1263532.0908 | 2699254.3211 | 1263532.5548
98 | 2699314.4657 | 1263359.9721 | 2699314.7742 | 1263355.7105
99 | 2699314.4657 | 1263359.9721 | 2699314.0151 | 1263366.1975
100 | 2699314.0151 | 1263366.1975 | 2699313.564 | 1263372.4279
101 | 2699312.9015 | 1263381.5803 | 2699313.564 | 1263372.4279
102 | 2699231.4919 | 1263192.5913 | 2699231.3975 | 1263196.2335
103 | 2699230.6585 | 1263224.7261 | 2699231.3975 | 1263196.2335
104 | 2699231.4919 | 1263192.5913 | 2699246.1653 | 1263193.6091
105 | 2699230.6585 | 1263224.7261 | 2699244.1801 | 1263225.4451
106 | 2699253.5233 | 1263194.1195 | 2699246.1653 | 1263193.6091
107 | 2699251.5818 | 1263225.8387 | 2699244.1801 | 1263225.4451
108 | 2699258.9816 | 1263226.2321 | 2699251.5818 | 1263225.8387
109 | 2699255.0505 | 1263366.6637 | 2699246.3617 | 1263366.0225
110 | 2699246.3617 | 1263366.0225 | 2699237.6142 | 1263365.377
111 | 2699312.9015 | 1263381.5803 | 2699312.1557 | 1263388.8514
112 | 2699312.1557 | 1263388.8514 | 2699311.5188 | 1263395.06
113 | 2699279.4662 | 1263388.7471 | 2699278.427 | 1263415.6296 | 2699278.3846 | 1263416.8076
114 | 2699279.4662 | 1263388.7471 | 2699271.5177 | 1263388.3133 | 2699271.3997 | 1263388.3718
115 | 2699271.3997 | 1263388.3718 | 2699259.1496 | 1263394.4441 | 2699254.9726 | 1263394.18
116 | 2699254.9726 | 1263394.18 | 2699248.1317 | 1263393.7475
117 | 2699248.1317 | 1263393.7475 | 2699248.1317 | 1263393.7475 | 2699242.9181 | 1263395.5504 | 2699240.0575 | 1263395.368
118 | 2699298.4065 | 1263247.0593 | 2699309.2241 | 1263247.8861
119 | 2699300.2855 | 1263225.8066 | 2699298.4065 | 1263247.0593
120 | 2699300.2855 | 1263225.8066 | 2699293.3238 | 1263228.0583 | 2699288.5992 | 1263227.8071
121 | 2699281.8716 | 1263259.0249 | 2699286.1448 | 1263259.1367
122 | 2699288.5992 | 1263227.8071 | 2699281.1852 | 1263227.4128
123 | 2699311.5188 | 1263395.06 | 2699310.8819 | 1263401.2688
124 | 2699310.8819 | 1263401.2688 | 2699310.2451 | 1263407.4772
125 | 2699305.9127 | 1263441.1209 | 2699304.9827 | 1263447.2956
126 | 2699281.1852 | 1263227.4128 | 2699273.7857 | 1263227.0193
127 | 2699273.7857 | 1263227.0193 | 2699266.3827 | 1263226.6257
128 | 2699266.3827 | 1263226.6257 | 2699258.9816 | 1263226.2321
129 | 2699303.0621 | 1263460.0465 | 2699304.9827 | 1263447.2956
130 | 2699303.0621 | 1263460.0465 | 2699301.0559 | 1263469.5763
131 | 2699301.0559 | 1263469.5763 | 2699299.7706 | 1263475.6813
132 | 2699299.7706 | 1263475.6813 | 2699298.4845 | 1263481.7903
133 | 2699298.4845 | 1263481.7903 | 2699297.1985 | 1263487.8992
134 | 2699281.8716 | 1263259.0249 | 2699278.4007 | 1263258.7757
135 | 2699281.8716 | 1263259.0249 | 2699266.8234 | 1263270.8487 | 2699266.8166 | 1263270.9453
136 | 2699278.4007 | 1263258.7757 | 2699271.0085 | 1263258.245
137 | 2699266.8166 | 1263270.9453 | 2699266.3286 | 1263277.8995
138 | 2699271.0085 | 1263258.245 | 2699263.6164 | 1263257.7143
139 | 2699266.3286 | 1263277.8995 | 2699265.8404 | 1263284.8571
140 | 2699263.6164 | 1263257.7143 | 2699256.2231 | 1263257.1835
141 | 2699256.2231 | 1263257.1835 | 2699248.8278 | 1263256.6526
142 | 2699248.8278 | 1263256.6526 | 2699241.4363 | 1263256.1219
143 | 2699265.8404 | 1263284.8571 | 2699265.3522 | 1263291.8146

## bus_geodata
| x | y | coords
0 | 2699353.8079 | 1263372.4779
1 | 2699355.2405 | 1263355.4213
2 | 2699352.0998 | 1263392.8146
3 | 2699357.2097 | 1263331.9761
4 | 2699349.7953 | 1263414.2714
5 | 2699358.9289 | 1263311.5067
6 | 2699347.9009 | 1263431.7223
7 | 2699336.4785 | 1263412.8173
8 | 2699357.9043 | 1263458.0326
9 | 2699343.0531 | 1263476.9765
10 | 2699360.1149 | 1263438.0486
11 | 2699366.1832 | 1263372.5011
12 | 2699368.6809 | 1263340.0051
13 | 2699376.4905 | 1263373.3416
14 | 2699340.5947 | 1263504.4579
15 | 2699343.893 | 1263468.817
16 | 2699253.9888 | 1263488.133
17 | 2699254.4397 | 1263482.8763
18 | 2699254.0718 | 1263494.6008
19 | 2699254.9906 | 1263478.7883
20 | 2699262.3139 | 1263474.0301
21 | 2699316.78 | 1263328.0033
22 | 2699316.7527 | 1263328.3794
23 | 2699318.0625 | 1263310.2859
24 | 2699316.7391 | 1263328.5676
25 | 2699330.1764 | 1263310.7787
26 | 2699312.6986 | 1263310.0716
27 | 2699315.3667 | 1263347.5266
28 | 2699330.9815 | 1263299.9743
29 | 2699305.1453 | 1263309.7698
30 | 2699374.1495 | 1263397.3387
31 | 2699371.0062 | 1263340.1665
32 | 2699359.4659 | 1263304.6656
33 | 2699390.7832 | 1263308.7841
34 | 2699360.2302 | 1263294.9127
35 | 2699396.1371 | 1263309.5412
36 | 2699281.7861 | 1263328.8199
37 | 2699288.2856 | 1263309.0961
38 | 2699281.53 | 1263335.4155
39 | 2699263.56 | 1263308.5918
40 | 2699280.6093 | 1263359.2753
41 | 2699270.2283 | 1263334.5398
42 | 2699296.3952 | 1263269.7249
43 | 2699296.8362 | 1263264.7364
44 | 2699297.3096 | 1263259.4289
45 | 2699264.2679 | 1263298.7378
46 | 2699270.5441 | 1263359.7355
47 | 2699261.9423 | 1263333.8977
48 | 2699313.1006 | 1263422.6286
49 | 2699308.6758 | 1263422.7767
50 | 2699309.6074 | 1263413.6946
51 | 2699301.6333 | 1263421.7872
52 | 2699306.8428 | 1263434.9458
53 | 2699347.3082 | 1263437.1818
54 | 2699345.8836 | 1263449.4782
55 | 2699367.2665 | 1263510.5888
56 | 2699321.5913 | 1263503.6915
57 | 2699368.5126 | 1263499.1539
58 | 2699238.8352 | 1263422.9481
59 | 2699246.4706 | 1263421.7761
60 | 2699253.1837 | 1263422.3918
61 | 2699269.7467 | 1263416.151
62 | 2699250.0139 | 1263449.9497
63 | 2699266.5348 | 1263444.5538
64 | 2699243.0707 | 1263449.599
65 | 2699274.6507 | 1263446.6807
66 | 2699230.4944 | 1263448.9638
67 | 2699272.5845 | 1263457.1102
68 | 2699231.2145 | 1263453.6353
69 | 2699314.9162 | 1263353.7494
70 | 2699269.0956 | 1263474.6439
71 | 2699296.3468 | 1263459.3995
72 | 2699235.4479 | 1263511.543
73 | 2699235.4483 | 1263531.2593
74 | 2699294.1899 | 1263502.9329
75 | 2699302.7784 | 1263502.9327
76 | 2699295.9117 | 1263494.0116
77 | 2699238.6164 | 1263333.6403
78 | 2699245.6434 | 1263332.6347
79 | 2699253.7946 | 1263333.2663
80 | 2699334.3635 | 1263254.5769
81 | 2699334.7116 | 1263249.8379
82 | 2699334.3599 | 1263254.6248
83 | 2699324.3101 | 1263249.0392
84 | 2699333.0864 | 1263271.723
85 | 2699316.768 | 1263248.4627
86 | 2699333.0197 | 1263272.6185
87 | 2699407.0458 | 1263309.9355
88 | 2699247.5621 | 1263532.0908
89 | 2699254.3211 | 1263532.5548
90 | 2699320.4876 | 1263503.6469
91 | 2699314.7742 | 1263355.7105
92 | 2699314.4657 | 1263359.9721
93 | 2699314.0151 | 1263366.1975
94 | 2699313.564 | 1263372.4279
95 | 2699231.3975 | 1263196.2335
96 | 2699231.4919 | 1263192.5913
97 | 2699230.6585 | 1263224.7261
98 | 2699246.1653 | 1263193.6091
99 | 2699244.1801 | 1263225.4451
100 | 2699253.5233 | 1263194.1195
101 | 2699251.5818 | 1263225.8387
102 | 2699255.0505 | 1263366.6637
103 | 2699246.3617 | 1263366.0225
104 | 2699237.6142 | 1263365.377
105 | 2699312.9015 | 1263381.5803
106 | 2699312.1557 | 1263388.8514
107 | 2699279.4662 | 1263388.7471
108 | 2699278.3846 | 1263416.8076
109 | 2699271.3997 | 1263388.3718
110 | 2699254.9726 | 1263394.18
111 | 2699248.1317 | 1263393.7475
112 | 2699240.0575 | 1263395.368
113 | 2699309.2241 | 1263247.8861
114 | 2699298.4065 | 1263247.0593
115 | 2699300.2855 | 1263225.8066
116 | 2699286.1448 | 1263259.1367
117 | 2699288.5992 | 1263227.8071
118 | 2699361.9408 | 1263273.0869
119 | 2699311.5188 | 1263395.06
120 | 2699310.8819 | 1263401.2688
121 | 2699310.2451 | 1263407.4772
122 | 2699305.9127 | 1263441.1209
123 | 2699281.1852 | 1263227.4128
124 | 2699273.7857 | 1263227.0194
125 | 2699266.3827 | 1263226.6257
126 | 2699258.9816 | 1263226.2321
127 | 2699304.9827 | 1263447.2956
128 | 2699303.0621 | 1263460.0465
129 | 2699301.0559 | 1263469.5763
130 | 2699299.7706 | 1263475.6813
131 | 2699298.4845 | 1263481.7903
132 | 2699297.1985 | 1263487.8992
133 | 2699281.8716 | 1263259.0249
134 | 2699278.4007 | 1263258.7757
135 | 2699266.8166 | 1263270.9453
136 | 2699271.0085 | 1263258.245
137 | 2699266.3286 | 1263277.8995
138 | 2699263.6164 | 1263257.7143
139 | 2699256.2231 | 1263257.1835
140 | 2699248.8278 | 1263256.6526
141 | 2699241.4363 | 1263256.1219
142 | 2699265.8404 | 1263284.8571
143 | 2699265.3522 | 1263291.8146
144 | 2699370.0014 | 1263485.4918
145 | 2699312.9015 | 1263381.5803

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97641 | -0.45305 | 0.01532 | 0.0038397
1 | 0.97541 | -0.47275 | 0.0040382 | 0.0010121
2 | 0.9779 | -0.42392 | 0 | 0
3 | 0.97411 | -0.49815 | 0.0048295 | 0.0012104
4 | 0.97947 | -0.39321 | 0 | 0
5 | 0.97308 | -0.51855 | 0 | 0
6 | 0.98097 | -0.36407 | 0.0018825 | 0.0004718
7 | 0.97931 | -0.39645 | 0.013323 | 0.0033391
8 | 0.9849 | -0.28799 | 0 | 0
9 | 0.98507 | -0.28471 | 0 | 0
10 | 0.98478 | -0.29024 | 0.0062364 | 0.001563
11 | 0.97088 | -0.56188 | 0 | 0
12 | 0.97156 | -0.54845 | 0 | 0
13 | 0.97067 | -0.56614 | 0.0025218 | 0.00063201
14 | 0.9878 | -0.23203 | 0 | 0
15 | 0.9843 | -0.29951 | 0.00224 | 0.00056139
16 | 0.99263 | -0.13985 | 0.0010318 | 0.0002586
17 | 0.99264 | -0.13965 | 0.0009932 | 0.00024892
18 | 0.99262 | -0.13997 | 0.0010631 | 0.00026645
19 | 0.99265 | -0.13943 | 0.0010282 | 0.00025768
20 | 0.99269 | -0.13876 | 0.0011784 | 0.00029534
21 | 0.99782 | -0.041671 | 0.0026649 | 0.00066788
22 | 0.99784 | -0.041332 | 0.0037566 | 0.0009415
23 | 0.99704 | -0.056789 | 0 | 0
24 | 0.99785 | -0.041151 | 0.0038678 | 0.00096935
25 | 0.99702 | -0.057156 | 0 | 0
26 | 0.99681 | -0.0612 | 0.0017314 | 0.00043392
27 | 0.99887 | -0.021582 | 0.0028288 | 0.00070897
28 | 0.997 | -0.057485 | 0.0017305 | 0.0004337
29 | 0.9965 | -0.067184 | 0.0017307 | 0.00043375
30 | 0.97022 | -0.57496 | 0.019767 | 0.0049541
31 | 0.97155 | -0.54863 | 0.0041883 | 0.0010497
32 | 0.97273 | -0.52538 | 0 | 0
33 | 0.97225 | -0.53493 | 0 | 0
34 | 0.97263 | -0.52739 | 0.0055871 | 0.0014002
35 | 0.97217 | -0.53656 | 0.015245 | 0.0038207
36 | 0.99571 | -0.082304 | 0.0008503 | 0.00021311
37 | 0.99583 | -0.080042 | 0 | 0
38 | 0.99568 | -0.082879 | 0 | 0
39 | 0.99498 | -0.09639 | 0 | 0
40 | 0.99563 | -0.083801 | 0 | 0
41 | 0.99565 | -0.08343 | 0.00056772 | 0.00014228
42 | 0.99281 | -0.13826 | 0.0017307 | 0.00043375
43 | 0.99282 | -0.13811 | 0 | 0
44 | 0.99283 | -0.13795 | 0 | 0
45 | 0.99464 | -0.10293 | 0.0010719 | 0.00026864
46 | 0.99561 | -0.084192 | 0.00050258 | 0.00012596
47 | 0.99564 | -0.08375 | 0.00052726 | 0.00013214
48 | 0.99569 | -0.081573 | 0.0018829 | 0.0004719
49 | 0.99569 | -0.081426 | 0 | 0
50 | 0.99636 | -0.068769 | 0.0013637 | 0.00034178
51 | 0.99564 | -0.082373 | 0.0013586 | 0.0003405
52 | 0.99485 | -0.097489 | 0.0010103 | 0.0002532
53 | 0.98145 | -0.35478 | 0 | 0
54 | 0.98252 | -0.33388 | 0.0046881 | 0.001175
55 | 0.98748 | -0.23825 | 0 | 0
56 | 0.98885 | -0.21201 | 0.0090445 | 0.0022668
57 | 0.98736 | -0.2406 | 0.0052009 | 0.0013035
58 | 0.9954 | -0.087063 | 0.0011212 | 0.00028101
59 | 0.99541 | -0.086903 | 0.0010292 | 0.00025793
60 | 0.99542 | -0.086648 | 0.00095765 | 0.00024001
61 | 0.99548 | -0.085647 | 0.0011527 | 0.0002889
62 | 0.99262 | -0.13996 | 0.001036 | 0.00025965
63 | 0.9927 | -0.13846 | 0.0012509 | 0.00031352
64 | 0.9926 | -0.14042 | 0.001035 | 0.00025939
65 | 0.99275 | -0.13757 | 0 | 0
66 | 0.99257 | -0.14102 | 0 | 0
67 | 0.99281 | -0.13644 | 0 | 0
68 | 0.99256 | -0.14124 | 0 | 0
69 | 0.99922 | -0.01486 | 0.0028289 | 0.000709
70 | 0.99272 | -0.13811 | 0 | 0
71 | 0.99305 | -0.13166 | 0.0010124 | 0.00025374
72 | 0.99242 | -0.14401 | 0 | 0
73 | 0.99237 | -0.14495 | 0 | 0
74 | 0.99047 | -0.18083 | 0 | 0
75 | 0.98997 | -0.19057 | 0 | 0
76 | 0.99101 | -0.17051 | 0.0010123 | 0.00025371
77 | 0.99561 | -0.08423 | 0.00061138 | 0.00015323
78 | 0.99562 | -0.084154 | 0.00052707 | 0.0001321
79 | 0.99562 | -0.08399 | 0.00052741 | 0.00013218
80 | 0.99229 | -0.14832 | 0.001495 | 0.00037467
81 | 0.99231 | -0.1479 | 0 | 0
82 | 0.99229 | -0.14832 | 0 | 0
83 | 0.99236 | -0.14699 | 0.0017315 | 0.00043396
84 | 0.99224 | -0.14937 | 0.0017296 | 0.00043347
85 | 0.99241 | -0.14609 | 0.0017315 | 0.00043396
86 | 0.99224 | -0.1494 | 0.0017313 | 0.0004339
87 | 0.97216 | -0.53679 | 0.0011295 | 0.00028308
88 | 0.99234 | -0.14553 | 0.0012123 | 0.00030383
89 | 0.99233 | -0.1457 | 0.0014773 | 0.00037026
90 | 0.98891 | -0.21076 | 0.00087942 | 0.0002204
91 | 0.99934 | -0.012645 | 0.0027485 | 0.00068885
92 | 0.9996 | -0.0076298 | 0.0028288 | 0.00070897
93 | 1 | 0 | -0.24534 | -0.062318
94 | 0.99951 | -0.0092808 | 0.0028328 | 0.00070997
95 | 0.99159 | -0.16201 | 0.0033862 | 0.00084866
96 | 0.99158 | -0.16215 | 0 | 0
97 | 0.99173 | -0.15923 | 0 | 0
98 | 0.99155 | -0.1627 | 0.0010607 | 0.00026584
99 | 0.9918 | -0.15791 | 0.0010589 | 0.00026539
100 | 0.99154 | -0.16284 | 0.0010602 | 0.00026571
101 | 0.99184 | -0.15705 | 0.0010583 | 0.00026523
102 | 0.99559 | -0.084735 | 0.00054705 | 0.0001371
103 | 0.99558 | -0.08491 | 0.00055974 | 0.00014028
104 | 0.99557 | -0.085 | 0.00058313 | 0.00014615
105 | 0.9988 | -0.022704 | 0 | 0
106 | 0.99823 | -0.033409 | 0.0028286 | 0.00070891
107 | 0.99546 | -0.085964 | 0 | 0
108 | 0.99551 | -0.084998 | 0 | 0
109 | 0.99544 | -0.086242 | 0.00050245 | 0.00012593
110 | 0.99542 | -0.086698 | 0.00041778 | 0.00010471
111 | 0.99541 | -0.086822 | 0.00044909 | 0.00011255
112 | 0.99541 | -0.086908 | 0.00058363 | 0.00014627
113 | 0.99247 | -0.14496 | 0.0017313 | 0.00043391
114 | 0.99257 | -0.14302 | 0 | 0
115 | 0.99231 | -0.14789 | 0 | 0
116 | 0.99308 | -0.13305 | 0.0010584 | 0.00026527
117 | 0.99217 | -0.15065 | 0.0010584 | 0.00026526
118 | 0.97252 | -0.52964 | 0.0055698 | 0.0013959
119 | 0.99775 | -0.042405 | 0.0028286 | 0.00070891
120 | 0.99729 | -0.051255 | 0.0013594 | 0.00034071
121 | 0.99682 | -0.060039 | 0.0013593 | 0.00034067
122 | 0.99442 | -0.10559 | 0.0010121 | 0.00025365
123 | 0.99209 | -0.15221 | 0.0010584 | 0.00026526
124 | 0.99202 | -0.15363 | 0.0010577 | 0.00026508
125 | 0.99195 | -0.15491 | 0.0010583 | 0.00026522
126 | 0.99189 | -0.15605 | 0.0010584 | 0.00026525
127 | 0.994 | -0.11365 | 0.0010101 | 0.00025316
128 | 0.99313 | -0.13019 | 0 | 0
129 | 0.99253 | -0.14165 | 0.0010107 | 0.0002533
130 | 0.99214 | -0.14893 | 0.0010107 | 0.0002533
131 | 0.99177 | -0.15618 | 0.0010114 | 0.00025348
132 | 0.99139 | -0.16337 | 0.0010104 | 0.00025324
133 | 0.99318 | -0.1311 | 0 | 0
134 | 0.99316 | -0.13149 | 0.0010584 | 0.00026527
135 | 0.99375 | -0.12015 | 0.0010724 | 0.00026876
136 | 0.99313 | -0.13218 | 0.0010583 | 0.00026523
137 | 0.99396 | -0.11606 | 0.0010718 | 0.00026863
138 | 0.9931 | -0.13273 | 0.0010583 | 0.00026525
139 | 0.99308 | -0.13315 | 0.0010582 | 0.00026522
140 | 0.99306 | -0.13343 | 0.0010577 | 0.00026508
141 | 0.99305 | -0.13357 | 0.0010583 | 0.00026525
142 | 0.99418 | -0.11183 | 0.0010736 | 0.00026907
143 | 0.9944 | -0.10748 | 0.0010718 | 0.00026863
144 | 0.98728 | -0.24214 | 0.0062315 | 0.0015618
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.063144 | 0.015927 | -0.063085 | -0.015889 | 5.9484e-05 | 3.7856e-05 | 0.096266 | 0.096266 | 0.096266 | 0.97641 | -0.45305 | 0.97541 | -0.47275 | 26.4467
1 | -0.078465 | -0.019766 | 0.078574 | 0.019836 | 0.0001095 | 6.9822e-05 | 0.11961 | 0.11961 | 0.11961 | 0.97641 | -0.45305 | 0.9779 | -0.42392 | 32.8609
2 | 0.059047 | 0.014877 | -0.058975 | -0.014831 | 7.1634e-05 | 4.5552e-05 | 0.090106 | 0.090106 | 0.090106 | 0.97541 | -0.47275 | 0.97411 | -0.49815 | 24.7544
3 | -0.078574 | -0.019836 | 0.07869 | 0.01991 | 0.00011578 | 7.383e-05 | 0.11961 | 0.11961 | 0.11961 | 0.9779 | -0.42392 | 0.97947 | -0.39321 | 32.8609
4 | 0.054145 | 0.013621 | -0.054093 | -0.013587 | 5.272e-05 | 3.3485e-05 | 0.082729 | 0.082729 | 0.082729 | 0.97411 | -0.49815 | 0.97308 | -0.51855 | 22.7276
5 | -0.092015 | -0.02325 | 0.092144 | 0.023332 | 0.00012876 | 8.2182e-05 | 0.13986 | 0.13986 | 0.13986 | 0.97947 | -0.39321 | 0.98097 | -0.36407 | 38.4224
6 | 0.013325 | 0.0033402 | -0.013323 | -0.0033391 | 2.0587e-06 | 1.149e-06 | 0.020244 | 0.020244 | 0.020244 | 0.97947 | -0.39321 | 0.97931 | -0.39645 | 5.5615
7 | 0.054093 | 0.013587 | -0.054075 | -0.013576 | 1.7614e-05 | 1.1188e-05 | 0.082729 | 0.082729 | 0.082729 | 0.97308 | -0.51855 | 0.97273 | -0.52538 | 22.7276
8 | -0.094026 | -0.023804 | 0.094068 | 0.023831 | 4.1943e-05 | 2.6774e-05 | 0.14271 | 0.14271 | 0.14271 | 0.98097 | -0.36407 | 0.98145 | -0.35478 | 39.2069
9 | -0.0062371 | -0.0015632 | 0.0062381 | 0.0015634 | 9.7513e-07 | 2.5134e-07 | 0.0094232 | 0.009423 | 0.0094232 | 0.9849 | -0.28799 | 0.98507 | -0.28471 | 2.5888
10 | 0.0062371 | 0.0015632 | -0.0062364 | -0.001563 | 6.695e-07 | 1.7264e-07 | 0.0094232 | 0.0094233 | 0.0094233 | 0.9849 | -0.28799 | 0.98478 | -0.29024 | 2.5888
11 | -0.10756 | -0.027342 | 0.10784 | 0.027516 | 0.00027365 | 0.00017478 | 0.16262 | 0.16262 | 0.16262 | 0.98507 | -0.28471 | 0.9878 | -0.23203 | 44.6764
12 | 0.10133 | 0.025778 | -0.10125 | -0.025732 | 7.2193e-05 | 4.6099e-05 | 0.1532 | 0.1532 | 0.1532 | 0.98507 | -0.28471 | 0.9843 | -0.29951 | 42.0877
13 | -0.022302 | -0.0055939 | 0.022316 | 0.0056027 | 1.4281e-05 | 8.7367e-06 | 0.034182 | 0.034182 | 0.034182 | 0.97088 | -0.56188 | 0.97156 | -0.54845 | 9.3907
14 | 0.022302 | 0.0055939 | -0.022297 | -0.0055912 | 4.5313e-06 | 2.7721e-06 | 0.034182 | 0.034182 | 0.034182 | 0.97088 | -0.56188 | 0.97067 | -0.56614 | 9.3908
15 | 0.0041884 | 0.0010497 | -0.0041883 | -0.0010497 | 3.5861e-08 | -5.8283e-09 | 0.0064148 | 0.0064148 | 0.0064148 | 0.97156 | -0.54845 | 0.97155 | -0.54863 | 1.7623
16 | -0.026504 | -0.0066524 | 0.026534 | 0.0066705 | 2.92e-05 | 1.8102e-05 | 0.040597 | 0.040597 | 0.040597 | 0.97156 | -0.54845 | 0.97273 | -0.52538 | 11.153
17 | 0.019776 | 0.0049592 | -0.019767 | -0.0049541 | 8.3101e-06 | 5.0206e-06 | 0.030317 | 0.030317 | 0.030317 | 0.97067 | -0.56614 | 0.97022 | -0.57496 | 8.3288
18 | 0.011438 | 0.0028678 | -0.011434 | -0.002866 | 3.39e-06 | 1.7799e-06 | 0.01723 | 0.01723 | 0.01723 | 0.9878 | -0.23203 | 0.98748 | -0.23825 | 4.7335
19 | -0.11928 | -0.030384 | 0.11939 | 0.030458 | 0.00011535 | 7.3336e-05 | 0.17985 | 0.17985 | 0.17985 | 0.9878 | -0.23203 | 0.98885 | -0.21201 | 24.7049
20 | 0.099015 | 0.025171 | -0.098851 | -0.025066 | 0.00016362 | 0.00010447 | 0.14981 | 0.14981 | 0.14981 | 0.9843 | -0.29951 | 0.98252 | -0.33388 | 41.1574
21 | -0.0020949 | -0.00052496 | 0.002095 | 0.00052491 | 1.9559e-08 | -5.5846e-08 | 0.0031404 | 0.0031404 | 0.0031404 | 0.99263 | -0.13985 | 0.99264 | -0.13965 | 0.86276
22 | 0.0010631 | 0.00026637 | -0.0010631 | -0.00026645 | 6.1608e-09 | -7.967e-08 | 0.0015937 | 0.0015937 | 0.0015937 | 0.99263 | -0.13985 | 0.99262 | -0.13997 | 0.43783
23 | -0.0030882 | -0.00077383 | 0.0030882 | 0.00077379 | 3.3149e-08 | -3.2108e-08 | 0.0046293 | 0.0046292 | 0.0046293 | 0.99264 | -0.13965 | 0.99265 | -0.13943 | 1.2718
24 | -0.0041164 | -0.0010315 | 0.0041165 | 0.0010314 | 1.3092e-07 | -3.4749e-08 | 0.0061705 | 0.0061705 | 0.0061705 | 0.99265 | -0.13943 | 0.99269 | -0.13876 | 1.6952
25 | -0.0052949 | -0.0013268 | 0.0052951 | 0.0013268 | 1.6273e-07 | 1.5085e-08 | 0.0079369 | 0.0079368 | 0.0079369 | 0.99269 | -0.13876 | 0.99272 | -0.13811 | 2.1805
26 | -0.051425 | -0.012958 | 0.051426 | 0.012959 | 8.3207e-07 | 5.276e-07 | 0.076713 | 0.076713 | 0.076713 | 0.99782 | -0.041671 | 0.99784 | -0.041332 | 21.0749
27 | 0.04876 | 0.01229 | -0.048725 | -0.012268 | 3.5245e-05 | 2.2325e-05 | 0.072739 | 0.072739 | 0.072739 | 0.99782 | -0.041671 | 0.99704 | -0.056789 | 19.9831
28 | -0.055182 | -0.0139 | 0.055183 | 0.0139 | 4.7942e-07 | 3.0436e-07 | 0.082315 | 0.082315 | 0.082315 | 0.99784 | -0.041332 | 0.99785 | -0.041151 | 22.6139
29 | 0.0017305 | 0.00043344 | -0.0017305 | -0.00043358 | 3.0236e-08 | -1.3829e-07 | 0.0025826 | 0.0025827 | 0.0025827 | 0.99704 | -0.056789 | 0.99702 | -0.057156 | 0.70953
30 | 0.046994 | 0.011834 | -0.046984 | -0.011828 | 9.9082e-06 | 6.2712e-06 | 0.070156 | 0.070156 | 0.070156 | 0.99704 | -0.056789 | 0.99681 | -0.0612 | 19.2736
31 | -0.059051 | -0.01487 | 0.059106 | 0.014905 | 5.5304e-05 | 3.5146e-05 | 0.088082 | 0.088082 | 0.088082 | 0.99785 | -0.041151 | 0.99887 | -0.021582 | 24.1984
32 | 0.0017305 | 0.00043358 | -0.0017305 | -0.0004337 | 2.7101e-08 | -1.2395e-07 | 0.0025827 | 0.0025827 | 0.0025827 | 0.99702 | -0.057156 | 0.997 | -0.057485 | 0.70955
33 | 0.045253 | 0.011394 | -0.04524 | -0.011386 | 1.2943e-05 | 8.1851e-06 | 0.067571 | 0.067571 | 0.067571 | 0.99681 | -0.0612 | 0.9965 | -0.067184 | 18.5636
34 | -0.061935 | -0.015614 | 0.061955 | 0.015627 | 1.9931e-05 | 1.2674e-05 | 0.092296 | 0.092296 | 0.092296 | 0.99887 | -0.021582 | 0.99922 | -0.01486 | 25.3561
35 | 0.043509 | 0.010952 | -0.043483 | -0.010935 | 2.6723e-05 | 1.6883e-05 | 0.064987 | 0.064987 | 0.064987 | 0.9965 | -0.067184 | 0.99583 | -0.080042 | 17.8536
36 | 0.016383 | 0.0041087 | -0.016375 | -0.0041044 | 7.452e-06 | 4.3768e-06 | 0.025062 | 0.025063 | 0.025063 | 0.97273 | -0.52538 | 0.97225 | -0.53493 | 6.8853
37 | 0.011158 | 0.0027968 | -0.011157 | -0.0027963 | 1.0689e-06 | 5.6267e-07 | 0.01707 | 0.01707 | 0.01707 | 0.97273 | -0.52538 | 0.97263 | -0.52739 | 4.6895
38 | 0.016375 | 0.0041044 | -0.016374 | -0.0041036 | 1.2736e-06 | 7.4808e-07 | 0.025063 | 0.025063 | 0.025063 | 0.97225 | -0.53493 | 0.97217 | -0.53656 | 6.8853
39 | 0.0055704 | 0.001396 | -0.0055698 | -0.0013959 | 5.9624e-07 | 1.0992e-07 | 0.008522 | 0.0085221 | 0.0085221 | 0.97263 | -0.52739 | 0.97252 | -0.52964 | 2.3412
40 | 0.0011295 | 0.00028296 | -0.0011295 | -0.00028308 | 1.2285e-08 | -1.2804e-07 | 0.0017288 | 0.0017289 | 0.0017289 | 0.97217 | -0.53656 | 0.97216 | -0.53679 | 0.47497
41 | -0.0058041 | -0.0014533 | 0.0058047 | 0.0014534 | 6.2504e-07 | 1.1179e-07 | 0.0086733 | 0.0086732 | 0.0086733 | 0.99571 | -0.082304 | 0.99583 | -0.080042 | 2.3828
42 | 0.0049538 | 0.0012402 | -0.0049537 | -0.0012402 | 1.3564e-07 | 9.5756e-10 | 0.0074026 | 0.0074026 | 0.0074026 | 0.99571 | -0.082304 | 0.99568 | -0.082879 | 2.0337
43 | 0.037678 | 0.009482 | -0.037649 | -0.0094635 | 2.9411e-05 | 1.8502e-05 | 0.056314 | 0.056314 | 0.056314 | 0.99583 | -0.080042 | 0.99498 | -0.09639 | 15.4709
44 | 0.0021927 | 0.00054871 | -0.0021926 | -0.00054896 | 9.6145e-08 | -2.4904e-07 | 0.0032766 | 0.0032767 | 0.0032767 | 0.99568 | -0.082879 | 0.99563 | -0.083801 | 0.9002
45 | 0.002761 | 0.00069146 | -0.0027609 | -0.00069156 | 7.2367e-08 | -1.0111e-07 | 0.004126 | 0.0041261 | 0.0041261 | 0.99568 | -0.082879 | 0.99565 | -0.08343 | 1.1335
46 | 0.037649 | 0.0094635 | -0.037637 | -0.0094561 | 1.1749e-05 | 7.391e-06 | 0.056314 | 0.056314 | 0.056314 | 0.99498 | -0.09639 | 0.99464 | -0.10293 | 15.4709
47 | 0.0021926 | 0.00054896 | -0.0021925 | -0.00054906 | 4.0841e-08 | -1.0577e-07 | 0.0032767 | 0.0032768 | 0.0032768 | 0.99563 | -0.083801 | 0.99561 | -0.084192 | 0.90021
48 | 0.0021932 | 0.00054928 | -0.0021932 | -0.00054936 | 3.348e-08 | -8.6656e-08 | 0.0032776 | 0.0032776 | 0.0032776 | 0.99565 | -0.08343 | 0.99564 | -0.08375 | 0.90045
49 | -0.0017307 | -0.00043375 | 0.0017307 | 0.00043369 | 1.2636e-08 | -5.6674e-08 | 0.0025939 | 0.0025939 | 0.0025939 | 0.99281 | -0.13826 | 0.99282 | -0.13811 | 0.71262
50 | -0.0017307 | -0.00043369 | 0.0017307 | 0.00043363 | 1.3446e-08 | -6.0308e-08 | 0.0025939 | 0.0025939 | 0.0025939 | 0.99282 | -0.13811 | 0.99283 | -0.13795 | 0.71261
51 | -0.024813 | -0.0062224 | 0.024819 | 0.006226 | 5.7929e-06 | 3.563e-06 | 0.03719 | 0.03719 | 0.03719 | 0.99283 | -0.13795 | 0.99308 | -0.13305 | 10.2172
52 | 0.023083 | 0.0057888 | -0.023077 | -0.0057854 | 5.5742e-06 | 3.407e-06 | 0.034597 | 0.034597 | 0.034597 | 0.99283 | -0.13795 | 0.99257 | -0.14302 | 9.5046
53 | 0.036565 | 0.0091875 | -0.036557 | -0.0091825 | 7.9364e-06 | 4.9876e-06 | 0.054711 | 0.054711 | 0.054711 | 0.99464 | -0.10293 | 0.9944 | -0.10748 | 15.0304
54 | 0.00169 | 0.0004231 | -0.0016899 | -0.00042331 | 4.3671e-08 | -2.0945e-07 | 0.0025256 | 0.0025257 | 0.0025257 | 0.99561 | -0.084192 | 0.99559 | -0.084735 | 0.69388
55 | 0.0016659 | 0.00041722 | -0.0016659 | -0.00041731 | 1.8995e-08 | -9.4121e-08 | 0.0024896 | 0.0024897 | 0.0024897 | 0.99564 | -0.08375 | 0.99562 | -0.08399 | 0.68398
56 | -0.0018829 | -0.0004719 | 0.0018829 | 0.00047185 | 1.3146e-08 | -4.917e-08 | 0.002814 | 0.0028139 | 0.002814 | 0.99569 | -0.081573 | 0.99569 | -0.081426 | 0.77306
57 | -0.16006 | -0.040983 | 0.16015 | 0.041046 | 9.8194e-05 | 6.2607e-05 | 0.2395 | 0.2395 | 0.2395 | 0.99569 | -0.081426 | 0.99636 | -0.068769 | 32.8989
58 | 0.0075739 | 0.001897 | -0.0075736 | -0.0018969 | 3.4165e-07 | 1.2616e-07 | 0.011318 | 0.011318 | 0.011318 | 0.99569 | -0.081426 | 0.99564 | -0.082373 | 3.1095
59 | 0.1506 | 0.038614 | -0.15048 | -0.038539 | 0.0001172 | 7.4689e-05 | 0.22537 | 0.22537 | 0.22537 | 0.99569 | -0.081426 | 0.99485 | -0.097489 | 30.9577
60 | -0.16152 | -0.041387 | 0.16159 | 0.041431 | 6.837e-05 | 4.3594e-05 | 0.24154 | 0.24154 | 0.24154 | 0.99636 | -0.068769 | 0.99682 | -0.060039 | 33.1787
61 | 0.006215 | 0.0015563 | -0.0062142 | -0.0015562 | 7.7658e-07 | 1.8486e-07 | 0.009288 | 0.0092881 | 0.0092881 | 0.99564 | -0.082373 | 0.99551 | -0.084998 | 2.5517
62 | 0.14947 | 0.038286 | -0.14941 | -0.038249 | 5.8678e-05 | 3.7392e-05 | 0.22386 | 0.22386 | 0.22386 | 0.99485 | -0.097489 | 0.99442 | -0.10559 | 30.7502
63 | -0.094068 | -0.023831 | 0.094163 | 0.023891 | 9.4546e-05 | 6.0353e-05 | 0.14271 | 0.14271 | 0.14271 | 0.98145 | -0.35478 | 0.98252 | -0.33388 | 39.2069
64 | 0.011434 | 0.002866 | -0.011433 | -0.0028654 | 1.2806e-06 | 6.7243e-07 | 0.01723 | 0.01723 | 0.01723 | 0.98748 | -0.23825 | 0.98736 | -0.2406 | 4.7335
65 | -0.12844 | -0.032724 | 0.12844 | 0.032729 | 7.752e-06 | 4.9329e-06 | 0.19346 | 0.19346 | 0.19346 | 0.98885 | -0.21201 | 0.98891 | -0.21076 | 26.5744
66 | 0.006232 | 0.0015619 | -0.0062315 | -0.0015618 | 4.546e-07 | 1.1519e-07 | 0.009392 | 0.009392 | 0.009392 | 0.98736 | -0.2406 | 0.98728 | -0.24214 | 2.5802
67 | -0.0011212 | -0.00028101 | 0.0011213 | 0.00028091 | 8.5493e-09 | -1.0002e-07 | 0.0016761 | 0.0016761 | 0.0016761 | 0.9954 | -0.087063 | 0.99541 | -0.086903 | 0.46048
68 | -0.0021504 | -0.00053884 | 0.0021504 | 0.00053877 | 2.6123e-08 | -7.0913e-08 | 0.0032146 | 0.0032145 | 0.0032146 | 0.99541 | -0.086903 | 0.99542 | -0.086648 | 0.88313
69 | -0.0031081 | -0.00077878 | 0.0031082 | 0.00077864 | 1.4809e-07 | -1.4306e-07 | 0.0046461 | 0.004646 | 0.0046461 | 0.99542 | -0.086648 | 0.99548 | -0.085647 | 1.2764
70 | -0.004261 | -0.0010675 | 0.0042611 | 0.0010675 | 1.3178e-07 | -2.829e-08 | 0.0063691 | 0.006369 | 0.0063691 | 0.99548 | -0.085647 | 0.99551 | -0.084998 | 1.7497
71 | -0.0047614 | -0.001192 | 0.0047617 | 0.001192 | 3.3898e-07 | -1.2458e-08 | 0.0071372 | 0.0071371 | 0.0071372 | 0.99262 | -0.13996 | 0.9927 | -0.13846 | 1.9608
72 | 0.0037254 | 0.00093239 | -0.0037253 | -0.00093243 | 8.1295e-08 | -3.7835e-08 | 0.0055841 | 0.0055842 | 0.0055842 | 0.99262 | -0.13996 | 0.9926 | -0.14042 | 1.5341
73 | -0.0060127 | -0.0015055 | 0.0060129 | 0.0015056 | 2.5554e-07 | 5.507e-08 | 0.0090123 | 0.0090122 | 0.0090123 | 0.9927 | -0.13846 | 0.99275 | -0.13757 | 2.4759
74 | 0.0026903 | 0.00067304 | -0.0026902 | -0.00067315 | 7.6793e-08 | -1.1361e-07 | 0.0040326 | 0.0040327 | 0.0040327 | 0.9926 | -0.14042 | 0.99257 | -0.14102 | 1.1079
75 | -0.0060129 | -0.0015056 | 0.0060133 | 0.0015057 | 3.2382e-07 | 6.977e-08 | 0.0090122 | 0.0090122 | 0.0090122 | 0.99275 | -0.13757 | 0.99281 | -0.13644 | 2.4759
76 | 0.0026902 | 0.00067315 | -0.0026902 | -0.0006732 | 2.8828e-08 | -4.2646e-08 | 0.0040327 | 0.0040327 | 0.0040327 | 0.99257 | -0.14102 | 0.99256 | -0.14124 | 1.1079
77 | -0.011309 | -0.0028325 | 0.011311 | 0.0028338 | 2.5716e-06 | 1.3371e-06 | 0.016949 | 0.016949 | 0.016949 | 0.99281 | -0.13644 | 0.99305 | -0.13166 | 4.6563
78 | 0.0052955 | 0.0013268 | -0.0052951 | -0.0013268 | 4.2248e-07 | 3.9135e-08 | 0.0079367 | 0.0079368 | 0.0079368 | 0.99281 | -0.13644 | 0.99272 | -0.13811 | 2.1804
79 | 0.0026902 | 0.0006732 | -0.0026898 | -0.00067372 | 3.544e-07 | -5.2412e-07 | 0.0040327 | 0.004033 | 0.004033 | 0.99256 | -0.14124 | 0.99242 | -0.14401 | 1.108
80 | -0.064784 | -0.016336 | 0.06479 | 0.01634 | 6.8676e-06 | 4.3695e-06 | 0.096509 | 0.096509 | 0.096509 | 0.99922 | -0.01486 | 0.99934 | -0.012645 | 26.5134
81 | -0.012324 | -0.0030876 | 0.012325 | 0.003088 | 8.6266e-07 | 4.6481e-07 | 0.018466 | 0.018466 | 0.018466 | 0.99305 | -0.13166 | 0.99313 | -0.13019 | 5.073
82 | 0.0026898 | 0.00067372 | -0.0026897 | -0.0006739 | 1.2027e-07 | -1.7779e-07 | 0.004033 | 0.0040331 | 0.0040331 | 0.99242 | -0.14401 | 0.99237 | -0.14495 | 1.108
83 | 0.0026897 | 0.0006739 | -0.0026897 | -0.00067401 | 7.4064e-08 | -1.0947e-07 | 0.0040331 | 0.0040331 | 0.0040331 | 0.99237 | -0.14495 | 0.99234 | -0.14553 | 1.108
84 | 0.12951 | 0.033069 | -0.12945 | -0.03303 | 6.0917e-05 | 3.8766e-05 | 0.19478 | 0.19478 | 0.19478 | 0.99047 | -0.18083 | 0.98997 | -0.19057 | 26.7561
85 | -0.12951 | -0.033069 | 0.12957 | 0.03311 | 6.4646e-05 | 4.114e-05 | 0.19478 | 0.19478 | 0.19478 | 0.99047 | -0.18083 | 0.99101 | -0.17051 | 26.7561
86 | 0.12945 | 0.03303 | -0.12932 | -0.03295 | 0.00012609 | 8.0239e-05 | 0.19478 | 0.19478 | 0.19478 | 0.98997 | -0.19057 | 0.98891 | -0.21076 | 26.7562
87 | -0.13059 | -0.033363 | 0.13063 | 0.033392 | 4.5132e-05 | 2.8724e-05 | 0.1963 | 0.1963 | 0.1963 | 0.99101 | -0.17051 | 0.99139 | -0.16337 | 26.9649
88 | -0.00061138 | -0.00015323 | 0.00061138 | 0.00015314 | 2.2272e-09 | -9.1084e-08 | 0.00091375 | 0.00091372 | 0.00091375 | 0.99561 | -0.08423 | 0.99562 | -0.084154 | 0.25103
89 | -0.0011385 | -0.00028523 | 0.0011385 | 0.00028513 | 8.8755e-09 | -1.0064e-07 | 0.0017015 | 0.0017014 | 0.0017015 | 0.99562 | -0.084154 | 0.99562 | -0.08399 | 0.46744
90 | -0.004956 | -0.0012419 | 0.0049561 | 0.0012419 | 9.8419e-08 | 1.6036e-09 | 0.0074318 | 0.0074318 | 0.0074318 | 0.99229 | -0.14832 | 0.99231 | -0.1479 | 2.0417
91 | 0.003461 | 0.00086725 | -0.003461 | -0.00086725 | 4.8713e-10 | -3.0863e-10 | 0.00519 | 0.00519 | 0.00519 | 0.99229 | -0.14832 | 0.99229 | -0.14832 | 1.4258
92 | -0.0049561 | -0.0012419 | 0.0049563 | 0.0012419 | 2.1607e-07 | 3.5099e-09 | 0.0074318 | 0.0074317 | 0.0074318 | 0.99231 | -0.1479 | 0.99236 | -0.14699 | 2.0417
93 | 0.003461 | 0.00086725 | -0.0034609 | -0.00086736 | 1.7319e-07 | -1.1063e-07 | 0.00519 | 0.0051901 | 0.0051901 | 0.99229 | -0.14832 | 0.99224 | -0.14937 | 1.4259
94 | -0.0066878 | -0.0016759 | 0.0066881 | 0.001676 | 2.8525e-07 | 8.483e-08 | 0.010028 | 0.010028 | 0.010028 | 0.99236 | -0.14699 | 0.99241 | -0.14609 | 2.755
95 | 0.0017313 | 0.00043389 | -0.0017313 | -0.0004339 | 2.27e-09 | -1.0146e-08 | 0.0025963 | 0.0025963 | 0.0025963 | 0.99224 | -0.14937 | 0.99224 | -0.1494 | 0.71328
96 | -0.0084196 | -0.0021099 | 0.0084201 | 0.0021101 | 4.5217e-07 | 1.9163e-07 | 0.012624 | 0.012624 | 0.012624 | 0.99241 | -0.14609 | 0.99247 | -0.14496 | 3.4682
97 | 0.0014774 | 0.00037018 | -0.0014773 | -0.00037026 | 1.2468e-08 | -7.9545e-08 | 0.0022153 | 0.0022153 | 0.0022153 | 0.99234 | -0.14553 | 0.99233 | -0.1457 | 0.6086
98 | -0.067539 | -0.017029 | 0.067555 | 0.017039 | 1.6216e-05 | 1.0322e-05 | 0.1006 | 0.1006 | 0.1006 | 0.99934 | -0.012645 | 0.9996 | -0.0076298 | 27.6378
99 | -0.070384 | -0.017748 | 0.07041 | 0.017764 | 2.5713e-05 | 1.6375e-05 | 0.10481 | 0.10481 | 0.10481 | 0.9996 | -0.0076298 | 1 | 0 | 28.7946
100 | 0.17328 | 0.044553 | -0.17321 | -0.044503 | 7.8115e-05 | 4.9829e-05 | 0.25825 | 0.25825 | 0.25825 | 1 | 0 | 0.99951 | -0.0092808 | 35.4739
101 | 0.17037 | 0.043793 | -0.17026 | -0.043722 | 0.00011103 | 7.0821e-05 | 0.25403 | 0.25403 | 0.25403 | 0.99951 | -0.0092808 | 0.9988 | -0.022704 | 34.8946
102 | 0.002121 | 0.00053127 | -0.002121 | -0.00053131 | 1.384e-08 | -3.8139e-08 | 0.0031827 | 0.0031828 | 0.0031828 | 0.99159 | -0.16201 | 0.99158 | -0.16215 | 0.87439
103 | -0.0055072 | -0.0013799 | 0.0055079 | 0.00138 | 7.2997e-07 | 9.9466e-08 | 0.0082642 | 0.0082641 | 0.0082642 | 0.99159 | -0.16201 | 0.99173 | -0.15923 | 2.2704
104 | 0.002121 | 0.00053131 | -0.0021209 | -0.00053146 | 5.5875e-08 | -1.5396e-07 | 0.0031828 | 0.0031828 | 0.0031828 | 0.99158 | -0.16215 | 0.99155 | -0.1627 | 0.8744
105 | -0.0055079 | -0.00138 | 0.0055083 | 0.0013801 | 3.4678e-07 | 4.7212e-08 | 0.0082641 | 0.008264 | 0.0082641 | 0.99173 | -0.15923 | 0.9918 | -0.15791 | 2.2704
106 | 0.0010602 | 0.00026562 | -0.0010602 | -0.00026571 | 7.0016e-09 | -9.0655e-08 | 0.001591 | 0.001591 | 0.001591 | 0.99155 | -0.1627 | 0.99154 | -0.16284 | 0.4371
107 | -0.0065672 | -0.0016455 | 0.0065675 | 0.0016455 | 2.6983e-07 | 7.7032e-08 | 0.0098527 | 0.0098527 | 0.0098527 | 0.9918 | -0.15791 | 0.99184 | -0.15705 | 2.7068
108 | -0.0076257 | -0.0019108 | 0.0076261 | 0.0019109 | 3.637e-07 | 1.3713e-07 | 0.01144 | 0.01144 | 0.01144 | 0.99184 | -0.15705 | 0.99189 | -0.15605 | 3.143
109 | 0.0011429 | 0.00028621 | -0.0011429 | -0.00028632 | 9.5324e-09 | -1.0719e-07 | 0.0017081 | 0.0017081 | 0.0017081 | 0.99559 | -0.084735 | 0.99558 | -0.08491 | 0.46927
110 | 0.00058313 | 0.00014603 | -0.00058313 | -0.00014615 | 2.4985e-09 | -1.1246e-07 | 0.00087152 | 0.00087156 | 0.00087156 | 0.99558 | -0.08491 | 0.99557 | -0.085 | 0.23944
111 | 0.17026 | 0.043722 | -0.17017 | -0.043666 | 8.8441e-05 | 5.6411e-05 | 0.25403 | 0.25403 | 0.25403 | 0.9988 | -0.022704 | 0.99823 | -0.033409 | 34.8946
112 | 0.16735 | 0.042957 | -0.16727 | -0.04291 | 7.3032e-05 | 4.6577e-05 | 0.24982 | 0.24982 | 0.24982 | 0.99823 | -0.033409 | 0.99775 | -0.042405 | 34.3155
113 | -0.001953 | -0.00048896 | 0.0019531 | 0.00048866 | 8.974e-08 | -3.0768e-07 | 0.0029192 | 0.0029191 | 0.0029192 | 0.99546 | -0.085964 | 0.99551 | -0.084998 | 0.80198
114 | 0.001953 | 0.00048896 | -0.001953 | -0.00048905 | 2.586e-08 | -8.8649e-08 | 0.0029192 | 0.0029192 | 0.0029192 | 0.99546 | -0.085964 | 0.99544 | -0.086242 | 0.80199
115 | 0.0014505 | 0.00036313 | -0.0014505 | -0.00036334 | 3.1482e-08 | -2.12e-07 | 0.0021682 | 0.0021682 | 0.0021682 | 0.99544 | -0.086242 | 0.99542 | -0.086698 | 0.59567
116 | 0.0010327 | 0.00025863 | -0.0010327 | -0.00025872 | 6.1258e-09 | -8.5184e-08 | 0.0015437 | 0.0015438 | 0.0015438 | 0.99542 | -0.086698 | 0.99541 | -0.086822 | 0.42411
117 | 0.00058364 | 0.00014616 | -0.00058363 | -0.00014627 | 2.3928e-09 | -1.0744e-07 | 0.00087242 | 0.00087246 | 0.00087246 | 0.99541 | -0.086822 | 0.99541 | -0.086908 | 0.23969
118 | -0.010151 | -0.002544 | 0.010152 | 0.0025445 | 9.4246e-07 | 4.6296e-07 | 0.01522 | 0.01522 | 0.01522 | 0.99247 | -0.14496 | 0.99257 | -0.14302 | 4.1813
119 | 0.012925 | 0.0032409 | -0.012922 | -0.0032392 | 3.0042e-06 | 1.6469e-06 | 0.019377 | 0.019377 | 0.019377 | 0.99257 | -0.14302 | 0.99231 | -0.14789 | 5.3233
120 | 0.012922 | 0.0032392 | -0.01292 | -0.0032383 | 1.6963e-06 | 9.3003e-07 | 0.019377 | 0.019377 | 0.019377 | 0.99231 | -0.14789 | 0.99217 | -0.15065 | 5.3233
121 | -0.025877 | -0.0064913 | 0.02588 | 0.0064927 | 2.4102e-06 | 1.4872e-06 | 0.038776 | 0.038776 | 0.038776 | 0.99308 | -0.13305 | 0.99318 | -0.1311 | 10.6528
122 | 0.011861 | 0.0029731 | -0.011861 | -0.0029726 | 8.8109e-07 | 4.6802e-07 | 0.017789 | 0.017789 | 0.017789 | 0.99217 | -0.15065 | 0.99209 | -0.15221 | 4.8872
123 | 0.16444 | 0.042202 | -0.16437 | -0.042157 | 7.0588e-05 | 4.5013e-05 | 0.2456 | 0.2456 | 0.2456 | 0.99775 | -0.042405 | 0.99729 | -0.051255 | 33.736
124 | 0.16301 | 0.041816 | -0.16294 | -0.041772 | 6.9422e-05 | 4.4267e-05 | 0.24357 | 0.24357 | 0.24357 | 0.99729 | -0.051255 | 0.99682 | -0.060039 | 33.4574
125 | 0.1484 | 0.037995 | -0.14834 | -0.037958 | 5.7882e-05 | 3.6883e-05 | 0.22235 | 0.22235 | 0.22235 | 0.99442 | -0.10559 | 0.994 | -0.11365 | 30.5422
126 | 0.010802 | 0.0027073 | -0.010801 | -0.002707 | 7.2942e-07 | 3.7116e-07 | 0.016202 | 0.016202 | 0.016202 | 0.99209 | -0.15221 | 0.99202 | -0.15363 | 4.4511
127 | 0.0097438 | 0.0024419 | -0.0097432 | -0.0024416 | 5.9386e-07 | 2.8436e-07 | 0.014615 | 0.014615 | 0.014615 | 0.99202 | -0.15363 | 0.99195 | -0.15491 | 4.0152
128 | 0.0086849 | 0.0021764 | -0.0086844 | -0.0021762 | 4.7173e-07 | 2.0624e-07 | 0.013028 | 0.013028 | 0.013028 | 0.99195 | -0.15491 | 0.99189 | -0.15605 | 3.5791
129 | 0.14733 | 0.037705 | -0.14721 | -0.03763 | 0.00011791 | 7.5128e-05 | 0.22083 | 0.22083 | 0.22083 | 0.994 | -0.11365 | 0.99313 | -0.13019 | 30.3345
130 | 0.13489 | 0.034542 | -0.13481 | -0.034494 | 7.4781e-05 | 4.7608e-05 | 0.20237 | 0.20237 | 0.20237 | 0.99313 | -0.13019 | 0.99253 | -0.14165 | 27.798
131 | 0.1338 | 0.034241 | -0.13376 | -0.034211 | 4.7192e-05 | 3.0042e-05 | 0.20085 | 0.20085 | 0.20085 | 0.99253 | -0.14165 | 0.99214 | -0.14893 | 27.5899
132 | 0.13275 | 0.033958 | -0.1327 | -0.033928 | 4.6512e-05 | 2.9607e-05 | 0.19934 | 0.19934 | 0.19934 | 0.99214 | -0.14893 | 0.99177 | -0.15618 | 27.3817
133 | 0.13169 | 0.033675 | -0.13164 | -0.033645 | 4.5807e-05 | 2.9155e-05 | 0.19782 | 0.19782 | 0.19782 | 0.99177 | -0.15618 | 0.99139 | -0.16337 | 27.1732
134 | 0.0063498 | 0.0015911 | -0.0063497 | -0.0015911 | 1.181e-07 | 3.0554e-08 | 0.0095134 | 0.0095134 | 0.0095134 | 0.99318 | -0.1311 | 0.99316 | -0.13149 | 2.6136
135 | -0.03223 | -0.0080838 | 0.032246 | 0.0080944 | 1.682e-05 | 1.0516e-05 | 0.04829 | 0.04829 | 0.04829 | 0.99318 | -0.1311 | 0.99375 | -0.12015 | 13.2664
136 | 0.0052913 | 0.0013258 | -0.0052911 | -0.0013258 | 1.7467e-07 | 1.5884e-08 | 0.0079276 | 0.0079276 | 0.0079276 | 0.99316 | -0.13149 | 0.99313 | -0.13218 | 2.1779
137 | -0.033319 | -0.0083631 | 0.033325 | 0.0083672 | 6.5083e-06 | 4.075e-06 | 0.049895 | 0.049895 | 0.049895 | 0.99375 | -0.12015 | 0.99396 | -0.11606 | 13.7075
138 | 0.0042328 | 0.0010605 | -0.0042327 | -0.0010606 | 1.1178e-07 | -2.4353e-08 | 0.006342 | 0.006342 | 0.006342 | 0.99313 | -0.13218 | 0.9931 | -0.13273 | 1.7423
139 | -0.034397 | -0.0086358 | 0.034404 | 0.0086402 | 6.9369e-06 | 4.3492e-06 | 0.0515 | 0.0515 | 0.0515 | 0.99396 | -0.11606 | 0.99418 | -0.11183 | 14.1483
140 | 0.0031744 | 0.00079532 | -0.0031743 | -0.00079538 | 6.2881e-08 | -5.5661e-08 | 0.0047563 | 0.0047563 | 0.0047563 | 0.9931 | -0.13273 | 0.99308 | -0.13315 | 1.3067
141 | 0.0021161 | 0.00053016 | -0.002116 | -0.00053024 | 2.7951e-08 | -7.8039e-08 | 0.0031706 | 0.0031707 | 0.0031707 | 0.99308 | -0.13315 | 0.99306 | -0.13343 | 0.87106
142 | 0.0010584 | 0.00026516 | -0.0010583 | -0.00026525 | 6.9887e-09 | -9.1403e-08 | 0.0015858 | 0.0015859 | 0.0015859 | 0.99306 | -0.13343 | 0.99305 | -0.13357 | 0.43567
143 | -0.035478 | -0.0089092 | 0.035485 | 0.0089139 | 7.3765e-06 | 4.6305e-06 | 0.053107 | 0.053107 | 0.053107 | 0.99418 | -0.11183 | 0.9944 | -0.10748 | 14.5898

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.24818 | 0.063027

## res_load
| p_mw | q_mvar
0 | 0.01532 | 0.0038397
1 | 0.0040382 | 0.0010121
2 | 0.0048295 | 0.0012104
3 | 0.0018825 | 0.0004718
4 | 0.013323 | 0.0033391
5 | 0.0062364 | 0.001563
6 | 0.0025218 | 0.00063201
7 | 0.00224 | 0.00056139
8 | 0.0010318 | 0.0002586
9 | 0.0009932 | 0.00024892
10 | 0.0010631 | 0.00026645
11 | 0.0010282 | 0.00025768
12 | 0.0011784 | 0.00029534
13 | 0.0026649 | 0.00066788
14 | 0.0037566 | 0.0009415
15 | 0.0038678 | 0.00096935
16 | 0.0017314 | 0.00043392
17 | 0.0028288 | 0.00070897
18 | 0.0017305 | 0.0004337
19 | 0.0017307 | 0.00043375
20 | 0.019767 | 0.0049541
21 | 0.0041883 | 0.0010497
22 | 0.0055871 | 0.0014002
23 | 0.015245 | 0.0038207
24 | 0.0008503 | 0.00021311
25 | 0.00056772 | 0.00014228
26 | 0.0017307 | 0.00043375
27 | 0.0010719 | 0.00026864
28 | 0.00050258 | 0.00012596
29 | 0.00052726 | 0.00013214
30 | 0.0018829 | 0.0004719
31 | 0.0013637 | 0.00034178
32 | 0.0013586 | 0.0003405
33 | 0.0010103 | 0.0002532
34 | 0.0046881 | 0.001175
35 | 0.0090445 | 0.0022668
36 | 0.0052009 | 0.0013035
37 | 0.0011212 | 0.00028101
38 | 0.0010292 | 0.00025793
39 | 0.00095765 | 0.00024001
40 | 0.0011527 | 0.0002889
41 | 0.001036 | 0.00025965
42 | 0.0012509 | 0.00031352
43 | 0.001035 | 0.00025939
44 | 0.0028289 | 0.000709
45 | 0.0010124 | 0.00025374
46 | 0.0010123 | 0.00025371
47 | 0.00061138 | 0.00015323
48 | 0.00052707 | 0.0001321
49 | 0.00052741 | 0.00013218
50 | 0.001495 | 0.00037467
51 | 0.0017315 | 0.00043396
52 | 0.0017296 | 0.00043347
53 | 0.0017315 | 0.00043396
54 | 0.0017313 | 0.0004339
55 | 0.0011295 | 0.00028308
56 | 0.0012123 | 0.00030383
57 | 0.0014773 | 0.00037026
58 | 0.00087942 | 0.0002204
59 | 0.0027485 | 0.00068885
60 | 0.0028288 | 0.00070897
61 | 0.0028314 | 0.00070961
62 | 0.0028328 | 0.00070997
63 | 0.0033862 | 0.00084866
64 | 0.0010607 | 0.00026584
65 | 0.0010589 | 0.00026539
66 | 0.0010602 | 0.00026571
67 | 0.0010583 | 0.00026523
68 | 0.00054705 | 0.0001371
69 | 0.00055974 | 0.00014028
70 | 0.00058313 | 0.00014615
71 | 0.0028286 | 0.00070891
72 | 0.00050245 | 0.00012593
73 | 0.00041778 | 0.00010471
74 | 0.00044909 | 0.00011255
75 | 0.00058363 | 0.00014627
76 | 0.0017313 | 0.00043391
77 | 0.0010584 | 0.00026527
78 | 0.0010584 | 0.00026526
79 | 0.0055698 | 0.0013959
80 | 0.0028286 | 0.00070891
81 | 0.0013594 | 0.00034071
82 | 0.0013593 | 0.00034067
83 | 0.0010121 | 0.00025365
84 | 0.0010584 | 0.00026526
85 | 0.0010577 | 0.00026508
86 | 0.0010583 | 0.00026522
87 | 0.0010584 | 0.00026525
88 | 0.0010101 | 0.00025316
89 | 0.0010107 | 0.0002533
90 | 0.0010107 | 0.0002533
91 | 0.0010114 | 0.00025348
92 | 0.0010104 | 0.00025324
93 | 0.0010584 | 0.00026527
94 | 0.0010724 | 0.00026876
95 | 0.0010583 | 0.00026523
96 | 0.0010718 | 0.00026863
97 | 0.0010583 | 0.00026525
98 | 0.0010582 | 0.00026522
99 | 0.0010577 | 0.00026508
100 | 0.0010583 | 0.00026525
101 | 0.0010736 | 0.00026907
102 | 0.0010718 | 0.00026863
103 | 0.0062315 | 0.0015618

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1