## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-211_1_5_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_230-211_1_5_node_70 | 0.4 | n |  | TRUE
2 | bus_LV_230-211_1_5_node_71 | 0.4 | n |  | TRUE
3 | bus_LV_230-211_1_5_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_230-211_1_5_node_48 | 0.4 | n |  | TRUE
5 | bus_LV_230-211_1_5_node_112 | 0.4 | n |  | TRUE
6 | bus_LV_230-211_1_5_node_99 | 0.4 | n |  | TRUE
7 | bus_LV_230-211_1_5_node_111 | 0.4 | n |  | TRUE
8 | bus_LV_230-211_1_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_230-211_1_5_node_66 | 0.4 | n |  | TRUE
10 | bus_LV_230-211_1_5_node_67 | 0.4 | n |  | TRUE
11 | bus_LV_230-211_1_5_node_63 | 0.4 | n |  | TRUE
12 | bus_LV_230-211_1_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_230-211_1_5_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_230-211_1_5_node_62 | 0.4 | n |  | TRUE
15 | bus_LV_230-211_1_5_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_230-211_1_5_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_230-211_1_5_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_230-211_1_5_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_230-211_1_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_230-211_1_5_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_230-211_1_5_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_230-211_1_5_node_52 | 0.4 | n |  | TRUE
23 | bus_LV_230-211_1_5_node_87 | 0.4 | n |  | TRUE
24 | bus_LV_230-211_1_5_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_230-211_1_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_230-211_1_5_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_230-211_1_5_node_89 | 0.4 | n |  | TRUE
28 | bus_LV_230-211_1_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_230-211_1_5_node_182 | 0.4 | n |  | TRUE
30 | bus_LV_230-211_1_5_node_181 | 0.4 | n |  | TRUE
31 | bus_LV_230-211_1_5_node_82 | 0.4 | n |  | TRUE
32 | bus_LV_230-211_1_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_230-211_1_5_node_84 | 0.4 | n |  | TRUE
34 | bus_LV_230-211_1_5_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_230-211_1_5_node_83 | 0.4 | n |  | TRUE
36 | bus_LV_230-211_1_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_230-211_1_5_node_92 | 0.4 | n |  | TRUE
38 | bus_LV_230-211_1_5_node_90 | 0.4 | n |  | TRUE
39 | bus_LV_230-211_1_5_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_230-211_1_5_node_100 | 0.4 | n |  | TRUE
41 | bus_LV_230-211_1_5_node_72 | 0.4 | n |  | TRUE
42 | bus_LV_230-211_1_5_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_230-211_1_5_node_98 | 0.4 | n |  | TRUE
44 | bus_LV_230-211_1_5_node_110 | 0.4 | n |  | TRUE
45 | bus_LV_230-211_1_5_node_238 | 0.4 | n |  | TRUE
46 | bus_LV_230-211_1_5_node_94 | 0.4 | n |  | TRUE
47 | bus_LV_230-211_1_5_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_230-211_1_5_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_230-211_1_5_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_230-211_1_5_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_230-211_1_5_node_88 | 0.4 | n |  | TRUE
52 | bus_LV_230-211_1_5_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_230-211_1_5_node_183 | 0.4 | n |  | TRUE
54 | bus_LV_230-211_1_5_node_227 | 0.4 | n |  | TRUE
55 | bus_LV_230-211_1_5_node_214 | 0.4 | n |  | TRUE
56 | bus_LV_230-211_1_5_node_213 | 0.4 | n |  | TRUE
57 | bus_LV_230-211_1_5_node_170 | 0.4 | n |  | TRUE
58 | bus_LV_230-211_1_5_node_81 | 0.4 | n |  | TRUE
59 | bus_LV_230-211_1_5_node_79 | 0.4 | n |  | TRUE
60 | bus_LV_230-211_1_5_node_80 | 0.4 | n |  | TRUE
61 | bus_LV_230-211_1_5_node_240 | 0.4 | n |  | TRUE
62 | bus_LV_230-211_1_5_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_230-211_1_5_node_242 | 0.4 | n |  | TRUE
64 | bus_LV_230-211_1_5_node_95 | 0.4 | n |  | TRUE
65 | bus_LV_230-211_1_5_node_91 | 0.4 | n |  | TRUE
66 | bus_LV_230-211_1_5_node_101 | 0.4 | n |  | TRUE
67 | bus_LV_230-211_1_5_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_230-211_1_5_node_77 | 0.4 | n |  | TRUE
69 | bus_LV_230-211_1_5_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_230-211_1_5_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_230-211_1_5_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_230-211_1_5_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_230-211_1_5_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_230-211_1_5_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_230-211_1_5_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_230-211_1_5_node_104 | 0.4 | n |  | TRUE
77 | bus_LV_230-211_1_5_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_230-211_1_5_node_171 | 0.4 | n |  | TRUE
79 | bus_LV_230-211_1_5_node_106 | 0.4 | n |  | TRUE
80 | bus_LV_230-211_1_5_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_230-211_1_5_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_230-211_1_5_node_45 | 0.4 | n |  | TRUE
83 | bus_LV_230-211_1_5_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_230-211_1_5_node_53 | 0.4 | n |  | TRUE
85 | bus_LV_230-211_1_5_node_54 | 0.4 | n |  | TRUE
86 | bus_LV_230-211_1_5_node_55 | 0.4 | n |  | TRUE
87 | bus_LV_230-211_1_5_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_230-211_1_5_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_230-211_1_5_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_230-211_1_5_node_57 | 0.4 | n |  | TRUE
91 | bus_LV_230-211_1_5_node_59 | 0.4 | n |  | TRUE
92 | bus_LV_230-211_1_5_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_230-211_1_5_node_229 | 0.4 | n |  | TRUE
94 | bus_LV_230-211_1_5_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_230-211_1_5_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_230-211_1_5_node_241 | 0.4 | n |  | TRUE
97 | bus_LV_230-211_1_5_node_103 | 0.4 | n |  | TRUE
98 | bus_LV_230-211_1_5_node_102 | 0.4 | n |  | TRUE
99 | bus_LV_230-211_1_5_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_230-211_1_5_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_230-211_1_5_node_235 | 0.4 | n |  | TRUE
102 | bus_LV_230-211_1_5_node_243 | 0.4 | n |  | TRUE
103 | bus_LV_230-211_1_5_node_236 | 0.4 | n |  | TRUE
104 | bus_LV_230-211_1_5_node_244 | 0.4 | n |  | TRUE
105 | bus_LV_230-211_1_5_node_157 | 0.4 | n |  | TRUE
106 | bus_LV_230-211_1_5_node_158 | 0.4 | n |  | TRUE
107 | bus_LV_230-211_1_5_node_159 | 0.4 | n |  | TRUE
108 | bus_LV_230-211_1_5_node_160 | 0.4 | n |  | TRUE
109 | bus_LV_230-211_1_5_node_166 | 0.4 | n |  | TRUE
110 | bus_LV_230-211_1_5_node_161 | 0.4 | n |  | TRUE
111 | bus_LV_230-211_1_5_node_163 | 0.4 | n |  | TRUE
112 | bus_LV_230-211_1_5_node_164 | 0.4 | n |  | TRUE
113 | bus_LV_230-211_1_5_node_178 | 0.4 | n |  | TRUE
114 | bus_LV_230-211_1_5_node_184 | 0.4 | n |  | TRUE
115 | bus_LV_230-211_1_5_node_165 | 0.4 | n |  | TRUE
116 | bus_LV_230-211_1_5_node_167 | 0.4 | n |  | TRUE
117 | bus_LV_230-211_1_5_node_168 | 0.4 | n |  | TRUE
118 | bus_LV_230-211_1_5_node_172 | 0.4 | n |  | TRUE
119 | bus_LV_230-211_1_5_node_248 | 0.4 | n |  | TRUE
120 | bus_LV_230-211_1_5_node_247 | 0.4 | n |  | TRUE
121 | bus_LV_230-211_1_5_node_249 | 0.4 | n |  | TRUE
122 | bus_LV_230-211_1_5_node_176 | 0.4 | n |  | TRUE
123 | bus_LV_230-211_1_5_node_179 | 0.4 | n |  | TRUE
124 | bus_LV_230-211_1_5_node_216 | 0.4 | n |  | TRUE
125 | bus_LV_230-211_1_5_node_185 | 0.4 | n |  | TRUE
126 | bus_LV_230-211_1_5_node_215 | 0.4 | n |  | TRUE
127 | bus_LV_230-211_1_5_node_228 | 0.4 | n |  | TRUE
128 | bus_LV_230-211_1_5_node_221 | 0.4 | n |  | TRUE
129 | bus_LV_230-211_1_5_node_211 | 0.4 | n |  | TRUE
130 | bus_LV_230-211_1_5_node_186 | 0.4 | n |  | TRUE
131 | bus_LV_230-211_1_5_node_222 | 0.4 | n |  | TRUE
132 | bus_LV_230-211_1_5_node_223 | 0.4 | n |  | TRUE
133 | bus_LV_230-211_1_5_node_212 | 0.4 | n |  | TRUE
134 | bus_LV_230-211_1_5_node_220 | 0.4 | n |  | TRUE
135 | bus_LV_230-211_1_5_node_217 | 0.4 | n |  | TRUE
136 | bus_LV_230-211_1_5_node_218 | 0.4 | n |  | TRUE
137 | bus_LV_230-211_1_5_node_219 | 0.4 | n |  | TRUE
138 | bus_LV_230-211_1_5_node_224 | 0.4 | n |  | TRUE
139 | bus_LV_230-211_1_5_node_225 | 0.4 | n |  | TRUE
140 | bus_LV_230-211_1_5_node_237 | 0.4 | n |  | TRUE
141 | bus_LV_230-211_1_5_node_239 | 0.4 | n |  | TRUE
142 | bus_LV_230-211_1_5_node_245 | 0.4 | n |  | TRUE
143 | bus_MV_511_0_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-211_1_5_load_70 | 1 | 0.0014611 | 0.00036618 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-211_1_5_load_71 | 2 | 0.0059569 | 0.0014929 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-211_1_5_load_48 | 4 | 0.0016415 | 0.00041139 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-211_1_5_load_112 | 5 | 0.0039498 | 0.00098992 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-211_1_5_load_99 | 6 | 0.0014878 | 0.00037287 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-211_1_5_load_111 | 7 | 0.0015708 | 0.00039367 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-211_1_5_load_66 | 9 | 0.0012395 | 0.00031066 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-211_1_5_load_63 | 11 | 0.0017473 | 0.00043791 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-211_1_5_load_65 | 13 | 0.0016377 | 0.00041044 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-211_1_5_load_62 | 14 | 0.002327 | 0.00058321 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-211_1_5_load_34 | 16 | 0.0011249 | 0.00028194 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-211_1_5_load_35 | 17 | 0.0011249 | 0.00028194 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-211_1_5_load_33 | 18 | 0.0017786 | 0.00044576 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-211_1_5_load_52 | 22 | 0.0010981 | 0.00027521 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-211_1_5_load_87 | 23 | 0.0033126 | 0.00083022 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-211_1_5_load_50 | 24 | 0.00084243 | 0.00021113 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-211_1_5_load_89 | 27 | 0.0010964 | 0.0002748 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-211_1_5_load_181 | 30 | 0.0012411 | 0.00031104 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-211_1_5_load_82 | 31 | 0.0015599 | 0.00039095 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-211_1_5_load_84 | 33 | 0.001407 | 0.00035262 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-211_1_5_load_83 | 35 | 0.0025853 | 0.00064793 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-211_1_5_load_92 | 37 | 0.0012987 | 0.00032549 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-211_1_5_load_90 | 38 | 0.0015244 | 0.00038204 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-211_1_5_load_32 | 39 | 0.0015438 | 0.00038692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-211_1_5_load_100 | 40 | 0.0013224 | 0.00033143 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-211_1_5_load_72 | 41 | 0.0012417 | 0.00031121 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-211_1_5_load_46 | 42 | 0.0021048 | 0.00052751 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-211_1_5_load_98 | 43 | 0.001284 | 0.00032181 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-211_1_5_load_110 | 44 | 0.002489 | 0.00062379 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-211_1_5_load_238 | 45 | 0.0012059 | 0.00030222 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-211_1_5_load_94 | 46 | 0.0015238 | 0.0003819 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-211_1_5_load_69 | 47 | 0.0019094 | 0.00047855 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-211_1_5_load_36 | 48 | 0.0035758 | 0.00089617 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-211_1_5_load_37 | 49 | 0.0014258 | 0.00035735 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-211_1_5_load_51 | 50 | 0.0067278 | 0.0016861 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-211_1_5_load_88 | 51 | 0.00112 | 0.0002807 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-211_1_5_load_49 | 52 | 0.0015539 | 0.00038945 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-211_1_5_load_227 | 54 | 0.0010009 | 0.00025086 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-211_1_5_load_214 | 55 | 0.00021839 | 5.4734e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-211_1_5_load_170 | 57 | 0.0023148 | 0.00058014 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-211_1_5_load_81 | 58 | 0.0015599 | 0.00039095 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-211_1_5_load_79 | 59 | 0.0013856 | 0.00034726 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-211_1_5_load_240 | 61 | 0.0013125 | 0.00032895 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-211_1_5_load_78 | 62 | 0.0025832 | 0.00064741 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-211_1_5_load_242 | 63 | 0.0014528 | 0.0003641 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-211_1_5_load_95 | 64 | 0.0013685 | 0.00034299 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-211_1_5_load_101 | 66 | 0.0015739 | 0.00039446 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-211_1_5_load_76 | 67 | 0.0011924 | 0.00029884 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-211_1_5_load_77 | 68 | 0.0013256 | 0.00033223 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-211_1_5_load_38 | 69 | 0.0014748 | 0.00036961 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-211_1_5_load_39 | 70 | 0.0014435 | 0.00036178 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-211_1_5_load_40 | 71 | 0.0018539 | 0.00046462 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-211_1_5_load_41 | 72 | 0.0011039 | 0.00027667 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-211_1_5_load_42 | 73 | 0.0017373 | 0.00043541 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-211_1_5_load_43 | 74 | 0.0011058 | 0.00027714 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-211_1_5_load_44 | 75 | 0.0024979 | 0.00062604 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-211_1_5_load_104 | 76 | 0.0011101 | 0.00027823 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-211_1_5_load_171 | 78 | 0.017003 | 0.0042615 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-211_1_5_load_106 | 79 | 0.0011077 | 0.00027762 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-211_1_5_load_61 | 80 | 0.0034529 | 0.00086537 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-211_1_5_load_58 | 81 | 0.0021705 | 0.00054398 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-211_1_5_load_45 | 82 | 0.0017582 | 0.00044064 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-211_1_5_load_47 | 83 | 0.0014239 | 0.00035686 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-211_1_5_load_53 | 84 | 0.0010823 | 0.00027124 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-211_1_5_load_54 | 85 | 0.001093 | 0.00027392 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-211_1_5_load_55 | 86 | 0.0011068 | 0.00027739 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-211_1_5_load_75 | 87 | 0.0011386 | 0.00028535 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-211_1_5_load_74 | 88 | 0.0011163 | 0.00027977 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-211_1_5_load_73 | 89 | 0.0011065 | 0.00027731 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-211_1_5_load_57 | 90 | 0.0018161 | 0.00045517 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-211_1_5_load_59 | 91 | 0.0018005 | 0.00045126 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-211_1_5_load_60 | 92 | 0.0021877 | 0.00054828 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-211_1_5_load_229 | 93 | 0.0019178 | 0.00048065 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-211_1_5_load_85 | 94 | 0.0014886 | 0.00037309 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-211_1_5_load_86 | 95 | 0.0020262 | 0.00050782 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-211_1_5_load_241 | 96 | 0.0054423 | 0.001364 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-211_1_5_load_103 | 97 | 0.0015621 | 0.00039151 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-211_1_5_load_102 | 98 | 0.0012766 | 0.00031995 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-211_1_5_load_93 | 99 | 0.0012997 | 0.00032573 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-211_1_5_load_96 | 100 | 0.0012972 | 0.0003251 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-211_1_5_load_235 | 101 | 0.0012987 | 0.00032548 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-211_1_5_load_243 | 102 | 0.0012983 | 0.00032538 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-211_1_5_load_236 | 103 | 0.0012978 | 0.00032525 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-211_1_5_load_244 | 104 | 0.0012978 | 0.00032525 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-211_1_5_load_157 | 105 | 0.0039943 | 0.0010011 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-211_1_5_load_158 | 106 | 0.0034986 | 0.00087683 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-211_1_5_load_159 | 107 | 0.0039813 | 0.0009978 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-211_1_5_load_160 | 108 | 0.0053442 | 0.0013394 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-211_1_5_load_161 | 110 | 0.0014376 | 0.00036031 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-211_1_5_load_163 | 111 | 0.0028543 | 0.00071535 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_230-211_1_5_load_164 | 112 | 0.0020257 | 0.00050768 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_230-211_1_5_load_178 | 113 | 0.006068 | 0.0015208 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_230-211_1_5_load_184 | 114 | 0.0017547 | 0.00043977 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_230-211_1_5_load_165 | 115 | 0.0039498 | 0.00098992 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_230-211_1_5_load_167 | 116 | 0.001385 | 0.00034712 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_230-211_1_5_load_247 | 120 | 0.0013033 | 0.00032665 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_230-211_1_5_load_249 | 121 | 0.0045517 | 0.0011408 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_230-211_1_5_load_176 | 122 | 0.0057582 | 0.0014431 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_230-211_1_5_load_179 | 123 | 0.005762 | 0.0014441 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_230-211_1_5_load_216 | 124 | 0.0026402 | 0.00066171 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_230-211_1_5_load_185 | 125 | 0.0018339 | 0.00045962 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_230-211_1_5_load_215 | 126 | 0.0026429 | 0.00066237 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_230-211_1_5_load_228 | 127 | 0.0010022 | 0.00025118 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_230-211_1_5_load_221 | 128 | 0.00021825 | 5.4699e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_230-211_1_5_load_211 | 129 | 0.00043285 | 0.00010848 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_230-211_1_5_load_186 | 130 | 0.0041184 | 0.0010322 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_230-211_1_5_load_222 | 131 | 0.0018849 | 0.00047241 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_230-211_1_5_load_223 | 132 | 0.0015899 | 0.00039846 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_230-211_1_5_load_212 | 133 | 0.0002123 | 5.3207e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_230-211_1_5_load_220 | 134 | 0.003206 | 0.00080351 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_230-211_1_5_load_217 | 135 | 0.0025725 | 0.00064472 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_230-211_1_5_load_218 | 136 | 0.00262 | 0.00065664 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_230-211_1_5_load_219 | 137 | 0.0025574 | 0.00064095 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_230-211_1_5_load_224 | 138 | 0.00095773 | 0.00024003 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_230-211_1_5_load_225 | 139 | 0.00095773 | 0.00024003 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_230-211_1_5_load_237 | 140 | 0.0012989 | 0.00032553 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_230-211_1_5_load_239 | 141 | 0.0012976 | 0.0003252 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_230-211_1_5_load_245 | 142 | 0.0012989 | 0.00032553 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-211_1_5_line_0 |  | 0 | 1 | 0.014393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-211_1_5_line_1 |  | 0 | 2 | 0.01363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-211_1_5_line_2 |  | 0 | 3 | 0.043312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-211_1_5_line_3 |  | 0 | 4 | 0.034867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-211_1_5_line_4 |  | 1 | 41 | 0.011437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-211_1_5_line_5 |  | 3 | 5 | 0.011696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-211_1_5_line_6 |  | 3 | 6 | 0.011106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-211_1_5_line_7 |  | 3 | 7 | 0.0098326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-211_1_5_line_8 |  | 4 | 42 | 0.0098958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-211_1_5_line_9 |  | 6 | 43 | 0.01024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-211_1_5_line_10 |  | 7 | 44 | 0.013017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-211_1_5_line_11 |  | 8 | 9 | 0.046117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-211_1_5_line_12 |  | 8 | 10 | 0.006612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-211_1_5_line_13 |  | 8 | 11 | 0.0047083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-211_1_5_line_14 |  | 9 | 45 | 0.00015448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-211_1_5_line_15 |  | 10 | 46 | 0.013038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-211_1_5_line_16 |  | 10 | 44 | 0.057287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-211_1_5_line_17 |  | 11 | 14 | 0.018611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-211_1_5_line_18 |  | 12 | 13 | 0.016584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-211_1_5_line_19 |  | 12 | 14 | 0.01427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-211_1_5_line_20 |  | 13 | 47 | 0.0053382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-211_1_5_line_21 |  | 15 | 16 | 0.020883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-211_1_5_line_22 |  | 15 | 17 | 0.025074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-211_1_5_line_23 |  | 15 | 18 | 0.018584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-211_1_5_line_24 |  | 16 | 48 | 0.017628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-211_1_5_line_25 |  | 17 | 49 | 0.0092501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-211_1_5_line_26 |  | 19 | 20 | 0.035789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-211_1_5_line_27 |  | 19 | 21 | 0.015534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-211_1_5_line_28 |  | 19 | 22 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-211_1_5_line_29 |  | 20 | 23 | 0.029348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-211_1_5_line_30 |  | 21 | 24 | 0.0413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-211_1_5_line_31 |  | 22 | 50 | 0.0061408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-211_1_5_line_32 |  | 23 | 51 | 0.001693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-211_1_5_line_33 |  | 24 | 52 | 0.011222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-211_1_5_line_34 |  | 25 | 26 | 0.025862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-211_1_5_line_35 |  | 25 | 27 | 0.039503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-211_1_5_line_36 |  | 26 | 31 | 0.072809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-211_1_5_line_37 |  | 27 | 51 | 0.017314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-211_1_5_line_38 |  | 28 | 29 | 0.091113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-211_1_5_line_39 |  | 28 | 30 | 0.053526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-211_1_5_line_40 |  | 29 | 53 | 0.023609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-211_1_5_line_41 |  | 29 | 54 | 0.042617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-211_1_5_line_42 |  | 30 | 57 | 0.0056771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-211_1_5_line_43 |  | 31 | 58 | 0.027223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-211_1_5_line_44 |  | 32 | 33 | 0.0093147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-211_1_5_line_45 |  | 32 | 34 | 0.013483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-211_1_5_line_46 |  | 33 | 61 | 0.0060325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-211_1_5_line_47 |  | 34 | 35 | 0.013723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-211_1_5_line_48 |  | 35 | 62 | 0.027438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-211_1_5_line_49 |  | 36 | 37 | 0.013608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-211_1_5_line_50 |  | 36 | 38 | 0.012995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-211_1_5_line_51 |  | 37 | 64 | 0.00014855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-211_1_5_line_52 |  | 38 | 65 | 0.018521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-211_1_5_line_53 |  | 39 | 40 | 0.0021942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-211_1_5_line_54 |  | 40 | 66 | 0.0059066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-211_1_5_line_55 |  | 41 | 94 | 0.019559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-211_1_5_line_56 |  | 42 | 82 | 0.019977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-211_1_5_line_57 |  | 43 | 49 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-211_1_5_line_58 |  | 45 | 63 | 0.00046196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-211_1_5_line_59 |  | 46 | 65 | 0.014277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-211_1_5_line_60 |  | 47 | 93 | 0.011675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-211_1_5_line_61 |  | 48 | 67 | 0.016325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-211_1_5_line_62 |  | 50 | 84 | 0.00043835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-211_1_5_line_63 |  | 52 | 83 | 0.019201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-211_1_5_line_64 |  | 53 | 55 | 0.071959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-211_1_5_line_65 |  | 53 | 56 | 0.018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-211_1_5_line_66 |  | 54 | 127 | 0.0058566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-211_1_5_line_67 |  | 55 | 128 | 5.0487e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-211_1_5_line_68 |  | 56 | 129 | 0.022717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-211_1_5_line_69 |  | 57 | 116 | 0.014415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-211_1_5_line_70 |  | 58 | 60 | 0.040605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-211_1_5_line_71 |  | 59 | 60 | 0.009207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-211_1_5_line_72 |  | 61 | 96 | 0.0018328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-211_1_5_line_73 |  | 62 | 68 | 0.0098444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-211_1_5_line_74 |  | 64 | 101 | 0.0068238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-211_1_5_line_75 |  | 65 | 99 | 0.014577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-211_1_5_line_76 |  | 66 | 98 | 0.005539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-211_1_5_line_77 |  | 67 | 68 | 0.0034071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-211_1_5_line_78 |  | 69 | 70 | 0.00026687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-211_1_5_line_79 |  | 69 | 71 | 0.014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-211_1_5_line_80 |  | 70 | 72 | 0.022691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-211_1_5_line_81 |  | 71 | 73 | 0.00037942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-211_1_5_line_82 |  | 72 | 74 | 8.6207e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_230-211_1_5_line_83 |  | 73 | 75 | 0.031401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-211_1_5_line_84 |  | 74 | 76 | 5.625e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-211_1_5_line_85 |  | 75 | 77 | 0.040639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_230-211_1_5_line_86 |  | 75 | 78 | 0.073585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_230-211_1_5_line_87 |  | 76 | 79 | 0.00010586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-211_1_5_line_88 |  | 77 | 80 | 0.016931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_230-211_1_5_line_89 |  | 77 | 81 | 0.014153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-211_1_5_line_90 |  | 78 | 106 | 0.017633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-211_1_5_line_91 |  | 80 | 89 | 0.03 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_230-211_1_5_line_92 |  | 81 | 90 | 0.011182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-211_1_5_line_93 |  | 82 | 83 | 0.0091767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-211_1_5_line_94 |  | 84 | 85 | 0.0066565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-211_1_5_line_95 |  | 85 | 86 | 0.0065803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-211_1_5_line_96 |  | 86 | 87 | 0.0067647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_230-211_1_5_line_97 |  | 87 | 88 | 0.0066913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_230-211_1_5_line_98 |  | 88 | 89 | 0.0067266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-211_1_5_line_99 |  | 90 | 91 | 0.00083633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-211_1_5_line_100 |  | 91 | 92 | 0.010587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_230-211_1_5_line_101 |  | 94 | 95 | 0.01114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_230-211_1_5_line_102 |  | 95 | 97 | 0.016161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-211_1_5_line_103 |  | 97 | 98 | 0.0015385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-211_1_5_line_104 |  | 99 | 100 | 0.0069725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-211_1_5_line_105 |  | 100 | 102 | 0.0069718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-211_1_5_line_106 |  | 101 | 103 | 0.0069699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-211_1_5_line_107 |  | 102 | 104 | 0.00697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-211_1_5_line_108 |  | 103 | 140 | 0.0069705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-211_1_5_line_109 |  | 104 | 142 | 0.0069707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-211_1_5_line_110 |  | 105 | 106 | 0.025979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-211_1_5_line_111 |  | 105 | 107 | 0.016955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_230-211_1_5_line_112 |  | 106 | 108 | 0.04655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_230-211_1_5_line_113 |  | 107 | 109 | 0.0085395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-211_1_5_line_114 |  | 109 | 117 | 0.010142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-211_1_5_line_115 |  | 109 | 110 | 0.01203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-211_1_5_line_116 |  | 110 | 111 | 0.0076936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-211_1_5_line_117 |  | 111 | 112 | 0.019296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-211_1_5_line_118 |  | 112 | 115 | 0.0016416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_230-211_1_5_line_119 |  | 113 | 114 | 0.030264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-211_1_5_line_120 |  | 114 | 125 | 0.0084159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-211_1_5_line_121 |  | 115 | 116 | 0.030439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-211_1_5_line_122 |  | 117 | 118 | 0.028718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-211_1_5_line_123 |  | 118 | 119 | 0.018077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-211_1_5_line_124 |  | 118 | 120 | 0.009937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-211_1_5_line_125 |  | 119 | 121 | 0.011946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_230-211_1_5_line_126 |  | 122 | 123 | 0.017011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-211_1_5_line_127 |  | 123 | 124 | 0.024176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-211_1_5_line_128 |  | 124 | 126 | 5.135e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_230-211_1_5_line_129 |  | 125 | 130 | 0.014901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_230-211_1_5_line_130 |  | 126 | 135 | 0.00062863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_230-211_1_5_line_131 |  | 127 | 139 | 0.016406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_230-211_1_5_line_132 |  | 128 | 134 | 0.024817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_230-211_1_5_line_133 |  | 129 | 133 | 0.014087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_230-211_1_5_line_134 |  | 130 | 131 | 0.0034056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-211_1_5_line_135 |  | 131 | 132 | 0.0090503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-211_1_5_line_136 |  | 132 | 138 | 0.019711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_230-211_1_5_line_137 |  | 134 | 137 | 0.0014716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_230-211_1_5_line_138 |  | 135 | 136 | 0.025498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_230-211_1_5_line_139 |  | 136 | 137 | 3.7033e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_230-211_1_5_line_140 |  | 138 | 139 | 0.0085834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_230-211_1_5_line_141 |  | 140 | 141 | 0.0051876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-211_1_5_trafo_56 | 0.63 MVA 20/0.4 kV | 143 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2699710.8824 | 1263598.4114 | 2699708.5719 | 1263612.6182
1 | 2699697.3806 | 1263596.2709 | 2699710.8824 | 1263598.4114
2 | 2699710.8824 | 1263598.4114 | 2699715.5108 | 1263599.1456 | 2699718.224 | 1263578.5409 | 2699720.992 | 1263565.8549 | 2699725.7112 | 1263567.0132
3 | 2699710.8824 | 1263598.4114 | 2699711.6306 | 1263593.8091 | 2699713.9913 | 1263577.5799 | 2699716.8065 | 1263565.2171 | 2699717.1121 | 1263564.1347
4 | 2699706.8329 | 1263623.9223 | 2699708.1338 | 1263615.3123 | 2699708.5719 | 1263612.6182
5 | 2699737.0999 | 1263569.8187 | 2699725.7112 | 1263567.0132
6 | 2699725.7112 | 1263567.0132 | 2699728.7307 | 1263556.3254
7 | 2699725.7112 | 1263567.0132 | 2699723.6892 | 1263576.6357
8 | 2699719.8002 | 1263554.611 | 2699717.1121 | 1263564.1347
9 | 2699732.1252 | 1263546.6698 | 2699729.3007 | 1263554.3077 | 2699728.7307 | 1263556.3254
10 | 2699723.6892 | 1263576.6357 | 2699722.9752 | 1263580.0334 | 2699721.3928 | 1263589.4468
11 | 2699716.0151 | 1263651.8532 | 2699721.0512 | 1263652.5276 | 2699761.6335 | 1263658.6089
12 | 2699716.0151 | 1263651.8532 | 2699717.1871 | 1263645.3454
13 | 2699716.0151 | 1263651.8532 | 2699715.1835 | 1263656.4875 | 2699715.1835 | 1263656.4875
14 | 2699761.6335 | 1263658.6089 | 2699761.7863 | 1263658.6318
15 | 2699717.1871 | 1263645.3454 | 2699719.9949 | 1263647.261 | 2699724.5195 | 1263648.3381 | 2699729.4428 | 1263649.1382
16 | 2699717.1871 | 1263645.3454 | 2699714.9371 | 1263642.5162 | 2699714.3107 | 1263639.0138 | 2699714.3104 | 1263635.0105 | 2699720.7141 | 1263593.4842 | 2699721.3928 | 1263589.4468
17 | 2699715.1835 | 1263656.4875 | 2699713.0105 | 1263657.1291 | 2699711.2941 | 1263658.8461 | 2699710.2756 | 1263661.1641 | 2699709.6811 | 1263663.3559 | 2699709.2748 | 1263666.4516 | 2699708.3483 | 1263672.3724
18 | 2699706.1421 | 1263686.4709 | 2699722.5093 | 1263689.1461
19 | 2699706.1421 | 1263686.4709 | 2699708.3483 | 1263672.3724
20 | 2699727.7776 | 1263690.0072 | 2699722.5093 | 1263689.1461
21 | 2699756.5429 | 1263497.6091 | 2699758.0749 | 1263498.7915 | 2699770.5035 | 1263509.1764 | 2699772.5128 | 1263511.0557
22 | 2699756.5429 | 1263497.6091 | 2699755.2919 | 1263501.6469 | 2699748.4318 | 1263512.6181 | 2699744.5617 | 1263519.5141
23 | 2699756.5429 | 1263497.6091 | 2699758.188 | 1263492.0879 | 2699759.3751 | 1263489.6058 | 2699761.378 | 1263486.993 | 2699766.4857 | 1263482.5351
24 | 2699783.1327 | 1263525.0445 | 2699781.3474 | 1263522.3925 | 2699777.5802 | 1263516.6131 | 2699774.2934 | 1263512.7211 | 2699772.5128 | 1263511.0557
25 | 2699744.5617 | 1263519.5141 | 2699743.585 | 1263521.2546 | 2699740.1733 | 1263527.6565
26 | 2699695.6634 | 1263446.2068 | 2699715.4862 | 1263476.0434
27 | 2699715.4862 | 1263476.0434 | 2699718.7498 | 1263475.5091 | 2699721.8903 | 1263473.338 | 2699728.6423 | 1263468.3255
28 | 2699715.4862 | 1263476.0434 | 2699694.0477 | 1263472.9421
29 | 2699695.6634 | 1263446.2068 | 2699694.213 | 1263444.2029 | 2699672.0332 | 1263429.0276
30 | 2699728.6423 | 1263468.3255 | 2699736.7348 | 1263479.8604 | 2699742.6059 | 1263485.5307 | 2699747.312 | 1263489.2465 | 2699748.8937 | 1263492.8428 | 2699748.3162 | 1263496.2581 | 2699745.2536 | 1263500.9548 | 2699745.2251 | 1263500.9982
31 | 2699694.0477 | 1263472.9421 | 2699687.9702 | 1263472.063
32 | 2699672.9078 | 1263427.578 | 2699672.0332 | 1263429.0276
33 | 2699739.0746 | 1263510.384 | 2699745.2251 | 1263500.9982
34 | 2699672.9791 | 1263363.5672 | 2699668.4048 | 1263364.9802 | 2699671.2767 | 1263373.8248 | 2699674.4277 | 1263379.5271 | 2699670.1274 | 1263382.5571
35 | 2699670.1274 | 1263382.5571 | 2699664.1573 | 1263386.7711 | 2699663.4172 | 1263390.8953 | 2699665.0354 | 1263393.6694 | 2699672.0999 | 1263394.7004 | 2699670.6278 | 1263404.706 | 2699673.0944 | 1263411.8319
36 | 2699672.9791 | 1263363.5672 | 2699674.5704 | 1263369.2766 | 2699677.3811 | 1263375.4957 | 2699680.7418 | 1263381.2683 | 2699710.8007 | 1263425.3771
37 | 2699673.0944 | 1263411.8319 | 2699676.4898 | 1263421.6411 | 2699672.9078 | 1263427.578
38 | 2699491.25 | 1263315.4343 | 2699496.8644 | 1263313.5494 | 2699503.6912 | 1263311.2513 | 2699507.6918 | 1263309.9064 | 2699544.3897 | 1263313.4935 | 2699548.3163 | 1263313.8599 | 2699581.1106 | 1263317.0591
39 | 2699581.1106 | 1263317.0591 | 2699575.5045 | 1263370.2906
40 | 2699484.3299 | 1263314.7729 | 2699479.4565 | 1263310.2316 | 2699482.6568 | 1263306.7493 | 2699491.25 | 1263315.4343
41 | 2699491.25 | 1263315.4343 | 2699498.4003 | 1263326.586 | 2699503.8432 | 1263342.0459 | 2699506.0991 | 1263354.8278
42 | 2699574.9099 | 1263375.9364 | 2699575.5045 | 1263370.2906
43 | 2699726.1309 | 1263447.8727 | 2699710.8007 | 1263425.3771
44 | 2699810.9039 | 1263598.5654 | 2699801.7238 | 1263596.9874
45 | 2699816.9163 | 1263586.4902 | 2699810.9039 | 1263598.5654
46 | 2699795.7786 | 1263595.9655 | 2699801.7238 | 1263596.9874
47 | 2699816.9163 | 1263586.4902 | 2699814.6364 | 1263576.0653 | 2699813.2678 | 1263573.3372
48 | 2699813.2678 | 1263573.3372 | 2699806.3205 | 1263559.489 | 2699799.6498 | 1263549.5799
49 | 2699774.806 | 1263655.0363 | 2699776.9949 | 1263641.6055
50 | 2699774.806 | 1263655.0363 | 2699766.5856 | 1263654.664 | 2699761.8424 | 1263654.1943
51 | 2699777.0188 | 1263641.4589 | 2699776.9949 | 1263641.6055
52 | 2699743.5348 | 1263651.428 | 2699758.3276 | 1263653.8462 | 2699761.8424 | 1263654.1943
53 | 2699697.2031 | 1263685.2053 | 2699697.5555 | 1263683.0396
54 | 2699698.4205 | 1263677.1968 | 2699697.6014 | 1263682.7572 | 2699697.5555 | 1263683.0396
55 | 2699706.8329 | 1263623.9223 | 2699704.3598 | 1263640.2916 | 2699703.8536 | 1263643.2526
56 | 2699719.8002 | 1263554.611 | 2699720.6927 | 1263551.449 | 2699725.6846 | 1263538.2334 | 2699726.6942 | 1263535.8764
57 | 2699732.1252 | 1263546.6698 | 2699733.8002 | 1263542.1402 | 2699738.5045 | 1263530.7879 | 2699740.1733 | 1263527.6565
58 | 2699761.7863 | 1263658.6318 | 2699762.2431 | 1263658.7003
59 | 2699743.5348 | 1263651.428 | 2699729.4428 | 1263649.1382
60 | 2699728.6244 | 1263699.7276 | 2699729.9651 | 1263690.3647 | 2699727.7776 | 1263690.0072
61 | 2699783.1327 | 1263525.0445 | 2699792.2496 | 1263538.5872
62 | 2699687.5364 | 1263472.0002 | 2699687.9702 | 1263472.063
63 | 2699739.0746 | 1263510.384 | 2699737.8299 | 1263512.2834 | 2699731.9744 | 1263523.5496 | 2699730.3075 | 1263527.441
64 | 2699484.3299 | 1263314.7729 | 2699489.3682 | 1263321.5966 | 2699495.2853 | 1263331.7156 | 2699499.122 | 1263342.3445 | 2699500.832 | 1263347.7222 | 2699502.116 | 1263355.1388 | 2699502.4798 | 1263361.2722 | 2699502.3069 | 1263368.4085 | 2699501.5595 | 1263376.5582 | 2699500.9648 | 1263382.3454
65 | 2699484.3299 | 1263314.7729 | 2699470.7996 | 1263326.8108
66 | 2699506.0991 | 1263354.8278 | 2699506.0991 | 1263354.8278 | 2699506.2608 | 1263360.6821
67 | 2699500.9597 | 1263382.3957 | 2699500.9648 | 1263382.3454
68 | 2699470.7996 | 1263326.8108 | 2699469.3101 | 1263347.7142 | 2699468.919 | 1263349.4305
69 | 2699574.9099 | 1263375.9364 | 2699573.4002 | 1263390.2719
70 | 2699752.6085 | 1263476.2918 | 2699748.8171 | 1263476.4057 | 2699745.7068 | 1263474.5517 | 2699741.6737 | 1263470.6805 | 2699726.1309 | 1263447.8727
71 | 2699752.6085 | 1263476.2918 | 2699756.563 | 1263474.546 | 2699760.5732 | 1263471.7578
72 | 2699793.9722 | 1263595.655 | 2699795.7786 | 1263595.9655
73 | 2699794.1523 | 1263541.4136 | 2699799.6498 | 1263549.5799
74 | 2699777.0188 | 1263641.4589 | 2699778.1164 | 1263634.7239
75 | 2699743.5348 | 1263651.428 | 2699745.6698 | 1263637.0083
76 | 2699699.2277 | 1263671.7169 | 2699698.4205 | 1263677.1968
77 | 2699794.1523 | 1263541.4136 | 2699792.2496 | 1263538.5872
78 | 2699624.6513 | 1263597.5201 | 2699624.6056 | 1263597.783
79 | 2699624.6513 | 1263597.5201 | 2699627.2038 | 1263582.8327
80 | 2699621.1872 | 1263620.2139 | 2699623.9434 | 1263601.5933 | 2699624.6056 | 1263597.783
81 | 2699627.2688 | 1263582.4588 | 2699627.2038 | 1263582.8327
82 | 2699621.1872 | 1263620.2139 | 2699621.1746 | 1263620.2992
83 | 2699632.6453 | 1263551.5212 | 2699627.2688 | 1263582.4588
84 | 2699621.1746 | 1263620.2992 | 2699621.1664 | 1263620.3548
85 | 2699639.6035 | 1263511.4826 | 2699632.6453 | 1263551.5212
86 | 2699568.089 | 1263516.2043 | 2699632.6453 | 1263551.5212
87 | 2699621.1664 | 1263620.3548 | 2699621.1509 | 1263620.4595
88 | 2699639.6035 | 1263511.4826 | 2699642.7994 | 1263494.8561
89 | 2699639.6035 | 1263511.4826 | 2699653.5986 | 1263513.5897
90 | 2699568.089 | 1263516.2043 | 2699552.3643 | 1263508.2253
91 | 2699654.4613 | 1263467.2156 | 2699642.7994 | 1263494.8561
92 | 2699653.5986 | 1263513.5897 | 2699664.6561 | 1263515.2545
93 | 2699730.3075 | 1263527.441 | 2699726.6942 | 1263535.8764
94 | 2699687.5364 | 1263472.0002 | 2699680.9484 | 1263471.0472
95 | 2699680.9484 | 1263471.0472 | 2699674.436 | 1263470.1051
96 | 2699674.436 | 1263470.1051 | 2699667.741 | 1263469.1366
97 | 2699667.741 | 1263469.1366 | 2699661.1186 | 1263468.1787
98 | 2699661.1186 | 1263468.1787 | 2699654.4613 | 1263467.2156
99 | 2699665.4831 | 1263515.379 | 2699664.6561 | 1263515.2545
100 | 2699675.9519 | 1263516.9552 | 2699665.4831 | 1263515.379
101 | 2699703.8536 | 1263643.2526 | 2699701.9763 | 1263654.2335
102 | 2699699.4519 | 1263670.1948 | 2699700.7239 | 1263661.559 | 2699701.9763 | 1263654.2335
103 | 2699699.2277 | 1263671.7169 | 2699699.4519 | 1263670.1948
104 | 2699745.6698 | 1263637.0083 | 2699746.691 | 1263630.111
105 | 2699746.691 | 1263630.111 | 2699747.7121 | 1263623.2144
106 | 2699778.1164 | 1263634.7239 | 2699779.2376 | 1263627.8447
107 | 2699747.7121 | 1263623.2144 | 2699748.733 | 1263616.3196
108 | 2699779.2376 | 1263627.8447 | 2699780.3588 | 1263620.965
109 | 2699748.733 | 1263616.3196 | 2699749.754 | 1263609.4241
110 | 2699559.6814 | 1263483.6468 | 2699559.2773 | 1263487.4211 | 2699558.4906 | 1263493.4239 | 2699557.2809 | 1263498.1519 | 2699554.6565 | 1263504.5686 | 2699552.3643 | 1263508.2253
111 | 2699559.6814 | 1263483.6468 | 2699561.4861 | 1263466.7881
112 | 2699552.3643 | 1263508.2253 | 2699551.3662 | 1263509.8175 | 2699548.5686 | 1263513.5513 | 2699544.6154 | 1263517.4547 | 2699540.3683 | 1263520.4746 | 2699536.2918 | 1263522.7523 | 2699532.0355 | 1263524.5266 | 2699526.7811 | 1263526.0727 | 2699521.462 | 1263526.984 | 2699515.9628 | 1263526.9581 | 2699512.4022 | 1263526.5501
113 | 2699566.4843 | 1263459.8641 | 2699561.4861 | 1263466.7881
114 | 2699566.4843 | 1263459.8641 | 2699576.5727 | 1263461.1684
115 | 2699566.4843 | 1263459.8641 | 2699563.4743 | 1263448.2167
116 | 2699564.2932 | 1263440.5668 | 2699563.4743 | 1263448.2167
117 | 2699570.1778 | 1263422.1897 | 2699564.2932 | 1263440.5668
118 | 2699570.1778 | 1263422.1897 | 2699570.3376 | 1263420.5559
119 | 2699496.2914 | 1263470.8741 | 2699499.4602 | 1263440.7761
120 | 2699500.3414 | 1263432.4064 | 2699499.4602 | 1263440.7761
121 | 2699573.4002 | 1263390.2719 | 2699572.0609 | 1263402.9888 | 2699571.2427 | 1263411.3041 | 2699570.3376 | 1263420.5559
122 | 2699576.5727 | 1263461.1684 | 2699605.1391 | 1263464.8524
123 | 2699605.1391 | 1263464.8524 | 2699623.1209 | 1263467.1683
124 | 2699606.5179 | 1263455.012 | 2699605.1391 | 1263464.8524
125 | 2699625.2027 | 1263455.4048 | 2699623.1209 | 1263467.1683
126 | 2699493.1222 | 1263458.6739 | 2699491.3835 | 1263475.596
127 | 2699493.1222 | 1263458.6739 | 2699495.5932 | 1263434.6247
128 | 2699495.5932 | 1263434.6247 | 2699495.5985 | 1263434.5737
129 | 2699501.9017 | 1263417.5871 | 2699500.3414 | 1263432.4064
130 | 2699495.5985 | 1263434.5737 | 2699495.6627 | 1263433.9483
131 | 2699506.2608 | 1263360.6821 | 2699506.5999 | 1263372.9623 | 2699506.1685 | 1263377.0604
132 | 2699500.9597 | 1263382.3957 | 2699498.4231 | 1263407.0827
133 | 2699468.919 | 1263349.4305 | 2699465.983 | 1263362.3147 | 2699465.2608 | 1263362.8042
134 | 2699502.2582 | 1263414.2002 | 2699501.9017 | 1263417.5871
135 | 2699502.2582 | 1263414.2002 | 2699503.2058 | 1263405.1997
136 | 2699505.2697 | 1263385.5966 | 2699503.2058 | 1263405.1997
137 | 2699498.2727 | 1263408.5466 | 2699498.4231 | 1263407.0827
138 | 2699495.6627 | 1263433.9483 | 2699498.2689 | 1263408.5834
139 | 2699498.2689 | 1263408.5834 | 2699498.2727 | 1263408.5466
140 | 2699506.1685 | 1263377.0604 | 2699505.2697 | 1263385.5966
141 | 2699781.1933 | 1263615.845 | 2699780.3588 | 1263620.965

## bus_geodata
| x | y | coords
0 | 2699710.8824 | 1263598.4114
1 | 2699708.5719 | 1263612.6182
2 | 2699697.3806 | 1263596.2709
3 | 2699725.7112 | 1263567.0132
4 | 2699717.1121 | 1263564.1347
5 | 2699737.0999 | 1263569.8187
6 | 2699728.7307 | 1263556.3254
7 | 2699723.6892 | 1263576.6357
8 | 2699716.0151 | 1263651.8532
9 | 2699761.6335 | 1263658.6089
10 | 2699717.1871 | 1263645.3454
11 | 2699715.1835 | 1263656.4875
12 | 2699706.1421 | 1263686.4709
13 | 2699722.5093 | 1263689.1461
14 | 2699708.3483 | 1263672.3724
15 | 2699756.5429 | 1263497.6091
16 | 2699772.5128 | 1263511.0557
17 | 2699744.5617 | 1263519.5141
18 | 2699766.4858 | 1263482.5351
19 | 2699715.4862 | 1263476.0434
20 | 2699695.6634 | 1263446.2068
21 | 2699728.6423 | 1263468.3255
22 | 2699694.0477 | 1263472.9421
23 | 2699672.0332 | 1263429.0276
24 | 2699745.2251 | 1263500.9982
25 | 2699670.1274 | 1263382.5571
26 | 2699672.9791 | 1263363.5672
27 | 2699673.0944 | 1263411.8319
28 | 2699581.1106 | 1263317.0591
29 | 2699491.25 | 1263315.4343
30 | 2699575.5045 | 1263370.2906
31 | 2699710.8007 | 1263425.3771
32 | 2699810.9039 | 1263598.5654
33 | 2699801.7238 | 1263596.9874
34 | 2699816.9163 | 1263586.4902
35 | 2699813.2678 | 1263573.3372
36 | 2699774.806 | 1263655.0363
37 | 2699776.9949 | 1263641.6055
38 | 2699761.8424 | 1263654.1943
39 | 2699697.2031 | 1263685.2053
40 | 2699697.5555 | 1263683.0396
41 | 2699706.8329 | 1263623.9223
42 | 2699719.8002 | 1263554.611
43 | 2699732.1252 | 1263546.6698
44 | 2699721.3928 | 1263589.4468
45 | 2699761.7863 | 1263658.6318
46 | 2699729.4428 | 1263649.1382
47 | 2699727.7776 | 1263690.0072
48 | 2699783.1327 | 1263525.0445
49 | 2699740.1733 | 1263527.6565
50 | 2699687.9702 | 1263472.063
51 | 2699672.9078 | 1263427.578
52 | 2699739.0746 | 1263510.384
53 | 2699484.3299 | 1263314.7729
54 | 2699506.0991 | 1263354.8278
55 | 2699500.9648 | 1263382.3454
56 | 2699470.7996 | 1263326.8108
57 | 2699574.9099 | 1263375.9364
58 | 2699726.1309 | 1263447.8727
59 | 2699760.5732 | 1263471.7578
60 | 2699752.6085 | 1263476.2918
61 | 2699795.7786 | 1263595.9655
62 | 2699799.6498 | 1263549.5799
63 | 2699762.2431 | 1263658.7003
64 | 2699777.0188 | 1263641.4589
65 | 2699743.5348 | 1263651.428
66 | 2699698.4205 | 1263677.1968
67 | 2699792.2496 | 1263538.5872
68 | 2699794.1523 | 1263541.4136
69 | 2699624.6513 | 1263597.5201
70 | 2699624.6056 | 1263597.783
71 | 2699627.2038 | 1263582.8327
72 | 2699621.1872 | 1263620.2139
73 | 2699627.2688 | 1263582.4588
74 | 2699621.1746 | 1263620.2992
75 | 2699632.6453 | 1263551.5212
76 | 2699621.1664 | 1263620.3548
77 | 2699639.6035 | 1263511.4826
78 | 2699568.089 | 1263516.2043
79 | 2699621.1509 | 1263620.4595
80 | 2699642.7994 | 1263494.8561
81 | 2699653.5986 | 1263513.5897
82 | 2699726.6942 | 1263535.8764
83 | 2699730.3075 | 1263527.441
84 | 2699687.5364 | 1263472.0002
85 | 2699680.9484 | 1263471.0472
86 | 2699674.436 | 1263470.1051
87 | 2699667.741 | 1263469.1366
88 | 2699661.1186 | 1263468.1787
89 | 2699654.4613 | 1263467.2156
90 | 2699664.6561 | 1263515.2545
91 | 2699665.4831 | 1263515.379
92 | 2699675.9519 | 1263516.9552
93 | 2699728.6244 | 1263699.7276
94 | 2699703.8536 | 1263643.2526
95 | 2699701.9763 | 1263654.2335
96 | 2699793.9722 | 1263595.655
97 | 2699699.4519 | 1263670.1948
98 | 2699699.2277 | 1263671.7169
99 | 2699745.6698 | 1263637.0083
100 | 2699746.691 | 1263630.111
101 | 2699778.1164 | 1263634.7239
102 | 2699747.7121 | 1263623.2144
103 | 2699779.2376 | 1263627.8447
104 | 2699748.733 | 1263616.3196
105 | 2699559.6814 | 1263483.6468
106 | 2699552.3643 | 1263508.2253
107 | 2699561.4861 | 1263466.7881
108 | 2699512.4022 | 1263526.5501
109 | 2699566.4843 | 1263459.8641
110 | 2699563.4743 | 1263448.2167
111 | 2699564.2932 | 1263440.5668
112 | 2699570.1778 | 1263422.1897
113 | 2699496.2914 | 1263470.8741
114 | 2699499.4602 | 1263440.7761
115 | 2699570.3376 | 1263420.5559
116 | 2699573.4002 | 1263390.2719
117 | 2699576.5727 | 1263461.1684
118 | 2699605.1391 | 1263464.8524
119 | 2699623.1209 | 1263467.1683
120 | 2699606.5179 | 1263455.012
121 | 2699625.2027 | 1263455.4048
122 | 2699491.3835 | 1263475.596
123 | 2699493.1222 | 1263458.6739
124 | 2699495.5932 | 1263434.6247
125 | 2699500.3414 | 1263432.4064
126 | 2699495.5985 | 1263434.5737
127 | 2699506.2608 | 1263360.6821
128 | 2699500.9597 | 1263382.3957
129 | 2699468.919 | 1263349.4305
130 | 2699501.9017 | 1263417.5871
131 | 2699502.2582 | 1263414.2002
132 | 2699503.2058 | 1263405.1997
133 | 2699465.2608 | 1263362.8042
134 | 2699498.4231 | 1263407.0827
135 | 2699495.6627 | 1263433.9483
136 | 2699498.2689 | 1263408.5834
137 | 2699498.2727 | 1263408.5466
138 | 2699505.2697 | 1263385.5966
139 | 2699506.1685 | 1263377.0604
140 | 2699780.3588 | 1263620.965
141 | 2699781.1933 | 1263615.845
142 | 2699749.754 | 1263609.4241
143 | 2699642.7994 | 1263494.8561

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97722 | -0.43654 | 0 | 0
1 | 0.97704 | -0.44009 | 0.0014611 | 0.00036618
2 | 0.97714 | -0.43802 | 0.0059569 | 0.0014929
3 | 0.97453 | -0.48927 | 0 | 0
4 | 0.98001 | -0.38198 | 0.0016415 | 0.00041139
5 | 0.97449 | -0.49012 | 0.0039498 | 0.00098992
6 | 0.97424 | -0.49491 | 0.0014878 | 0.00037287
7 | 0.97421 | -0.49557 | 0.0015708 | 0.00039367
8 | 0.97207 | -0.53772 | 0 | 0
9 | 0.97191 | -0.54103 | 0.0012395 | 0.00031066
10 | 0.97216 | -0.53608 | 0 | 0
11 | 0.97203 | -0.53854 | 0.0017473 | 0.00043791
12 | 0.97182 | -0.54266 | 0 | 0
13 | 0.97174 | -0.54433 | 0.0016377 | 0.00041044
14 | 0.9719 | -0.54122 | 0.002327 | 0.00058321
15 | 0.97279 | -0.52358 | 0 | 0
16 | 0.97239 | -0.53149 | 0.0011249 | 0.00028194
17 | 0.97331 | -0.51327 | 0.0011249 | 0.00028194
18 | 0.97276 | -0.52419 | 0.0017786 | 0.00044576
19 | 0.99097 | -0.17094 | 0 | 0
20 | 0.99064 | -0.17732 | 0 | 0
21 | 0.98959 | -0.19725 | 0 | 0
22 | 0.99309 | -0.13052 | 0.0010981 | 0.00027521
23 | 0.99037 | -0.18256 | 0.0033126 | 0.00083022
24 | 0.98592 | -0.26757 | 0.00084243 | 0.00021113
25 | 0.99011 | -0.18765 | 0 | 0
26 | 0.99 | -0.18973 | 0 | 0
27 | 0.99027 | -0.18449 | 0.0010964 | 0.0002748
28 | 0.98173 | -0.34996 | 0 | 0
29 | 0.97749 | -0.43275 | 0 | 0
30 | 0.98423 | -0.30166 | 0.0012411 | 0.00031104
31 | 0.9897 | -0.19557 | 0.0015599 | 0.00039095
32 | 0.97118 | -0.55547 | 0 | 0
33 | 0.9711 | -0.55688 | 0.001407 | 0.00035262
34 | 0.97128 | -0.55344 | 0 | 0
35 | 0.97138 | -0.55137 | 0.0025853 | 0.00064793
36 | 0.97148 | -0.54954 | 0 | 0
37 | 0.97138 | -0.55152 | 0.0012987 | 0.00032549
38 | 0.97157 | -0.54766 | 0.0015244 | 0.00038204
39 | 0.97646 | -0.45148 | 0.0015438 | 0.00038692
40 | 0.97646 | -0.45142 | 0.0013224 | 0.00033143
41 | 0.97691 | -0.4426 | 0.0012417 | 0.00031121
42 | 0.98082 | -0.36626 | 0.0021048 | 0.00052751
43 | 0.97399 | -0.49983 | 0.001284 | 0.00032181
44 | 0.9738 | -0.50354 | 0.002489 | 0.00062379
45 | 0.97191 | -0.54104 | 0.0012059 | 0.00030222
46 | 0.97194 | -0.54026 | 0.0015238 | 0.0003819
47 | 0.97172 | -0.54471 | 0.0019094 | 0.00047855
48 | 0.97207 | -0.53781 | 0.0035758 | 0.00089617
49 | 0.97351 | -0.50928 | 0.0014258 | 0.00035735
50 | 0.9937 | -0.11898 | 0.0067278 | 0.0016861
51 | 0.99036 | -0.18276 | 0.00112 | 0.0002807
52 | 0.98493 | -0.28659 | 0.0015539 | 0.00038945
53 | 0.97686 | -0.44518 | 0 | 0
54 | 0.97665 | -0.44922 | 0.0010009 | 0.00025086
55 | 0.97497 | -0.48231 | 0.00021839 | 5.4734e-05
56 | 0.97685 | -0.44539 | 0 | 0
57 | 0.9845 | -0.29643 | 0.0023148 | 0.00058014
58 | 0.98963 | -0.197 | 0.0015599 | 0.00039095
59 | 0.98956 | -0.19823 | 0.0013856 | 0.00034726
60 | 0.98957 | -0.198 | 0 | 0
61 | 0.97107 | -0.55763 | 0.0013125 | 0.00032895
62 | 0.97166 | -0.54592 | 0.0025832 | 0.00064741
63 | 0.9719 | -0.54105 | 0.0014528 | 0.0003641
64 | 0.97137 | -0.55154 | 0.0013685 | 0.00034299
65 | 0.97173 | -0.54445 | 0 | 0
66 | 0.97648 | -0.45111 | 0.0015739 | 0.00039446
67 | 0.97183 | -0.54258 | 0.0011924 | 0.00029884
68 | 0.97178 | -0.5435 | 0.0013256 | 0.00033223
69 | 0.99737 | -0.050008 | 0.0014748 | 0.00036961
70 | 0.99737 | -0.050036 | 0.0014435 | 0.00036178
71 | 0.99747 | -0.048089 | 0.0018539 | 0.00046462
72 | 0.99728 | -0.051796 | 0.0011039 | 0.00027667
73 | 0.99747 | -0.048028 | 0.0017373 | 0.00043541
74 | 0.99727 | -0.051801 | 0.0011058 | 0.00027714
75 | 0.99778 | -0.042013 | 0.0024979 | 0.00062604
76 | 0.99727 | -0.051804 | 0.0011101 | 0.00027823
77 | 1 | 0 | -0.25537 | -0.065185
78 | 0.99422 | -0.10984 | 0.017003 | 0.0042615
79 | 0.99727 | -0.051806 | 0.0011077 | 0.00027762
80 | 0.99903 | -0.018207 | 0.0034529 | 0.00086537
81 | 0.9999 | -0.0019676 | 0.0021705 | 0.00054398
82 | 0.98249 | -0.33384 | 0.0017582 | 0.00044064
83 | 0.98327 | -0.3187 | 0.0014239 | 0.00035686
84 | 0.99374 | -0.1181 | 0.0010823 | 0.00027124
85 | 0.99445 | -0.10469 | 0.001093 | 0.00027392
86 | 0.99516 | -0.091321 | 0.0011068 | 0.00027739
87 | 0.99589 | -0.077466 | 0.0011386 | 0.00028535
88 | 0.99662 | -0.063648 | 0.0011163 | 0.00027977
89 | 0.99736 | -0.049646 | 0.0011065 | 0.00027731
90 | 0.99984 | -0.0030993 | 0.0018161 | 0.00045517
91 | 0.99984 | -0.0031575 | 0.0018005 | 0.00045126
92 | 0.99981 | -0.0035613 | 0.0021877 | 0.00054828
93 | 0.9717 | -0.54512 | 0.0019178 | 0.00048065
94 | 0.97671 | -0.44646 | 0.0014886 | 0.00037309
95 | 0.97662 | -0.44835 | 0.0020262 | 0.00050782
96 | 0.97106 | -0.55782 | 0.0054423 | 0.001364
97 | 0.97651 | -0.4505 | 0.0015621 | 0.00039151
98 | 0.9765 | -0.45066 | 0.0012766 | 0.00031995
99 | 0.97164 | -0.54619 | 0.0012997 | 0.00032573
100 | 0.97161 | -0.54686 | 0.0012972 | 0.0003251
101 | 0.97134 | -0.55219 | 0.0012987 | 0.00032548
102 | 0.97159 | -0.54736 | 0.0012983 | 0.00032538
103 | 0.97132 | -0.55269 | 0.0012978 | 0.00032525
104 | 0.97157 | -0.5477 | 0.0012978 | 0.00032525
105 | 0.99088 | -0.17361 | 0.0039943 | 0.0010011
106 | 0.99278 | -0.13721 | 0.0034986 | 0.00087683
107 | 0.9897 | -0.19623 | 0.0039813 | 0.0009978
108 | 0.99256 | -0.14162 | 0.0053442 | 0.0013394
109 | 0.98914 | -0.20704 | 0 | 0
110 | 0.98841 | -0.22104 | 0.0014376 | 0.00036031
111 | 0.98795 | -0.2298 | 0.0028543 | 0.00071535
112 | 0.98686 | -0.25082 | 0.0020257 | 0.00050768
113 | 0.97525 | -0.47687 | 0.006068 | 0.0015208
114 | 0.97542 | -0.47351 | 0.0017547 | 0.00043977
115 | 0.98677 | -0.25255 | 0.0039498 | 0.00098992
116 | 0.98521 | -0.28255 | 0.001385 | 0.00034712
117 | 0.98908 | -0.2081 | 0 | 0
118 | 0.98893 | -0.2111 | 0 | 0
119 | 0.98885 | -0.21257 | 0 | 0
120 | 0.98892 | -0.21133 | 0.0013033 | 0.00032665
121 | 0.9888 | -0.21354 | 0.0045517 | 0.0011408
122 | 0.97347 | -0.51186 | 0.0057582 | 0.0014431
123 | 0.97356 | -0.51006 | 0.005762 | 0.0014441
124 | 0.97382 | -0.50494 | 0.0026402 | 0.00066171
125 | 0.97548 | -0.4723 | 0.0018339 | 0.00045962
126 | 0.97382 | -0.50493 | 0.0026429 | 0.00066237
127 | 0.97655 | -0.45138 | 0.0010022 | 0.00025118
128 | 0.97497 | -0.48234 | 0.00021825 | 5.4699e-05
129 | 0.97683 | -0.44566 | 0.00043285 | 0.00010848
130 | 0.97562 | -0.46966 | 0.0041184 | 0.0010322
131 | 0.97566 | -0.4688 | 0.0018849 | 0.00047241
132 | 0.97579 | -0.46621 | 0.0015899 | 0.00039846
133 | 0.97683 | -0.44571 | 0.0002123 | 5.3207e-05
134 | 0.97433 | -0.49498 | 0.003206 | 0.00080351
135 | 0.97383 | -0.50474 | 0.0025725 | 0.00064472
136 | 0.97429 | -0.49566 | 0.00262 | 0.00065664
137 | 0.97429 | -0.49564 | 0.0025574 | 0.00064095
138 | 0.97611 | -0.45999 | 0.00095773 | 0.00024003
139 | 0.97625 | -0.45713 | 0.00095773 | 0.00024003
140 | 0.9713 | -0.55303 | 0.0012989 | 0.00032553
141 | 0.97129 | -0.55315 | 0.0012976 | 0.0003252
142 | 0.97156 | -0.54787 | 0.0012989 | 0.00032553
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.013504 | 0.0033863 | -0.013502 | -0.003385 | 2.2824e-06 | 1.2804e-06 | 0.020563 | 0.020564 | 0.020564 | 0.97722 | -0.43654 | 0.97704 | -0.44009 | 5.6493
1 | 0.0059573 | 0.001493 | -0.0059569 | -0.0014929 | 4.206e-07 | 9.8435e-08 | 0.0090713 | 0.0090713 | 0.0090713 | 0.97722 | -0.43654 | 0.97714 | -0.43802 | 2.4921
2 | 0.066816 | 0.016862 | -0.066648 | -0.016755 | 0.00016827 | 0.00010715 | 0.10178 | 0.10178 | 0.10178 | 0.97722 | -0.43654 | 0.97453 | -0.48927 | 27.9627
3 | -0.086278 | -0.021741 | 0.086504 | 0.021886 | 0.00022582 | 0.00014408 | 0.13142 | 0.13142 | 0.13142 | 0.97722 | -0.43654 | 0.98001 | -0.38198 | 36.104
4 | 0.012041 | 0.0030188 | -0.012039 | -0.003018 | 1.4424e-06 | 7.7989e-07 | 0.018338 | 0.018338 | 0.018338 | 0.97704 | -0.44009 | 0.97691 | -0.4426 | 5.038
5 | 0.00395 | 0.00098987 | -0.0039498 | -0.00098992 | 1.5954e-07 | -4.3611e-08 | 0.0060312 | 0.0060313 | 0.0060313 | 0.97453 | -0.48927 | 0.97449 | -0.49012 | 1.6569
6 | 0.027715 | 0.0069685 | -0.027708 | -0.0069638 | 7.4614e-06 | 4.637e-06 | 0.042326 | 0.042327 | 0.042327 | 0.97453 | -0.48927 | 0.97424 | -0.49491 | 11.6282
7 | 0.034983 | 0.0087967 | -0.034973 | -0.0087901 | 1.0525e-05 | 6.6134e-06 | 0.053426 | 0.053427 | 0.053427 | 0.97453 | -0.48927 | 0.97421 | -0.49557 | 14.6776
8 | -0.088145 | -0.022297 | 0.088212 | 0.022339 | 6.6545e-05 | 4.2464e-05 | 0.13391 | 0.13391 | 0.13391 | 0.98001 | -0.38198 | 0.98082 | -0.36626 | 36.7887
9 | 0.02622 | 0.006591 | -0.026214 | -0.0065871 | 6.1607e-06 | 3.8154e-06 | 0.040054 | 0.040054 | 0.040054 | 0.97424 | -0.49491 | 0.97399 | -0.49983 | 11.0039
10 | 0.033402 | 0.0083964 | -0.033389 | -0.0083885 | 1.2711e-05 | 7.9727e-06 | 0.051027 | 0.051027 | 0.051027 | 0.97421 | -0.49557 | 0.9738 | -0.50354 | 14.0185
11 | 0.0038988 | 0.0009768 | -0.0038982 | -0.00097697 | 6.1598e-07 | -1.7737e-07 | 0.005968 | 0.0059683 | 0.0059683 | 0.97207 | -0.53772 | 0.97191 | -0.54103 | 1.6396
12 | -0.01344 | -0.0033681 | 0.013441 | 0.0033687 | 1.0495e-06 | 5.8973e-07 | 0.020574 | 0.020574 | 0.020574 | 0.97207 | -0.53772 | 0.97216 | -0.53608 | 5.6522
13 | 0.0095415 | 0.0023913 | -0.0095411 | -0.0023912 | 3.7666e-07 | 1.827e-07 | 0.014606 | 0.014606 | 0.014606 | 0.97207 | -0.53772 | 0.97203 | -0.53854 | 4.0126
14 | 0.0026587 | 0.00066632 | -0.0026587 | -0.00066632 | 9.5942e-10 | -1.2995e-09 | 0.0040705 | 0.0040705 | 0.0040705 | 0.97191 | -0.54103 | 0.97191 | -0.54104 | 1.1183
15 | 0.017411 | 0.004366 | -0.017407 | -0.0043639 | 3.4726e-06 | 2.0608e-06 | 0.026651 | 0.026651 | 0.026651 | 0.97216 | -0.53608 | 0.97194 | -0.54026 | 7.3216
16 | -0.030852 | -0.0077347 | 0.0309 | 0.0077647 | 4.7909e-05 | 2.995e-05 | 0.047224 | 0.047224 | 0.047224 | 0.97216 | -0.53608 | 0.9738 | -0.50354 | 12.9737
17 | 0.0077939 | 0.0019532 | -0.0077929 | -0.0019528 | 9.9351e-07 | 4.0518e-07 | 0.011931 | 0.011931 | 0.011931 | 0.97203 | -0.53854 | 0.9719 | -0.54122 | 3.2778
18 | 0.0054655 | 0.0013696 | -0.005465 | -0.0013695 | 4.3554e-07 | 7.3274e-08 | 0.0083684 | 0.0083685 | 0.0083685 | 0.97182 | -0.54266 | 0.97174 | -0.54433 | 2.299
19 | -0.0054655 | -0.0013696 | 0.0054659 | 0.0013696 | 3.7475e-07 | 6.3016e-08 | 0.0083684 | 0.0083684 | 0.0083684 | 0.97182 | -0.54266 | 0.9719 | -0.54122 | 2.299
20 | 0.0038274 | 0.00095906 | -0.0038273 | -0.00095908 | 6.876e-08 | -2.2124e-08 | 0.0058607 | 0.0058608 | 0.0058608 | 0.97174 | -0.54433 | 0.97172 | -0.54471 | 1.6101
21 | 0.020574 | 0.0051641 | -0.020566 | -0.0051594 | 7.757e-06 | 4.7053e-06 | 0.031473 | 0.031473 | 0.031473 | 0.97279 | -0.52358 | 0.97239 | -0.53149 | 8.6464
22 | -0.022352 | -0.0056096 | 0.022363 | 0.0056164 | 1.0994e-05 | 6.7245e-06 | 0.034194 | 0.034193 | 0.034194 | 0.97279 | -0.52358 | 0.97331 | -0.51327 | 9.3938
23 | 0.0017787 | 0.00044556 | -0.0017786 | -0.00044576 | 5.1585e-08 | -1.977e-07 | 0.0027206 | 0.0027207 | 0.0027207 | 0.97279 | -0.52358 | 0.97276 | -0.52419 | 0.74745
24 | 0.019441 | 0.0048774 | -0.019435 | -0.0048739 | 5.8513e-06 | 3.5263e-06 | 0.029752 | 0.029752 | 0.029752 | 0.97239 | -0.53149 | 0.97207 | -0.53781 | 8.1735
25 | -0.023488 | -0.0058983 | 0.023493 | 0.005901 | 4.4739e-06 | 2.7483e-06 | 0.035913 | 0.035913 | 0.035913 | 0.97331 | -0.51327 | 0.97351 | -0.50928 | 9.8663
26 | 0.010043 | 0.0025166 | -0.01004 | -0.0025151 | 3.0522e-06 | 1.4925e-06 | 0.015081 | 0.015081 | 0.015081 | 0.99097 | -0.17094 | 0.99064 | -0.17732 | 4.1431
27 | 0.096787 | 0.024834 | -0.096664 | -0.024756 | 0.00012339 | 7.8771e-05 | 0.14554 | 0.14554 | 0.14554 | 0.99097 | -0.17094 | 0.98959 | -0.19725 | 39.9836
28 | -0.10683 | -0.027351 | 0.10704 | 0.027485 | 0.00020957 | 0.00013384 | 0.16062 | 0.16062 | 0.16062 | 0.99097 | -0.17094 | 0.99309 | -0.13052 | 44.1265
29 | 0.01004 | 0.0025151 | -0.010038 | -0.0025139 | 2.503e-06 | 1.2242e-06 | 0.015081 | 0.015081 | 0.015081 | 0.99064 | -0.17732 | 0.99037 | -0.18256 | 4.1431
30 | 0.096664 | 0.024756 | -0.096336 | -0.024546 | 0.00032806 | 0.00020943 | 0.14554 | 0.14554 | 0.14554 | 0.98959 | -0.19725 | 0.98592 | -0.26757 | 39.9836
31 | -0.10814 | -0.02776 | 0.1082 | 0.027799 | 6.0633e-05 | 3.8726e-05 | 0.16227 | 0.16227 | 0.16227 | 0.99309 | -0.13052 | 0.9937 | -0.11898 | 44.5785
32 | 0.006725 | 0.0016837 | -0.006725 | -0.0016837 | 6.4812e-08 | 1.9694e-08 | 0.010104 | 0.010104 | 0.010104 | 0.99037 | -0.18256 | 0.99036 | -0.18276 | 2.7757
33 | 0.095493 | 0.024335 | -0.095406 | -0.024279 | 8.7585e-05 | 5.5911e-05 | 0.14427 | 0.14427 | 0.14427 | 0.98592 | -0.26757 | 0.98493 | -0.28659 | 39.6344
34 | 0.0045074 | 0.0011282 | -0.0045069 | -0.0011282 | 4.4498e-07 | -4.7793e-08 | 0.0067735 | 0.0067737 | 0.0067737 | 0.99011 | -0.18765 | 0.99 | -0.18973 | 1.8609
35 | -0.0045074 | -0.0011282 | 0.0045081 | 0.0011281 | 6.7964e-07 | -7.3157e-08 | 0.0067735 | 0.0067734 | 0.0067735 | 0.99011 | -0.18765 | 0.99027 | -0.18449 | 1.8609
36 | 0.0045069 | 0.0011282 | -0.0045057 | -0.0011284 | 1.2528e-06 | -1.3411e-07 | 0.0067737 | 0.006774 | 0.006774 | 0.99 | -0.18973 | 0.9897 | -0.19557 | 1.861
37 | -0.0056045 | -0.0014029 | 0.005605 | 0.001403 | 4.6041e-07 | 7.1894e-08 | 0.0084209 | 0.0084209 | 0.0084209 | 0.99027 | -0.18449 | 0.99036 | -0.18276 | 2.3134
38 | 0.050342 | 0.01274 | -0.050143 | -0.012614 | 0.00019916 | 0.00012632 | 0.076348 | 0.076349 | 0.076349 | 0.98173 | -0.34996 | 0.97749 | -0.43275 | 20.9749
39 | -0.050342 | -0.01274 | 0.050459 | 0.012814 | 0.000117 | 7.4202e-05 | 0.076348 | 0.076348 | 0.076348 | 0.98173 | -0.34996 | 0.98423 | -0.30166 | 20.9748
40 | 0.028938 | 0.0072871 | -0.028921 | -0.0072764 | 1.719e-05 | 1.0706e-05 | 0.044064 | 0.044064 | 0.044064 | 0.97749 | -0.43275 | 0.97686 | -0.44518 | 12.1055
41 | 0.021205 | 0.0053269 | -0.021189 | -0.0053167 | 1.6657e-05 | 1.0127e-05 | 0.032285 | 0.032285 | 0.032285 | 0.97749 | -0.43275 | 0.97665 | -0.44922 | 8.8695
42 | -0.0517 | -0.013126 | 0.051713 | 0.013134 | 1.3027e-05 | 8.2649e-06 | 0.078224 | 0.078224 | 0.078224 | 0.98423 | -0.30166 | 0.9845 | -0.29643 | 21.4902
43 | 0.0029458 | 0.0007374 | -0.0029456 | -0.00073762 | 2.0022e-07 | -2.2165e-07 | 0.0044287 | 0.0044288 | 0.0044288 | 0.9897 | -0.19557 | 0.98963 | -0.197 | 1.2167
44 | 0.0081626 | 0.0020458 | -0.008162 | -0.0020456 | 5.4636e-07 | 2.3442e-07 | 0.012507 | 0.012507 | 0.012507 | 0.97118 | -0.55547 | 0.9711 | -0.55688 | 3.4359
45 | -0.0081626 | -0.0020458 | 0.0081634 | 0.0020462 | 7.9085e-07 | 3.3929e-07 | 0.012507 | 0.012507 | 0.012507 | 0.97118 | -0.55547 | 0.97128 | -0.55344 | 3.4359
46 | 0.0067551 | 0.001693 | -0.0067548 | -0.0016929 | 2.4237e-07 | 8.0483e-08 | 0.010351 | 0.010351 | 0.010351 | 0.9711 | -0.55688 | 0.97107 | -0.55763 | 2.8436
47 | -0.0081634 | -0.0020462 | 0.0081642 | 0.0020465 | 8.0495e-07 | 3.453e-07 | 0.012507 | 0.012506 | 0.012507 | 0.97128 | -0.55344 | 0.97138 | -0.55137 | 3.4359
48 | -0.010749 | -0.0026945 | 0.010752 | 0.0026959 | 2.79e-06 | 1.4458e-06 | 0.016467 | 0.016467 | 0.016467 | 0.97138 | -0.55137 | 0.97166 | -0.54592 | 4.5238
49 | 0.0078613 | 0.0019701 | -0.0078605 | -0.0019698 | 7.3988e-07 | 3.0505e-07 | 0.012041 | 0.012041 | 0.012041 | 0.97148 | -0.54954 | 0.97138 | -0.55152 | 3.308
50 | -0.0078613 | -0.0019701 | 0.007862 | 0.0019704 | 7.0655e-07 | 2.9128e-07 | 0.012041 | 0.012041 | 0.012041 | 0.97148 | -0.54954 | 0.97157 | -0.54766 | 3.308
51 | 0.0065618 | 0.0016443 | -0.0065618 | -0.0016443 | 5.6284e-09 | 1.7632e-09 | 0.010052 | 0.010052 | 0.010052 | 0.97138 | -0.55152 | 0.97137 | -0.55154 | 2.7615
52 | -0.0093863 | -0.0023525 | 0.0093878 | 0.0023532 | 1.4353e-06 | 6.8921e-07 | 0.014376 | 0.014376 | 0.014376 | 0.97157 | -0.54766 | 0.97173 | -0.54445 | 3.9494
53 | -0.0015438 | -0.00038692 | 0.0015438 | 0.00038689 | 4.5541e-09 | -2.4532e-08 | 0.0023526 | 0.0023526 | 0.0023526 | 0.97646 | -0.45148 | 0.97646 | -0.45142 | 0.64632
54 | -0.0028662 | -0.00071832 | 0.0028663 | 0.00071828 | 4.2257e-08 | -4.6842e-08 | 0.0043678 | 0.0043678 | 0.0043678 | 0.97646 | -0.45142 | 0.97648 | -0.45111 | 1.2
55 | 0.010798 | 0.0027068 | -0.010796 | -0.0027058 | 1.984e-06 | 1.0249e-06 | 0.016447 | 0.016447 | 0.016447 | 0.97691 | -0.4426 | 0.97671 | -0.44646 | 4.5184
56 | -0.090316 | -0.022867 | 0.090457 | 0.022957 | 0.00014082 | 8.987e-05 | 0.1371 | 0.1371 | 0.1371 | 0.98082 | -0.36626 | 0.98249 | -0.33384 | 37.6659
57 | 0.02493 | 0.0062653 | -0.024918 | -0.0062584 | 1.1245e-05 | 6.9399e-06 | 0.038093 | 0.038093 | 0.038093 | 0.97399 | -0.49983 | 0.97351 | -0.50928 | 10.465
58 | 0.0014528 | 0.0003641 | -0.0014528 | -0.0003641 | 8.5713e-10 | -5.1762e-09 | 0.0022242 | 0.0022242 | 0.0022242 | 0.97191 | -0.54104 | 0.9719 | -0.54105 | 0.61106
59 | 0.015884 | 0.003982 | -0.01588 | -0.0039802 | 3.166e-06 | 1.8493e-06 | 0.024318 | 0.024318 | 0.024318 | 0.97194 | -0.54026 | 0.97173 | -0.54445 | 6.6807
60 | 0.0019178 | 0.00048053 | -0.0019178 | -0.00048065 | 3.7761e-08 | -1.2046e-07 | 0.0029368 | 0.0029368 | 0.0029368 | 0.97172 | -0.54471 | 0.9717 | -0.54512 | 0.80682
61 | 0.015859 | 0.0039777 | -0.015856 | -0.0039756 | 3.6085e-06 | 2.1071e-06 | 0.024278 | 0.024278 | 0.024278 | 0.97207 | -0.53781 | 0.97183 | -0.54258 | 6.6698
62 | -0.11493 | -0.029485 | 0.11493 | 0.029488 | 4.8823e-06 | 3.119e-06 | 0.17234 | 0.17234 | 0.17234 | 0.9937 | -0.11898 | 0.99374 | -0.1181 | 47.3462
63 | 0.093852 | 0.02389 | -0.093707 | -0.023797 | 0.00014503 | 9.2575e-05 | 0.14192 | 0.14192 | 0.14192 | 0.98493 | -0.28659 | 0.98327 | -0.3187 | 38.9894
64 | 0.028275 | 0.0071154 | -0.028225 | -0.0070842 | 5.0084e-05 | 3.1154e-05 | 0.043081 | 0.043082 | 0.043082 | 0.97686 | -0.44518 | 0.97497 | -0.48231 | 11.8356
65 | 0.00064516 | 0.00016101 | -0.00064515 | -0.00016123 | 6.5458e-09 | -2.2217e-07 | 0.00098251 | 0.00098259 | 0.00098259 | 0.97686 | -0.44518 | 0.97685 | -0.44539 | 0.26994
66 | 0.020188 | 0.0050659 | -0.020186 | -0.0050646 | 2.078e-06 | 1.2566e-06 | 0.03076 | 0.03076 | 0.03076 | 0.97665 | -0.44922 | 0.97655 | -0.45138 | 8.4505
67 | 0.028007 | 0.0070295 | -0.028007 | -0.0070295 | 3.46e-08 | 2.1513e-08 | 0.042748 | 0.042748 | 0.042748 | 0.97497 | -0.48231 | 0.97497 | -0.48234 | 11.7441
68 | 0.00064515 | 0.00016123 | -0.00064515 | -0.00016151 | 8.2255e-09 | -2.7912e-07 | 0.00098259 | 0.00098269 | 0.00098269 | 0.97685 | -0.44539 | 0.97683 | -0.44566 | 0.26997
69 | -0.054028 | -0.013714 | 0.054064 | 0.013737 | 3.6102e-05 | 2.2922e-05 | 0.081723 | 0.081723 | 0.081723 | 0.9845 | -0.29643 | 0.98521 | -0.28255 | 22.4513
70 | 0.0013856 | 0.00034667 | -0.0013856 | -0.00034715 | 6.609e-08 | -4.7938e-07 | 0.0020833 | 0.0020834 | 0.0020834 | 0.98963 | -0.197 | 0.98957 | -0.198 | 0.57238
71 | -0.0013856 | -0.00034726 | 0.0013856 | 0.00034715 | 1.4987e-08 | -1.0869e-07 | 0.0020835 | 0.0020834 | 0.0020835 | 0.98956 | -0.19823 | 0.98957 | -0.198 | 0.57239
72 | 0.0054423 | 0.001364 | -0.0054423 | -0.001364 | 4.7801e-08 | 7.9187e-09 | 0.0083395 | 0.0083395 | 0.0083395 | 0.97107 | -0.55763 | 0.97106 | -0.55782 | 2.2911
73 | -0.013335 | -0.0033433 | 0.013337 | 0.0033442 | 1.5397e-06 | 8.6346e-07 | 0.020423 | 0.020422 | 0.020423 | 0.97166 | -0.54592 | 0.97178 | -0.5435 | 5.6106
74 | 0.0051932 | 0.0013013 | -0.0051931 | -0.0013013 | 1.6195e-07 | 1.9177e-08 | 0.0079553 | 0.0079553 | 0.0079553 | 0.97137 | -0.55154 | 0.97134 | -0.55219 | 2.1855
75 | 0.0064927 | 0.001627 | -0.0064921 | -0.0016269 | 5.4033e-07 | 1.6525e-07 | 0.0099422 | 0.0099422 | 0.0099422 | 0.97173 | -0.54445 | 0.97164 | -0.54619 | 2.7314
76 | -0.0044402 | -0.0011127 | 0.0044403 | 0.0011127 | 9.5095e-08 | -8.4307e-09 | 0.0067662 | 0.0067662 | 0.0067662 | 0.97648 | -0.45111 | 0.9765 | -0.45066 | 1.8589
77 | 0.014663 | 0.0036768 | -0.014663 | -0.0036764 | 6.4409e-07 | 3.7e-07 | 0.022452 | 0.022452 | 0.022452 | 0.97183 | -0.54258 | 0.97178 | -0.5435 | 6.1682
78 | 0.0058715 | 0.0014714 | -0.0058715 | -0.0014714 | 7.6798e-09 | 1.4317e-09 | 0.0087599 | 0.0087599 | 0.0087599 | 0.99737 | -0.050008 | 0.99737 | -0.050036 | 2.4066
79 | -0.0073463 | -0.001841 | 0.007347 | 0.0018412 | 6.7154e-07 | 2.3522e-07 | 0.01096 | 0.01096 | 0.01096 | 0.99737 | -0.050008 | 0.99747 | -0.048089 | 3.011
80 | 0.004428 | 0.0011096 | -0.0044276 | -0.0011097 | 3.7136e-07 | -5.8422e-08 | 0.0066063 | 0.0066064 | 0.0066064 | 0.99737 | -0.050036 | 0.99728 | -0.051796 | 1.8149
81 | -0.0092008 | -0.0023059 | 0.0092008 | 0.0023059 | 2.6805e-08 | 1.2202e-08 | 0.013726 | 0.013726 | 0.013726 | 0.99747 | -0.048089 | 0.99747 | -0.048028 | 3.7708
82 | 0.0033237 | 0.00083299 | -0.0033237 | -0.00083299 | 7.9405e-10 | -6.1586e-10 | 0.0049592 | 0.0049592 | 0.0049592 | 0.99728 | -0.051796 | 0.99727 | -0.051801 | 1.3624
83 | -0.010938 | -0.0027413 | 0.010941 | 0.0027429 | 3.1353e-06 | 1.5966e-06 | 0.016317 | 0.016317 | 0.016317 | 0.99747 | -0.048028 | 0.99778 | -0.042013 | 4.4828
84 | 0.0022179 | 0.00055585 | -0.0022179 | -0.00055585 | 2.3215e-10 | -5.8503e-10 | 0.0033093 | 0.0033093 | 0.0033093 | 0.99727 | -0.051801 | 0.99727 | -0.051804 | 0.90914
85 | -0.11978 | -0.030572 | 0.12002 | 0.030726 | 0.00024367 | 0.00015489 | 0.17883 | 0.17883 | 0.17883 | 0.99778 | -0.042013 | 1 | 0 | 24.5642
86 | 0.10634 | 0.027203 | -0.10599 | -0.026982 | 0.00034787 | 0.00022072 | 0.15879 | 0.15879 | 0.15879 | 0.99778 | -0.042013 | 0.99422 | -0.10984 | 21.8113
87 | 0.0011077 | 0.00027762 | -0.0011077 | -0.00027762 | 1.072e-10 | -1.3111e-09 | 0.0016528 | 0.0016528 | 0.0016528 | 0.99727 | -0.051804 | 0.99727 | -0.051806 | 0.45407
88 | 0.12572 | 0.03246 | -0.12561 | -0.032389 | 0.0001115 | 7.0917e-05 | 0.18741 | 0.18741 | 0.18741 | 1 | 0 | 0.99903 | -0.018207 | 25.7434
89 | 0.007976 | 0.0019989 | -0.0079752 | -0.0019986 | 7.4758e-07 | 2.928e-07 | 0.011868 | 0.011868 | 0.011868 | 1 | 0 | 0.9999 | -0.0019676 | 3.2606
90 | 0.08899 | 0.02272 | -0.088873 | -0.022645 | 0.00011756 | 7.5012e-05 | 0.13334 | 0.13334 | 0.13334 | 0.99422 | -0.10984 | 0.99278 | -0.13721 | 36.6313
91 | 0.12216 | 0.031524 | -0.12197 | -0.031405 | 0.00018687 | 0.00011881 | 0.18227 | 0.18227 | 0.18227 | 0.99903 | -0.018207 | 0.99736 | -0.049646 | 25.037
92 | 0.0058047 | 0.0014546 | -0.0058044 | -0.0014546 | 3.1291e-07 | 5.3599e-08 | 0.0086383 | 0.0086384 | 0.0086384 | 0.9999 | -0.0019676 | 0.99984 | -0.0030993 | 2.3732
93 | -0.092215 | -0.023397 | 0.092283 | 0.02344 | 6.7224e-05 | 4.2907e-05 | 0.13977 | 0.13977 | 0.13977 | 0.98249 | -0.33384 | 0.98327 | -0.3187 | 38.3974
94 | -0.11601 | -0.029759 | 0.11609 | 0.029808 | 7.5541e-05 | 4.826e-05 | 0.17396 | 0.17396 | 0.17396 | 0.99374 | -0.1181 | 0.99445 | -0.10469 | 47.7914
95 | -0.11718 | -0.030082 | 0.11726 | 0.03013 | 7.6086e-05 | 4.8609e-05 | 0.1756 | 0.1756 | 0.1756 | 0.99445 | -0.10469 | 0.99516 | -0.091321 | 48.2406
96 | -0.11836 | -0.030408 | 0.11844 | 0.030458 | 7.9699e-05 | 5.092e-05 | 0.17725 | 0.17725 | 0.17725 | 0.99516 | -0.091321 | 0.99589 | -0.077466 | 48.6953
97 | -0.11958 | -0.030744 | 0.11966 | 0.030795 | 8.0356e-05 | 5.134e-05 | 0.17895 | 0.17895 | 0.17895 | 0.99589 | -0.077466 | 0.99662 | -0.063648 | 49.1626
98 | -0.12078 | -0.031075 | 0.12086 | 0.031128 | 8.2291e-05 | 5.2579e-05 | 0.18062 | 0.18062 | 0.18062 | 0.99662 | -0.063648 | 0.99736 | -0.049646 | 49.6205
99 | 0.0039883 | 0.00099942 | -0.0039883 | -0.00099943 | 1.1049e-08 | -3.8973e-09 | 0.0059355 | 0.0059355 | 0.0059355 | 0.99984 | -0.0030993 | 0.99984 | -0.0031575 | 1.6306
100 | 0.0021877 | 0.00054817 | -0.0021877 | -0.00054828 | 4.2085e-08 | -1.1191e-07 | 0.0032559 | 0.0032559 | 0.0032559 | 0.99984 | -0.0031575 | 0.99981 | -0.0035613 | 0.89448
101 | 0.0093069 | 0.0023327 | -0.0093061 | -0.0023323 | 8.3989e-07 | 3.9812e-07 | 0.014179 | 0.014179 | 0.014179 | 0.97671 | -0.44646 | 0.97662 | -0.44835 | 3.8954
102 | 0.0072798 | 0.0018245 | -0.0072791 | -0.0018242 | 7.456e-07 | 2.7499e-07 | 0.011092 | 0.011092 | 0.011092 | 0.97662 | -0.44835 | 0.97651 | -0.4505 | 3.0472
103 | 0.0057169 | 0.0014327 | -0.0057169 | -0.0014327 | 4.3785e-08 | 8.7753e-09 | 0.0087115 | 0.0087115 | 0.0087115 | 0.97651 | -0.4505 | 0.9765 | -0.45066 | 2.3933
104 | 0.0051924 | 0.0013011 | -0.0051923 | -0.0013011 | 1.6533e-07 | 1.9455e-08 | 0.0079518 | 0.0079518 | 0.0079518 | 0.97164 | -0.54619 | 0.97161 | -0.54686 | 2.1846
105 | 0.0038951 | 0.000976 | -0.003895 | -0.00097603 | 9.3033e-08 | -2.6802e-08 | 0.0059653 | 0.0059653 | 0.0059653 | 0.97161 | -0.54686 | 0.97159 | -0.54736 | 1.6388
106 | 0.0038944 | 0.00097584 | -0.0038943 | -0.00097587 | 9.3025e-08 | -2.6736e-08 | 0.0059658 | 0.0059658 | 0.0059658 | 0.97134 | -0.55219 | 0.97132 | -0.55269 | 1.639
107 | 0.0025967 | 0.00065065 | -0.0025967 | -0.00065071 | 4.1339e-08 | -5.986e-08 | 0.0039769 | 0.0039769 | 0.0039769 | 0.97159 | -0.54736 | 0.97157 | -0.5477 | 1.0926
108 | 0.0025965 | 0.00065062 | -0.0025965 | -0.00065068 | 4.1358e-08 | -5.9806e-08 | 0.0039777 | 0.0039777 | 0.0039777 | 0.97132 | -0.55269 | 0.9713 | -0.55303 | 1.0928
109 | 0.0012989 | 0.00032545 | -0.0012989 | -0.00032553 | 1.0345e-08 | -7.9703e-08 | 0.0019893 | 0.0019893 | 0.0019893 | 0.97157 | -0.5477 | 0.97156 | -0.54787 | 0.54652
110 | -0.079888 | -0.02034 | 0.080029 | 0.020429 | 0.00014048 | 8.9571e-05 | 0.12008 | 0.12008 | 0.12008 | 0.99088 | -0.17361 | 0.99278 | -0.13721 | 32.9897
111 | 0.075894 | 0.019338 | -0.075811 | -0.019286 | 8.2753e-05 | 5.2744e-05 | 0.11408 | 0.11408 | 0.11408 | 0.99088 | -0.17361 | 0.9897 | -0.19623 | 31.3418
112 | 0.0053454 | 0.0013395 | -0.0053442 | -0.0013394 | 1.1205e-06 | 1.1534e-07 | 0.0080117 | 0.0080119 | 0.0080119 | 0.99278 | -0.13721 | 0.99256 | -0.14162 | 2.2011
113 | 0.07183 | 0.018288 | -0.071793 | -0.018264 | 3.742e-05 | 2.3839e-05 | 0.1081 | 0.1081 | 0.1081 | 0.9897 | -0.19623 | 0.98914 | -0.20704 | 29.6974
114 | 0.0058568 | 0.0014675 | -0.0058565 | -0.0014674 | 2.9523e-07 | 5.8773e-08 | 0.0088105 | 0.0088106 | 0.0088106 | 0.98914 | -0.20704 | 0.98908 | -0.2081 | 2.4205
115 | 0.065936 | 0.016797 | -0.065891 | -0.016768 | 4.4473e-05 | 2.8308e-05 | 0.099288 | 0.099288 | 0.099288 | 0.98914 | -0.20704 | 0.98841 | -0.22104 | 27.277
116 | 0.064454 | 0.016408 | -0.064427 | -0.016391 | 2.7215e-05 | 1.7319e-05 | 0.097124 | 0.097124 | 0.097124 | 0.98841 | -0.22104 | 0.98795 | -0.2298 | 26.6824
117 | 0.061572 | 0.015675 | -0.06151 | -0.015636 | 6.235e-05 | 3.9657e-05 | 0.092825 | 0.092825 | 0.092825 | 0.98795 | -0.2298 | 0.98686 | -0.25082 | 25.5014
118 | 0.059484 | 0.015128 | -0.059479 | -0.015125 | 4.9609e-06 | 3.154e-06 | 0.089771 | 0.089771 | 0.089771 | 0.98686 | -0.25082 | 0.98677 | -0.25255 | 24.6623
119 | -0.006068 | -0.0015208 | 0.006069 | 0.001521 | 9.7282e-07 | 2.449e-07 | 0.0092585 | 0.0092583 | 0.0092585 | 0.97525 | -0.47687 | 0.97542 | -0.47351 | 2.5435
120 | -0.0078237 | -0.0019608 | 0.0078242 | 0.001961 | 4.4956e-07 | 1.8266e-07 | 0.011935 | 0.011935 | 0.011935 | 0.97542 | -0.47351 | 0.97548 | -0.4723 | 3.2789
121 | 0.055529 | 0.014135 | -0.055449 | -0.014084 | 8.0185e-05 | 5.093e-05 | 0.083814 | 0.083815 | 0.083815 | 0.98677 | -0.25255 | 0.98521 | -0.28255 | 23.026
122 | 0.0058565 | 0.0014674 | -0.0058556 | -0.0014673 | 8.3599e-07 | 1.6651e-07 | 0.0088106 | 0.0088107 | 0.0088107 | 0.98908 | -0.2081 | 0.98893 | -0.2111 | 2.4205
123 | 0.0045523 | 0.0011407 | -0.0045519 | -0.0011408 | 3.1805e-07 | -2.8366e-08 | 0.0068496 | 0.0068497 | 0.0068497 | 0.98893 | -0.2111 | 0.98885 | -0.21257 | 1.8818
124 | 0.0013034 | 0.00032653 | -0.0013033 | -0.00032665 | 1.4332e-08 | -1.1832e-07 | 0.0019611 | 0.0019611 | 0.0019611 | 0.98893 | -0.2111 | 0.98892 | -0.21133 | 0.53877
125 | 0.0045519 | 0.0011408 | -0.0045517 | -0.0011408 | 2.1018e-07 | -1.8724e-08 | 0.0068497 | 0.0068497 | 0.0068497 | 0.98885 | -0.21257 | 0.9888 | -0.21354 | 1.8818
126 | -0.0057582 | -0.0014431 | 0.0057587 | 0.0014432 | 4.942e-07 | 1.0477e-07 | 0.0088017 | 0.0088017 | 0.0088017 | 0.97347 | -0.51186 | 0.97356 | -0.51006 | 2.4181
127 | -0.011521 | -0.0028873 | 0.011523 | 0.0028888 | 2.8109e-06 | 1.4983e-06 | 0.017608 | 0.017608 | 0.017608 | 0.97356 | -0.51006 | 0.97382 | -0.50494 | 4.8375
128 | -0.014164 | -0.0035505 | 0.014164 | 0.0035505 | 9.0142e-09 | 5.135e-09 | 0.021643 | 0.021643 | 0.021643 | 0.97382 | -0.50494 | 0.97382 | -0.50493 | 5.9458
129 | -0.0096581 | -0.0024206 | 0.0096593 | 0.0024212 | 1.2129e-06 | 5.9018e-07 | 0.014733 | 0.014733 | 0.014733 | 0.97548 | -0.4723 | 0.97562 | -0.46966 | 4.0474
130 | -0.016807 | -0.0042129 | 0.016807 | 0.004213 | 1.5547e-07 | 9.1681e-08 | 0.025681 | 0.025681 | 0.025681 | 0.97382 | -0.50493 | 0.97383 | -0.50474 | 7.0552
131 | 0.019183 | 0.0048134 | -0.019178 | -0.0048103 | 5.2573e-06 | 3.1595e-06 | 0.029233 | 0.029233 | 0.029233 | 0.97655 | -0.45138 | 0.97625 | -0.45713 | 8.031
132 | 0.027789 | 0.0069748 | -0.027772 | -0.0069644 | 1.6743e-05 | 1.0406e-05 | 0.042415 | 0.042415 | 0.042415 | 0.97497 | -0.48234 | 0.97433 | -0.49498 | 11.6526
133 | 0.0002123 | 5.3031e-05 | -0.0002123 | -5.3207e-05 | 5.5238e-10 | -1.7599e-07 | 0.00032333 | 0.0003234 | 0.0003234 | 0.97683 | -0.44566 | 0.97683 | -0.44571 | 0.088845
134 | -0.013778 | -0.0034534 | 0.013778 | 0.0034537 | 5.6395e-07 | 3.184e-07 | 0.021014 | 0.021014 | 0.021014 | 0.97562 | -0.46966 | 0.97566 | -0.4688 | 5.7731
135 | -0.015663 | -0.0039261 | 0.015665 | 0.0039272 | 1.9368e-06 | 1.1265e-06 | 0.023889 | 0.023889 | 0.023889 | 0.97566 | -0.4688 | 0.97579 | -0.46621 | 6.5628
136 | -0.017255 | -0.0043257 | 0.01726 | 0.0043287 | 5.1179e-06 | 3.0292e-06 | 0.026313 | 0.026313 | 0.026313 | 0.97579 | -0.46621 | 0.97611 | -0.45999 | 7.2289
137 | 0.024566 | 0.0061609 | -0.024565 | -0.0061604 | 7.7682e-07 | 4.7884e-07 | 0.037519 | 0.037519 | 0.037519 | 0.97433 | -0.49498 | 0.97429 | -0.49564 | 10.3074
138 | -0.019379 | -0.0048577 | 0.019388 | 0.0048628 | 8.3844e-06 | 5.0486e-06 | 0.029612 | 0.029612 | 0.029612 | 0.97383 | -0.50474 | 0.97429 | -0.49566 | 8.1351
139 | -0.022008 | -0.0055194 | 0.022008 | 0.0055194 | 1.5694e-08 | 9.5777e-09 | 0.033613 | 0.033613 | 0.033613 | 0.97429 | -0.49566 | 0.97429 | -0.49564 | 9.2344
140 | -0.018218 | -0.0045688 | 0.01822 | 0.0045702 | 2.4828e-06 | 1.4817e-06 | 0.027773 | 0.027773 | 0.027773 | 0.97611 | -0.45999 | 0.97625 | -0.45713 | 7.63
141 | 0.0012976 | 0.00032514 | -0.0012976 | -0.0003252 | 7.6873e-09 | -5.9287e-08 | 0.0019879 | 0.0019879 | 0.0019879 | 0.9713 | -0.55303 | 0.97129 | -0.55315 | 0.54612

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25537 | 0.065185

## res_load
| p_mw | q_mvar
0 | 0.0014611 | 0.00036618
1 | 0.0059569 | 0.0014929
2 | 0.0016415 | 0.00041139
3 | 0.0039498 | 0.00098992
4 | 0.0014878 | 0.00037287
5 | 0.0015708 | 0.00039367
6 | 0.0012395 | 0.00031066
7 | 0.0017473 | 0.00043791
8 | 0.0016377 | 0.00041044
9 | 0.002327 | 0.00058321
10 | 0.0011249 | 0.00028194
11 | 0.0011249 | 0.00028194
12 | 0.0017786 | 0.00044576
13 | 0.0010981 | 0.00027521
14 | 0.0033126 | 0.00083022
15 | 0.00084243 | 0.00021113
16 | 0.0010964 | 0.0002748
17 | 0.0012411 | 0.00031104
18 | 0.0015599 | 0.00039095
19 | 0.001407 | 0.00035262
20 | 0.0025853 | 0.00064793
21 | 0.0012987 | 0.00032549
22 | 0.0015244 | 0.00038204
23 | 0.0015438 | 0.00038692
24 | 0.0013224 | 0.00033143
25 | 0.0012417 | 0.00031121
26 | 0.0021048 | 0.00052751
27 | 0.001284 | 0.00032181
28 | 0.002489 | 0.00062379
29 | 0.0012059 | 0.00030222
30 | 0.0015238 | 0.0003819
31 | 0.0019094 | 0.00047855
32 | 0.0035758 | 0.00089617
33 | 0.0014258 | 0.00035735
34 | 0.0067278 | 0.0016861
35 | 0.00112 | 0.0002807
36 | 0.0015539 | 0.00038945
37 | 0.0010009 | 0.00025086
38 | 0.00021839 | 5.4734e-05
39 | 0.0023148 | 0.00058014
40 | 0.0015599 | 0.00039095
41 | 0.0013856 | 0.00034726
42 | 0.0013125 | 0.00032895
43 | 0.0025832 | 0.00064741
44 | 0.0014528 | 0.0003641
45 | 0.0013685 | 0.00034299
46 | 0.0015739 | 0.00039446
47 | 0.0011924 | 0.00029884
48 | 0.0013256 | 0.00033223
49 | 0.0014748 | 0.00036961
50 | 0.0014435 | 0.00036178
51 | 0.0018539 | 0.00046462
52 | 0.0011039 | 0.00027667
53 | 0.0017373 | 0.00043541
54 | 0.0011058 | 0.00027714
55 | 0.0024979 | 0.00062604
56 | 0.0011101 | 0.00027823
57 | 0.017003 | 0.0042615
58 | 0.0011077 | 0.00027762
59 | 0.0034529 | 0.00086537
60 | 0.0021705 | 0.00054398
61 | 0.0017582 | 0.00044064
62 | 0.0014239 | 0.00035686
63 | 0.0010823 | 0.00027124
64 | 0.001093 | 0.00027392
65 | 0.0011068 | 0.00027739
66 | 0.0011386 | 0.00028535
67 | 0.0011163 | 0.00027977
68 | 0.0011065 | 0.00027731
69 | 0.0018161 | 0.00045517
70 | 0.0018005 | 0.00045126
71 | 0.0021877 | 0.00054828
72 | 0.0019178 | 0.00048065
73 | 0.0014886 | 0.00037309
74 | 0.0020262 | 0.00050782
75 | 0.0054423 | 0.001364
76 | 0.0015621 | 0.00039151
77 | 0.0012766 | 0.00031995
78 | 0.0012997 | 0.00032573
79 | 0.0012972 | 0.0003251
80 | 0.0012987 | 0.00032548
81 | 0.0012983 | 0.00032538
82 | 0.0012978 | 0.00032525
83 | 0.0012978 | 0.00032525
84 | 0.0039943 | 0.0010011
85 | 0.0034986 | 0.00087683
86 | 0.0039813 | 0.0009978
87 | 0.0053442 | 0.0013394
88 | 0.0014376 | 0.00036031
89 | 0.0028543 | 0.00071535
90 | 0.0020257 | 0.00050768
91 | 0.006068 | 0.0015208
92 | 0.0017547 | 0.00043977
93 | 0.0039498 | 0.00098992
94 | 0.001385 | 0.00034712
95 | 0.0013033 | 0.00032665
96 | 0.0045517 | 0.0011408
97 | 0.0057582 | 0.0014431
98 | 0.005762 | 0.0014441
99 | 0.0026402 | 0.00066171
100 | 0.0018339 | 0.00045962
101 | 0.0026429 | 0.00066237
102 | 0.0010022 | 0.00025118
103 | 0.00021825 | 5.4699e-05
104 | 0.00043285 | 0.00010848
105 | 0.0041184 | 0.0010322
106 | 0.0018849 | 0.00047241
107 | 0.0015899 | 0.00039846
108 | 0.0002123 | 5.3207e-05
109 | 0.003206 | 0.00080351
110 | 0.0025725 | 0.00064472
111 | 0.00262 | 0.00065664
112 | 0.0025574 | 0.00064095
113 | 0.00095773 | 0.00024003
114 | 0.00095773 | 0.00024003
115 | 0.0012989 | 0.00032553
116 | 0.0012976 | 0.0003252
117 | 0.0012989 | 0.00032553

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1