## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-224_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-224_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-224_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-224_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-224_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-224_0_4_node_56 | 0.4 | n |  | TRUE
6 | bus_LV_230-224_0_4_node_65 | 0.4 | n |  | TRUE
7 | bus_LV_230-224_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_230-224_0_4_node_51 | 0.4 | n |  | TRUE
9 | bus_LV_230-224_0_4_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_230-224_0_4_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_230-224_0_4_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_230-224_0_4_node_69 | 0.4 | n |  | TRUE
13 | bus_LV_230-224_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_230-224_0_4_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_230-224_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_230-224_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_230-224_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_230-224_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_230-224_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_230-224_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_230-224_0_4_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_230-224_0_4_node_77 | 0.4 | n |  | TRUE
23 | bus_LV_230-224_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_230-224_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_230-224_0_4_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_230-224_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_230-224_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_230-224_0_4_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_230-224_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_230-224_0_4_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_230-224_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_230-224_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_230-224_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_230-224_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_230-224_0_4_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_230-224_0_4_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_230-224_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_230-224_0_4_node_78 | 0.4 | n |  | TRUE
39 | bus_LV_230-224_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_230-224_0_4_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_230-224_0_4_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_230-224_0_4_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_230-224_0_4_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_230-224_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_230-224_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_230-224_0_4_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_230-224_0_4_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_230-224_0_4_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_230-224_0_4_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_230-224_0_4_node_70 | 0.4 | n |  | TRUE
51 | bus_LV_230-224_0_4_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_230-224_0_4_node_61 | 0.4 | n |  | TRUE
53 | bus_LV_230-224_0_4_node_76 | 0.4 | n |  | TRUE
54 | bus_LV_230-224_0_4_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_230-224_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_230-224_0_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_230-224_0_4_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_230-224_0_4_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_230-224_0_4_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_230-224_0_4_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_230-224_0_4_node_72 | 0.4 | n |  | TRUE
62 | bus_LV_230-224_0_4_node_64 | 0.4 | n |  | TRUE
63 | bus_LV_230-224_0_4_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_230-224_0_4_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_230-224_0_4_node_74 | 0.4 | n |  | TRUE
66 | bus_LV_230-224_0_4_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_230-224_0_4_node_42 | 0.4 | n |  | TRUE
68 | bus_LV_230-224_0_4_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_230-224_0_4_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_230-224_0_4_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_230-224_0_4_node_38 | 0.4 | n |  | TRUE
72 | bus_MV_370_0_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-224_0_4_load_0 | 0 | 0.0073739 | 0.0018481 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-224_0_4_load_1 | 1 | 0.012501 | 0.0031332 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-224_0_4_load_3 | 3 | 0.012572 | 0.0031509 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-224_0_4_load_65 | 6 | 0.01566 | 0.0039249 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-224_0_4_load_5 | 7 | 0.0096112 | 0.0024088 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-224_0_4_load_51 | 8 | 0.0059489 | 0.0014909 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-224_0_4_load_57 | 9 | 0.0080226 | 0.0020107 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-224_0_4_load_55 | 10 | 0.012596 | 0.0031569 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-224_0_4_load_66 | 11 | 0.0094259 | 0.0023624 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-224_0_4_load_69 | 12 | 0.0093645 | 0.002347 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-224_0_4_load_6 | 15 | 0.019008 | 0.0047638 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-224_0_4_load_9 | 18 | 0.036453 | 0.009136 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-224_0_4_load_75 | 21 | 0.0058023 | 0.0014542 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-224_0_4_load_77 | 22 | 0.0062086 | 0.001556 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-224_0_4_load_59 | 25 | 0.0096121 | 0.002409 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-224_0_4_load_71 | 28 | 0.011184 | 0.002803 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-224_0_4_load_73 | 30 | 0.0075163 | 0.0018838 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-224_0_4_load_36 | 34 | 0.0076512 | 0.0019176 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-224_0_4_load_49 | 35 | 0.0057111 | 0.0014313 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-224_0_4_load_60 | 36 | 0.0075247 | 0.0018859 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-224_0_4_load_78 | 38 | 0.005962 | 0.0014942 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-224_0_4_load_54 | 40 | 0.0049186 | 0.0012327 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-224_0_4_load_53 | 41 | 0.0095669 | 0.0023977 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-224_0_4_load_44 | 44 | 0.010549 | 0.0026438 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-224_0_4_load_67 | 47 | 0.0092017 | 0.0023062 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-224_0_4_load_43 | 49 | 0.012445 | 0.003119 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-224_0_4_load_70 | 50 | 0.019483 | 0.0048829 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-224_0_4_load_76 | 53 | 0.0080547 | 0.0020187 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-224_0_4_load_41 | 55 | 0.010993 | 0.0027551 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-224_0_4_load_40 | 56 | 0.0096416 | 0.0024164 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-224_0_4_load_50 | 58 | 0.0040263 | 0.0010091 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-224_0_4_load_48 | 59 | 0.0091197 | 0.0022856 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-224_0_4_load_58 | 60 | 0.0096209 | 0.0024112 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-224_0_4_load_72 | 61 | 0.0075219 | 0.0018852 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-224_0_4_load_37 | 63 | 0.02711 | 0.0067943 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-224_0_4_load_74 | 65 | 0.0080539 | 0.0020185 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-224_0_4_load_46 | 66 | 0.011585 | 0.0029035 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-224_0_4_load_42 | 67 | 0.012128 | 0.0030395 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-224_0_4_load_68 | 68 | 0.0088918 | 0.0022285 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-224_0_4_load_62 | 69 | 0.0080563 | 0.0020191 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-224_0_4_load_39 | 70 | 0.0083885 | 0.0021023 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-224_0_4_load_38 | 71 | 0.0080786 | 0.0020247 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-224_0_4_line_0 |  | 0 | 1 | 0.0037194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_230-224_0_4_line_1 |  | 0 | 2 | 0.034638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_230-224_0_4_line_2 |  | 1 | 3 | 0.011171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_230-224_0_4_line_3 |  | 2 | 4 | 0.001275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_230-224_0_4_line_4 |  | 3 | 5 | 0.01675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_230-224_0_4_line_5 |  | 4 | 6 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_230-224_0_4_line_6 |  | 5 | 9 | 0.028098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_230-224_0_4_line_7 |  | 5 | 10 | 0.0031733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-224_0_4_line_8 |  | 6 | 13 | 0.0177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_230-224_0_4_line_9 |  | 7 | 8 | 0.037568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-224_0_4_line_10 |  | 8 | 14 | 0.012921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-224_0_4_line_11 |  | 9 | 22 | 0.039096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_230-224_0_4_line_12 |  | 11 | 12 | 0.015031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_230-224_0_4_line_13 |  | 12 | 68 | 0.016272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_230-224_0_4_line_14 |  | 13 | 48 | 0.020832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_230-224_0_4_line_15 |  | 14 | 37 | 0.02349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-224_0_4_line_16 |  | 14 | 39 | 0.004724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-224_0_4_line_17 |  | 15 | 16 | 0.0225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-224_0_4_line_18 |  | 15 | 17 | 0.056992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-224_0_4_line_19 |  | 16 | 18 | 0.0061826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-224_0_4_line_20 |  | 16 | 19 | 0.13021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-224_0_4_line_21 |  | 17 | 20 | 0.15111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-224_0_4_line_22 |  | 19 | 21 | 0.021462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-224_0_4_line_23 |  | 20 | 22 | 0.035763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-224_0_4_line_24 |  | 23 | 24 | 0.021527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-224_0_4_line_25 |  | 23 | 25 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-224_0_4_line_26 |  | 24 | 36 | 0.021364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-224_0_4_line_27 |  | 25 | 60 | 0.019087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-224_0_4_line_28 |  | 26 | 27 | 0.031323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-224_0_4_line_29 |  | 26 | 28 | 0.014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-224_0_4_line_30 |  | 27 | 29 | 0.021441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_230-224_0_4_line_31 |  | 27 | 30 | 0.024779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_230-224_0_4_line_32 |  | 28 | 61 | 0.0057465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-224_0_4_line_33 |  | 29 | 35 | 0.031019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_230-224_0_4_line_34 |  | 30 | 62 | 0.0027898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_230-224_0_4_line_35 |  | 31 | 32 | 0.018328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-224_0_4_line_36 |  | 31 | 33 | 0.082544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-224_0_4_line_37 |  | 31 | 34 | 0.021393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-224_0_4_line_38 |  | 32 | 40 | 0.016998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-224_0_4_line_39 |  | 32 | 41 | 0.0050807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-224_0_4_line_40 |  | 32 | 39 | 0.030733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-224_0_4_line_41 |  | 33 | 50 | 0.015459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-224_0_4_line_42 |  | 34 | 63 | 0.012289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-224_0_4_line_43 |  | 35 | 59 | 0.017239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_230-224_0_4_line_44 |  | 36 | 52 | 0.026605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_230-224_0_4_line_45 |  | 37 | 38 | 0.0064937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-224_0_4_line_46 |  | 40 | 60 | 0.017721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-224_0_4_line_47 |  | 42 | 43 | 0.019338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_230-224_0_4_line_48 |  | 42 | 44 | 0.0070334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_230-224_0_4_line_49 |  | 43 | 46 | 0.014053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_230-224_0_4_line_50 |  | 43 | 66 | 0.021544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-224_0_4_line_51 |  | 44 | 48 | 0.011545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_230-224_0_4_line_52 |  | 45 | 46 | 0.00378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_230-224_0_4_line_53 |  | 45 | 47 | 0.017279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_230-224_0_4_line_54 |  | 46 | 58 | 0.029073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_230-224_0_4_line_55 |  | 47 | 68 | 0.016434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_230-224_0_4_line_56 |  | 48 | 49 | 0.0084465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-224_0_4_line_57 |  | 49 | 67 | 0.019301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-224_0_4_line_58 |  | 51 | 52 | 0.032352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_230-224_0_4_line_59 |  | 51 | 53 | 0.010117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_230-224_0_4_line_60 |  | 52 | 69 | 0.012845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-224_0_4_line_61 |  | 53 | 64 | 0.019536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_230-224_0_4_line_62 |  | 54 | 55 | 0.0084684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-224_0_4_line_63 |  | 54 | 56 | 0.016845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-224_0_4_line_64 |  | 55 | 66 | 0.020575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-224_0_4_line_65 |  | 56 | 70 | 0.019666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-224_0_4_line_66 |  | 57 | 58 | 0.0029529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_230-224_0_4_line_67 |  | 57 | 59 | 0.019254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_230-224_0_4_line_68 |  | 62 | 64 | 0.015263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_230-224_0_4_line_69 |  | 62 | 65 | 0.012756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-224_0_4_line_70 |  | 70 | 71 | 0.019064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-224_0_4_trafo_66 | 0.63 MVA 20/0.4 kV | 72 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2699689.4566 | 1260732.3267 | 2699687.474 | 1260735.4736 | 2699687.474 | 1260735.4736
1 | 2699685.0613 | 1260697.969 | 2699689.4566 | 1260732.3267
2 | 2699688.9579 | 1260746.5457 | 2699687.474 | 1260735.4736
3 | 2699685.0613 | 1260697.969 | 2699683.7924 | 1260698.1255
4 | 2699691.183 | 1260763.1477 | 2699688.9579 | 1260746.5457
5 | 2699683.7924 | 1260698.1255 | 2699665.8577 | 1260700.4023
6 | 2699691.183 | 1260763.1477 | 2699719.0904 | 1260759.884
7 | 2699691.183 | 1260763.1477 | 2699689.8755 | 1260766.0391
8 | 2699648.2985 | 1260702.6313 | 2699665.8577 | 1260700.4023
9 | 2699720.3913 | 1260701.3838 | 2699724.6063 | 1260700.8488 | 2699733.8366 | 1260699.6812 | 2699732.9912 | 1260693.0504 | 2699750.1837 | 1260690.8623
10 | 2699763.0015 | 1260689.231 | 2699750.1837 | 1260690.8623
11 | 2699755.1358 | 1260765.6785 | 2699742.5771 | 1260766.8613 | 2699731.738 | 1260758.405 | 2699719.0904 | 1260759.884
12 | 2699663.3418 | 1260649.5606 | 2699678.2516 | 1260647.6576
13 | 2699647.2006 | 1260651.6209 | 2699663.3418 | 1260649.5606
14 | 2699627.6322 | 1260705.2521 | 2699632.1644 | 1260704.6724 | 2699648.2985 | 1260702.6313
15 | 2699763.0015 | 1260689.231 | 2699771.3364 | 1260711.2006
16 | 2699763.0015 | 1260689.231 | 2699761.3046 | 1260684.821
17 | 2699841.3563 | 1260697.9153 | 2699832.8651 | 1260701.2859 | 2699837.2261 | 1260713.9189
18 | 2699807.4985 | 1260745.6943 | 2699843.2558 | 1260731.3858 | 2699837.2261 | 1260713.9189
19 | 2699841.3563 | 1260697.9153 | 2699839.0943 | 1260692.1613
20 | 2699934.9272 | 1260651.4013 | 2699935.9806 | 1260655.5225 | 2699891.8141 | 1260670.5334 | 2699897.3215 | 1260684.5045 | 2699844.195 | 1260704.7799 | 2699841.3563 | 1260697.9153
21 | 2699807.4985 | 1260745.6943 | 2699832.4921 | 1260809.9685 | 2699818.8175 | 1260815.4534 | 2699815.228 | 1260816.894 | 2699813.8199 | 1260812.8003 | 2699800.3052 | 1260773.985 | 2699795.1712 | 1260774.4988 | 2699790.7413 | 1260762.3252
22 | 2699934.9272 | 1260651.4013 | 2699913.7537 | 1260654.9107
23 | 2699790.7413 | 1260762.3252 | 2699755.1358 | 1260765.6785
24 | 2699717.7755 | 1260574.9419 | 2699720.8178 | 1260573.3251 | 2699725.8917 | 1260590.6804
25 | 2699725.8917 | 1260590.6804 | 2699731.493 | 1260605.7138
26 | 2699717.7755 | 1260574.9419 | 2699715.1363 | 1260573.2182 | 2699705.5883 | 1260573.1017 | 2699696.9893 | 1260574.1503
27 | 2699738.1573 | 1260623.6001 | 2699731.493 | 1260605.7138
28 | 2699592.6611 | 1260562.847 | 2699602.2058 | 1260592.6876
29 | 2699602.2058 | 1260592.6876 | 2699605.6978 | 1260596.1381 | 2699614.9688 | 1260595.1848
30 | 2699578.3092 | 1260562.4274 | 2699578.7513 | 1260556.7635 | 2699582.7063 | 1260557.3417 | 2699586.6988 | 1260557.9316 | 2699588.3865 | 1260559.3166 | 2699592.6611 | 1260562.847
31 | 2699592.6611 | 1260562.847 | 2699598.2494 | 1260559.9832 | 2699616.6362 | 1260557.9449
32 | 2699614.9688 | 1260595.1848 | 2699620.6852 | 1260594.597
33 | 2699578.3092 | 1260562.4274 | 2699578.4928 | 1260567.6347 | 2699579.1338 | 1260572.5384 | 2699580.5967 | 1260578.7681 | 2699582.5026 | 1260584.6494 | 2699585.4688 | 1260592.3817
34 | 2699619.409 | 1260557.6375 | 2699616.6362 | 1260557.9449
35 | 2699750.2791 | 1260656.1339 | 2699753.514 | 1260664.5397 | 2699758.4587 | 1260662.7439 | 2699762.2735 | 1260661.3515
36 | 2699780.5876 | 1260604.7362 | 2699779.3277 | 1260605.2487 | 2699775.5045 | 1260608.031 | 2699762.8578 | 1260612.4324 | 2699746.1352 | 1260619.4007 | 2699762.2735 | 1260661.3515
37 | 2699762.2735 | 1260661.3515 | 2699766.0046 | 1260661.3477 | 2699782.4644 | 1260654.9422
38 | 2699750.2791 | 1260656.1339 | 2699744.3444 | 1260640.2058
39 | 2699750.2791 | 1260656.1339 | 2699745.9383 | 1260658.774
40 | 2699750.2791 | 1260656.1339 | 2699753.514 | 1260664.5397 | 2699761.3046 | 1260684.821
41 | 2699780.5876 | 1260604.7362 | 2699770.7184 | 1260592.8378
42 | 2699793.9179 | 1260650.4873 | 2699789.9044 | 1260652.0431 | 2699786.9832 | 1260653.1837 | 2699782.4644 | 1260654.9422
43 | 2699591.643 | 1260608.4767 | 2699585.4688 | 1260592.3817
44 | 2699670.5801 | 1260577.3709 | 2699696.9893 | 1260574.1503
45 | 2699771.3364 | 1260711.2006 | 2699773.6407 | 1260717.2717
46 | 2699738.1573 | 1260623.6001 | 2699744.3444 | 1260640.2058
47 | 2699615.0219 | 1260669.4884 | 2699616.6884 | 1260673.92 | 2699621.506 | 1260687.7124
48 | 2699621.506 | 1260687.7124 | 2699623.8252 | 1260694.3524
49 | 2699615.0219 | 1260669.4884 | 2699609.9971 | 1260656.3597
50 | 2699615.0219 | 1260669.4884 | 2699593.7565 | 1260672.9416
51 | 2699627.6322 | 1260705.2521 | 2699623.8252 | 1260694.3524
52 | 2699609.9971 | 1260656.3597 | 2699613.7586 | 1260655.8893
53 | 2699613.7586 | 1260655.8893 | 2699630.8986 | 1260653.7016
54 | 2699609.9971 | 1260656.3597 | 2699600.7268 | 1260632.1617 | 2699599.5959 | 1260629.2108
55 | 2699630.8986 | 1260653.7016 | 2699647.2006 | 1260651.6209
56 | 2699627.6322 | 1260705.2521 | 2699630.4185 | 1260713.2259
57 | 2699630.4185 | 1260713.2259 | 2699634.8947 | 1260726.0359 | 2699636.6656 | 1260731.4866
58 | 2699663.0065 | 1260549.9987 | 2699665.7523 | 1260572.6746 | 2699670.0118 | 1260572.1793 | 2699670.5801 | 1260577.3709
59 | 2699663.0065 | 1260549.9987 | 2699659.1394 | 1260550.4673 | 2699652.9637 | 1260551.2228
60 | 2699670.5801 | 1260577.3709 | 2699671.9822 | 1260590.1391
61 | 2699633.5722 | 1260553.5949 | 2699647.2358 | 1260551.9236 | 2699652.9637 | 1260551.2228
62 | 2699565.2743 | 1260678.5029 | 2699573.4924 | 1260676.4591
63 | 2699565.2743 | 1260678.5029 | 2699567.0552 | 1260695.2533
64 | 2699593.7565 | 1260672.9416 | 2699576.1207 | 1260675.8054 | 2699573.4924 | 1260676.4591
65 | 2699568.8918 | 1260714.8305 | 2699568.3324 | 1260707.2667 | 2699567.0552 | 1260695.2533
66 | 2699598.5391 | 1260626.4535 | 2699599.5959 | 1260629.2108
67 | 2699598.5391 | 1260626.4535 | 2699591.643 | 1260608.4767
68 | 2699633.5722 | 1260553.5949 | 2699628.8068 | 1260554.5932 | 2699626.9171 | 1260556.6965 | 2699619.409 | 1260557.6375
69 | 2699619.409 | 1260557.6375 | 2699617.9788 | 1260544.9617
70 | 2699570.298 | 1260733.8426 | 2699568.8918 | 1260714.8305

## bus_geodata
| x | y | coords
0 | 2699689.4566 | 1260732.3267
1 | 2699687.474 | 1260735.4736
2 | 2699685.0613 | 1260697.969
3 | 2699688.9579 | 1260746.5457
4 | 2699683.7924 | 1260698.1255
5 | 2699691.183 | 1260763.1477
6 | 2699665.8577 | 1260700.4023
7 | 2699720.3913 | 1260701.3838
8 | 2699750.1837 | 1260690.8623
9 | 2699719.0904 | 1260759.884
10 | 2699689.8755 | 1260766.0391
11 | 2699678.2516 | 1260647.6576
12 | 2699663.3418 | 1260649.5606
13 | 2699648.2985 | 1260702.6313
14 | 2699763.0015 | 1260689.231
15 | 2699837.2261 | 1260713.9189
16 | 2699841.3563 | 1260697.9153
17 | 2699807.4985 | 1260745.6943
18 | 2699839.0943 | 1260692.1613
19 | 2699934.9272 | 1260651.4013
20 | 2699790.7413 | 1260762.3252
21 | 2699913.7537 | 1260654.9107
22 | 2699755.1358 | 1260765.6785
23 | 2699725.8917 | 1260590.6804
24 | 2699717.7755 | 1260574.9419
25 | 2699731.493 | 1260605.7138
26 | 2699602.2058 | 1260592.6876
27 | 2699592.6611 | 1260562.847
28 | 2699614.9688 | 1260595.1848
29 | 2699578.3092 | 1260562.4274
30 | 2699616.6362 | 1260557.9449
31 | 2699762.2735 | 1260661.3515
32 | 2699750.2791 | 1260656.1339
33 | 2699780.5876 | 1260604.7362
34 | 2699782.4644 | 1260654.9422
35 | 2699585.4688 | 1260592.3817
36 | 2699696.9893 | 1260574.1503
37 | 2699771.3364 | 1260711.2006
38 | 2699773.6407 | 1260717.2717
39 | 2699761.3046 | 1260684.821
40 | 2699744.3444 | 1260640.2058
41 | 2699745.9383 | 1260658.774
42 | 2699621.506 | 1260687.7124
43 | 2699615.0219 | 1260669.4884
44 | 2699623.8252 | 1260694.3524
45 | 2699613.7586 | 1260655.8893
46 | 2699609.9971 | 1260656.3597
47 | 2699630.8986 | 1260653.7016
48 | 2699627.6322 | 1260705.2521
49 | 2699630.4185 | 1260713.2259
50 | 2699770.7183 | 1260592.8378
51 | 2699663.0065 | 1260549.9987
52 | 2699670.5801 | 1260577.3709
53 | 2699652.9637 | 1260551.2228
54 | 2699565.2743 | 1260678.5029
55 | 2699573.4924 | 1260676.4591
56 | 2699567.0552 | 1260695.2533
57 | 2699598.5391 | 1260626.4535
58 | 2699599.5959 | 1260629.2108
59 | 2699591.643 | 1260608.4767
60 | 2699738.1573 | 1260623.6001
61 | 2699620.6852 | 1260594.597
62 | 2699619.409 | 1260557.6375
63 | 2699793.9179 | 1260650.4873
64 | 2699633.5722 | 1260553.5949
65 | 2699617.9788 | 1260544.9617
66 | 2699593.7565 | 1260672.9416
67 | 2699636.6656 | 1260731.4866
68 | 2699647.2006 | 1260651.6209
69 | 2699671.9822 | 1260590.1391
70 | 2699568.8918 | 1260714.8305
71 | 2699570.298 | 1260733.8426
72 | 2699683.7924 | 1260698.1255

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98844 | -0.2206 | 0.0073739 | 0.0018481
1 | 0.98834 | -0.22247 | 0.012501 | 0.0031332
2 | 0.9894 | -0.20199 | 0 | 0
3 | 0.98808 | -0.22749 | 0.012572 | 0.0031509
4 | 0.98944 | -0.20131 | 0 | 0
5 | 0.98773 | -0.23408 | 0 | 0
6 | 0.98994 | -0.19161 | 0.01566 | 0.0039249
7 | 0.9715 | -0.54979 | 0.0096112 | 0.0024088
8 | 0.97183 | -0.54312 | 0.0059489 | 0.0014909
9 | 0.98724 | -0.24356 | 0.0080226 | 0.0020107
10 | 0.9877 | -0.2348 | 0.012596 | 0.0031569
11 | 1 | 0 | -0.44238 | -0.11315
12 | 0.99849 | -0.028456 | 0.0093645 | 0.002347
13 | 0.9905 | -0.18089 | 0 | 0
14 | 0.97202 | -0.53941 | 0 | 0
15 | 0.97205 | -0.53891 | 0.019008 | 0.0047638
16 | 0.97116 | -0.55646 | 0 | 0
17 | 0.97531 | -0.47471 | 0 | 0
18 | 0.97095 | -0.56063 | 0.036453 | 0.009136
19 | 0.97046 | -0.57044 | 0 | 0
20 | 0.98396 | -0.30655 | 0 | 0
21 | 0.97034 | -0.57275 | 0.0058023 | 0.0014542
22 | 0.98601 | -0.26718 | 0.0062086 | 0.001556
23 | 0.979 | -0.40248 | 0 | 0
24 | 0.9812 | -0.35971 | 0 | 0
25 | 0.97736 | -0.43447 | 0.0096121 | 0.002409
26 | 0.98788 | -0.23108 | 0 | 0
27 | 0.98841 | -0.22062 | 0 | 0
28 | 0.98763 | -0.23584 | 0.011184 | 0.002803
29 | 0.98925 | -0.20462 | 0 | 0
30 | 0.98756 | -0.23707 | 0.0075163 | 0.0018838
31 | 0.9718 | -0.54368 | 0 | 0
32 | 0.97273 | -0.52534 | 0 | 0
33 | 0.9703 | -0.57341 | 0 | 0
34 | 0.97111 | -0.55741 | 0.0076512 | 0.0019176
35 | 0.99045 | -0.18153 | 0.0057111 | 0.0014313
36 | 0.98338 | -0.31745 | 0.0075247 | 0.0018859
37 | 0.97189 | -0.542 | 0 | 0
38 | 0.97185 | -0.54271 | 0.005962 | 0.0014942
39 | 0.97211 | -0.53754 | 0 | 0
40 | 0.97409 | -0.49866 | 0.0049186 | 0.0012327
41 | 0.97269 | -0.52624 | 0.0095669 | 0.0023977
42 | 0.99186 | -0.15473 | 0 | 0
43 | 0.99263 | -0.14006 | 0 | 0
44 | 0.99159 | -0.16007 | 0.010549 | 0.0026438
45 | 0.9937 | -0.11961 | 0 | 0
46 | 0.99334 | -0.1264 | 0 | 0
47 | 0.99532 | -0.088681 | 0.0092017 | 0.0023062
48 | 0.99116 | -0.1683 | 0 | 0
49 | 0.99097 | -0.17198 | 0.012445 | 0.003119
50 | 0.97002 | -0.57898 | 0.019483 | 0.0048829
51 | 0.98609 | -0.26523 | 0 | 0
52 | 0.98483 | -0.28944 | 0 | 0
53 | 0.98639 | -0.25956 | 0.0080547 | 0.0020187
54 | 0.99077 | -0.1761 | 0 | 0
55 | 0.99097 | -0.17217 | 0.010993 | 0.0027551
56 | 0.99037 | -0.18391 | 0.0096416 | 0.0024164
57 | 0.99196 | -0.15273 | 0 | 0
58 | 0.99209 | -0.15034 | 0.0040263 | 0.0010091
59 | 0.99115 | -0.16828 | 0.0091197 | 0.0022856
60 | 0.97558 | -0.46932 | 0.0096209 | 0.0024112
61 | 0.98759 | -0.23661 | 0.0075219 | 0.0018852
62 | 0.98747 | -0.23883 | 0 | 0
63 | 0.9708 | -0.56357 | 0.02711 | 0.0067943
64 | 0.98699 | -0.24792 | 0 | 0
65 | 0.98737 | -0.24067 | 0.0080539 | 0.0020185
66 | 0.99167 | -0.15863 | 0.011585 | 0.0029035
67 | 0.99075 | -0.17614 | 0.012128 | 0.0030395
68 | 0.9969 | -0.05869 | 0.0088918 | 0.0022285
69 | 0.98474 | -0.2913 | 0.0080563 | 0.0020191
70 | 0.99007 | -0.18967 | 0.0083885 | 0.0021023
71 | 0.98993 | -0.19241 | 0.0080786 | 0.0020247
72 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.11419 | 0.029011 | -0.11418 | -0.029005 | 1.0322e-05 | 6.4153e-06 | 0.17205 | 0.17205 | 0.17205 | 0.98844 | -0.2206 | 0.98834 | -0.22247 | 11.8166
1 | -0.12157 | -0.030859 | 0.12168 | 0.030927 | 0.00010893 | 6.7936e-05 | 0.18315 | 0.18315 | 0.18315 | 0.98844 | -0.2206 | 0.9894 | -0.20199 | 12.5791
2 | 0.10168 | 0.025872 | -0.10166 | -0.025856 | 2.4589e-05 | 1.5165e-05 | 0.15323 | 0.15323 | 0.15323 | 0.98834 | -0.22247 | 0.98808 | -0.22749 | 10.5239
3 | -0.12168 | -0.030927 | 0.12168 | 0.03093 | 4.0096e-06 | 2.5006e-06 | 0.18315 | 0.18315 | 0.18315 | 0.9894 | -0.20199 | 0.98944 | -0.20131 | 12.579
4 | 0.089085 | 0.022705 | -0.089057 | -0.022688 | 2.8322e-05 | 1.7268e-05 | 0.1343 | 0.1343 | 0.1343 | 0.98808 | -0.22749 | 0.98773 | -0.23408 | 9.2236
5 | -0.12168 | -0.03093 | 0.12174 | 0.030965 | 5.6853e-05 | 3.5456e-05 | 0.18315 | 0.18315 | 0.18315 | 0.98944 | -0.20131 | 0.98994 | -0.19161 | 12.579
6 | 0.07646 | 0.019531 | -0.076425 | -0.01951 | 3.503e-05 | 2.0981e-05 | 0.11532 | 0.11532 | 0.11532 | 0.98773 | -0.23408 | 0.98724 | -0.24356 | 7.9203
7 | 0.012597 | 0.0031572 | -0.012596 | -0.0031569 | 4.2854e-07 | 2.3365e-07 | 0.018977 | 0.018977 | 0.018977 | 0.98773 | -0.23408 | 0.9877 | -0.2348 | 5.2134
8 | -0.1374 | -0.03489 | 0.13747 | 0.034934 | 7.089e-05 | 4.4459e-05 | 0.20669 | 0.20669 | 0.20669 | 0.98994 | -0.19161 | 0.9905 | -0.18089 | 14.1957
9 | -0.0096112 | -0.0024088 | 0.0096142 | 0.0024103 | 3.0531e-06 | 1.4886e-06 | 0.014721 | 0.014721 | 0.014721 | 0.9715 | -0.54979 | 0.97183 | -0.54312 | 4.0443
10 | -0.015563 | -0.0039012 | 0.015566 | 0.0039028 | 2.7515e-06 | 1.6008e-06 | 0.02383 | 0.02383 | 0.02383 | 0.97183 | -0.54312 | 0.97202 | -0.53941 | 6.5466
11 | 0.068402 | 0.017499 | -0.068324 | -0.01745 | 7.8112e-05 | 4.8993e-05 | 0.10323 | 0.10323 | 0.10323 | 0.98724 | -0.24356 | 0.98601 | -0.26718 | 14.1796
12 | 0.44073 | 0.11315 | -0.44012 | -0.11276 | 0.00060783 | 0.00038822 | 0.65677 | 0.65677 | 0.65677 | 1 | 0 | 0.99849 | -0.028456 | 45.1079
13 | 0.43076 | 0.11041 | -0.43013 | -0.11001 | 0.00063036 | 0.00040258 | 0.64282 | 0.64282 | 0.64282 | 0.99849 | -0.028456 | 0.9969 | -0.05869 | 44.1494
14 | -0.13747 | -0.034934 | 0.13755 | 0.034987 | 8.3432e-05 | 5.2323e-05 | 0.20669 | 0.20669 | 0.20669 | 0.9905 | -0.18089 | 0.99116 | -0.1683 | 14.1957
15 | 0.005963 | 0.0014945 | -0.0059622 | -0.0014943 | 7.3402e-07 | 1.7865e-07 | 0.0091284 | 0.0091285 | 0.0091285 | 0.97202 | -0.53941 | 0.97189 | -0.542 | 2.5078
16 | -0.021529 | -0.0053973 | 0.021531 | 0.0053984 | 1.9243e-06 | 1.173e-06 | 0.032958 | 0.032958 | 0.032958 | 0.97202 | -0.53941 | 0.97211 | -0.53754 | 9.0544
17 | 0.042302 | 0.010618 | -0.042267 | -0.010596 | 3.5389e-05 | 2.237e-05 | 0.064762 | 0.064762 | 0.064762 | 0.97205 | -0.53891 | 0.97116 | -0.55646 | 17.7919
18 | -0.06131 | -0.015382 | 0.061498 | 0.015502 | 0.00018828 | 0.00011979 | 0.093859 | 0.093859 | 0.093859 | 0.97205 | -0.53891 | 0.97531 | -0.47471 | 25.7855
19 | 0.03646 | 0.0091405 | -0.036453 | -0.009136 | 7.2359e-06 | 4.5545e-06 | 0.055865 | 0.055865 | 0.055865 | 0.97116 | -0.55646 | 0.97095 | -0.56063 | 15.3477
20 | 0.0058068 | 0.0014552 | -0.0058029 | -0.0014543 | 3.8655e-06 | 8.6389e-07 | 0.0088971 | 0.0088976 | 0.0088976 | 0.97116 | -0.55646 | 0.97046 | -0.57044 | 2.4444
21 | -0.061498 | -0.015502 | 0.061998 | 0.015819 | 0.00049919 | 0.00031758 | 0.093859 | 0.093858 | 0.093859 | 0.97531 | -0.47471 | 0.98396 | -0.30655 | 25.7855
22 | 0.0058029 | 0.0014543 | -0.0058023 | -0.0014542 | 6.3718e-07 | 1.4265e-07 | 0.0088976 | 0.0088977 | 0.0088977 | 0.97046 | -0.57044 | 0.97034 | -0.57275 | 2.4444
23 | -0.061998 | -0.015819 | 0.062116 | 0.015894 | 0.00011814 | 7.5157e-05 | 0.093858 | 0.093858 | 0.093858 | 0.98396 | -0.30655 | 0.98601 | -0.26718 | 25.7853
24 | -0.11019 | -0.027886 | 0.11042 | 0.028031 | 0.0002267 | 0.00014482 | 0.16758 | 0.16758 | 0.16758 | 0.979 | -0.40248 | 0.9812 | -0.35971 | 46.038
25 | 0.11019 | 0.027886 | -0.11002 | -0.027778 | 0.00016895 | 0.00010793 | 0.16758 | 0.16758 | 0.16758 | 0.979 | -0.40248 | 0.97736 | -0.43447 | 46.038
26 | -0.11042 | -0.028031 | 0.11064 | 0.028175 | 0.00022498 | 0.00014372 | 0.16758 | 0.16758 | 0.16758 | 0.9812 | -0.35971 | 0.98338 | -0.31745 | 46.038
27 | 0.10041 | 0.025369 | -0.10024 | -0.025263 | 0.00016744 | 0.00010692 | 0.15294 | 0.15294 | 0.15294 | 0.97736 | -0.43447 | 0.97558 | -0.46932 | 42.0177
28 | -0.018711 | -0.0046908 | 0.01872 | 0.0046964 | 9.3303e-06 | 5.5701e-06 | 0.028184 | 0.028184 | 0.028184 | 0.98788 | -0.23108 | 0.98841 | -0.22062 | 7.7428
29 | 0.018711 | 0.0046908 | -0.018706 | -0.0046883 | 4.2385e-06 | 2.5305e-06 | 0.028184 | 0.028184 | 0.028184 | 0.98788 | -0.23108 | 0.98763 | -0.23584 | 7.7428
30 | -0.16918 | -0.043082 | 0.16931 | 0.043164 | 0.00013064 | 8.2508e-05 | 0.25493 | 0.25493 | 0.25493 | 0.98841 | -0.22062 | 0.98925 | -0.20462 | 17.5091
31 | 0.15046 | 0.038385 | -0.15034 | -0.03831 | 0.00011944 | 7.5171e-05 | 0.22675 | 0.22675 | 0.22675 | 0.98841 | -0.22062 | 0.98756 | -0.23707 | 15.5735
32 | 0.0075222 | 0.0018853 | -0.0075219 | -0.0018852 | 2.7679e-07 | 1.0361e-07 | 0.011333 | 0.011333 | 0.011333 | 0.98763 | -0.23584 | 0.98759 | -0.23661 | 3.1135
33 | -0.16931 | -0.043164 | 0.1695 | 0.043284 | 0.000189 | 0.00011936 | 0.25493 | 0.25493 | 0.25493 | 0.98925 | -0.20462 | 0.99045 | -0.18153 | 17.5091
34 | 0.14282 | 0.036426 | -0.14281 | -0.036419 | 1.2137e-05 | 7.6252e-06 | 0.21542 | 0.21542 | 0.21542 | 0.98756 | -0.23707 | 0.98747 | -0.23883 | 14.7956
35 | -0.054307 | -0.013634 | 0.054355 | 0.013664 | 4.7536e-05 | 3.0195e-05 | 0.083163 | 0.083163 | 0.083163 | 0.9718 | -0.54368 | 0.97273 | -0.52534 | 22.847
36 | 0.019516 | 0.0049027 | -0.019488 | -0.004886 | 2.7649e-05 | 1.6674e-05 | 0.029887 | 0.029887 | 0.029887 | 0.9718 | -0.54368 | 0.9703 | -0.57341 | 8.2107
37 | 0.034791 | 0.0087311 | -0.034769 | -0.0087168 | 2.2771e-05 | 1.4309e-05 | 0.053277 | 0.053277 | 0.053277 | 0.9718 | -0.54368 | 0.97111 | -0.55741 | 14.6364
38 | -0.085465 | -0.021468 | 0.085574 | 0.021537 | 0.00010898 | 6.9536e-05 | 0.13076 | 0.13076 | 0.13076 | 0.97273 | -0.52534 | 0.97409 | -0.49866 | 35.9221
39 | 0.0095673 | 0.0023979 | -0.0095669 | -0.0023977 | 4.081e-07 | 1.9812e-07 | 0.014635 | 0.014635 | 0.014635 | 0.97273 | -0.52534 | 0.97269 | -0.52624 | 4.0207
40 | 0.021543 | 0.0054061 | -0.021531 | -0.0053984 | 1.2519e-05 | 7.6307e-06 | 0.032958 | 0.032958 | 0.032958 | 0.97273 | -0.52534 | 0.97211 | -0.53754 | 9.0544
41 | 0.019488 | 0.004886 | -0.019483 | -0.0048829 | 5.1781e-06 | 3.1231e-06 | 0.029887 | 0.029887 | 0.029887 | 0.9703 | -0.57341 | 0.97002 | -0.57898 | 8.2107
42 | 0.027117 | 0.0067992 | -0.02711 | -0.0067943 | 7.9572e-06 | 4.9406e-06 | 0.041553 | 0.041553 | 0.041553 | 0.97111 | -0.55741 | 0.9708 | -0.56357 | 11.4156
43 | -0.17521 | -0.044715 | 0.17532 | 0.044786 | 0.00011222 | 7.0933e-05 | 0.26351 | 0.26351 | 0.26351 | 0.99045 | -0.18153 | 0.99115 | -0.16828 | 18.0983
44 | -0.11817 | -0.030061 | 0.11833 | 0.030162 | 0.00015977 | 0.00010158 | 0.17896 | 0.17896 | 0.17896 | 0.98338 | -0.31745 | 0.98483 | -0.28944 | 24.583
45 | 0.0059622 | 0.0014943 | -0.005962 | -0.0014942 | 2.0292e-07 | 4.9401e-08 | 0.0091285 | 0.0091285 | 0.0091285 | 0.97189 | -0.542 | 0.97185 | -0.54271 | 2.5078
46 | -0.090493 | -0.02277 | 0.09062 | 0.022851 | 0.00012705 | 8.1091e-05 | 0.13827 | 0.13827 | 0.13827 | 0.97409 | -0.49866 | 0.97558 | -0.46932 | 37.9863
47 | -0.17279 | -0.043862 | 0.17291 | 0.043939 | 0.00012201 | 7.7087e-05 | 0.25942 | 0.25942 | 0.25942 | 0.99186 | -0.15473 | 0.99263 | -0.14006 | 17.8174
48 | 0.17279 | 0.043862 | -0.17275 | -0.043834 | 4.4376e-05 | 2.8037e-05 | 0.25942 | 0.25942 | 0.25942 | 0.99186 | -0.15473 | 0.99159 | -0.16007 | 17.8174
49 | -0.22169 | -0.056195 | 0.22183 | 0.056288 | 0.0001457 | 9.2518e-05 | 0.33255 | 0.33255 | 0.33255 | 0.99263 | -0.14006 | 0.99334 | -0.1264 | 22.8398
50 | 0.048774 | 0.012257 | -0.048731 | -0.012229 | 4.3203e-05 | 2.7372e-05 | 0.073127 | 0.073127 | 0.073127 | 0.99263 | -0.14006 | 0.99167 | -0.15863 | 20.0899
51 | 0.1622 | 0.04119 | -0.16213 | -0.041149 | 6.4225e-05 | 4.0509e-05 | 0.24359 | 0.24359 | 0.24359 | 0.99159 | -0.16007 | 0.99116 | -0.1683 | 16.7301
52 | 0.41081 | 0.10469 | -0.41068 | -0.10461 | 0.00013438 | 8.5805e-05 | 0.61579 | 0.61579 | 0.61579 | 0.9937 | -0.11961 | 0.99334 | -0.1264 | 42.2931
53 | -0.41081 | -0.10469 | 0.41142 | 0.10509 | 0.00061426 | 0.00039223 | 0.61579 | 0.61579 | 0.61579 | 0.9937 | -0.11961 | 0.99532 | -0.088681 | 42.2931
54 | 0.18884 | 0.04832 | -0.18863 | -0.048182 | 0.00021866 | 0.00013844 | 0.28324 | 0.28324 | 0.28324 | 0.99334 | -0.1264 | 0.99209 | -0.15034 | 19.4534
55 | -0.42063 | -0.10739 | 0.42124 | 0.10778 | 0.00061062 | 0.00038994 | 0.62954 | 0.62954 | 0.62954 | 0.99532 | -0.088681 | 0.9969 | -0.05869 | 43.2379
56 | 0.02458 | 0.0061625 | -0.024575 | -0.0061599 | 4.3133e-06 | 2.6517e-06 | 0.036902 | 0.036902 | 0.036902 | 0.99116 | -0.1683 | 0.99097 | -0.17198 | 10.138
57 | 0.01213 | 0.0030408 | -0.012128 | -0.0030395 | 2.4014e-06 | 1.2883e-06 | 0.018215 | 0.018215 | 0.018215 | 0.99097 | -0.17198 | 0.99075 | -0.17614 | 5.0041
58 | 0.12653 | 0.032275 | -0.12638 | -0.032182 | 0.00014774 | 9.3319e-05 | 0.19114 | 0.19114 | 0.19114 | 0.98609 | -0.26523 | 0.98483 | -0.28944 | 17.5034
59 | -0.12653 | -0.032275 | 0.12656 | 0.032297 | 3.4651e-05 | 2.166e-05 | 0.19114 | 0.19114 | 0.19114 | 0.98609 | -0.26523 | 0.98639 | -0.25956 | 13.1275
60 | 0.008057 | 0.0020194 | -0.0080563 | -0.0020191 | 7.1385e-07 | 2.9343e-07 | 0.012174 | 0.012174 | 0.012174 | 0.98483 | -0.28944 | 0.98474 | -0.2913 | 3.3444
61 | -0.13462 | -0.034315 | 0.1347 | 0.034363 | 7.5688e-05 | 4.7442e-05 | 0.20329 | 0.20329 | 0.20329 | 0.98639 | -0.25956 | 0.98699 | -0.24792 | 13.9621
62 | -0.026124 | -0.0065525 | 0.026129 | 0.0065556 | 4.8891e-06 | 3.0199e-06 | 0.039237 | 0.039237 | 0.039237 | 0.99077 | -0.1761 | 0.99097 | -0.17217 | 10.7794
63 | 0.026124 | 0.0065525 | -0.026114 | -0.0065465 | 9.7251e-06 | 6.0072e-06 | 0.039237 | 0.039237 | 0.039237 | 0.99077 | -0.1761 | 0.99037 | -0.18391 | 10.7794
64 | -0.037122 | -0.0093107 | 0.037146 | 0.0093257 | 2.3975e-05 | 1.5079e-05 | 0.055744 | 0.055744 | 0.055744 | 0.99097 | -0.17217 | 0.99167 | -0.15863 | 15.3142
65 | 0.016473 | 0.0041301 | -0.016468 | -0.0041275 | 4.5176e-06 | 2.6383e-06 | 0.024751 | 0.024751 | 0.024751 | 0.99037 | -0.18391 | 0.99007 | -0.18967 | 6.7997
66 | -0.18458 | -0.047159 | 0.1846 | 0.047173 | 2.1272e-05 | 1.3462e-05 | 0.2772 | 0.2772 | 0.2772 | 0.99196 | -0.15273 | 0.99209 | -0.15034 | 19.0386
67 | 0.18458 | 0.047159 | -0.18444 | -0.047071 | 0.0001387 | 8.7777e-05 | 0.2772 | 0.2772 | 0.2772 | 0.99196 | -0.15273 | 0.99115 | -0.16828 | 19.0386
68 | 0.13475 | 0.0344 | -0.1347 | -0.034363 | 5.9134e-05 | 3.7065e-05 | 0.20329 | 0.20329 | 0.20329 | 0.98747 | -0.23883 | 0.98699 | -0.24792 | 13.962
69 | 0.0080546 | 0.0020188 | -0.0080539 | -0.0020185 | 7.0472e-07 | 2.8785e-07 | 0.012138 | 0.012138 | 0.012138 | 0.98747 | -0.23883 | 0.98737 | -0.24067 | 3.3345
70 | 0.0080797 | 0.0020251 | -0.0080786 | -0.0020247 | 1.0542e-06 | 4.2956e-07 | 0.012143 | 0.012143 | 0.012143 | 0.99007 | -0.18967 | 0.98993 | -0.19241 | 3.3361

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45181 | 0.11551

## res_load
| p_mw | q_mvar
0 | 0.0073739 | 0.0018481
1 | 0.012501 | 0.0031332
2 | 0.012572 | 0.0031509
3 | 0.01566 | 0.0039249
4 | 0.0096112 | 0.0024088
5 | 0.0059489 | 0.0014909
6 | 0.0080226 | 0.0020107
7 | 0.012596 | 0.0031569
8 | 0.0094259 | 0.0023624
9 | 0.0093645 | 0.002347
10 | 0.019008 | 0.0047638
11 | 0.036453 | 0.009136
12 | 0.0058023 | 0.0014542
13 | 0.0062086 | 0.001556
14 | 0.0096121 | 0.002409
15 | 0.011184 | 0.002803
16 | 0.0075163 | 0.0018838
17 | 0.0076512 | 0.0019176
18 | 0.0057111 | 0.0014313
19 | 0.0075247 | 0.0018859
20 | 0.005962 | 0.0014942
21 | 0.0049186 | 0.0012327
22 | 0.0095669 | 0.0023977
23 | 0.010549 | 0.0026438
24 | 0.0092017 | 0.0023062
25 | 0.012445 | 0.003119
26 | 0.019483 | 0.0048829
27 | 0.0080547 | 0.0020187
28 | 0.010993 | 0.0027551
29 | 0.0096416 | 0.0024164
30 | 0.0040263 | 0.0010091
31 | 0.0091197 | 0.0022856
32 | 0.0096209 | 0.0024112
33 | 0.0075219 | 0.0018852
34 | 0.02711 | 0.0067943
35 | 0.0080539 | 0.0020185
36 | 0.011585 | 0.0029035
37 | 0.012128 | 0.0030395
38 | 0.0088918 | 0.0022285
39 | 0.0080563 | 0.0020191
40 | 0.0083885 | 0.0021023
41 | 0.0080786 | 0.0020247

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1