## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-230_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-230_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-230_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-230_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-230_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-230_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_230-230_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_230-230_0_3_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_230-230_0_3_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_230-230_0_3_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_230-230_0_3_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_230-230_0_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_230-230_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_230-230_0_3_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_230-230_0_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_230-230_0_3_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_230-230_0_3_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_230-230_0_3_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_230-230_0_3_node_49 | 0.4 | n |  | TRUE
19 | bus_LV_230-230_0_3_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_230-230_0_3_node_100 | 0.4 | n |  | TRUE
21 | bus_LV_230-230_0_3_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_230-230_0_3_node_57 | 0.4 | n |  | TRUE
23 | bus_LV_230-230_0_3_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_230-230_0_3_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_230-230_0_3_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_230-230_0_3_node_101 | 0.4 | n |  | TRUE
27 | bus_LV_230-230_0_3_node_46 | 0.4 | n |  | TRUE
28 | bus_LV_230-230_0_3_node_47 | 0.4 | n |  | TRUE
29 | bus_LV_230-230_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_230-230_0_3_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_230-230_0_3_node_65 | 0.4 | n |  | TRUE
32 | bus_LV_230-230_0_3_node_64 | 0.4 | n |  | TRUE
33 | bus_LV_230-230_0_3_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_230-230_0_3_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_230-230_0_3_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_230-230_0_3_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_230-230_0_3_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_230-230_0_3_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_230-230_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_230-230_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_230-230_0_3_node_97 | 0.4 | n |  | TRUE
42 | bus_LV_230-230_0_3_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_230-230_0_3_node_83 | 0.4 | n |  | TRUE
44 | bus_LV_230-230_0_3_node_86 | 0.4 | n |  | TRUE
45 | bus_LV_230-230_0_3_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_230-230_0_3_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_230-230_0_3_node_78 | 0.4 | n |  | TRUE
48 | bus_LV_230-230_0_3_node_102 | 0.4 | n |  | TRUE
49 | bus_LV_230-230_0_3_node_98 | 0.4 | n |  | TRUE
50 | bus_LV_230-230_0_3_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_230-230_0_3_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_230-230_0_3_node_85 | 0.4 | n |  | TRUE
53 | bus_LV_230-230_0_3_node_82 | 0.4 | n |  | TRUE
54 | bus_LV_230-230_0_3_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_230-230_0_3_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_230-230_0_3_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_230-230_0_3_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_230-230_0_3_node_96 | 0.4 | n |  | TRUE
59 | bus_LV_230-230_0_3_node_95 | 0.4 | n |  | TRUE
60 | bus_LV_230-230_0_3_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_230-230_0_3_node_73 | 0.4 | n |  | TRUE
62 | bus_LV_230-230_0_3_node_75 | 0.4 | n |  | TRUE
63 | bus_LV_230-230_0_3_node_99 | 0.4 | n |  | TRUE
64 | bus_LV_230-230_0_3_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_230-230_0_3_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_230-230_0_3_node_72 | 0.4 | n |  | TRUE
67 | bus_LV_230-230_0_3_node_70 | 0.4 | n |  | TRUE
68 | bus_LV_230-230_0_3_node_88 | 0.4 | n |  | TRUE
69 | bus_LV_230-230_0_3_node_77 | 0.4 | n |  | TRUE
70 | bus_LV_230-230_0_3_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_230-230_0_3_node_45 | 0.4 | n |  | TRUE
72 | bus_LV_230-230_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_230-230_0_3_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_230-230_0_3_node_93 | 0.4 | n |  | TRUE
75 | bus_LV_230-230_0_3_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_230-230_0_3_node_94 | 0.4 | n |  | TRUE
77 | bus_LV_230-230_0_3_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_230-230_0_3_node_63 | 0.4 | n |  | TRUE
79 | bus_LV_230-230_0_3_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_230-230_0_3_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_230-230_0_3_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_230-230_0_3_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_230-230_0_3_node_71 | 0.4 | n |  | TRUE
84 | bus_LV_230-230_0_3_node_87 | 0.4 | n |  | TRUE
85 | bus_LV_230-230_0_3_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_230-230_0_3_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_230-230_0_3_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_230-230_0_3_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_230-230_0_3_node_84 | 0.4 | n |  | TRUE
90 | bus_LV_230-230_0_3_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_230-230_0_3_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_230-230_0_3_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_230-230_0_3_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_230-230_0_3_node_92 | 0.4 | n |  | TRUE
95 | bus_MV_370_0_node_114 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-230_0_3_load_0 | 0 | 0.0082802 | 0.0020752 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-230_0_3_load_1 | 1 | 0.012397 | 0.0031069 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-230_0_3_load_4 | 4 | 0.0055429 | 0.0013892 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-230_0_3_load_5 | 5 | 0.0028788 | 0.0007215 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-230_0_3_load_12 | 6 | 0.0081997 | 0.002055 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-230_0_3_load_54 | 8 | 0.002645 | 0.00066291 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-230_0_3_load_58 | 9 | 0.0049092 | 0.0012304 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-230_0_3_load_14 | 11 | 0.0093442 | 0.0023419 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-230_0_3_load_31 | 13 | 0.006093 | 0.001527 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-230_0_3_load_28 | 16 | 0.0093142 | 0.0023344 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-230_0_3_load_100 | 20 | 0.00419 | 0.0010501 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-230_0_3_load_56 | 25 | 0.00089704 | 0.00022482 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-230_0_3_load_101 | 26 | 0.0040118 | 0.0010055 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-230_0_3_load_46 | 27 | 0.0073814 | 0.00185 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-230_0_3_load_47 | 28 | 0.0077987 | 0.0019545 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-230_0_3_load_59 | 30 | 0.0016844 | 0.00042215 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-230_0_3_load_65 | 31 | 0.0015952 | 0.00039978 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-230_0_3_load_64 | 32 | 0.0013574 | 0.00034019 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-230_0_3_load_17 | 33 | 0.0017823 | 0.00044669 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-230_0_3_load_18 | 34 | 0.0020345 | 0.00050988 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-230_0_3_load_20 | 36 | 0.0012924 | 0.00032391 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-230_0_3_load_36 | 39 | 0.0012915 | 0.00032369 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-230_0_3_load_33 | 40 | 0.0019965 | 0.00050036 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-230_0_3_load_97 | 41 | 0.0023751 | 0.00059524 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-230_0_3_load_86 | 44 | 0.0020198 | 0.00050621 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-230_0_3_load_78 | 47 | 0.0049257 | 0.0012345 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-230_0_3_load_102 | 48 | 0.0017677 | 0.00044303 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-230_0_3_load_35 | 50 | 0.0018649 | 0.00046738 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-230_0_3_load_34 | 51 | 0.0017816 | 0.0004465 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-230_0_3_load_85 | 52 | 0.00038905 | 9.7506e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-230_0_3_load_82 | 53 | 0.00072534 | 0.00018179 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-230_0_3_load_38 | 55 | 0.00075663 | 0.00018963 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-230_0_3_load_96 | 58 | 0.00075493 | 0.0001892 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-230_0_3_load_95 | 59 | 0.0030444 | 0.00076299 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-230_0_3_load_99 | 63 | 0.0021427 | 0.000537 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-230_0_3_load_43 | 64 | 0.0020424 | 0.00051188 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-230_0_3_load_42 | 65 | 0.0028912 | 0.0007246 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-230_0_3_load_70 | 67 | 0.0076398 | 0.0019147 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-230_0_3_load_88 | 68 | 0.0049411 | 0.0012383 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-230_0_3_load_77 | 69 | 0.0049315 | 0.0012359 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-230_0_3_load_44 | 70 | 0.0021001 | 0.00052633 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-230_0_3_load_45 | 71 | 0.0027113 | 0.00067951 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-230_0_3_load_66 | 72 | 0.0025706 | 0.00064427 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-230_0_3_load_67 | 73 | 0.00126 | 0.00031578 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-230_0_3_load_93 | 74 | 0.003504 | 0.0008782 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-230_0_3_load_55 | 75 | 0.0052151 | 0.001307 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-230_0_3_load_94 | 76 | 0.0011633 | 0.00029154 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-230_0_3_load_63 | 78 | 0.0013581 | 0.00034037 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-230_0_3_load_61 | 79 | 0.0048969 | 0.0012273 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-230_0_3_load_62 | 80 | 0.0049074 | 0.0012299 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-230_0_3_load_68 | 81 | 0.0013322 | 0.00033388 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-230_0_3_load_69 | 82 | 0.0032309 | 0.00080973 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-230_0_3_load_71 | 83 | 0.0059088 | 0.0014809 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-230_0_3_load_87 | 84 | 0.010007 | 0.0025079 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-230_0_3_load_74 | 85 | 0.0023459 | 0.00058794 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-230_0_3_load_80 | 88 | 0.0080049 | 0.0020062 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-230_0_3_load_84 | 89 | 0.00038888 | 9.7464e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-230_0_3_load_81 | 90 | 0.00086744 | 0.0002174 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-230_0_3_load_89 | 91 | 0.0019081 | 0.00047821 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-230_0_3_load_91 | 92 | 0.00044025 | 0.00011034 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-230_0_3_load_90 | 93 | 0.0019188 | 0.00048091 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-230_0_3_load_92 | 94 | 0.00089726 | 0.00022488 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-230_0_3_line_0 |  | 0 | 1 | 0.014741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_230-230_0_3_line_1 |  | 0 | 2 | 0.028786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_230-230_0_3_line_2 |  | 1 | 3 | 0.039962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_230-230_0_3_line_3 |  | 2 | 4 | 0.019284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-230_0_3_line_4 |  | 2 | 5 | 0.078754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_230-230_0_3_line_5 |  | 3 | 6 | 0.022226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-230_0_3_line_6 |  | 3 | 7 | 0.011256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_230-230_0_3_line_7 |  | 5 | 8 | 0.00040477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_230-230_0_3_line_8 |  | 7 | 9 | 0.020088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_230-230_0_3_line_9 |  | 8 | 10 | 0.024263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_230-230_0_3_line_10 |  | 9 | 30 | 0.00097457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_230-230_0_3_line_11 |  | 10 | 23 | 0.007703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_230-230_0_3_line_12 |  | 10 | 28 | 0.029851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-230_0_3_line_13 |  | 11 | 12 | 0.022185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-230_0_3_line_14 |  | 12 | 29 | 0.02043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-230_0_3_line_15 |  | 13 | 14 | 0.014922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-230_0_3_line_16 |  | 14 | 15 | 0.011616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-230_0_3_line_17 |  | 15 | 64 | 0.0092691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-230_0_3_line_18 |  | 15 | 17 | 0.033801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-230_0_3_line_19 |  | 16 | 17 | 0.020359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-230_0_3_line_20 |  | 17 | 29 | 0.018941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-230_0_3_line_21 |  | 18 | 19 | 0.037711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-230_0_3_line_22 |  | 18 | 20 | 0.060361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-230_0_3_line_23 |  | 19 | 26 | 0.038758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-230_0_3_line_24 |  | 20 | 57 | 0.05599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-230_0_3_line_25 |  | 21 | 22 | 0.005611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_230-230_0_3_line_26 |  | 21 | 23 | 0.066611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_230-230_0_3_line_27 |  | 22 | 74 | 0.011485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-230_0_3_line_28 |  | 22 | 59 | 0.029016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_230-230_0_3_line_29 |  | 23 | 24 | 0.026399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-230_0_3_line_30 |  | 24 | 25 | 0.0083762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-230_0_3_line_31 |  | 25 | 75 | 0.0084168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-230_0_3_line_32 |  | 27 | 28 | 0.015216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-230_0_3_line_33 |  | 29 | 31 | 0.025296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-230_0_3_line_34 |  | 30 | 77 | 0.0070428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_230-230_0_3_line_35 |  | 31 | 32 | 0.018765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-230_0_3_line_36 |  | 32 | 78 | 0.0081092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-230_0_3_line_37 |  | 33 | 34 | 0.031987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-230_0_3_line_38 |  | 33 | 35 | 0.00012664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-230_0_3_line_39 |  | 34 | 36 | 0.0092784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-230_0_3_line_40 |  | 35 | 37 | 0.027554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-230_0_3_line_41 |  | 35 | 38 | 0.032236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-230_0_3_line_42 |  | 36 | 39 | 0.0072084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-230_0_3_line_43 |  | 37 | 40 | 0.0045311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-230_0_3_line_44 |  | 38 | 41 | 0.0050386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-230_0_3_line_45 |  | 39 | 50 | 0.0088052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-230_0_3_line_46 |  | 40 | 51 | 0.01758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-230_0_3_line_47 |  | 41 | 49 | 0.042909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-230_0_3_line_48 |  | 42 | 43 | 0.037956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-230_0_3_line_49 |  | 42 | 44 | 0.019051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-230_0_3_line_50 |  | 43 | 52 | 0.015961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-230_0_3_line_51 |  | 43 | 53 | 0.0046121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-230_0_3_line_52 |  | 45 | 46 | 0.039748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-230_0_3_line_53 |  | 45 | 47 | 0.043653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-230_0_3_line_54 |  | 46 | 48 | 0.002317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-230_0_3_line_55 |  | 46 | 49 | 0.025795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-230_0_3_line_56 |  | 47 | 62 | 0.012843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-230_0_3_line_57 |  | 49 | 63 | 0.002389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-230_0_3_line_58 |  | 52 | 92 | 0.00050848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-230_0_3_line_59 |  | 53 | 90 | 0.011145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-230_0_3_line_60 |  | 54 | 55 | 0.016911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-230_0_3_line_61 |  | 54 | 56 | 0.017659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-230_0_3_line_62 |  | 56 | 57 | 0.005806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_230-230_0_3_line_63 |  | 56 | 58 | 0.034215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-230_0_3_line_64 |  | 56 | 59 | 0.026545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_230-230_0_3_line_65 |  | 57 | 60 | 0.016395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_230-230_0_3_line_66 |  | 60 | 61 | 0.017929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_230-230_0_3_line_67 |  | 61 | 68 | 0.00074509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_230-230_0_3_line_68 |  | 61 | 66 | 0.004364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-230_0_3_line_69 |  | 62 | 69 | 0.020687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-230_0_3_line_70 |  | 62 | 85 | 0.016749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-230_0_3_line_71 |  | 64 | 65 | 0.0095073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-230_0_3_line_72 |  | 65 | 70 | 0.01194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-230_0_3_line_73 |  | 66 | 67 | 0.019833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-230_0_3_line_74 |  | 67 | 83 | 0.020767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-230_0_3_line_75 |  | 68 | 84 | 0.017198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_230-230_0_3_line_76 |  | 70 | 71 | 0.0077641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-230_0_3_line_77 |  | 71 | 72 | 0.013809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-230_0_3_line_78 |  | 72 | 73 | 0.0065056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-230_0_3_line_79 |  | 73 | 81 | 0.0064455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-230_0_3_line_80 |  | 74 | 76 | 0.017029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-230_0_3_line_81 |  | 77 | 78 | 0.022068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-230_0_3_line_82 |  | 77 | 79 | 0.021089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_230-230_0_3_line_83 |  | 79 | 80 | 0.0087028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-230_0_3_line_84 |  | 81 | 82 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-230_0_3_line_85 |  | 84 | 88 | 0.018214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-230_0_3_line_86 |  | 85 | 86 | 0.017467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-230_0_3_line_87 |  | 86 | 87 | 0.015346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-230_0_3_line_88 |  | 86 | 88 | 0.020461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-230_0_3_line_89 |  | 87 | 89 | 0.016851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-230_0_3_line_90 |  | 87 | 90 | 0.024019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-230_0_3_line_91 |  | 89 | 91 | 0.0009683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-230_0_3_line_92 |  | 91 | 93 | 0.0048493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-230_0_3_line_93 |  | 92 | 94 | 0.038354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-230_0_3_trafo_61 | 0.63 MVA 20/0.4 kV | 95 | 79 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2700037.8278 | 1259721.7327 | 2700052.5663 | 1259721.4883
1 | 2700009.7301 | 1259715.8786 | 2700034.7412 | 1259721.7839 | 2700037.8278 | 1259721.7327
2 | 2700091.6225 | 1259714.0616 | 2700078.3128 | 1259718.3066 | 2700074.6579 | 1259719.1233 | 2700057.9742 | 1259721.3986 | 2700052.5663 | 1259721.4883
3 | 2700009.7301 | 1259715.8786 | 2700006.5123 | 1259719.3715 | 2700005.3313 | 1259723.6773 | 2699995.5144 | 1259721.4325
4 | 2700009.7301 | 1259715.8786 | 2700010.49 | 1259722.6525 | 2700007.6421 | 1259736.3711 | 2700005.4802 | 1259750.0902 | 2700001.6172 | 1259793.959
5 | 2700091.6225 | 1259714.0616 | 2700082.379 | 1259704.3307 | 2700076.3235 | 1259697.9388
6 | 2700101.6971 | 1259708.9834 | 2700091.6225 | 1259714.0616
7 | 2700001.5817 | 1259794.3622 | 2700001.6172 | 1259793.959
8 | 2700101.6971 | 1259708.9834 | 2700113.8349 | 1259724.9896
9 | 2699992.4153 | 1259815.6563 | 2700000.5816 | 1259805.7195 | 2700001.5817 | 1259794.3622
10 | 2700114.4238 | 1259725.7661 | 2700113.8349 | 1259724.9896
11 | 2699998.54 | 1259820.3525 | 2699992.4153 | 1259815.6563
12 | 2699992.4153 | 1259815.6563 | 2699967.5615 | 1259799.1229
13 | 2700125.1305 | 1259694.9795 | 2700116.8448 | 1259687.9002 | 2700115.2344 | 1259686.394 | 2700108.3963 | 1259680.4171
14 | 2700141.1029 | 1259682.1838 | 2700125.1305 | 1259694.9795
15 | 2700182.6144 | 1259638.3617 | 2700179.2543 | 1259630.2204 | 2700179.3034 | 1259624.1064
16 | 2700181.8595 | 1259648.6574 | 2700184.881 | 1259643.849 | 2700182.6144 | 1259638.3617
17 | 2700181.8595 | 1259648.6574 | 2700188.9041 | 1259654.6815
18 | 2700181.8595 | 1259648.6574 | 2700169.8247 | 1259659.9629 | 2700155.9137 | 1259670.3248
19 | 2700155.9137 | 1259670.3248 | 2700147.7797 | 1259665.4164 | 2700145.312 | 1259663.3396 | 2700139.0272 | 1259659.0063
20 | 2700141.1029 | 1259682.1838 | 2700155.9137 | 1259670.3248
21 | 2700079.3084 | 1259892.877 | 2700067.6465 | 1259902.6767 | 2700060.9679 | 1259909.7807 | 2700072.3447 | 1259915.4889
22 | 2700072.3447 | 1259915.4889 | 2700098.7222 | 1259901.6348 | 2700103.6403 | 1259893.4335 | 2700105.0249 | 1259883.7824 | 2700104.2004 | 1259872.5587
23 | 2700079.3084 | 1259892.877 | 2700085.3852 | 1259893.7138 | 2700100.5362 | 1259884.4292 | 2700100.427 | 1259870.8385 | 2700099.1129 | 1259870.983
24 | 2700110.3994 | 1259817.4636 | 2700103.6387 | 1259842.7699 | 2700104.1121 | 1259871.3568 | 2700104.2004 | 1259872.5587
25 | 2700052.6313 | 1259822.8577 | 2700054.4108 | 1259828.181
26 | 2699998.54 | 1259820.3525 | 2700006.4395 | 1259829.3155 | 2700008.6591 | 1259834.9131 | 2700009.8664 | 1259837.9694 | 2700052.6313 | 1259822.8577
27 | 2700054.4108 | 1259828.181 | 2700058.0549 | 1259839.0729
28 | 2700054.4108 | 1259828.181 | 2700069.9264 | 1259822.75 | 2700076.2672 | 1259820.4665 | 2700081.6139 | 1259818.1217
29 | 2699998.54 | 1259820.3525 | 2700006.4395 | 1259829.3155 | 2700020.2038 | 1259824.9112
30 | 2700020.2038 | 1259824.9112 | 2700018.3491 | 1259816.7429
31 | 2700016.4854 | 1259808.535 | 2700016.4854 | 1259808.535 | 2700018.3491 | 1259816.7429
32 | 2699952.7877 | 1259797.0798 | 2699959.1334 | 1259796.4561 | 2699967.5615 | 1259799.1229
33 | 2700141.1029 | 1259682.1838 | 2700152.4924 | 1259697.8449 | 2700152.114 | 1259703.7639
34 | 2700118.6793 | 1259731.3779 | 2700114.4238 | 1259725.7661
35 | 2700143.3188 | 1259718.5106 | 2700151.5899 | 1259711.9633 | 2700152.114 | 1259703.7639
36 | 2700136.9606 | 1259723.5436 | 2700143.3188 | 1259718.5106
37 | 2700239.644 | 1259693.5357 | 2700255.6825 | 1259681.312 | 2700265.0827 | 1259674.1438
38 | 2700265.0827 | 1259674.1438 | 2700265.1834 | 1259674.067
39 | 2700232.2645 | 1259699.1599 | 2700239.644 | 1259693.5357
40 | 2700265.1834 | 1259674.067 | 2700279.7424 | 1259662.4042 | 2700275.9665 | 1259654.3447
41 | 2700265.1834 | 1259674.067 | 2700267.6648 | 1259677.5563 | 2700271.0149 | 1259682.2725 | 2700269.976 | 1259704.4174
42 | 2700232.2645 | 1259699.1599 | 2700226.5314 | 1259703.5294
43 | 2700275.9665 | 1259654.3447 | 2700275.6511 | 1259649.8246
44 | 2700269.976 | 1259704.4174 | 2700269.7448 | 1259709.4507
45 | 2700219.5282 | 1259708.8668 | 2700226.5314 | 1259703.5294
46 | 2700276.6796 | 1259632.2744 | 2700275.6511 | 1259649.8246
47 | 2700241.1518 | 1259730.8952 | 2700269.1037 | 1259723.407 | 2700269.7448 | 1259709.4507
48 | 2700249.0241 | 1259790.3548 | 2700273.123 | 1259782.4567 | 2700280.2771 | 1259780.2316 | 2700285.27 | 1259778.7595
49 | 2700285.27 | 1259778.7595 | 2700286.0388 | 1259759.7238
50 | 2700249.0241 | 1259790.3548 | 2700254.2407 | 1259805.4397
51 | 2700249.0241 | 1259790.3548 | 2700244.6416 | 1259791.7917
52 | 2700193.6403 | 1259733.7596 | 2700195.8933 | 1259732.0408 | 2700198.047 | 1259730.3981 | 2700213.3339 | 1259750.9404 | 2700220.1841 | 1259745.741
53 | 2700193.6403 | 1259733.7596 | 2700207.6993 | 1259756.0269 | 2700207.8968 | 1259756.8309 | 2700207.5036 | 1259758.2365 | 2700195.5799 | 1259767.389
54 | 2700220.1841 | 1259745.741 | 2700218.7678 | 1259743.9045
55 | 2700220.1841 | 1259745.741 | 2700238.9935 | 1259731.4702 | 2700241.1518 | 1259730.8952
56 | 2700185.3919 | 1259775.2093 | 2700195.5799 | 1259767.389
57 | 2700241.1518 | 1259730.8952 | 2700240.5502 | 1259728.5831
58 | 2700254.4069 | 1259805.9203 | 2700254.2407 | 1259805.4397
59 | 2700234.0512 | 1259795.2639 | 2700244.6416 | 1259791.7917
60 | 2700098.4098 | 1259801.1919 | 2700083.9519 | 1259809.9644
61 | 2700098.4098 | 1259801.1919 | 2700104.1083 | 1259807.4601 | 2700106.4979 | 1259809.2464 | 2700105.0164 | 1259815.2707
62 | 2700110.3994 | 1259817.4636 | 2700107.5965 | 1259816.4932 | 2700105.0164 | 1259815.2707
63 | 2700105.0164 | 1259815.2707 | 2700098.7178 | 1259840.8851 | 2700091.1199 | 1259842.8076
64 | 2700105.0164 | 1259815.2707 | 2700100.4753 | 1259812.3249 | 2700098.3239 | 1259811.1653 | 2700096.2808 | 1259810.7304 | 2700094.2267 | 1259810.9403 | 2700092.6398 | 1259811.614 | 2700088.9218 | 1259813.9308 | 2700085.5618 | 1259816.0312 | 2700081.6139 | 1259818.1217
65 | 2700110.3994 | 1259817.4636 | 2700111.5746 | 1259813.0577 | 2700123.249 | 1259815.0012
66 | 2700141.215 | 1259815.7836 | 2700123.249 | 1259815.0012
67 | 2700141.215 | 1259815.7836 | 2700141.9594 | 1259815.8156
68 | 2700141.215 | 1259815.7836 | 2700140.2909 | 1259820.0492
69 | 2700185.3919 | 1259775.2093 | 2700165.8726 | 1259782.0605
70 | 2700185.3919 | 1259775.2093 | 2700190.8805 | 1259791.0339
71 | 2700189.6935 | 1259664.156 | 2700188.9041 | 1259654.6815 | 2700188.9041 | 1259654.6815
72 | 2700189.6935 | 1259664.156 | 2700189.9127 | 1259666.7863 | 2700188.4359 | 1259675.9687
73 | 2700140.2909 | 1259820.0492 | 2700136.0986 | 1259839.4341
74 | 2700136.0986 | 1259839.4341 | 2700131.709 | 1259859.7315
75 | 2700141.9594 | 1259815.8156 | 2700157.8704 | 1259816.4994 | 2700159.1384 | 1259816.3923
76 | 2700188.4359 | 1259675.9687 | 2700187.203 | 1259683.6343
77 | 2700187.203 | 1259683.6343 | 2700186.7949 | 1259686.1715 | 2700184.6716 | 1259697.2086
78 | 2700184.6716 | 1259697.2086 | 2700183.4425 | 1259703.597
79 | 2700183.4425 | 1259703.597 | 2700182.2248 | 1259709.9264
80 | 2700064.7721 | 1259854.7001 | 2700059.3834 | 1259843.0439 | 2700058.0549 | 1259839.0729
81 | 2700118.6793 | 1259731.3779 | 2700122.7006 | 1259732.5246 | 2700127.6711 | 1259727.9161 | 2700130.6153 | 1259728.5664 | 2700136.9606 | 1259723.5436
82 | 2700118.6793 | 1259731.3779 | 2700118.04 | 1259738.862 | 2700125.6596 | 1259750.1001
83 | 2700128.5436 | 1259758.3112 | 2700125.6596 | 1259750.1001
84 | 2700175.2719 | 1259723.3401 | 2700181.0992 | 1259715.777 | 2700182.2248 | 1259709.9264
85 | 2700177.029 | 1259813.4876 | 2700170.4777 | 1259815.4341 | 2700159.1384 | 1259816.3923
86 | 2700196.6042 | 1259807.5367 | 2700190.8805 | 1259791.0339
87 | 2700196.6042 | 1259807.5367 | 2700211.2271 | 1259802.747
88 | 2700196.6042 | 1259807.5367 | 2700192.2529 | 1259808.9641 | 2700177.029 | 1259813.4876
89 | 2700211.2271 | 1259802.747 | 2700216.7178 | 1259818.6783
90 | 2700211.2271 | 1259802.747 | 2700234.0512 | 1259795.2639
91 | 2700217.0333 | 1259819.5938 | 2700216.7178 | 1259818.6783
92 | 2700218.6134 | 1259824.1785 | 2700217.0333 | 1259819.5938
93 | 2700256.2076 | 1259843.3087 | 2700259.2676 | 1259830.45 | 2700257.3098 | 1259814.3148 | 2700254.4069 | 1259805.9203

## bus_geodata
| x | y | coords
0 | 2700037.8278 | 1259721.7327
1 | 2700052.5663 | 1259721.4883
2 | 2700009.7301 | 1259715.8786
3 | 2700091.6225 | 1259714.0616
4 | 2699995.5144 | 1259721.4325
5 | 2700001.6172 | 1259793.959
6 | 2700076.3235 | 1259697.9388
7 | 2700101.6971 | 1259708.9834
8 | 2700001.5817 | 1259794.3622
9 | 2700113.8349 | 1259724.9896
10 | 2699992.4153 | 1259815.6563
11 | 2700108.3963 | 1259680.4171
12 | 2700125.1305 | 1259694.9795
13 | 2700179.3034 | 1259624.1064
14 | 2700182.6144 | 1259638.3617
15 | 2700181.8595 | 1259648.6574
16 | 2700139.0272 | 1259659.0063
17 | 2700155.9137 | 1259670.3248
18 | 2700072.3447 | 1259915.4889
19 | 2700079.3084 | 1259892.877
20 | 2700104.2004 | 1259872.5587
21 | 2700052.6313 | 1259822.8577
22 | 2700054.4108 | 1259828.181
23 | 2699998.54 | 1259820.3525
24 | 2700020.2038 | 1259824.9112
25 | 2700018.3491 | 1259816.7429
26 | 2700099.1129 | 1259870.983
27 | 2699952.7877 | 1259797.0798
28 | 2699967.5615 | 1259799.1229
29 | 2700141.1029 | 1259682.1838
30 | 2700114.4238 | 1259725.7661
31 | 2700152.114 | 1259703.7639
32 | 2700143.3188 | 1259718.5106
33 | 2700265.0827 | 1259674.1438
34 | 2700239.644 | 1259693.5357
35 | 2700265.1834 | 1259674.067
36 | 2700232.2645 | 1259699.1599
37 | 2700275.9665 | 1259654.3447
38 | 2700269.976 | 1259704.4174
39 | 2700226.5314 | 1259703.5294
40 | 2700275.6511 | 1259649.8246
41 | 2700269.7448 | 1259709.4507
42 | 2700285.27 | 1259778.7595
43 | 2700249.0241 | 1259790.3548
44 | 2700286.0388 | 1259759.7238
45 | 2700193.6403 | 1259733.7596
46 | 2700220.1841 | 1259745.741
47 | 2700195.5799 | 1259767.389
48 | 2700218.7678 | 1259743.9045
49 | 2700241.1518 | 1259730.8952
50 | 2700219.5282 | 1259708.8668
51 | 2700276.6796 | 1259632.2744
52 | 2700254.2407 | 1259805.4397
53 | 2700244.6416 | 1259791.7917
54 | 2700098.4098 | 1259801.1919
55 | 2700083.9519 | 1259809.9644
56 | 2700105.0164 | 1259815.2707
57 | 2700110.3994 | 1259817.4636
58 | 2700091.1199 | 1259842.8076
59 | 2700081.6139 | 1259818.1217
60 | 2700123.249 | 1259815.0012
61 | 2700141.215 | 1259815.7836
62 | 2700185.3919 | 1259775.2093
63 | 2700240.5502 | 1259728.5831
64 | 2700188.9041 | 1259654.6815
65 | 2700189.6935 | 1259664.156
66 | 2700140.2909 | 1259820.0492
67 | 2700136.0986 | 1259839.4341
68 | 2700141.9594 | 1259815.8156
69 | 2700165.8726 | 1259782.0605
70 | 2700188.4359 | 1259675.9687
71 | 2700187.203 | 1259683.6343
72 | 2700184.6716 | 1259697.2086
73 | 2700183.4425 | 1259703.597
74 | 2700058.0549 | 1259839.0729
75 | 2700016.4854 | 1259808.535
76 | 2700064.7721 | 1259854.7001
77 | 2700118.6793 | 1259731.3779
78 | 2700136.9606 | 1259723.5436
79 | 2700125.6596 | 1259750.1001
80 | 2700128.5436 | 1259758.3112
81 | 2700182.2248 | 1259709.9264
82 | 2700175.2719 | 1259723.3401
83 | 2700131.709 | 1259859.7315
84 | 2700159.1384 | 1259816.3923
85 | 2700190.8805 | 1259791.0339
86 | 2700196.6042 | 1259807.5367
87 | 2700211.2271 | 1259802.747
88 | 2700177.029 | 1259813.4876
89 | 2700216.7178 | 1259818.6783
90 | 2700234.0512 | 1259795.2639
91 | 2700217.0333 | 1259819.5938
92 | 2700254.4069 | 1259805.9203
93 | 2700218.6134 | 1259824.1785
94 | 2700256.2076 | 1259843.3087
95 | 2700128.5436 | 1259758.3112

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99147 | -0.16207 | 0.0082802 | 0.0020752
1 | 0.99239 | -0.14448 | 0.012397 | 0.0031069
2 | 0.98978 | -0.19439 | 0 | 0
3 | 0.99511 | -0.092606 | 0 | 0
4 | 0.98968 | -0.19629 | 0.0055429 | 0.0013892
5 | 0.98536 | -0.27945 | 0.0028788 | 0.0007215
6 | 0.99495 | -0.095814 | 0.0081997 | 0.002055
7 | 0.99592 | -0.077233 | 0 | 0
8 | 0.98534 | -0.27988 | 0.002645 | 0.00066291
9 | 0.99737 | -0.049861 | 0.0049092 | 0.0012304
10 | 0.98404 | -0.30504 | 0 | 0
11 | 0.99456 | -0.10404 | 0.0093442 | 0.0023419
12 | 0.99475 | -0.10039 | 0 | 0
13 | 0.99345 | -0.12553 | 0.006093 | 0.001527
14 | 0.99353 | -0.12393 | 0 | 0
15 | 0.9936 | -0.12268 | 0 | 0
16 | 0.99417 | -0.11157 | 0.0093142 | 0.0023344
17 | 0.99434 | -0.10823 | 0 | 0
18 | 0.97737 | -0.43503 | 0 | 0
19 | 0.97723 | -0.43779 | 0 | 0
20 | 0.97759 | -0.4306 | 0.00419 | 0.0010501
21 | 0.98077 | -0.36857 | 0 | 0
22 | 0.98052 | -0.37336 | 0 | 0
23 | 0.98368 | -0.31198 | 0 | 0
24 | 0.98353 | -0.31489 | 0 | 0
25 | 0.98348 | -0.31581 | 0.00089704 | 0.00022482
26 | 0.97708 | -0.44063 | 0.0040118 | 0.0010055
27 | 0.98352 | -0.31522 | 0.0073814 | 0.00185
28 | 0.98362 | -0.3132 | 0.0077987 | 0.0019545
29 | 0.99492 | -0.09703 | 0 | 0
30 | 0.99744 | -0.048494 | 0.0016844 | 0.00042215
31 | 0.99591 | -0.077943 | 0.0015952 | 0.00039978
32 | 0.99668 | -0.063282 | 0.0013574 | 0.00034019
33 | 0.97069 | -0.56663 | 0.0017823 | 0.00044669
34 | 0.97049 | -0.57047 | 0.0020345 | 0.00050988
35 | 0.97069 | -0.56661 | 0 | 0
36 | 0.97045 | -0.57123 | 0.0012924 | 0.00032391
37 | 0.97059 | -0.56854 | 0 | 0
38 | 0.97105 | -0.55943 | 0 | 0
39 | 0.97043 | -0.57165 | 0.0012915 | 0.00032369
40 | 0.97057 | -0.56885 | 0.0019965 | 0.00050036
41 | 0.97111 | -0.55831 | 0.0023751 | 0.00059524
42 | 0.97434 | -0.49455 | 0 | 0
43 | 0.97441 | -0.49314 | 0 | 0
44 | 0.9743 | -0.49525 | 0.0020198 | 0.00050621
45 | 0.97276 | -0.52555 | 0 | 0
46 | 0.97208 | -0.53899 | 0 | 0
47 | 0.97351 | -0.51082 | 0.0049257 | 0.0012345
48 | 0.97208 | -0.53906 | 0.0017677 | 0.00044303
49 | 0.97169 | -0.54687 | 0 | 0
50 | 0.97042 | -0.57196 | 0.0018649 | 0.00046738
51 | 0.97055 | -0.56943 | 0.0017816 | 0.0004465
52 | 0.97438 | -0.49364 | 0.00038905 | 9.7506e-05
53 | 0.97443 | -0.49282 | 0.00072534 | 0.00018179
54 | 0.97824 | -0.41799 | 0 | 0
55 | 0.97822 | -0.41822 | 0.00075663 | 0.00018963
56 | 0.97825 | -0.41774 | 0 | 0
57 | 0.97802 | -0.42223 | 0 | 0
58 | 0.97823 | -0.41821 | 0.00075493 | 0.0001892
59 | 0.97931 | -0.39689 | 0.0030444 | 0.00076299
60 | 0.97744 | -0.43368 | 0 | 0
61 | 0.9768 | -0.44622 | 0 | 0
62 | 0.97379 | -0.50533 | 0 | 0
63 | 0.97168 | -0.54697 | 0.0021427 | 0.000537
64 | 0.99344 | -0.12565 | 0.0020424 | 0.00051188
65 | 0.9933 | -0.12835 | 0.0028912 | 0.0007246
66 | 0.97674 | -0.4473 | 0 | 0
67 | 0.97649 | -0.45221 | 0.0076398 | 0.0019147
68 | 0.97677 | -0.44665 | 0.0049411 | 0.0012383
69 | 0.9737 | -0.5072 | 0.0049315 | 0.0012359
70 | 0.99316 | -0.13114 | 0.0021001 | 0.00052633
71 | 0.99308 | -0.13266 | 0.0027113 | 0.00067951
72 | 0.99298 | -0.13471 | 0.0025706 | 0.00064427
73 | 0.99294 | -0.13538 | 0.00126 | 0.00031578
74 | 0.98047 | -0.37433 | 0.003504 | 0.0008782
75 | 0.98344 | -0.3166 | 0.0052151 | 0.001307
76 | 0.98045 | -0.37469 | 0.0011633 | 0.00029154
77 | 0.99797 | -0.038511 | 0 | 0
78 | 0.99702 | -0.05676 | 0.0013581 | 0.00034037
79 | 1 | 0 | -0.21872 | -0.055588
80 | 0.99996 | -0.00074442 | 0.0049074 | 0.0012299
81 | 0.99291 | -0.1359 | 0.0013322 | 0.00033388
82 | 0.99287 | -0.13679 | 0.0032309 | 0.00080973
83 | 0.97638 | -0.45445 | 0.0059088 | 0.0014809
84 | 0.97631 | -0.45578 | 0.010007 | 0.0025079
85 | 0.97423 | -0.49665 | 0.0023459 | 0.00058794
86 | 0.97473 | -0.48686 | 0 | 0
87 | 0.97459 | -0.48955 | 0 | 0
88 | 0.97549 | -0.47182 | 0.0080049 | 0.0020062
89 | 0.97453 | -0.49085 | 0.00038888 | 9.7464e-05
90 | 0.97447 | -0.49191 | 0.00086744 | 0.0002174
91 | 0.97452 | -0.49092 | 0.0019081 | 0.00047821
92 | 0.97438 | -0.49366 | 0.00044025 | 0.00011034
93 | 0.97451 | -0.49109 | 0.0019188 | 0.00048091
94 | 0.97435 | -0.49429 | 0.00089726 | 0.00022488
95 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13629 | -0.034776 | 0.13641 | 0.034849 | 0.00011589 | 7.379e-05 | 0.20477 | 0.20477 | 0.20477 | 0.99147 | -0.16207 | 0.99239 | -0.14448 | 28.128
1 | 0.12801 | 0.0327 | -0.12781 | -0.032573 | 0.00019968 | 0.00012706 | 0.19234 | 0.19235 | 0.19235 | 0.99147 | -0.16207 | 0.98978 | -0.19439 | 26.421
2 | -0.14881 | -0.037956 | 0.14918 | 0.038195 | 0.00037382 | 0.00023821 | 0.22336 | 0.22336 | 0.22336 | 0.99239 | -0.14448 | 0.99511 | -0.092606 | 30.6813
3 | 0.0055434 | 0.0013892 | -0.0055429 | -0.0013892 | 5.0226e-07 | 7.3617e-08 | 0.0083338 | 0.0083339 | 0.0083339 | 0.98978 | -0.19439 | 0.98968 | -0.19629 | 2.2895
4 | 0.12227 | 0.031184 | -0.12177 | -0.030866 | 0.0005 | 0.00031798 | 0.18401 | 0.18401 | 0.18401 | 0.98978 | -0.19439 | 0.98536 | -0.27945 | 25.2764
5 | 0.0082009 | 0.0020555 | -0.0081997 | -0.002055 | 1.2534e-06 | 5.135e-07 | 0.012263 | 0.012263 | 0.012263 | 0.99511 | -0.092606 | 0.99495 | -0.095814 | 3.369
6 | -0.15738 | -0.04025 | 0.1575 | 0.040325 | 0.00011717 | 7.4696e-05 | 0.23562 | 0.23562 | 0.23562 | 0.99511 | -0.092606 | 0.99592 | -0.077233 | 32.3657
7 | 0.11889 | 0.030145 | -0.11889 | -0.030143 | 2.4498e-06 | 1.5576e-06 | 0.17966 | 0.17966 | 0.17966 | 0.98536 | -0.27945 | 0.98534 | -0.27988 | 24.6792
8 | -0.1575 | -0.040325 | 0.15771 | 0.040458 | 0.00020911 | 0.0001333 | 0.23562 | 0.23562 | 0.23562 | 0.99592 | -0.077233 | 0.99737 | -0.049861 | 32.3657
9 | 0.11624 | 0.02948 | -0.1161 | -0.029391 | 0.00014039 | 8.9234e-05 | 0.17567 | 0.17567 | 0.17567 | 0.98534 | -0.27988 | 0.98404 | -0.30504 | 24.1306
10 | -0.16262 | -0.041689 | 0.16263 | 0.041695 | 1.0785e-05 | 6.8772e-06 | 0.24295 | 0.24295 | 0.24295 | 0.99737 | -0.049861 | 0.99744 | -0.048494 | 33.3717
11 | 0.10092 | 0.025583 | -0.10088 | -0.025561 | 3.368e-05 | 2.1359e-05 | 0.15271 | 0.15271 | 0.15271 | 0.98404 | -0.30504 | 0.98368 | -0.31198 | 20.976
12 | 0.015187 | 0.0038082 | -0.015181 | -0.0038048 | 5.9038e-06 | 3.3994e-06 | 0.022965 | 0.022966 | 0.022966 | 0.98404 | -0.30504 | 0.98362 | -0.3132 | 6.3092
13 | -0.0093442 | -0.0023419 | 0.0093458 | 0.0023426 | 1.626e-06 | 7.5269e-07 | 0.01398 | 0.01398 | 0.01398 | 0.99456 | -0.10404 | 0.99475 | -0.10039 | 3.8407
14 | -0.0093458 | -0.0023426 | 0.0093473 | 0.0023433 | 1.4973e-06 | 6.9303e-07 | 0.01398 | 0.01398 | 0.01398 | 0.99475 | -0.10039 | 0.99492 | -0.09703 | 3.8407
15 | -0.006093 | -0.001527 | 0.0060934 | 0.0015271 | 4.6604e-07 | 1.0505e-07 | 0.0091262 | 0.0091261 | 0.0091262 | 0.99345 | -0.12553 | 0.99353 | -0.12393 | 2.5072
16 | -0.0060934 | -0.0015271 | 0.0060938 | 0.0015272 | 3.6279e-07 | 8.1749e-08 | 0.0091261 | 0.0091261 | 0.0091261 | 0.99353 | -0.12393 | 0.9936 | -0.12268 | 2.5072
17 | 0.018147 | 0.0045503 | -0.018145 | -0.0045488 | 2.5675e-06 | 1.5232e-06 | 0.027178 | 0.027178 | 0.027178 | 0.9936 | -0.12268 | 0.99344 | -0.12565 | 7.4665
18 | -0.024241 | -0.0060776 | 0.024258 | 0.0060878 | 1.6706e-05 | 1.0254e-05 | 0.036304 | 0.036304 | 0.036304 | 0.9936 | -0.12268 | 0.99434 | -0.10823 | 9.9737
19 | -0.0093142 | -0.0023344 | 0.0093157 | 0.0023351 | 1.4838e-06 | 6.856e-07 | 0.013941 | 0.013941 | 0.013941 | 0.99417 | -0.11157 | 0.99434 | -0.10823 | 3.8299
20 | -0.033573 | -0.0084229 | 0.033591 | 0.0084341 | 1.7931e-05 | 1.123e-05 | 0.050245 | 0.050245 | 0.050245 | 0.99434 | -0.10823 | 0.99492 | -0.09703 | 13.8035
21 | 0.0040129 | 0.0010052 | -0.0040124 | -0.0010053 | 5.2784e-07 | -1.3472e-07 | 0.0061093 | 0.0061095 | 0.0061095 | 0.97737 | -0.43503 | 0.97723 | -0.43779 | 1.6784
22 | -0.0040129 | -0.0010052 | 0.0040137 | 0.001005 | 8.4481e-07 | -2.1596e-07 | 0.0061093 | 0.0061091 | 0.0061093 | 0.97737 | -0.43503 | 0.97759 | -0.4306 | 1.6784
23 | 0.0040124 | 0.0010053 | -0.0040118 | -0.0010055 | 5.4252e-07 | -1.383e-07 | 0.0061095 | 0.0061097 | 0.0061097 | 0.97723 | -0.43779 | 0.97708 | -0.44063 | 1.6785
24 | -0.0082038 | -0.0020551 | 0.0082071 | 0.0020565 | 3.2737e-06 | 1.3928e-06 | 0.012487 | 0.012487 | 0.012487 | 0.97759 | -0.4306 | 0.97802 | -0.42223 | 3.4304
25 | 0.094512 | 0.023867 | -0.09449 | -0.023853 | 2.1652e-05 | 1.3715e-05 | 0.14346 | 0.14346 | 0.14346 | 0.98077 | -0.36857 | 0.98052 | -0.37336 | 19.7058
26 | -0.094512 | -0.023867 | 0.094769 | 0.024029 | 0.00025704 | 0.00016282 | 0.14346 | 0.14346 | 0.14346 | 0.98077 | -0.36857 | 0.98368 | -0.31198 | 19.7058
27 | 0.0046675 | 0.0011695 | -0.0046673 | -0.0011695 | 2.1609e-07 | -6.5587e-09 | 0.0070833 | 0.0070833 | 0.0070833 | 0.98052 | -0.37336 | 0.98047 | -0.37433 | 1.946
28 | 0.089823 | 0.022683 | -0.089722 | -0.022619 | 0.00010118 | 6.4027e-05 | 0.13637 | 0.13638 | 0.13638 | 0.98052 | -0.37336 | 0.97931 | -0.39689 | 18.7328
29 | 0.0061134 | 0.0015321 | -0.0061126 | -0.0015319 | 8.4665e-07 | 2.0678e-07 | 0.0092478 | 0.0092479 | 0.0092479 | 0.98368 | -0.31198 | 0.98353 | -0.31489 | 2.5406
30 | 0.0061126 | 0.0015319 | -0.0061123 | -0.0015319 | 2.6864e-07 | 6.5635e-08 | 0.0092479 | 0.009248 | 0.009248 | 0.98353 | -0.31489 | 0.98348 | -0.31581 | 2.5407
31 | 0.0052153 | 0.001307 | -0.0052151 | -0.001307 | 1.9653e-07 | 1.8976e-08 | 0.0078908 | 0.0078908 | 0.0078908 | 0.98348 | -0.31581 | 0.98344 | -0.3166 | 2.1678
32 | -0.0073814 | -0.00185 | 0.0073822 | 0.0018502 | 7.1166e-07 | 2.6234e-07 | 0.011168 | 0.011168 | 0.011168 | 0.98352 | -0.31522 | 0.98362 | -0.3132 | 3.0681
33 | -0.042939 | -0.010777 | 0.042978 | 0.010802 | 3.9128e-05 | 2.4713e-05 | 0.064225 | 0.064225 | 0.064225 | 0.99492 | -0.09703 | 0.99591 | -0.077943 | 17.6442
34 | -0.16431 | -0.042118 | 0.16439 | 0.042168 | 7.9561e-05 | 5.0735e-05 | 0.24546 | 0.24546 | 0.24546 | 0.99744 | -0.048494 | 0.99797 | -0.038511 | 33.7169
35 | -0.044573 | -0.011202 | 0.044604 | 0.011222 | 3.122e-05 | 1.9736e-05 | 0.066608 | 0.066608 | 0.066608 | 0.99591 | -0.077943 | 0.99668 | -0.063282 | 18.2989
36 | -0.045961 | -0.011562 | 0.045976 | 0.011571 | 1.4325e-05 | 9.0622e-06 | 0.068634 | 0.068634 | 0.068634 | 0.99668 | -0.063282 | 0.99702 | -0.05676 | 18.8556
37 | 0.0064847 | 0.0016251 | -0.0064835 | -0.0016247 | 1.1853e-06 | 3.633e-07 | 0.0099407 | 0.0099408 | 0.0099408 | 0.97069 | -0.56663 | 0.97049 | -0.57047 | 2.731
38 | -0.008267 | -0.0020718 | 0.008267 | 0.0020718 | 7.6277e-09 | 3.3161e-09 | 0.012673 | 0.012673 | 0.012673 | 0.97069 | -0.56663 | 0.97069 | -0.56661 | 3.4816
39 | 0.0044491 | 0.0011148 | -0.0044489 | -0.0011148 | 1.6191e-07 | -1.1024e-08 | 0.0068215 | 0.0068215 | 0.0068215 | 0.97049 | -0.57047 | 0.97045 | -0.57123 | 1.874
40 | 0.0037785 | 0.00094654 | -0.0037781 | -0.00094665 | 3.4665e-07 | -1.1872e-07 | 0.005792 | 0.0057922 | 0.0057922 | 0.97069 | -0.56661 | 0.97059 | -0.56854 | 1.5913
41 | -0.012046 | -0.0030183 | 0.01205 | 0.0030205 | 4.1216e-06 | 2.2392e-06 | 0.018465 | 0.018465 | 0.018465 | 0.97069 | -0.56661 | 0.97105 | -0.55943 | 5.0728
42 | 0.0031565 | 0.00079093 | -0.0031564 | -0.00079098 | 6.332e-08 | -4.8537e-08 | 0.0048399 | 0.0048399 | 0.0048399 | 0.97045 | -0.57123 | 0.97043 | -0.57165 | 1.3296
43 | 0.0037781 | 0.00094665 | -0.0037781 | -0.00094667 | 5.7006e-08 | -1.9515e-08 | 0.0057922 | 0.0057922 | 0.0057922 | 0.97059 | -0.56854 | 0.97057 | -0.56885 | 1.5913
44 | -0.01205 | -0.0030205 | 0.01205 | 0.0030209 | 6.4422e-07 | 3.4996e-07 | 0.018465 | 0.018465 | 0.018465 | 0.97105 | -0.55943 | 0.97111 | -0.55831 | 5.0728
45 | 0.0018649 | 0.00046729 | -0.0018649 | -0.00046738 | 2.7e-08 | -9.1507e-08 | 0.0028595 | 0.0028595 | 0.0028595 | 0.97043 | -0.57165 | 0.97042 | -0.57196 | 0.78559
46 | 0.0017816 | 0.00044631 | -0.0017816 | -0.0004465 | 4.9184e-08 | -1.8578e-07 | 0.0027314 | 0.0027314 | 0.0027314 | 0.97057 | -0.56885 | 0.97055 | -0.56943 | 0.7504
47 | -0.014425 | -0.0036161 | 0.014433 | 0.0036206 | 7.8617e-06 | 4.5003e-06 | 0.022104 | 0.022104 | 0.022104 | 0.97111 | -0.55831 | 0.97169 | -0.54687 | 6.0725
48 | -0.0020199 | -0.00050601 | 0.00202 | 0.00050563 | 1.3543e-07 | -3.8609e-07 | 0.0030847 | 0.0030845 | 0.0030847 | 0.97434 | -0.49455 | 0.97441 | -0.49314 | 0.84744
49 | 0.0020199 | 0.00050601 | -0.0020198 | -0.00050621 | 6.798e-08 | -1.9376e-07 | 0.0030847 | 0.0030848 | 0.0030848 | 0.97434 | -0.49455 | 0.9743 | -0.49525 | 0.84746
50 | 0.0017266 | 0.00043208 | -0.0017266 | -0.00043225 | 4.1607e-08 | -1.7219e-07 | 0.0026365 | 0.0026366 | 0.0026366 | 0.97441 | -0.49314 | 0.97438 | -0.49364 | 0.72433
51 | -0.0037466 | -0.00093771 | 0.0037467 | 0.00093769 | 5.6607e-08 | -2.1222e-08 | 0.005721 | 0.005721 | 0.005721 | 0.97441 | -0.49314 | 0.97443 | -0.49282 | 1.5717
52 | 0.018362 | 0.0046113 | -0.01835 | -0.0046043 | 1.1762e-05 | 7.0346e-06 | 0.028091 | 0.028091 | 0.028091 | 0.97276 | -0.52555 | 0.97208 | -0.53899 | 7.7173
53 | -0.018362 | -0.0046113 | 0.018375 | 0.0046191 | 1.2917e-05 | 7.7247e-06 | 0.028091 | 0.028091 | 0.028091 | 0.97276 | -0.52555 | 0.97351 | -0.51082 | 7.7172
54 | 0.0017677 | 0.000443 | -0.0017677 | -0.00044303 | 6.3619e-09 | -2.4652e-08 | 0.0027059 | 0.0027059 | 0.0027059 | 0.97208 | -0.53899 | 0.97208 | -0.53906 | 0.74339
55 | 0.016582 | 0.0041613 | -0.016576 | -0.0041576 | 6.2334e-06 | 3.6697e-06 | 0.025385 | 0.025385 | 0.025385 | 0.97208 | -0.53899 | 0.97169 | -0.54687 | 6.9739
56 | -0.0233 | -0.0058536 | 0.023306 | 0.0058573 | 6.1106e-06 | 3.7511e-06 | 0.035619 | 0.035619 | 0.035619 | 0.97351 | -0.51082 | 0.97379 | -0.50533 | 9.7856
57 | 0.0021427 | 0.00053698 | -0.0021427 | -0.000537 | 9.6455e-09 | -2.3419e-08 | 0.0032812 | 0.0032813 | 0.0032813 | 0.97169 | -0.54687 | 0.97168 | -0.54697 | 0.90144
58 | 0.0013375 | 0.00033475 | -0.0013375 | -0.00033475 | 7.9537e-10 | -5.8246e-09 | 0.0020424 | 0.0020424 | 0.0020424 | 0.97438 | -0.49364 | 0.97438 | -0.49366 | 0.56111
59 | -0.004472 | -0.0011195 | 0.0044722 | 0.0011195 | 1.9489e-07 | -1.4113e-08 | 0.0068286 | 0.0068286 | 0.0068286 | 0.97443 | -0.49282 | 0.97447 | -0.49191 | 1.876
60 | 0.00075664 | 0.00018942 | -0.00075663 | -0.00018963 | 8.4001e-09 | -2.0693e-07 | 0.0011509 | 0.0011509 | 0.0011509 | 0.97824 | -0.41799 | 0.97822 | -0.41822 | 0.31619
61 | -0.00075664 | -0.00018942 | 0.00075665 | 0.00018921 | 8.7701e-09 | -2.1608e-07 | 0.0011509 | 0.0011508 | 0.0011509 | 0.97824 | -0.41799 | 0.97825 | -0.41774 | 0.31617
62 | 0.085079 | 0.021424 | -0.085061 | -0.021412 | 1.8243e-05 | 1.153e-05 | 0.12945 | 0.12945 | 0.12945 | 0.97825 | -0.41774 | 0.97802 | -0.42223 | 17.7817
63 | 0.00075495 | 0.00018879 | -0.00075493 | -0.0001892 | 1.6918e-08 | -4.1872e-07 | 0.0011482 | 0.0011484 | 0.0011484 | 0.97825 | -0.41774 | 0.97823 | -0.41821 | 0.31548
64 | -0.086591 | -0.021802 | 0.086677 | 0.021856 | 8.6394e-05 | 5.4625e-05 | 0.13175 | 0.13175 | 0.13175 | 0.97825 | -0.41774 | 0.97931 | -0.39689 | 18.0975
65 | 0.076854 | 0.019356 | -0.076812 | -0.019329 | 4.2055e-05 | 2.6504e-05 | 0.11696 | 0.11696 | 0.11696 | 0.97802 | -0.42223 | 0.97744 | -0.43368 | 16.0665
66 | 0.076812 | 0.019329 | -0.076766 | -0.0193 | 4.599e-05 | 2.8985e-05 | 0.11696 | 0.11696 | 0.11696 | 0.97744 | -0.43368 | 0.9768 | -0.44622 | 16.0665
67 | 0.063213 | 0.015902 | -0.063212 | -0.015901 | 1.2961e-06 | 8.1082e-07 | 0.096318 | 0.096318 | 0.096318 | 0.9768 | -0.44622 | 0.97677 | -0.44665 | 13.2305
68 | 0.013553 | 0.0033979 | -0.013552 | -0.0033975 | 6.9762e-07 | 3.9185e-07 | 0.020647 | 0.020647 | 0.020647 | 0.9768 | -0.44622 | 0.97674 | -0.4473 | 5.6722
69 | 0.0049319 | 0.001236 | -0.0049315 | -0.0012359 | 4.406e-07 | 2.4651e-08 | 0.0075363 | 0.0075363 | 0.0075363 | 0.97379 | -0.50533 | 0.9737 | -0.5072 | 2.0704
70 | -0.028238 | -0.0070933 | 0.02825 | 0.0071006 | 1.1698e-05 | 7.2782e-06 | 0.043156 | 0.043156 | 0.043156 | 0.97379 | -0.50533 | 0.97423 | -0.49665 | 11.856
71 | 0.016102 | 0.0040369 | -0.0161 | -0.0040357 | 2.074e-06 | 1.2043e-06 | 0.024119 | 0.024119 | 0.024119 | 0.99344 | -0.12565 | 0.9933 | -0.12835 | 6.6261
72 | 0.013209 | 0.0033111 | -0.013207 | -0.0033102 | 1.7532e-06 | 9.6749e-07 | 0.019788 | 0.019788 | 0.019788 | 0.9933 | -0.12835 | 0.99316 | -0.13114 | 5.4362
73 | 0.013552 | 0.0033975 | -0.013549 | -0.0033957 | 3.1705e-06 | 1.7809e-06 | 0.020647 | 0.020647 | 0.020647 | 0.97674 | -0.4473 | 0.97649 | -0.45221 | 5.6722
74 | 0.0059094 | 0.001481 | -0.0059088 | -0.0014809 | 6.3149e-07 | 1.444e-07 | 0.009005 | 0.0090051 | 0.0090051 | 0.97649 | -0.45221 | 0.97638 | -0.45445 | 2.4739
75 | 0.058271 | 0.014663 | -0.058245 | -0.014647 | 2.5423e-05 | 1.584e-05 | 0.088791 | 0.088791 | 0.088791 | 0.97677 | -0.44665 | 0.97631 | -0.45578 | 12.1965
76 | 0.011107 | 0.0027838 | -0.011106 | -0.0027834 | 8.063e-07 | 4.1557e-07 | 0.016641 | 0.016641 | 0.016641 | 0.99316 | -0.13114 | 0.99308 | -0.13266 | 4.5718
77 | 0.0083949 | 0.0021039 | -0.0083941 | -0.0021036 | 8.1938e-07 | 3.4575e-07 | 0.012579 | 0.012579 | 0.012579 | 0.99308 | -0.13266 | 0.99298 | -0.13471 | 3.4557
78 | 0.0058235 | 0.0014593 | -0.0058233 | -0.0014593 | 1.8579e-07 | 3.4753e-08 | 0.0087267 | 0.0087267 | 0.0087267 | 0.99298 | -0.13471 | 0.99294 | -0.13538 | 2.3974
79 | 0.0045633 | 0.0011435 | -0.0045632 | -0.0011435 | 1.1303e-07 | -1.1027e-08 | 0.0068385 | 0.0068385 | 0.0068385 | 0.99294 | -0.13538 | 0.99291 | -0.1359 | 1.8787
80 | 0.0011633 | 0.00029134 | -0.0011633 | -0.00029154 | 1.9903e-08 | -2.0202e-07 | 0.0017654 | 0.0017655 | 0.0017655 | 0.98047 | -0.37433 | 0.98045 | -0.37469 | 0.48502
81 | 0.047375 | 0.011937 | -0.047334 | -0.011911 | 4.1319e-05 | 2.6156e-05 | 0.070661 | 0.070661 | 0.070661 | 0.99797 | -0.038511 | 0.99702 | -0.05676 | 19.4125
82 | -0.21177 | -0.054106 | 0.21216 | 0.054358 | 0.00039515 | 0.00025234 | 0.31612 | 0.31612 | 0.31612 | 0.99797 | -0.038511 | 1 | 0 | 43.423
83 | 0.0049076 | 0.0012299 | -0.0049074 | -0.0012299 | 1.7404e-07 | -2.7872e-09 | 0.0073025 | 0.0073026 | 0.0073026 | 1 | 0 | 0.99996 | -0.00074442 | 2.0062
84 | 0.003231 | 0.00080962 | -0.0032309 | -0.00080973 | 1.3633e-07 | -1.1329e-07 | 0.004842 | 0.0048421 | 0.0048421 | 0.99291 | -0.1359 | 0.99287 | -0.13679 | 1.3302
85 | 0.048238 | 0.012139 | -0.048202 | -0.012116 | 3.6938e-05 | 2.3413e-05 | 0.073539 | 0.073539 | 0.073539 | 0.97631 | -0.45578 | 0.97549 | -0.47182 | 20.2031
86 | -0.030596 | -0.0076885 | 0.03061 | 0.0076974 | 1.4309e-05 | 8.9401e-06 | 0.046739 | 0.046739 | 0.046739 | 0.97423 | -0.49665 | 0.97473 | -0.48686 | 12.8403
87 | 0.0095576 | 0.002394 | -0.0095564 | -0.0023934 | 1.225e-06 | 5.9276e-07 | 0.01459 | 0.01459 | 0.01459 | 0.97473 | -0.48686 | 0.97459 | -0.48955 | 4.0083
88 | -0.040168 | -0.010091 | 0.040197 | 0.01011 | 2.886e-05 | 1.8215e-05 | 0.061329 | 0.061329 | 0.061329 | 0.97473 | -0.48686 | 0.97549 | -0.47182 | 16.8485
89 | 0.0042161 | 0.0010565 | -0.0042158 | -0.0010565 | 2.6185e-07 | -4.2386e-08 | 0.0064371 | 0.0064372 | 0.0064372 | 0.97459 | -0.48955 | 0.97453 | -0.49085 | 1.7685
90 | 0.0053403 | 0.0013369 | -0.0053397 | -0.0013369 | 5.9874e-07 | 8.3924e-08 | 0.0081531 | 0.0081532 | 0.0081532 | 0.97459 | -0.48955 | 0.97447 | -0.49191 | 2.2399
91 | 0.003827 | 0.00095906 | -0.0038269 | -0.00095907 | 1.2399e-08 | -4.1292e-09 | 0.0058434 | 0.0058434 | 0.0058434 | 0.97453 | -0.49085 | 0.97452 | -0.49092 | 1.6053
92 | 0.0019189 | 0.00048086 | -0.0019188 | -0.00048091 | 1.5611e-08 | -5.0428e-08 | 0.0029299 | 0.0029299 | 0.0029299 | 0.97452 | -0.49092 | 0.97451 | -0.49109 | 0.80493
93 | 0.00089729 | 0.00022442 | -0.00089726 | -0.00022488 | 2.7003e-08 | -4.6043e-07 | 0.0013701 | 0.0013703 | 0.0013703 | 0.97438 | -0.49366 | 0.97435 | -0.49429 | 0.37645

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.22362 | 0.056815

## res_load
| p_mw | q_mvar
0 | 0.0082802 | 0.0020752
1 | 0.012397 | 0.0031069
2 | 0.0055429 | 0.0013892
3 | 0.0028788 | 0.0007215
4 | 0.0081997 | 0.002055
5 | 0.002645 | 0.00066291
6 | 0.0049092 | 0.0012304
7 | 0.0093442 | 0.0023419
8 | 0.006093 | 0.001527
9 | 0.0093142 | 0.0023344
10 | 0.00419 | 0.0010501
11 | 0.00089704 | 0.00022482
12 | 0.0040118 | 0.0010055
13 | 0.0073814 | 0.00185
14 | 0.0077987 | 0.0019545
15 | 0.0016844 | 0.00042215
16 | 0.0015952 | 0.00039978
17 | 0.0013574 | 0.00034019
18 | 0.0017823 | 0.00044669
19 | 0.0020345 | 0.00050988
20 | 0.0012924 | 0.00032391
21 | 0.0012915 | 0.00032369
22 | 0.0019965 | 0.00050036
23 | 0.0023751 | 0.00059524
24 | 0.0020198 | 0.00050621
25 | 0.0049257 | 0.0012345
26 | 0.0017677 | 0.00044303
27 | 0.0018649 | 0.00046738
28 | 0.0017816 | 0.0004465
29 | 0.00038905 | 9.7506e-05
30 | 0.00072534 | 0.00018179
31 | 0.00075663 | 0.00018963
32 | 0.00075493 | 0.0001892
33 | 0.0030444 | 0.00076299
34 | 0.0021427 | 0.000537
35 | 0.0020424 | 0.00051188
36 | 0.0028912 | 0.0007246
37 | 0.0076398 | 0.0019147
38 | 0.0049411 | 0.0012383
39 | 0.0049315 | 0.0012359
40 | 0.0021001 | 0.00052633
41 | 0.0027113 | 0.00067951
42 | 0.0025706 | 0.00064427
43 | 0.00126 | 0.00031578
44 | 0.003504 | 0.0008782
45 | 0.0052151 | 0.001307
46 | 0.0011633 | 0.00029154
47 | 0.0013581 | 0.00034037
48 | 0.0048969 | 0.0012273
49 | 0.0049074 | 0.0012299
50 | 0.0013322 | 0.00033388
51 | 0.0032309 | 0.00080973
52 | 0.0059088 | 0.0014809
53 | 0.010007 | 0.0025079
54 | 0.0023459 | 0.00058794
55 | 0.0080049 | 0.0020062
56 | 0.00038888 | 9.7464e-05
57 | 0.00086744 | 0.0002174
58 | 0.0019081 | 0.00047821
59 | 0.00044025 | 0.00011034
60 | 0.0019188 | 0.00048091
61 | 0.00089726 | 0.00022488

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1