## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-231_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-231_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-231_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-231_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-231_0_5_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_230-231_0_5_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_230-231_0_5_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_230-231_0_5_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_230-231_0_5_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_230-231_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_230-231_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_230-231_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_230-231_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_230-231_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_230-231_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_230-231_0_5_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_230-231_0_5_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_230-231_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_230-231_0_5_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_230-231_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_230-231_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_230-231_0_5_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_230-231_0_5_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_230-231_0_5_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_230-231_0_5_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_230-231_0_5_node_26 | 0.4 | n |  | TRUE
26 | bus_MV_512_0_node_32 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-231_0_5_load_0 | 0 | 0.012159 | 0.0030473 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-231_0_5_load_1 | 1 | 0.014077 | 0.003528 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-231_0_5_load_2 | 2 | 0.011613 | 0.0029105 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-231_0_5_load_3 | 3 | 0.016971 | 0.0042533 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-231_0_5_load_22 | 7 | 0.048097 | 0.012054 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-231_0_5_load_21 | 8 | 0.091504 | 0.022933 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-231_0_5_load_5 | 9 | 0.04653 | 0.011661 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-231_0_5_load_6 | 10 | 0.039108 | 0.0098013 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-231_0_5_load_7 | 11 | 0.010718 | 0.0026861 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-231_0_5_load_8 | 12 | 0.040457 | 0.010139 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-231_0_5_load_20 | 15 | 0.010051 | 0.002519 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-231_0_5_load_19 | 16 | 0.030208 | 0.0075708 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-231_0_5_load_10 | 17 | 0.020768 | 0.0052048 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-231_0_5_load_24 | 18 | 0.0079414 | 0.0019903 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-231_0_5_load_13 | 20 | 0.0056568 | 0.0014177 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-231_0_5_load_28 | 22 | 0.017303 | 0.0043366 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-231_0_5_load_27 | 23 | 0.053551 | 0.013421 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-231_0_5_load_25 | 24 | 0.049108 | 0.012308 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-231_0_5_load_26 | 25 | 0.04805 | 0.012043 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-231_0_5_line_0 |  | 0 | 1 | 8.7163e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-231_0_5_line_1 |  | 0 | 2 | 6.3486e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-231_0_5_line_2 |  | 1 | 3 | 0.0030921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-231_0_5_line_3 |  | 3 | 4 | 0.031308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-231_0_5_line_4 |  | 4 | 5 | 0.062881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_230-231_0_5_line_5 |  | 4 | 6 | 0.052596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_230-231_0_5_line_6 |  | 5 | 24 | 0.032401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_230-231_0_5_line_7 |  | 6 | 18 | 0.0014094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_230-231_0_5_line_8 |  | 7 | 8 | 0.0040123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-231_0_5_line_9 |  | 8 | 15 | 0.015761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_230-231_0_5_line_10 |  | 9 | 10 | 0.01433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_230-231_0_5_line_11 |  | 9 | 11 | 0.0095759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_230-231_0_5_line_12 |  | 10 | 12 | 0.0017691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_230-231_0_5_line_13 |  | 11 | 13 | 0.0066845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_230-231_0_5_line_14 |  | 12 | 14 | 0.015666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_230-231_0_5_line_15 |  | 13 | 15 | 0.015552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_230-231_0_5_line_16 |  | 14 | 16 | 0.021616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-231_0_5_line_17 |  | 14 | 17 | 0.028592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_230-231_0_5_line_18 |  | 17 | 19 | 0.016028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_230-231_0_5_line_19 |  | 18 | 20 | 0.012161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_230-231_0_5_line_20 |  | 19 | 20 | 0.025306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_230-231_0_5_line_21 |  | 21 | 22 | 0.02418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-231_0_5_line_22 |  | 21 | 23 | 0.0042009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-231_0_5_line_23 |  | 23 | 25 | 0.026134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-231_0_5_line_24 |  | 24 | 25 | 0.036075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-231_0_5_trafo_21 | 0.63 MVA 20/0.4 kV | 26 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2697003.861 | 1261655.0999 | 2697003.8523 | 1261655.099
1 | 2697003.8523 | 1261655.099 | 2697003.7892 | 1261655.0926
2 | 2697006.9374 | 1261655.4114 | 2697003.861 | 1261655.0999
3 | 2697038.0123 | 1261659.2125 | 2697013.3535 | 1261656.0611 | 2697006.9374 | 1261655.4114
4 | 2697038.0123 | 1261659.2125 | 2697036.4691 | 1261634.3225 | 2697027.8226 | 1261608.3151 | 2697027.3465 | 1261607.0174 | 2697018.7274 | 1261610.1008
5 | 2697038.0123 | 1261659.2125 | 2697036.9302 | 1261699.4275 | 2697036.7891 | 1261704.8073 | 2697035.8546 | 1261710.3187 | 2697035.621 | 1261711.6938
6 | 2697018.7274 | 1261610.1008 | 2697011.5928 | 1261612.7303 | 2697007.8194 | 1261622.2429 | 2696994.6161 | 1261628.3899
7 | 2697035.621 | 1261711.6938 | 2697035.3862 | 1261713.0835
8 | 2696977.4904 | 1261695.7753 | 2696981.4182 | 1261696.5947
9 | 2696996.8469 | 1261699.8134 | 2696981.4182 | 1261696.5947
10 | 2697002.9326 | 1261716.4389 | 2696994.8793 | 1261728.2917
11 | 2697002.9326 | 1261716.4389 | 2697008.3143 | 1261708.5184
12 | 2696994.8793 | 1261728.2917 | 2696993.8851 | 1261729.7549
13 | 2697012.0709 | 1261702.9894 | 2697008.3143 | 1261708.5184
14 | 2696985.0811 | 1261742.7125 | 2696993.8851 | 1261729.7549
15 | 2697012.0709 | 1261702.9894 | 2696996.8469 | 1261699.8134
16 | 2696985.0811 | 1261742.7125 | 2696963.7305 | 1261739.3343
17 | 2696985.0811 | 1261742.7125 | 2697013.2874 | 1261747.3938
18 | 2697029.0988 | 1261750.018 | 2697013.2874 | 1261747.3938
19 | 2697035.3862 | 1261713.0835 | 2697033.3605 | 1261725.0748
20 | 2697029.0988 | 1261750.018 | 2697029.3358 | 1261748.8987 | 2697033.3605 | 1261725.0748
21 | 2696937.5294 | 1261654.0388 | 2696916.6767 | 1261666.2798
22 | 2696937.5294 | 1261654.0388 | 2696938.8222 | 1261656.0839 | 2696939.7392 | 1261657.6112
23 | 2696962.5316 | 1261644.8251 | 2696946.8127 | 1261653.6461 | 2696939.7392 | 1261657.6112
24 | 2696994.6161 | 1261628.3899 | 2696978.1951 | 1261636.0351 | 2696962.5316 | 1261644.8251

## bus_geodata
| x | y | coords
0 | 2697003.8523 | 1261655.099
1 | 2697003.861 | 1261655.0999
2 | 2697003.7892 | 1261655.0926
3 | 2697006.9374 | 1261655.4114
4 | 2697038.0123 | 1261659.2125
5 | 2697018.7274 | 1261610.1008
6 | 2697035.621 | 1261711.6938
7 | 2696977.4904 | 1261695.7753
8 | 2696981.4182 | 1261696.5947
9 | 2697002.9326 | 1261716.4389
10 | 2696994.8793 | 1261728.2917
11 | 2697008.3143 | 1261708.5184
12 | 2696993.8851 | 1261729.7549
13 | 2697012.0709 | 1261702.9894
14 | 2696985.0811 | 1261742.7125
15 | 2696996.8469 | 1261699.8134
16 | 2696963.7305 | 1261739.3343
17 | 2697013.2874 | 1261747.3938
18 | 2697035.3862 | 1261713.0835
19 | 2697029.0988 | 1261750.018
20 | 2697033.3605 | 1261725.0748
21 | 2696937.5294 | 1261654.0388
22 | 2696916.6767 | 1261666.2798
23 | 2696939.7392 | 1261657.6112
24 | 2696994.6161 | 1261628.3899
25 | 2696962.5316 | 1261644.8251
26 | 2696956.1243 | 1261690.1173

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98386 | -0.30951 | 0.012159 | 0.0030473
1 | 0.98386 | -0.3095 | 0.014077 | 0.003528
2 | 0.98386 | -0.30952 | 0.011613 | 0.0029105
3 | 0.98396 | -0.3074 | 0.016971 | 0.0042533
4 | 0.98555 | -0.27655 | 0 | 0
5 | 0.98309 | -0.32406 | 0 | 0
6 | 0.98826 | -0.22411 | 0 | 0
7 | 0.99983 | -0.0033642 | 0.048097 | 0.012054
8 | 1 | 0 | -0.48968 | -0.1245
9 | 0.99534 | -0.088601 | 0.04653 | 0.011661
10 | 0.99413 | -0.11176 | 0.039108 | 0.0098013
11 | 0.99625 | -0.0712 | 0.010718 | 0.0026861
12 | 0.99399 | -0.11432 | 0.040457 | 0.010139
13 | 0.99691 | -0.058758 | 0 | 0
14 | 0.99295 | -0.1342 | 0 | 0
15 | 0.99842 | -0.029874 | 0.010051 | 0.002519
16 | 0.99236 | -0.14575 | 0.030208 | 0.0075708
17 | 0.99125 | -0.16676 | 0.020768 | 0.0052048
18 | 0.98834 | -0.22271 | 0.0079414 | 0.0019903
19 | 0.99037 | -0.18358 | 0 | 0
20 | 0.98899 | -0.2102 | 0.0056568 | 0.0014177
21 | 0.97479 | -0.48659 | 0 | 0
22 | 0.9744 | -0.49427 | 0.017303 | 0.0043366
23 | 0.97486 | -0.48526 | 0.053551 | 0.013421
24 | 0.98057 | -0.37328 | 0.049108 | 0.012308
25 | 0.97658 | -0.45135 | 0.04805 | 0.012043
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.023772 | -0.0059577 | 0.023772 | 0.0059578 | 4.2244e-09 | 2.5895e-09 | 0.035953 | 0.035953 | 0.035953 | 0.98386 | -0.30951 | 0.98386 | -0.3095 | 9.8772
1 | 0.011613 | 0.0029105 | -0.011613 | -0.0029105 | 7.3453e-09 | 3.8932e-09 | 0.017564 | 0.017564 | 0.017564 | 0.98386 | -0.30951 | 0.98386 | -0.30952 | 4.8252
2 | -0.037848 | -0.0094857 | 0.037852 | 0.0094881 | 3.7996e-06 | 2.3925e-06 | 0.057243 | 0.057243 | 0.057243 | 0.98386 | -0.3095 | 0.98396 | -0.3074 | 15.7261
3 | -0.054823 | -0.013741 | 0.054904 | 0.013793 | 8.0701e-05 | 5.125e-05 | 0.082908 | 0.082907 | 0.082908 | 0.98396 | -0.3074 | 0.98555 | -0.27655 | 22.7768
4 | 0.16936 | 0.042968 | -0.16898 | -0.042724 | 0.00038604 | 0.00024387 | 0.2559 | 0.2559 | 0.2559 | 0.98555 | -0.27655 | 0.98309 | -0.32406 | 17.5756
5 | -0.22427 | -0.05676 | 0.22483 | 0.05712 | 0.00056601 | 0.00035956 | 0.33881 | 0.33881 | 0.33881 | 0.98555 | -0.27655 | 0.98826 | -0.22411 | 23.2697
6 | 0.16898 | 0.042724 | -0.16858 | -0.04247 | 0.00039784 | 0.0002538 | 0.2559 | 0.2559 | 0.2559 | 0.98309 | -0.32406 | 0.98057 | -0.37328 | 35.1512
7 | -0.22483 | -0.05712 | 0.22485 | 0.057129 | 1.5167e-05 | 9.6348e-06 | 0.33881 | 0.33881 | 0.33881 | 0.98826 | -0.22411 | 0.98834 | -0.22271 | 23.2696
8 | -0.048097 | -0.012054 | 0.048105 | 0.012059 | 7.7097e-06 | 4.8816e-06 | 0.071582 | 0.071582 | 0.071582 | 0.99983 | -0.0033642 | 1 | 0 | 19.6655
9 | 0.43992 | 0.11244 | -0.43929 | -0.11204 | 0.00063467 | 0.00040536 | 0.65539 | 0.65539 | 0.65539 | 1 | 0 | 0.99842 | -0.029874 | 45.0129
10 | 0.37079 | 0.094399 | -0.37037 | -0.094135 | 0.00041357 | 0.00026394 | 0.55484 | 0.55484 | 0.55484 | 0.99534 | -0.088601 | 0.99413 | -0.11176 | 38.1072
11 | -0.41732 | -0.10606 | 0.41767 | 0.10628 | 0.00035001 | 0.00022351 | 0.6244 | 0.6244 | 0.6244 | 0.99534 | -0.088601 | 0.99625 | -0.0712 | 42.8847
12 | 0.33127 | 0.084334 | -0.33122 | -0.084308 | 4.0852e-05 | 2.6053e-05 | 0.49631 | 0.49631 | 0.49631 | 0.99413 | -0.11176 | 0.99399 | -0.11432 | 34.0869
13 | -0.42838 | -0.10897 | 0.42864 | 0.10913 | 0.00025701 | 0.00016414 | 0.64041 | 0.64041 | 0.64041 | 0.99625 | -0.0712 | 0.99691 | -0.058758 | 43.9841
14 | 0.29077 | 0.074168 | -0.29049 | -0.073991 | 0.00027885 | 0.00017765 | 0.43574 | 0.43574 | 0.43574 | 0.99399 | -0.11432 | 0.99295 | -0.1342 | 29.9273
15 | -0.42864 | -0.10913 | 0.42924 | 0.10952 | 0.00059795 | 0.00038188 | 0.64041 | 0.64041 | 0.64041 | 0.99691 | -0.058758 | 0.99842 | -0.029874 | 43.9841
16 | 0.030225 | 0.0075812 | -0.030208 | -0.0075708 | 1.6632e-05 | 1.0365e-05 | 0.045296 | 0.045296 | 0.045296 | 0.99295 | -0.1342 | 0.99236 | -0.14575 | 12.444
17 | 0.26026 | 0.066409 | -0.25986 | -0.066149 | 0.00040864 | 0.00026005 | 0.39045 | 0.39045 | 0.39045 | 0.99295 | -0.1342 | 0.99125 | -0.16676 | 26.8164
18 | 0.23909 | 0.060945 | -0.23889 | -0.060821 | 0.00019395 | 0.0001233 | 0.35927 | 0.35927 | 0.35927 | 0.99125 | -0.16676 | 0.99037 | -0.18358 | 24.6753
19 | -0.23279 | -0.05912 | 0.23293 | 0.059209 | 0.00014027 | 8.9151e-05 | 0.35076 | 0.35076 | 0.35076 | 0.98834 | -0.22271 | 0.98899 | -0.2102 | 24.0908
20 | 0.23889 | 0.060821 | -0.23859 | -0.060627 | 0.00030622 | 0.00019468 | 0.35927 | 0.35927 | 0.35927 | 0.99037 | -0.18358 | 0.98899 | -0.2102 | 24.6753
21 | 0.01731 | 0.0043404 | -0.017303 | -0.0043366 | 6.3312e-06 | 3.7507e-06 | 0.026424 | 0.026424 | 0.026424 | 0.97479 | -0.48659 | 0.9744 | -0.49427 | 7.2594
22 | -0.01731 | -0.0043404 | 0.017311 | 0.004341 | 1.0999e-06 | 6.5159e-07 | 0.026424 | 0.026424 | 0.026424 | 0.97479 | -0.48659 | 0.97486 | -0.48526 | 7.2593
23 | -0.070862 | -0.017762 | 0.070977 | 0.017835 | 0.00011466 | 7.3055e-05 | 0.10816 | 0.10816 | 0.10816 | 0.97486 | -0.48526 | 0.97658 | -0.45135 | 29.7156
24 | 0.11947 | 0.030162 | -0.11903 | -0.029878 | 0.00044505 | 0.00028438 | 0.18138 | 0.18138 | 0.18138 | 0.98057 | -0.37328 | 0.97658 | -0.45135 | 49.8294

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58118 | 0.14743

## res_load
| p_mw | q_mvar
0 | 0.012159 | 0.0030473
1 | 0.014077 | 0.003528
2 | 0.011613 | 0.0029105
3 | 0.016971 | 0.0042533
4 | 0.048097 | 0.012054
5 | 0.091504 | 0.022933
6 | 0.04653 | 0.011661
7 | 0.039108 | 0.0098013
8 | 0.010718 | 0.0026861
9 | 0.040457 | 0.010139
10 | 0.010051 | 0.002519
11 | 0.030208 | 0.0075708
12 | 0.020768 | 0.0052048
13 | 0.0079414 | 0.0019903
14 | 0.0056568 | 0.0014177
15 | 0.017303 | 0.0043366
16 | 0.053551 | 0.013421
17 | 0.049108 | 0.012308
18 | 0.04805 | 0.012043

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1