## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-28_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-28_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_230-28_0_3_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_230-28_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_230-28_0_3_node_48 | 0.4 | n |  | TRUE
5 | bus_LV_230-28_0_3_node_45 | 0.4 | n |  | TRUE
6 | bus_LV_230-28_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_230-28_0_3_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_230-28_0_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_230-28_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_230-28_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_230-28_0_3_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_230-28_0_3_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_230-28_0_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_230-28_0_3_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_230-28_0_3_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_230-28_0_3_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_230-28_0_3_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_230-28_0_3_node_46 | 0.4 | n |  | TRUE
19 | bus_LV_230-28_0_3_node_44 | 0.4 | n |  | TRUE
20 | bus_LV_230-28_0_3_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_230-28_0_3_node_26 | 0.4 | n |  | TRUE
22 | bus_MV_510_0_node_91 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-28_0_3_load_0 | 0 | 0.01539 | 0.003857 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-28_0_3_load_48 | 4 | 0.0063962 | 0.001603 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-28_0_3_load_24 | 8 | 0.067606 | 0.016944 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-28_0_3_load_25 | 11 | 0.01599 | 0.0040076 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-28_0_3_load_39 | 12 | 0.014712 | 0.0036871 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-28_0_3_load_41 | 14 | 0.014576 | 0.0036531 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-28_0_3_load_27 | 15 | 0.0095575 | 0.0023953 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-28_0_3_load_42 | 16 | 0.036763 | 0.0092138 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-28_0_3_load_43 | 17 | 0.016107 | 0.0040367 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-28_0_3_load_46 | 18 | 0.0061764 | 0.0015479 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-28_0_3_load_44 | 19 | 0.030958 | 0.0077588 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-28_0_3_load_40 | 20 | 0.013363 | 0.0033491 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-28_0_3_load_26 | 21 | 0.011621 | 0.0029126 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-28_0_3_line_0 |  | 0 | 1 | 0.010772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-28_0_3_line_1 |  | 1 | 2 | 0.05676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-28_0_3_line_2 |  | 2 | 12 | 0.022932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-28_0_3_line_3 |  | 2 | 3 | 0.078844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-28_0_3_line_4 |  | 3 | 4 | 0.000863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-28_0_3_line_5 |  | 3 | 5 | 0.021511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-28_0_3_line_6 |  | 5 | 18 | 0.0015014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-28_0_3_line_7 |  | 5 | 19 | 0.032081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-28_0_3_line_8 |  | 6 | 7 | 0.01176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-28_0_3_line_9 |  | 6 | 8 | 0.022396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-28_0_3_line_10 |  | 7 | 17 | 0.024207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-28_0_3_line_11 |  | 8 | 11 | 0.0042707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-28_0_3_line_12 |  | 9 | 10 | 0.031971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_230-28_0_3_line_13 |  | 9 | 11 | 0.030049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-28_0_3_line_14 |  | 10 | 15 | 0.016908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-28_0_3_line_15 |  | 10 | 16 | 0.016341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-28_0_3_line_16 |  | 10 | 13 | 0.094572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-28_0_3_line_17 |  | 12 | 20 | 0.019061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-28_0_3_line_18 |  | 13 | 14 | 0.015679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-28_0_3_line_19 |  | 14 | 20 | 0.018972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-28_0_3_line_20 |  | 15 | 21 | 0.0065607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-28_0_3_trafo_8 | 0.63 MVA 20/0.4 kV | 22 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2697005.3094 | 1262009.8393 | 2697000.3989 | 1262019.4269
1 | 2697005.3094 | 1262009.8393 | 2697015.204 | 1261990.5303 | 2697017.0105 | 1261986.9793 | 2697021.5901 | 1261983.4293 | 2697024.4661 | 1261983.1317 | 2697028.793 | 1261984.4149 | 2697033.3948 | 1261987.782 | 2697037.0347 | 1261993.7354 | 2697039.6739 | 1261998.2157
2 | 2697039.6739 | 1261998.2157 | 2697044.8134 | 1262006.4623 | 2697051.6793 | 1262017.7535
3 | 2697039.6739 | 1261998.2157 | 2697037.0347 | 1261993.7354 | 2697042.798 | 1261990.6052 | 2697046.6149 | 1261988.5328 | 2697053.8575 | 1262001.3287 | 2697054.9412 | 1262003.248 | 2697073.2821 | 1262034.0296 | 2697074.6496 | 1262033.3515 | 2697075.6526 | 1262032.8453 | 2697079.9452 | 1262030.2581 | 2697080.8806 | 1262029.7397 | 2697082.0055 | 1262029.1465
4 | 2697081.5276 | 1262028.427 | 2697082.0055 | 1262029.1465
5 | 2697093.3833 | 1262040.209 | 2697093.4107 | 1262036.2506 | 2697091.9533 | 1262031.3894 | 2697089.8049 | 1262028.6853 | 2697088.5542 | 1262027.297 | 2697086.9276 | 1262026.7698 | 2697084.0505 | 1262028.057 | 2697083.0324 | 1262028.5629 | 2697082.0055 | 1262029.1465
6 | 2697093.3833 | 1262040.209 | 2697092.2131 | 1262041.1496
7 | 2697093.3833 | 1262040.209 | 2697101.0731 | 1262034.0301 | 2697123.2313 | 1262032.4259
8 | 2697048.7723 | 1262154.5367 | 2697054.8385 | 1262164.6223
9 | 2697054.8385 | 1262164.6223 | 2697074.1111 | 1262153.2145
10 | 2697048.7723 | 1262154.5367 | 2697042.7094 | 1262154.3482 | 2697027.0952 | 1262163.5844
11 | 2697074.1111 | 1262153.2145 | 2697077.7862 | 1262151.0391
12 | 2697103.6448 | 1262135.733 | 2697104.8907 | 1262137.8663 | 2697119.0409 | 1262129.6919 | 2697124.541 | 1262126.5241 | 2697128.047 | 1262132.3642
13 | 2697103.6448 | 1262135.733 | 2697077.7862 | 1262151.0391
14 | 2697128.047 | 1262132.3642 | 2697132.0372 | 1262128.4487 | 2697136.2554 | 1262128.5514 | 2697136.4374 | 1262121.4556
15 | 2697128.047 | 1262132.3642 | 2697136.452 | 1262146.3782
16 | 2697079.5852 | 1262063.646 | 2697081.0742 | 1262067.0399 | 2697093.2492 | 1262086.9115 | 2697095.5765 | 1262091.5646 | 2697095.5431 | 1262093.599 | 2697095.4635 | 1262098.4461 | 2697098.8057 | 1262105.5401 | 2697098.7018 | 1262108.1961 | 2697101.1198 | 1262108.2469 | 2697103.3755 | 1262108.5509 | 2697106.6624 | 1262109.8392 | 2697109.0262 | 1262111.8129 | 2697117.4273 | 1262126.0847 | 2697117.8647 | 1262126.9815 | 2697119.0409 | 1262129.6919 | 2697124.541 | 1262126.5241 | 2697128.047 | 1262132.3642
17 | 2697051.6793 | 1262017.7535 | 2697061.5824 | 1262034.0396
18 | 2697079.5852 | 1262063.646 | 2697071.4392 | 1262050.2496
19 | 2697061.5824 | 1262034.0396 | 2697071.4392 | 1262050.2496
20 | 2697136.4374 | 1262121.4556 | 2697136.6056 | 1262114.8971

## bus_geodata
| x | y | coords
0 | 2697000.3989 | 1262019.4269
1 | 2697005.3094 | 1262009.8393
2 | 2697039.6739 | 1261998.2157
3 | 2697082.0056 | 1262029.1465
4 | 2697081.5276 | 1262028.427
5 | 2697093.3833 | 1262040.209
6 | 2697054.8385 | 1262164.6223
7 | 2697048.7723 | 1262154.5367
8 | 2697074.1111 | 1262153.2145
9 | 2697103.6448 | 1262135.733
10 | 2697128.047 | 1262132.3642
11 | 2697077.7862 | 1262151.0391
12 | 2697051.6793 | 1262017.7535
13 | 2697079.5852 | 1262063.646
14 | 2697071.4392 | 1262050.2496
15 | 2697136.4374 | 1262121.4556
16 | 2697136.452 | 1262146.3782
17 | 2697027.0952 | 1262163.5844
18 | 2697092.2131 | 1262041.1496
19 | 2697123.2313 | 1262032.4259
20 | 2697061.5824 | 1262034.0396
21 | 2697136.6056 | 1262114.8971
22 | 2697095.4811 | 1262121.6875

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98228 | -0.34058 | 0.01539 | 0.003857
1 | 0.98243 | -0.33759 | 0 | 0
2 | 0.98324 | -0.32182 | 0 | 0
3 | 0.98006 | -0.38391 | 0 | 0
4 | 0.98005 | -0.38401 | 0.0063962 | 0.001603
5 | 0.97932 | -0.39841 | 0 | 0
6 | 0.99662 | -0.064958 | 0 | 0
7 | 0.99645 | -0.068282 | 0 | 0
8 | 0.99695 | -0.058629 | 0.067606 | 0.016944
9 | 1 | 0 | -0.26298 | -0.066312
10 | 0.99766 | -0.044552 | 0 | 0
11 | 0.99727 | -0.052362 | 0.01599 | 0.0040076
12 | 0.98449 | -0.29749 | 0.014712 | 0.0036871
13 | 0.98878 | -0.21429 | 0 | 0
14 | 0.98731 | -0.24273 | 0.014576 | 0.0036531
15 | 0.99733 | -0.050824 | 0.0095575 | 0.0023953
16 | 0.99711 | -0.055078 | 0.036763 | 0.0092138
17 | 0.99609 | -0.075129 | 0.016107 | 0.0040367
18 | 0.97931 | -0.39858 | 0.0061764 | 0.0015479
19 | 0.97839 | -0.41648 | 0.030958 | 0.0077588
20 | 0.98578 | -0.27228 | 0.013363 | 0.0033491
21 | 0.99726 | -0.052161 | 0.011621 | 0.0029126
22 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01539 | -0.003857 | 0.015392 | 0.0038583 | 2.1955e-06 | 1.2687e-06 | 0.023313 | 0.023313 | 0.023313 | 0.98228 | -0.34058 | 0.98243 | -0.33759 | 6.4047
1 | -0.015392 | -0.0038583 | 0.015403 | 0.003865 | 1.1568e-05 | 6.6844e-06 | 0.023313 | 0.023313 | 0.023313 | 0.98243 | -0.33759 | 0.98324 | -0.32182 | 6.4047
2 | -0.059116 | -0.014889 | 0.059185 | 0.014933 | 6.8871e-05 | 4.3786e-05 | 0.089491 | 0.089491 | 0.089491 | 0.98324 | -0.32182 | 0.98449 | -0.29749 | 24.5856
3 | 0.043712 | 0.011025 | -0.043583 | -0.010943 | 0.00012949 | 8.1877e-05 | 0.066179 | 0.066179 | 0.066179 | 0.98324 | -0.32182 | 0.98006 | -0.38391 | 18.181
4 | 0.0063962 | 0.001603 | -0.0063962 | -0.001603 | 3.0521e-08 | 8.6588e-09 | 0.0097113 | 0.0097113 | 0.0097113 | 0.98006 | -0.38391 | 0.98005 | -0.38401 | 2.6679
5 | 0.037187 | 0.0093396 | -0.037161 | -0.0093234 | 2.5721e-05 | 1.6191e-05 | 0.056468 | 0.056468 | 0.056468 | 0.98006 | -0.38391 | 0.97932 | -0.39841 | 15.5131
6 | 0.0061764 | 0.001548 | -0.0061764 | -0.0015479 | 4.9588e-08 | 1.2845e-08 | 0.0093848 | 0.0093848 | 0.0093848 | 0.97932 | -0.39841 | 0.97931 | -0.39858 | 2.5782
7 | 0.030985 | 0.0077754 | -0.030958 | -0.0077588 | 2.6669e-05 | 1.6665e-05 | 0.047083 | 0.047083 | 0.047083 | 0.97932 | -0.39841 | 0.97839 | -0.41648 | 12.9349
8 | 0.016114 | 0.0040412 | -0.016112 | -0.0040397 | 2.553e-06 | 1.4807e-06 | 0.024061 | 0.024061 | 0.024061 | 0.99662 | -0.064958 | 0.99645 | -0.068282 | 6.6101
9 | -0.016114 | -0.0040412 | 0.016119 | 0.004044 | 4.8619e-06 | 2.8197e-06 | 0.024061 | 0.024061 | 0.024061 | 0.99662 | -0.064958 | 0.99695 | -0.058629 | 6.6101
10 | 0.016112 | 0.0040397 | -0.016107 | -0.0040367 | 5.2553e-06 | 3.0482e-06 | 0.024061 | 0.024061 | 0.024061 | 0.99645 | -0.068282 | 0.99609 | -0.075129 | 6.6101
11 | -0.083725 | -0.020988 | 0.08375 | 0.021004 | 2.501e-05 | 1.5951e-05 | 0.12497 | 0.12497 | 0.12497 | 0.99695 | -0.058629 | 0.99727 | -0.052362 | 34.3315
12 | 0.16134 | 0.041142 | -0.161 | -0.040921 | 0.00034623 | 0.00022075 | 0.24033 | 0.24033 | 0.24033 | 1 | 0 | 0.99766 | -0.044552 | 33.0122
13 | 0.09999 | 0.02517 | -0.09974 | -0.025011 | 0.00024958 | 0.00015934 | 0.14883 | 0.14883 | 0.14883 | 1 | 0 | 0.99727 | -0.052362 | 40.8861
14 | 0.021186 | 0.0053122 | -0.02118 | -0.0053083 | 6.3314e-06 | 3.8314e-06 | 0.0316 | 0.0316 | 0.0316 | 0.99766 | -0.044552 | 0.99733 | -0.050824 | 8.6813
15 | 0.036782 | 0.0092254 | -0.036763 | -0.0092138 | 1.8445e-05 | 1.1592e-05 | 0.054863 | 0.054863 | 0.054863 | 0.99766 | -0.044552 | 0.99711 | -0.055078 | 15.0723
16 | 0.10303 | 0.026383 | -0.10219 | -0.025847 | 0.00083962 | 0.00053614 | 0.15387 | 0.15387 | 0.15387 | 0.99766 | -0.044552 | 0.98878 | -0.21429 | 42.2711
17 | -0.073896 | -0.01862 | 0.073986 | 0.018677 | 8.9225e-05 | 5.6861e-05 | 0.11173 | 0.11173 | 0.11173 | 0.98449 | -0.29749 | 0.98578 | -0.27228 | 30.6944
18 | 0.10219 | 0.025847 | -0.10205 | -0.025758 | 0.0001392 | 8.8886e-05 | 0.15387 | 0.15387 | 0.15387 | 0.98878 | -0.21429 | 0.98731 | -0.24273 | 42.2711
19 | 0.087472 | 0.022105 | -0.087349 | -0.022026 | 0.00012377 | 7.8971e-05 | 0.1319 | 0.1319 | 0.1319 | 0.98731 | -0.24273 | 0.98578 | -0.27228 | 36.2359
20 | 0.011622 | 0.002913 | -0.011621 | -0.0029126 | 7.3976e-07 | 3.8784e-07 | 0.01734 | 0.01734 | 0.01734 | 0.99733 | -0.050824 | 0.99726 | -0.052161 | 4.7638

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26298 | 0.066312

## res_load
| p_mw | q_mvar
0 | 0.01539 | 0.003857
1 | 0.0063962 | 0.001603
2 | 0.067606 | 0.016944
3 | 0.01599 | 0.0040076
4 | 0.014712 | 0.0036871
5 | 0.014576 | 0.0036531
6 | 0.0095575 | 0.0023953
7 | 0.036763 | 0.0092138
8 | 0.016107 | 0.0040367
9 | 0.0061764 | 0.0015479
10 | 0.030958 | 0.0077588
11 | 0.013363 | 0.0033491
12 | 0.011621 | 0.0029126

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1