## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-33_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-33_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-33_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-33_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-33_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-33_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_230-33_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_230-33_0_3_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_230-33_0_3_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_230-33_0_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_230-33_0_3_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_230-33_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_230-33_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_230-33_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_230-33_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_230-33_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_230-33_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_230-33_0_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_230-33_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_230-33_0_3_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_230-33_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_230-33_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_MV_512_0_node_38 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-33_0_3_load_0 | 0 | 0.077337 | 0.019383 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-33_0_3_load_1 | 1 | 0.082445 | 0.020663 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-33_0_3_load_26 | 8 | 0.071863 | 0.018011 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-33_0_3_load_25 | 9 | 0.041579 | 0.010421 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-33_0_3_load_24 | 10 | 0.075179 | 0.018842 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-33_0_3_load_14 | 12 | 0.0092479 | 0.0023177 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-33_0_3_load_10 | 13 | 0.0081616 | 0.0020455 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-33_0_3_load_21 | 14 | 0.041992 | 0.010524 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-33_0_3_load_11 | 15 | 0.0031746 | 0.00079562 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-33_0_3_load_13 | 16 | 0.003176 | 0.00079598 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-33_0_3_load_20 | 19 | 0.03804 | 0.0095338 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-33_0_3_load_23 | 21 | 0.0082774 | 0.0020745 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-33_0_3_line_0 |  | 0 | 1 | 0.025935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-33_0_3_line_1 |  | 0 | 2 | 0.016684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_230-33_0_3_line_2 |  | 1 | 3 | 0.032797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-33_0_3_line_3 |  | 2 | 4 | 0.018575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_230-33_0_3_line_4 |  | 3 | 5 | 0.054664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-33_0_3_line_5 |  | 4 | 6 | 0.021569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-33_0_3_line_6 |  | 4 | 7 | 0.069947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-33_0_3_line_7 |  | 4 | 8 | 0.014911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-33_0_3_line_8 |  | 5 | 9 | 0.040015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-33_0_3_line_9 |  | 6 | 10 | 0.029642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-33_0_3_line_10 |  | 7 | 14 | 0.011006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-33_0_3_line_11 |  | 7 | 11 | 0.079111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-33_0_3_line_12 |  | 11 | 12 | 0.043039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-33_0_3_line_13 |  | 11 | 13 | 0.028795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-33_0_3_line_14 |  | 12 | 17 | 0.0017003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-33_0_3_line_15 |  | 13 | 15 | 0.025895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-33_0_3_line_16 |  | 14 | 20 | 0.0026814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-33_0_3_line_17 |  | 15 | 16 | 0.0084868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-33_0_3_line_18 |  | 17 | 18 | 0.017899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-33_0_3_line_19 |  | 18 | 19 | 0.047484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-33_0_3_line_20 |  | 20 | 21 | 0.005902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-33_0_3_trafo_0 | 0.63 MVA 20/0.4 kV | 22 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2696954.955 | 1261547.5213 | 2696980.7561 | 1261544.8932
1 | 2696940.6618 | 1261553.097 | 2696941.9483 | 1261550.0155 | 2696946.1646 | 1261548.4167 | 2696954.955 | 1261547.5213
2 | 2697004.1664 | 1261554.6169 | 2697005.1299 | 1261551.9305 | 2697005.3988 | 1261549.3217 | 2697002.9735 | 1261545.5677 | 2696997.881 | 1261543.1489 | 2696980.7561 | 1261544.8932
3 | 2696922.1088 | 1261553.9603 | 2696930.9911 | 1261553.6723 | 2696940.6618 | 1261553.097
4 | 2697004.1664 | 1261554.6169 | 2697010.2484 | 1261559.187 | 2697007.5988 | 1261563.5916 | 2697012.1718 | 1261568.7263 | 2697015.9086 | 1261575.2262 | 2697019.3477 | 1261583.7895 | 2697022.0576 | 1261592.6968 | 2697013.5392 | 1261595.615
5 | 2696922.1088 | 1261553.9603 | 2696930.9911 | 1261553.6723 | 2696931.3941 | 1261559.884 | 2696931.9141 | 1261566.3199
6 | 2696922.1088 | 1261553.9603 | 2696928.3159 | 1261532.5224 | 2696931.1656 | 1261522.3497 | 2696933.8995 | 1261512.3419 | 2696946.7652 | 1261510.8738 | 2696960.3747 | 1261512.765
7 | 2696922.1088 | 1261553.9603 | 2696912.7359 | 1261554.296 | 2696907.2047 | 1261554.1791
8 | 2697013.5392 | 1261595.615 | 2696997.943 | 1261601.831 | 2696977.9445 | 1261613.6413
9 | 2696931.9141 | 1261566.3199 | 2696933.9715 | 1261565.3973 | 2696961.2197 | 1261562.646
10 | 2696960.3747 | 1261512.765 | 2696962.6722 | 1261502.001
11 | 2696948.1185 | 1261461.9006 | 2696945.758 | 1261472.1147 | 2696933.8995 | 1261512.3419 | 2696946.7652 | 1261510.8738 | 2696960.3747 | 1261512.765
12 | 2696948.1185 | 1261461.9006 | 2696990.7954 | 1261456.3319
13 | 2696948.1185 | 1261461.9006 | 2696924.6554 | 1261463.4507 | 2696919.3811 | 1261463.7127
14 | 2696992.4814 | 1261456.1119 | 2696990.7954 | 1261456.3319
15 | 2696919.3811 | 1261463.7127 | 2696893.5179 | 1261464.997
16 | 2696963.2319 | 1261499.3787 | 2696962.6722 | 1261502.001
17 | 2696893.5179 | 1261464.997 | 2696885.0415 | 1261465.4179
18 | 2697010.2159 | 1261453.7118 | 2696999.4325 | 1261455.025 | 2696992.4814 | 1261456.1119
19 | 2697010.2159 | 1261453.7118 | 2697014.2172 | 1261478.075 | 2697014.8769 | 1261484.7135 | 2697014.5156 | 1261488.822 | 2697012.5709 | 1261493.8942 | 2697009.2823 | 1261499.5782
20 | 2696964.457 | 1261493.6052 | 2696963.2319 | 1261499.3787

## bus_geodata
| x | y | coords
0 | 2696954.955 | 1261547.5213
1 | 2696980.7561 | 1261544.8932
2 | 2696940.6618 | 1261553.097
3 | 2697004.1664 | 1261554.6169
4 | 2696922.1088 | 1261553.9603
5 | 2697013.5392 | 1261595.615
6 | 2696931.9141 | 1261566.3199
7 | 2696960.3747 | 1261512.765
8 | 2696907.2047 | 1261554.1791
9 | 2696977.9445 | 1261613.6413
10 | 2696961.2197 | 1261562.646
11 | 2696948.1185 | 1261461.9006
12 | 2696990.7954 | 1261456.3319
13 | 2696919.3811 | 1261463.7127
14 | 2696962.6722 | 1261502.001
15 | 2696893.5179 | 1261464.997
16 | 2696885.0415 | 1261465.4179
17 | 2696992.4814 | 1261456.1119
18 | 2697010.2159 | 1261453.7118
19 | 2697009.2823 | 1261499.5782
20 | 2696963.2319 | 1261499.3787
21 | 2696964.457 | 1261493.6052
22 | 2696940.6618 | 1261553.097

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.38783 | -0.097963
1 | 0.99707 | -0.056229 | 0.082445 | 0.020663
2 | 0.99802 | -0.037752 | 0 | 0
3 | 0.99582 | -0.080169 | 0 | 0
4 | 0.99581 | -0.079958 | 0 | 0
5 | 0.99375 | -0.1202 | 0 | 0
6 | 0.99433 | -0.1085 | 0 | 0
7 | 0.98858 | -0.21876 | 0 | 0
8 | 0.99483 | -0.098811 | 0.071863 | 0.018011
9 | 0.99223 | -0.14961 | 0.041579 | 0.010421
10 | 0.99229 | -0.14787 | 0.075179 | 0.018842
11 | 0.98406 | -0.30636 | 0 | 0
12 | 0.98218 | -0.34306 | 0.0092479 | 0.0023177
13 | 0.98368 | -0.31389 | 0.0081616 | 0.0020455
14 | 0.98808 | -0.22863 | 0.041992 | 0.010524
15 | 0.98353 | -0.31685 | 0.0031746 | 0.00079562
16 | 0.9835 | -0.31733 | 0.003176 | 0.00079598
17 | 0.98212 | -0.34423 | 0 | 0
18 | 0.98149 | -0.35654 | 0 | 0
19 | 0.97982 | -0.38928 | 0.03804 | 0.0095338
20 | 0.98806 | -0.22903 | 0 | 0
21 | 0.98801 | -0.2299 | 0.0082774 | 0.0020745
22 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12454 | 0.031414 | -0.12421 | -0.031201 | 0.00033428 | 0.0002136 | 0.18539 | 0.18539 | 0.18539 | 1 | 0 | 0.99707 | -0.056229 | 50.9325
1 | 0.26164 | 0.066549 | -0.26116 | -0.066245 | 0.000475 | 0.00030356 | 0.38966 | 0.38966 | 0.38966 | 1 | 0 | 0.99802 | -0.037752 | 53.5253
2 | 0.041765 | 0.010538 | -0.041717 | -0.010508 | 4.7819e-05 | 3.0177e-05 | 0.062354 | 0.062355 | 0.062355 | 0.99707 | -0.056229 | 0.99582 | -0.080169 | 17.1304
3 | 0.26116 | 0.066245 | -0.26063 | -0.065907 | 0.00052882 | 0.00033796 | 0.38966 | 0.38966 | 0.38966 | 0.99802 | -0.037752 | 0.99581 | -0.079958 | 53.5253
4 | 0.041717 | 0.010508 | -0.041637 | -0.010458 | 7.9703e-05 | 5.03e-05 | 0.062355 | 0.062355 | 0.062355 | 0.99582 | -0.080169 | 0.99375 | -0.1202 | 17.1305
5 | 0.075423 | 0.018997 | -0.075321 | -0.018932 | 0.0001028 | 6.5511e-05 | 0.11274 | 0.11274 | 0.11274 | 0.99581 | -0.079958 | 0.99433 | -0.1085 | 30.9717
6 | 0.11328 | 0.028858 | -0.11253 | -0.028377 | 0.00075305 | 0.00048105 | 0.16944 | 0.16944 | 0.16944 | 0.99581 | -0.079958 | 0.98858 | -0.21876 | 46.5492
7 | 0.071928 | 0.018052 | -0.071863 | -0.018011 | 6.4607e-05 | 4.1155e-05 | 0.10749 | 0.10749 | 0.10749 | 0.99581 | -0.079958 | 0.99483 | -0.098811 | 29.53
8 | 0.041637 | 0.010458 | -0.041579 | -0.010421 | 5.8344e-05 | 3.6822e-05 | 0.062355 | 0.062355 | 0.062355 | 0.99375 | -0.1202 | 0.99223 | -0.14961 | 17.1305
9 | 0.075321 | 0.018932 | -0.075179 | -0.018842 | 0.00014127 | 9.0032e-05 | 0.11274 | 0.11274 | 0.11274 | 0.99433 | -0.1085 | 0.99229 | -0.14787 | 30.9717
10 | 0.050293 | 0.012614 | -0.05027 | -0.012599 | 2.3655e-05 | 1.4998e-05 | 0.075705 | 0.075705 | 0.075705 | 0.98858 | -0.21876 | 0.98808 | -0.22863 | 20.7981
11 | 0.062234 | 0.015763 | -0.061974 | -0.015597 | 0.00026066 | 0.00016581 | 0.093734 | 0.093735 | 0.093735 | 0.98858 | -0.21876 | 0.98406 | -0.30636 | 25.7513
12 | 0.047455 | 0.011957 | -0.047372 | -0.011904 | 8.3159e-05 | 5.2676e-05 | 0.071781 | 0.071781 | 0.071781 | 0.98406 | -0.30636 | 0.98218 | -0.34306 | 19.72
13 | 0.014518 | 0.0036402 | -0.014513 | -0.0036373 | 5.2045e-06 | 2.9652e-06 | 0.021954 | 0.021954 | 0.021954 | 0.98406 | -0.30636 | 0.98368 | -0.31389 | 6.0313
14 | 0.038124 | 0.0095867 | -0.038122 | -0.0095854 | 2.1279e-06 | 1.3404e-06 | 0.05777 | 0.05777 | 0.05777 | 0.98218 | -0.34306 | 0.98212 | -0.34423 | 15.871
15 | 0.0063515 | 0.0015918 | -0.0063506 | -0.0015915 | 8.9643e-07 | 2.4504e-07 | 0.009608 | 0.0096081 | 0.0096081 | 0.98368 | -0.31389 | 0.98353 | -0.31685 | 2.6396
16 | 0.0082779 | 0.0020747 | -0.0082777 | -0.0020747 | 1.5627e-07 | 6.5668e-08 | 0.012466 | 0.012466 | 0.012466 | 0.98808 | -0.22863 | 0.98806 | -0.22903 | 3.4248
17 | 0.0031761 | 0.00079592 | -0.003176 | -0.00079598 | 7.3485e-08 | -6.067e-08 | 0.0048052 | 0.0048052 | 0.0048052 | 0.98353 | -0.31685 | 0.9835 | -0.31733 | 1.3201
18 | 0.038122 | 0.0095854 | -0.0381 | -0.0095713 | 2.2401e-05 | 1.411e-05 | 0.05777 | 0.05777 | 0.05777 | 0.98212 | -0.34423 | 0.98149 | -0.35654 | 15.871
19 | 0.0381 | 0.0095713 | -0.03804 | -0.0095338 | 5.9428e-05 | 3.7435e-05 | 0.05777 | 0.057771 | 0.057771 | 0.98149 | -0.35654 | 0.97982 | -0.38928 | 15.8711
20 | 0.0082777 | 0.0020747 | -0.0082774 | -0.0020745 | 3.4396e-07 | 1.4455e-07 | 0.012466 | 0.012466 | 0.012466 | 0.98806 | -0.22903 | 0.98801 | -0.2299 | 3.4248

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46517 | 0.11735

## res_load
| p_mw | q_mvar
0 | 0.077337 | 0.019383
1 | 0.082445 | 0.020663
2 | 0.071863 | 0.018011
3 | 0.041579 | 0.010421
4 | 0.075179 | 0.018842
5 | 0.0092479 | 0.0023177
6 | 0.0081616 | 0.0020455
7 | 0.041992 | 0.010524
8 | 0.0031746 | 0.00079562
9 | 0.003176 | 0.00079598
10 | 0.03804 | 0.0095338
11 | 0.0082774 | 0.0020745

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1