## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-41_1_2_node_20 | 0.4 | n |  | TRUE
1 | bus_LV_230-41_1_2_node_27 | 0.4 | n |  | TRUE
2 | bus_LV_230-41_1_2_node_58 | 0.4 | n |  | TRUE
3 | bus_LV_230-41_1_2_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_230-41_1_2_node_44 | 0.4 | n |  | TRUE
5 | bus_LV_230-41_1_2_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_230-41_1_2_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_230-41_1_2_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_230-41_1_2_node_63 | 0.4 | n |  | TRUE
9 | bus_LV_230-41_1_2_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_230-41_1_2_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_230-41_1_2_node_64 | 0.4 | n |  | TRUE
12 | bus_LV_230-41_1_2_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_230-41_1_2_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_230-41_1_2_node_66 | 0.4 | n |  | TRUE
15 | bus_LV_230-41_1_2_node_42 | 0.4 | n |  | TRUE
16 | bus_LV_230-41_1_2_node_59 | 0.4 | n |  | TRUE
17 | bus_LV_230-41_1_2_node_61 | 0.4 | n |  | TRUE
18 | bus_LV_230-41_1_2_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_230-41_1_2_node_65 | 0.4 | n |  | TRUE
20 | bus_MV_512_0_node_139 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-41_1_2_load_58 | 2 | 0.015194 | 0.003808 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-41_1_2_load_44 | 4 | 0.0005845 | 0.00014649 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-41_1_2_load_41 | 5 | 0.00054268 | 0.00013601 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-41_1_2_load_63 | 8 | 0.0068004 | 0.0017043 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-41_1_2_load_43 | 12 | 0.00029774 | 7.462e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-41_1_2_load_60 | 13 | 0.0097827 | 0.0024518 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-41_1_2_load_66 | 14 | 0.0078529 | 0.0019681 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-41_1_2_load_42 | 15 | 0.00029768 | 7.4606e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-41_1_2_load_59 | 16 | 0.022805 | 0.0057154 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-41_1_2_load_61 | 17 | 0.0033947 | 0.0008508 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-41_1_2_load_65 | 19 | 0.025956 | 0.0065051 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-41_1_2_line_0 |  | 0 | 1 | 0.94804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_230-41_1_2_line_1 |  | 0 | 2 | 0.013784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-41_1_2_line_2 |  | 1 | 13 | 0.031725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-41_1_2_line_3 |  | 1 | 14 | 0.15615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-41_1_2_line_4 |  | 1 | 7 | 0.035744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_230-41_1_2_line_5 |  | 2 | 16 | 0.013616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-41_1_2_line_6 |  | 3 | 4 | 0.023504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-41_1_2_line_7 |  | 3 | 5 | 0.015351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-41_1_2_line_8 |  | 5 | 15 | 0.0075515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-41_1_2_line_9 |  | 6 | 7 | 0.050018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_230-41_1_2_line_10 |  | 6 | 8 | 0.043745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_230-41_1_2_line_11 |  | 8 | 11 | 0.040396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_230-41_1_2_line_12 |  | 9 | 10 | 0.035754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-41_1_2_line_13 |  | 9 | 11 | 0.028696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-41_1_2_line_14 |  | 10 | 12 | 0.027058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-41_1_2_line_15 |  | 11 | 18 | 0.040173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_230-41_1_2_line_16 |  | 12 | 15 | 0.0062388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-41_1_2_line_17 |  | 17 | 18 | 0.036535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_230-41_1_2_line_18 |  | 18 | 19 | 0.028644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-41_1_2_trafo_61 | 0.63 MVA 20/0.4 kV | 20 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46
0 | 2696189.8128 | 1261452.8491 | 2696183.053 | 1261459.3222 | 2696197.6356 | 1261473.682 | 2696235.0914 | 1261509.7315 | 2696266.5112 | 1261539.7114 | 2696287.3106 | 1261560.0886 | 2696299.1307 | 1261570.5117 | 2696301.3408 | 1261572.238 | 2696308.3938 | 1261577.3681 | 2696319.0211 | 1261583.7574 | 2696321.1656 | 1261584.8821 | 2696331.8781 | 1261590.6612 | 2696348.573 | 1261597.9056 | 2696363.9452 | 1261601.2253 | 2696438.7707 | 1261617.3799 | 2696441.5268 | 1261617.9698 | 2696460.8424 | 1261622.0769 | 2696494.652 | 1261629.2785 | 2696503.2583 | 1261631.1093 | 2696514.5456 | 1261633.5176 | 2696516.7536 | 1261633.9873 | 2696519.771 | 1261619.4914 | 2696522.1342 | 1261609.533 | 2696534.9059 | 1261555.6532 | 2696543.7037 | 1261518.5445 | 2696546.1651 | 1261508.1095 | 2696547.1691 | 1261503.8558 | 2696555.4112 | 1261471.7086 | 2696555.7391 | 1261468.2445 | 2696555.5387 | 1261465.2833 | 2696553.7598 | 1261460.695 | 2696550.3135 | 1261455.7569 | 2696546.7018 | 1261451.7169 | 2696472.5168 | 1261380.4935 | 2696457.9956 | 1261366.5565 | 2696452.1911 | 1261361.5689 | 2696441.5895 | 1261352.6667 | 2696429.5124 | 1261338.5806 | 2696414.1376 | 1261317.8244 | 2696393.6761 | 1261289.1788 | 2696381.8573 | 1261272.6396 | 2696352.9617 | 1261293.964 | 2696342.0433 | 1261279.0519 | 2696333.8886 | 1261285.0795 | 2696321.5078 | 1261294.2298 | 2696313.437 | 1261300.2032 | 2696298.6897 | 1261279.7577
1 | 2696189.8128 | 1261452.8491 | 2696192.65 | 1261449.3924 | 2696198.9488 | 1261442.5337
2 | 2696298.6897 | 1261279.7577 | 2696273.6199 | 1261299.1996
3 | 2696298.6897 | 1261279.7577 | 2696426.7615 | 1261369.0827
4 | 2696298.6897 | 1261279.7577 | 2696277.774 | 1261250.7272
5 | 2696198.9488 | 1261442.5337 | 2696198.9488 | 1261442.5337 | 2696190.8682 | 1261431.5746
6 | 2696186.9707 | 1261229.6554 | 2696171.9274 | 1261211.5965
7 | 2696186.9707 | 1261229.6554 | 2696179.9554 | 1261235.1458 | 2696174.8364 | 1261239.0572
8 | 2696168.8361 | 1261243.6421 | 2696174.8364 | 1261239.0572
9 | 2696246.2615 | 1261223.5702 | 2696254.175 | 1261218.0056 | 2696263.2254 | 1261230.563 | 2696266.3797 | 1261234.9401 | 2696275.9019 | 1261248.139 | 2696277.774 | 1261250.7272
10 | 2696246.2615 | 1261223.5702 | 2696235.1314 | 1261228.1151 | 2696209.9851 | 1261247.4544
11 | 2696180.9979 | 1261273.9052 | 2696181.8067 | 1261269.1256 | 2696209.9851 | 1261247.4544
12 | 2696142.3787 | 1261263.8583 | 2696145.0618 | 1261267.0934 | 2696141.5902 | 1261269.7058 | 2696158.1204 | 1261291.3141
13 | 2696158.1204 | 1261291.3141 | 2696180.9979 | 1261273.9052
14 | 2696142.3787 | 1261263.8583 | 2696163.8788 | 1261247.43
15 | 2696180.9979 | 1261273.9052 | 2696184.2316 | 1261278.0389 | 2696185.1174 | 1261279.1765 | 2696196.5316 | 1261293.7516 | 2696205.7527 | 1261305.5444
16 | 2696163.8788 | 1261247.43 | 2696168.8361 | 1261243.6421
17 | 2696228.3 | 1261334.3456 | 2696225.1475 | 1261330.3244 | 2696215.0404 | 1261317.4051 | 2696205.7527 | 1261305.5444
18 | 2696205.7527 | 1261305.5444 | 2696228.5461 | 1261288.1966

## bus_geodata
| x | y | coords
0 | 2696189.8128 | 1261452.8491
1 | 2696298.6897 | 1261279.7577
2 | 2696198.9488 | 1261442.5337
3 | 2696186.9707 | 1261229.6554
4 | 2696171.9274 | 1261211.5965
5 | 2696174.8364 | 1261239.0572
6 | 2696246.2615 | 1261223.5702
7 | 2696277.774 | 1261250.7272
8 | 2696209.9851 | 1261247.4544
9 | 2696158.1204 | 1261291.3141
10 | 2696142.3787 | 1261263.8583
11 | 2696180.9979 | 1261273.9052
12 | 2696163.8788 | 1261247.43
13 | 2696273.6199 | 1261299.1996
14 | 2696426.7615 | 1261369.0827
15 | 2696168.8361 | 1261243.6421
16 | 2696190.8682 | 1261431.5746
17 | 2696228.3 | 1261334.3456
18 | 2696205.7527 | 1261305.5444
19 | 2696228.5461 | 1261288.1966
20 | 2696205.7527 | 1261305.5444

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97604 | -0.46133 | 0 | 0
1 | 0.9928 | -0.13708 | 0 | 0
2 | 0.97555 | -0.47092 | 0.015194 | 0.003808
3 | 0.99713 | -0.054581 | 0 | 0
4 | 0.99712 | -0.054822 | 0.0005845 | 0.00014649
5 | 0.99714 | -0.054424 | 0.00054268 | 0.00013601
6 | 0.995 | -0.094931 | 0 | 0
7 | 0.99372 | -0.11949 | 0 | 0
8 | 0.99613 | -0.073503 | 0.0068004 | 0.0017043
9 | 0.99725 | -0.052219 | 0 | 0
10 | 0.99719 | -0.0533 | 0 | 0
11 | 0.9973 | -0.05135 | 0 | 0
12 | 0.99715 | -0.054118 | 0.00029774 | 7.462e-05
13 | 0.99251 | -0.14257 | 0.0097827 | 0.0024518
14 | 0.99167 | -0.15879 | 0.0078529 | 0.0019681
15 | 0.99714 | -0.054274 | 0.00029768 | 7.4606e-05
16 | 0.97526 | -0.47661 | 0.022805 | 0.0057154
17 | 1 | 0 | -0.092849 | -0.023244
18 | 0.99849 | -0.028764 | 0 | 0
19 | 0.99781 | -0.04177 | 0.025956 | 0.0065051
20 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.038023 | -0.0095382 | 0.03862 | 0.0098963 | 0.00059728 | 0.00035815 | 0.05797 | 0.057962 | 0.05797 | 0.97604 | -0.46133 | 0.9928 | -0.13708 | 7.963
1 | 0.038023 | 0.0095382 | -0.038005 | -0.0095272 | 1.7371e-05 | 1.0945e-05 | 0.05797 | 0.05797 | 0.05797 | 0.97604 | -0.46133 | 0.97555 | -0.47092 | 15.9259
2 | 0.0097852 | 0.002453 | -0.0097827 | -0.0024518 | 2.5591e-06 | 1.2277e-06 | 0.014666 | 0.014667 | 0.014667 | 0.9928 | -0.13708 | 0.99251 | -0.14257 | 4.0293
3 | 0.007861 | 0.0019713 | -0.0078529 | -0.0019681 | 8.1296e-06 | 3.1861e-06 | 0.011783 | 0.011783 | 0.011783 | 0.9928 | -0.13708 | 0.99167 | -0.15879 | 3.2372
4 | -0.056266 | -0.014321 | 0.056314 | 0.01435 | 4.7752e-05 | 2.9636e-05 | 0.08441 | 0.08441 | 0.08441 | 0.9928 | -0.13708 | 0.99372 | -0.11949 | 11.5948
5 | 0.022811 | 0.0057192 | -0.022805 | -0.0057154 | 6.1817e-06 | 3.7863e-06 | 0.034795 | 0.034795 | 0.034795 | 0.97555 | -0.47092 | 0.97526 | -0.47661 | 9.559
6 | 0.00058451 | 0.00014619 | -0.0005845 | -0.00014649 | 6.7051e-09 | -3.0229e-07 | 0.00087215 | 0.00087226 | 0.00087226 | 0.99713 | -0.054581 | 0.99712 | -0.054822 | 0.23963
7 | -0.00058451 | -0.00014619 | 0.00058451 | 0.00014599 | 4.3783e-09 | -1.9743e-07 | 0.00087215 | 0.00087208 | 0.00087215 | 0.99713 | -0.054581 | 0.99714 | -0.054424 | 0.2396
8 | -0.0011272 | -0.000282 | 0.0011272 | 0.00028191 | 8.0107e-09 | -9.3378e-08 | 0.0016819 | 0.0016819 | 0.0016819 | 0.99714 | -0.054424 | 0.99714 | -0.054274 | 0.46207
9 | 0.056381 | 0.014392 | -0.056314 | -0.01435 | 6.6821e-05 | 4.1468e-05 | 0.08441 | 0.08441 | 0.08441 | 0.995 | -0.094931 | 0.99372 | -0.11949 | 11.5948
10 | -0.056381 | -0.014392 | 0.056439 | 0.014428 | 5.844e-05 | 3.6264e-05 | 0.08441 | 0.084409 | 0.08441 | 0.995 | -0.094931 | 0.99613 | -0.073503 | 11.5947
11 | -0.06324 | -0.016132 | 0.063307 | 0.016175 | 6.7736e-05 | 4.2298e-05 | 0.094568 | 0.094567 | 0.094568 | 0.99613 | -0.073503 | 0.9973 | -0.05135 | 12.99
12 | 0.0017228 | 0.00043034 | -0.0017227 | -0.00043075 | 8.8568e-08 | -4.0978e-07 | 0.0025701 | 0.0025703 | 0.0025703 | 0.99725 | -0.052219 | 0.99719 | -0.0533 | 0.70612
13 | -0.0017228 | -0.00043034 | 0.0017229 | 0.00043001 | 7.1077e-08 | -3.2893e-07 | 0.0025701 | 0.00257 | 0.0025701 | 0.99725 | -0.052219 | 0.9973 | -0.05135 | 0.70607
14 | 0.0017227 | 0.00043075 | -0.0017226 | -0.00043106 | 6.7036e-08 | -3.1008e-07 | 0.0025703 | 0.0025704 | 0.0025704 | 0.99719 | -0.0533 | 0.99715 | -0.054118 | 0.70615
15 | -0.06503 | -0.016605 | 0.065101 | 0.016649 | 7.1072e-05 | 4.4437e-05 | 0.097137 | 0.097137 | 0.097137 | 0.9973 | -0.05135 | 0.99849 | -0.028764 | 13.343
16 | 0.0014249 | 0.00035644 | -0.0014249 | -0.00035651 | 1.0575e-08 | -7.4614e-08 | 0.0021261 | 0.0021261 | 0.0021261 | 0.99715 | -0.054118 | 0.99714 | -0.054274 | 0.5841
17 | 0.091199 | 0.023244 | -0.091073 | -0.023164 | 0.00012641 | 7.9946e-05 | 0.13584 | 0.13584 | 0.13584 | 1 | 0 | 0.99849 | -0.028764 | 18.6598
18 | 0.025972 | 0.006515 | -0.025956 | -0.0065051 | 1.6094e-05 | 9.9255e-06 | 0.038707 | 0.038707 | 0.038707 | 0.99849 | -0.028764 | 0.99781 | -0.04177 | 10.6339

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.096244 | 0.024095

## res_load
| p_mw | q_mvar
0 | 0.015194 | 0.003808
1 | 0.0005845 | 0.00014649
2 | 0.00054268 | 0.00013601
3 | 0.0068004 | 0.0017043
4 | 0.00029774 | 7.462e-05
5 | 0.0097827 | 0.0024518
6 | 0.0078529 | 0.0019681
7 | 0.00029768 | 7.4606e-05
8 | 0.022805 | 0.0057154
9 | 0.0033947 | 0.0008508
10 | 0.025956 | 0.0065051

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1