## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-45_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-45_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-45_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_230-45_0_6_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_230-45_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-45_0_6_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_230-45_0_6_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_230-45_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_230-45_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_230-45_0_6_node_44 | 0.4 | n |  | TRUE
10 | bus_LV_230-45_0_6_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_230-45_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_230-45_0_6_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_230-45_0_6_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_230-45_0_6_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_230-45_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_230-45_0_6_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_230-45_0_6_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_230-45_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_230-45_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_230-45_0_6_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_230-45_0_6_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_230-45_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_230-45_0_6_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_230-45_0_6_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_230-45_0_6_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_230-45_0_6_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_230-45_0_6_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_230-45_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_230-45_0_6_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_230-45_0_6_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_230-45_0_6_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_230-45_0_6_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_230-45_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_230-45_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_230-45_0_6_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_230-45_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_230-45_0_6_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_230-45_0_6_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_230-45_0_6_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_230-45_0_6_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_230-45_0_6_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_230-45_0_6_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_230-45_0_6_node_39 | 0.4 | n |  | TRUE
44 | bus_MV_512_0_node_133 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-45_0_6_load_0 | 0 | 0.03194 | 0.0080048 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-45_0_6_load_1 | 1 | 0.084948 | 0.02129 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-45_0_6_load_28 | 6 | 0.0032925 | 0.00082518 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-45_0_6_load_44 | 9 | 0.032187 | 0.0080669 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-45_0_6_load_19 | 10 | 0.061935 | 0.015522 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-45_0_6_load_20 | 12 | 0.015349 | 0.0038468 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-45_0_6_load_34 | 14 | 0.0046386 | 0.0011625 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-45_0_6_load_42 | 16 | 0.0097902 | 0.0024536 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-45_0_6_load_40 | 17 | 0.0049449 | 0.0012393 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-45_0_6_load_21 | 20 | 0.002678 | 0.00067118 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-45_0_6_load_43 | 21 | 0.051311 | 0.01286 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-45_0_6_load_18 | 23 | 0.033644 | 0.008432 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-45_0_6_load_15 | 24 | 0.024237 | 0.0060743 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-45_0_6_load_29 | 25 | 0.0037644 | 0.00094344 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-45_0_6_load_32 | 26 | 0.0019864 | 0.00049785 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-45_0_6_load_41 | 27 | 0.0048999 | 0.001228 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-45_0_6_load_22 | 28 | 0.029378 | 0.0073628 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-45_0_6_load_37 | 29 | 0.010506 | 0.002633 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-45_0_6_load_16 | 30 | 0.023952 | 0.006003 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-45_0_6_load_17 | 31 | 0.047138 | 0.011814 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-45_0_6_load_38 | 32 | 0.00837 | 0.0020977 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-45_0_6_load_23 | 33 | 0.0074567 | 0.0018688 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-45_0_6_load_24 | 34 | 0.005726 | 0.0014351 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-45_0_6_load_25 | 35 | 0.0037949 | 0.0009511 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-45_0_6_load_26 | 36 | 0.013307 | 0.003335 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-45_0_6_load_27 | 37 | 0.0041324 | 0.0010357 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-45_0_6_load_36 | 38 | 0.0051657 | 0.0012946 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-45_0_6_load_31 | 39 | 0.015286 | 0.003831 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-45_0_6_load_35 | 40 | 0.0052436 | 0.0013142 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-45_0_6_load_30 | 41 | 0.0039988 | 0.0010022 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-45_0_6_load_33 | 42 | 0.0049297 | 0.0012355 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-45_0_6_load_39 | 43 | 0.010231 | 0.0025641 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-45_0_6_line_0 |  | 0 | 1 | 0.062435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-45_0_6_line_1 |  | 1 | 2 | 0.060701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-45_0_6_line_2 |  | 2 | 3 | 0.06342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-45_0_6_line_3 |  | 3 | 13 | 0.00971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_230-45_0_6_line_4 |  | 3 | 14 | 0.054582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_230-45_0_6_line_5 |  | 4 | 5 | 0.037507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_230-45_0_6_line_6 |  | 4 | 6 | 0.02815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_230-45_0_6_line_7 |  | 5 | 9 | 0.013707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_230-45_0_6_line_8 |  | 6 | 25 | 0.010825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_230-45_0_6_line_9 |  | 7 | 8 | 0.009111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_230-45_0_6_line_10 |  | 7 | 9 | 0.012704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_230-45_0_6_line_11 |  | 8 | 10 | 0.0020254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_230-45_0_6_line_12 |  | 10 | 11 | 0.0073629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_230-45_0_6_line_13 |  | 11 | 12 | 0.012948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_230-45_0_6_line_14 |  | 12 | 15 | 0.013615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_230-45_0_6_line_15 |  | 13 | 17 | 0.059769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_230-45_0_6_line_16 |  | 14 | 26 | 0.0013345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_230-45_0_6_line_17 |  | 15 | 16 | 0.020471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_230-45_0_6_line_18 |  | 16 | 21 | 0.018318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_230-45_0_6_line_19 |  | 17 | 27 | 0.010806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_230-45_0_6_line_20 |  | 18 | 19 | 0.033403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_230-45_0_6_line_21 |  | 18 | 20 | 0.062017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_230-45_0_6_line_22 |  | 19 | 21 | 0.048734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_230-45_0_6_line_23 |  | 20 | 28 | 0.06884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-45_0_6_line_24 |  | 22 | 23 | 0.0092649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_230-45_0_6_line_25 |  | 22 | 24 | 0.011178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-45_0_6_line_26 |  | 23 | 29 | 0.014532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_230-45_0_6_line_27 |  | 24 | 30 | 0.016055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-45_0_6_line_28 |  | 25 | 41 | 0.011766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_230-45_0_6_line_29 |  | 26 | 42 | 0.008784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_230-45_0_6_line_30 |  | 27 | 43 | 0.01208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_230-45_0_6_line_31 |  | 29 | 32 | 0.014964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_230-45_0_6_line_32 |  | 30 | 31 | 0.014302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-45_0_6_line_33 |  | 32 | 43 | 0.016442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_230-45_0_6_line_34 |  | 33 | 34 | 0.014259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_230-45_0_6_line_35 |  | 33 | 35 | 0.012659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_230-45_0_6_line_36 |  | 34 | 36 | 0.0026231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_230-45_0_6_line_37 |  | 35 | 37 | 0.0089962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_230-45_0_6_line_38 |  | 36 | 38 | 0.0097697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_230-45_0_6_line_39 |  | 37 | 39 | 0.009848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_230-45_0_6_line_40 |  | 38 | 40 | 0.010412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_230-45_0_6_line_41 |  | 39 | 41 | 0.011159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_230-45_0_6_line_42 |  | 40 | 42 | 0.0012652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-45_0_6_trafo_14 | 0.63 MVA 20/0.4 kV | 44 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2696666.6675 | 1261861.6073 | 2696654.2203 | 1261867.4991 | 2696652.7727 | 1261868.4651 | 2696652.0765 | 1261869.5658 | 2696650.9111 | 1261871.2481 | 2696611.6148 | 1261890.0772
1 | 2696557.4788 | 1261916.2812 | 2696557.9356 | 1261915.0766 | 2696558.8431 | 1261913.9571 | 2696560.7613 | 1261912.7764 | 2696565.2945 | 1261910.6709 | 2696600.1486 | 1261894.4267 | 2696610.7174 | 1261890.5072 | 2696611.6148 | 1261890.0772
2 | 2696557.4788 | 1261916.2812 | 2696559.0034 | 1261919.3641 | 2696581.2509 | 1261966.2654 | 2696582.5564 | 1261968.9222 | 2696584.2471 | 1261969.6727 | 2696585.8997 | 1261969.5329 | 2696587.3356 | 1261968.8224
3 | 2696587.3356 | 1261968.8224 | 2696589.2326 | 1261973.0902 | 2696591.2824 | 1261977.6941
4 | 2696587.3356 | 1261968.8224 | 2696590.321 | 1261967.3589 | 2696611.4292 | 1261957.1508 | 2696636.5239 | 1261945.1649
5 | 2696764.6231 | 1261884.2509 | 2696766.6975 | 1261888.7218 | 2696770.797 | 1261897.4626 | 2696780.6236 | 1261918.1735
6 | 2696764.6231 | 1261884.2509 | 2696739.2713 | 1261896.4864
7 | 2696780.6236 | 1261918.1735 | 2696786.6048 | 1261930.5065
8 | 2696739.2713 | 1261896.4864 | 2696733.6023 | 1261899.2224 | 2696729.4737 | 1261901.0863
9 | 2696792.1483 | 1261941.937 | 2696796.0525 | 1261950.1742
10 | 2696792.1483 | 1261941.937 | 2696786.6048 | 1261930.5065
11 | 2696796.0525 | 1261950.1742 | 2696796.9199 | 1261952.0045
12 | 2696800.0732 | 1261958.658 | 2696796.9199 | 1261952.0045
13 | 2696800.0732 | 1261958.658 | 2696805.5488 | 1261970.3908
14 | 2696811.3064 | 1261982.7281 | 2696805.5488 | 1261970.3908
15 | 2696591.2824 | 1261977.6941 | 2696645.1618 | 1261951.8222
16 | 2696637.7281 | 1261944.5897 | 2696636.5239 | 1261945.1649
17 | 2696811.3064 | 1261982.7281 | 2696805.8129 | 1261985.496 | 2696792.8662 | 1261991.6141
18 | 2696792.8662 | 1261991.6141 | 2696776.3044 | 1261999.4406
19 | 2696645.1618 | 1261951.8222 | 2696654.9027 | 1261947.1448
20 | 2696732.3779 | 1262020.5455 | 2696728.666 | 1262022.1973 | 2696701.7943 | 1262034.1788
21 | 2696701.7943 | 1262034.1788 | 2696675.9123 | 1261977.821
22 | 2696732.3779 | 1262020.5455 | 2696735.7731 | 1262018.9108 | 2696775.0863 | 1262000.0162 | 2696776.3044 | 1261999.4406
23 | 2696738.4681 | 1261949.087 | 2696675.9123 | 1261977.821
24 | 2696715.5557 | 1261918.0204 | 2696707.2039 | 1261922.0308
25 | 2696715.5557 | 1261918.0204 | 2696717.7664 | 1261922.4601 | 2696723.4028 | 1261919.8338
26 | 2696707.2039 | 1261922.0308 | 2696694.104 | 1261928.3211
27 | 2696723.4028 | 1261919.8338 | 2696737.9558 | 1261913.0527
28 | 2696718.7495 | 1261905.9281 | 2696729.4737 | 1261901.0863
29 | 2696637.7281 | 1261944.5897 | 2696638.3531 | 1261944.2912 | 2696645.636 | 1261940.7657
30 | 2696665.7925 | 1261941.9158 | 2696654.9027 | 1261947.1448
31 | 2696694.104 | 1261928.3211 | 2696680.6144 | 1261934.7986
32 | 2696750.9199 | 1261907.0119 | 2696737.9558 | 1261913.0527
33 | 2696665.7925 | 1261941.9158 | 2696680.6144 | 1261934.7986
34 | 2696667.3365 | 1261930.352 | 2696680.1996 | 1261924.1984
35 | 2696691.6134 | 1261918.723 | 2696685.8993 | 1261921.4718 | 2696680.1996 | 1261924.1984
36 | 2696664.9702 | 1261931.484 | 2696667.3365 | 1261930.352
37 | 2696691.6134 | 1261918.723 | 2696699.7204 | 1261914.8232
38 | 2696656.148 | 1261935.6812 | 2696664.8837 | 1261931.5254 | 2696664.9702 | 1261931.484
39 | 2696708.5949 | 1261910.5542 | 2696699.7204 | 1261914.8232
40 | 2696656.148 | 1261935.6812 | 2696655.641 | 1261935.9224 | 2696646.7747 | 1261940.2144
41 | 2696708.5949 | 1261910.5542 | 2696709.9995 | 1261909.8785 | 2696718.7495 | 1261905.9281
42 | 2696645.636 | 1261940.7657 | 2696646.7747 | 1261940.2144

## bus_geodata
| x | y | coords
0 | 2696666.6675 | 1261861.6073
1 | 2696611.6148 | 1261890.0772
2 | 2696557.4788 | 1261916.2812
3 | 2696587.3356 | 1261968.8224
4 | 2696764.6231 | 1261884.2509
5 | 2696780.6236 | 1261918.1735
6 | 2696739.2713 | 1261896.4864
7 | 2696792.1483 | 1261941.937
8 | 2696796.0525 | 1261950.1742
9 | 2696786.6048 | 1261930.5065
10 | 2696796.9199 | 1261952.0045
11 | 2696800.0732 | 1261958.658
12 | 2696805.5488 | 1261970.3908
13 | 2696591.2824 | 1261977.6941
14 | 2696636.5239 | 1261945.1649
15 | 2696811.3064 | 1261982.7281
16 | 2696792.8662 | 1261991.6141
17 | 2696645.1618 | 1261951.8222
18 | 2696701.7943 | 1262034.1788
19 | 2696732.3779 | 1262020.5455
20 | 2696675.9123 | 1261977.821
21 | 2696776.3044 | 1261999.4406
22 | 2696715.5557 | 1261918.0204
23 | 2696707.2039 | 1261922.0308
24 | 2696723.4028 | 1261919.8338
25 | 2696729.4737 | 1261901.0863
26 | 2696637.7281 | 1261944.5897
27 | 2696654.9027 | 1261947.1448
28 | 2696738.4681 | 1261949.087
29 | 2696694.104 | 1261928.3211
30 | 2696737.9558 | 1261913.0527
31 | 2696750.9199 | 1261907.0119
32 | 2696680.6144 | 1261934.7986
33 | 2696680.1996 | 1261924.1984
34 | 2696667.3365 | 1261930.352
35 | 2696691.6134 | 1261918.723
36 | 2696664.9702 | 1261931.484
37 | 2696699.7204 | 1261914.8232
38 | 2696656.148 | 1261935.6812
39 | 2696708.5949 | 1261910.5542
40 | 2696646.7747 | 1261940.2144
41 | 2696718.7495 | 1261905.9281
42 | 2696645.636 | 1261940.7657
43 | 2696665.7925 | 1261941.9158
44 | 2696713.6368 | 1261914.1748

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9732 | -0.51597 | 0.03194 | 0.0080048
1 | 0.97506 | -0.47934 | 0.084948 | 0.02129
2 | 0.98167 | -0.35014 | 0 | 0
3 | 0.98857 | -0.21699 | 0 | 0
4 | 0.97958 | -0.39122 | 0 | 0
5 | 0.97817 | -0.41888 | 0 | 0
6 | 0.98064 | -0.37052 | 0.0032925 | 0.00082518
7 | 0.97725 | -0.4369 | 0 | 0
8 | 0.97696 | -0.44257 | 0 | 0
9 | 0.97766 | -0.429 | 0.032187 | 0.0080669
10 | 0.9769 | -0.44383 | 0.061935 | 0.015522
11 | 0.97675 | -0.44675 | 0 | 0
12 | 0.97649 | -0.45189 | 0.015349 | 0.0038468
13 | 0.9893 | -0.20307 | 0 | 0
14 | 0.98568 | -0.27273 | 0.0046386 | 0.0011625
15 | 0.97625 | -0.45653 | 0 | 0
16 | 0.9759 | -0.46351 | 0.0097902 | 0.0024536
17 | 0.99376 | -0.11781 | 0.0049449 | 0.0012393
18 | 0.97512 | -0.47875 | 0 | 0
19 | 0.97532 | -0.47483 | 0 | 0
20 | 0.9742 | -0.49699 | 0.002678 | 0.00067118
21 | 0.97562 | -0.4691 | 0.051311 | 0.01286
22 | 1 | 0 | -0.5808 | -0.14861
23 | 0.99918 | -0.015351 | 0.033644 | 0.008432
24 | 0.99903 | -0.01859 | 0.024237 | 0.0060743
25 | 0.98106 | -0.36244 | 0.0037644 | 0.00094344
26 | 0.98561 | -0.27407 | 0.0019864 | 0.00049785
27 | 0.99458 | -0.10229 | 0.0048999 | 0.001228
28 | 0.97231 | -0.53421 | 0.029378 | 0.0073628
29 | 0.99799 | -0.037769 | 0.010506 | 0.002633
30 | 0.99799 | -0.038543 | 0.023952 | 0.006003
31 | 0.99738 | -0.050349 | 0.047138 | 0.011814
32 | 0.9968 | -0.060357 | 0.00837 | 0.0020977
33 | 0.98333 | -0.31834 | 0.0074567 | 0.0018688
34 | 0.98397 | -0.30578 | 0.005726 | 0.0014351
35 | 0.98277 | -0.32916 | 0.0037949 | 0.0009511
36 | 0.98409 | -0.30342 | 0.013307 | 0.003335
37 | 0.98238 | -0.33673 | 0.0041324 | 0.0010357
38 | 0.98457 | -0.29416 | 0.0051657 | 0.0012946
39 | 0.98196 | -0.34488 | 0.015286 | 0.003831
40 | 0.98509 | -0.28411 | 0.0052436 | 0.0013142
41 | 0.98152 | -0.35351 | 0.0039988 | 0.0010022
42 | 0.98516 | -0.28286 | 0.0049297 | 0.0012355
43 | 0.99551 | -0.084756 | 0.010231 | 0.0025641
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.03194 | -0.0080048 | 0.031995 | 0.0080398 | 5.5837e-05 | 3.4958e-05 | 0.048835 | 0.048835 | 0.048835 | 0.9732 | -0.51597 | 0.97506 | -0.47934 | 13.4162
1 | -0.11694 | -0.02933 | 0.11767 | 0.029793 | 0.00072505 | 0.00046327 | 0.17847 | 0.17847 | 0.17847 | 0.97506 | -0.47934 | 0.98167 | -0.35014 | 49.0308
2 | -0.11767 | -0.029793 | 0.11843 | 0.030277 | 0.00075753 | 0.00048401 | 0.17847 | 0.17847 | 0.17847 | 0.98167 | -0.35014 | 0.98857 | -0.21699 | 49.0307
3 | -0.40658 | -0.10356 | 0.40686 | 0.10373 | 0.00027329 | 0.00017428 | 0.61259 | 0.61259 | 0.61259 | 0.98857 | -0.21699 | 0.9893 | -0.20307 | 33.659
4 | 0.28816 | 0.073283 | -0.28739 | -0.072793 | 0.0007715 | 0.00049027 | 0.43412 | 0.43412 | 0.43412 | 0.98857 | -0.21699 | 0.98568 | -0.27273 | 23.8529
5 | 0.20333 | 0.051214 | -0.20306 | -0.051044 | 0.00026851 | 0.00016949 | 0.30895 | 0.30895 | 0.30895 | 0.97958 | -0.39122 | 0.97817 | -0.41888 | 16.9753
6 | -0.20333 | -0.051214 | 0.20353 | 0.051341 | 0.00020152 | 0.0001272 | 0.30895 | 0.30895 | 0.30895 | 0.97958 | -0.39122 | 0.98064 | -0.37052 | 16.9753
7 | 0.20306 | 0.051044 | -0.20296 | -0.050982 | 9.8125e-05 | 6.194e-05 | 0.30895 | 0.30895 | 0.30895 | 0.97817 | -0.41888 | 0.97766 | -0.429 | 16.9754
8 | -0.20682 | -0.052166 | 0.2069 | 0.052216 | 8.0016e-05 | 5.0527e-05 | 0.31395 | 0.31395 | 0.31395 | 0.98064 | -0.37052 | 0.98106 | -0.36244 | 17.2498
9 | 0.17071 | 0.042875 | -0.17066 | -0.042846 | 4.6179e-05 | 2.8984e-05 | 0.25996 | 0.25996 | 0.25996 | 0.97725 | -0.4369 | 0.97696 | -0.44257 | 14.2836
10 | -0.17071 | -0.042875 | 0.17077 | 0.042915 | 6.4389e-05 | 4.0413e-05 | 0.25996 | 0.25996 | 0.25996 | 0.97725 | -0.4369 | 0.97766 | -0.429 | 14.2836
11 | 0.17066 | 0.042846 | -0.17065 | -0.042839 | 1.0266e-05 | 6.4434e-06 | 0.25996 | 0.25996 | 0.25996 | 0.97696 | -0.44257 | 0.9769 | -0.44383 | 14.2836
12 | 0.10872 | 0.027317 | -0.1087 | -0.027308 | 1.5148e-05 | 9.2338e-06 | 0.16562 | 0.16562 | 0.16562 | 0.9769 | -0.44383 | 0.97675 | -0.44675 | 9.1001
13 | 0.1087 | 0.027308 | -0.10867 | -0.027291 | 2.6637e-05 | 1.6238e-05 | 0.16562 | 0.16562 | 0.16562 | 0.97675 | -0.44675 | 0.97649 | -0.45189 | 9.1002
14 | 0.093326 | 0.023445 | -0.093305 | -0.023432 | 2.0657e-05 | 1.2369e-05 | 0.14223 | 0.14223 | 0.14223 | 0.97649 | -0.45189 | 0.97625 | -0.45653 | 7.8151
15 | -0.40686 | -0.10373 | 0.40854 | 0.10481 | 0.0016822 | 0.0010728 | 0.61259 | 0.61259 | 0.61259 | 0.9893 | -0.20307 | 0.99376 | -0.11781 | 33.6589
16 | 0.28275 | 0.07163 | -0.28273 | -0.071618 | 1.8259e-05 | 1.1601e-05 | 0.42712 | 0.42712 | 0.42712 | 0.98568 | -0.27273 | 0.98561 | -0.27407 | 23.4681
17 | 0.093305 | 0.023432 | -0.093274 | -0.023414 | 3.106e-05 | 1.8599e-05 | 0.14223 | 0.14223 | 0.14223 | 0.97625 | -0.45653 | 0.9759 | -0.46351 | 7.8151
18 | 0.083484 | 0.02096 | -0.083462 | -0.020947 | 2.2266e-05 | 1.3106e-05 | 0.12731 | 0.12731 | 0.12731 | 0.9759 | -0.46351 | 0.97562 | -0.4691 | 6.9949
19 | -0.41348 | -0.10605 | 0.4138 | 0.10625 | 0.00031153 | 0.00019868 | 0.62 | 0.62 | 0.62 | 0.99376 | -0.11781 | 0.99458 | -0.10229 | 34.0657
20 | -0.032136 | -0.0080829 | 0.032142 | 0.0080847 | 6.0271e-06 | 1.7735e-06 | 0.049049 | 0.049049 | 0.049049 | 0.97512 | -0.47875 | 0.97532 | -0.47483 | 2.695
21 | 0.032136 | 0.0080829 | -0.032108 | -0.0080665 | 2.7976e-05 | 1.6359e-05 | 0.049049 | 0.04905 | 0.04905 | 0.97512 | -0.47875 | 0.9742 | -0.49699 | 6.7376
22 | -0.032142 | -0.0080847 | 0.032151 | 0.0080873 | 8.793e-06 | 2.5857e-06 | 0.049049 | 0.049048 | 0.049049 | 0.97532 | -0.47483 | 0.97562 | -0.4691 | 2.695
23 | 0.02943 | 0.0073954 | -0.029378 | -0.0073628 | 5.2181e-05 | 3.2541e-05 | 0.04496 | 0.04496 | 0.04496 | 0.9742 | -0.49699 | 0.97231 | -0.53421 | 12.3516
24 | 0.48365 | 0.1246 | -0.48328 | -0.12437 | 0.0003611 | 0.00023049 | 0.72088 | 0.72088 | 0.72088 | 1 | 0 | 0.99918 | -0.015351 | 39.6087
25 | 0.095506 | 0.024005 | -0.095421 | -0.023951 | 8.4687e-05 | 5.4053e-05 | 0.14214 | 0.14214 | 0.14214 | 1 | 0 | 0.99903 | -0.01859 | 39.0492
26 | 0.44964 | 0.11594 | -0.44915 | -0.11563 | 0.00049038 | 0.00031289 | 0.67078 | 0.67078 | 0.67078 | 0.99918 | -0.015351 | 0.99799 | -0.037769 | 36.8558
27 | 0.071185 | 0.017877 | -0.071117 | -0.017834 | 6.7699e-05 | 4.3118e-05 | 0.10604 | 0.10604 | 0.10604 | 0.99903 | -0.01859 | 0.99799 | -0.038543 | 29.1317
28 | -0.21066 | -0.05316 | 0.21076 | 0.053217 | 9.0172e-05 | 5.6967e-05 | 0.31966 | 0.31965 | 0.31966 | 0.98106 | -0.36244 | 0.98152 | -0.35351 | 17.5635
29 | 0.28074 | 0.071121 | -0.28062 | -0.071045 | 0.0001185 | 7.5283e-05 | 0.42412 | 0.42412 | 0.42412 | 0.98561 | -0.27407 | 0.98516 | -0.28286 | 23.3034
30 | -0.4187 | -0.10747 | 0.41905 | 0.1077 | 0.00035655 | 0.00022741 | 0.62733 | 0.62733 | 0.62733 | 0.99458 | -0.10229 | 0.99551 | -0.084756 | 34.4685
31 | 0.43864 | 0.11299 | -0.43816 | -0.11269 | 0.00048167 | 0.00030729 | 0.65511 | 0.65511 | 0.65511 | 0.99799 | -0.037769 | 0.9968 | -0.060357 | 35.9952
32 | 0.047165 | 0.011831 | -0.047138 | -0.011814 | 2.6526e-05 | 1.679e-05 | 0.070326 | 0.070326 | 0.070326 | 0.99799 | -0.038543 | 0.99738 | -0.050349 | 19.3204
33 | 0.42979 | 0.11059 | -0.42928 | -0.11026 | 0.00050924 | 0.00032484 | 0.64262 | 0.64262 | 0.64262 | 0.9968 | -0.060357 | 0.99551 | -0.084756 | 35.3087
34 | -0.24581 | -0.062151 | 0.24596 | 0.062245 | 0.00014813 | 9.3897e-05 | 0.37217 | 0.37217 | 0.37217 | 0.98333 | -0.31834 | 0.98397 | -0.30578 | 20.4488
35 | 0.23835 | 0.060282 | -0.23823 | -0.060204 | 0.00012365 | 7.8336e-05 | 0.36089 | 0.36089 | 0.36089 | 0.98333 | -0.31834 | 0.98277 | -0.32916 | 19.8289
36 | -0.25169 | -0.06368 | 0.25171 | 0.063698 | 2.8532e-05 | 1.8094e-05 | 0.38083 | 0.38083 | 0.38083 | 0.98397 | -0.30578 | 0.98409 | -0.30342 | 20.9246
37 | 0.23444 | 0.059253 | -0.23435 | -0.059199 | 8.5097e-05 | 5.3893e-05 | 0.35514 | 0.35514 | 0.35514 | 0.98277 | -0.32916 | 0.98238 | -0.33673 | 19.5132
38 | -0.26502 | -0.067033 | 0.26514 | 0.067108 | 0.00011779 | 7.4767e-05 | 0.40095 | 0.40095 | 0.40095 | 0.98409 | -0.30342 | 0.98457 | -0.29416 | 22.0301
39 | 0.23022 | 0.058163 | -0.23013 | -0.058106 | 8.9901e-05 | 5.6913e-05 | 0.34888 | 0.34888 | 0.34888 | 0.98238 | -0.33673 | 0.98196 | -0.34488 | 19.1693
40 | -0.2703 | -0.068402 | 0.27043 | 0.068485 | 0.00013047 | 8.284e-05 | 0.40876 | 0.40875 | 0.40876 | 0.98457 | -0.29416 | 0.98509 | -0.28411 | 22.4591
41 | 0.21484 | 0.054275 | -0.21475 | -0.054219 | 8.8792e-05 | 5.6121e-05 | 0.32572 | 0.32572 | 0.32572 | 0.98196 | -0.34488 | 0.98152 | -0.35351 | 17.8965
42 | -0.27568 | -0.069799 | 0.27569 | 0.06981 | 1.6474e-05 | 1.0463e-05 | 0.41668 | 0.41668 | 0.41668 | 0.98509 | -0.28411 | 0.98516 | -0.28286 | 22.8943

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5808 | 0.14861

## res_load
| p_mw | q_mvar
0 | 0.03194 | 0.0080048
1 | 0.084948 | 0.02129
2 | 0.0032925 | 0.00082518
3 | 0.032187 | 0.0080669
4 | 0.061935 | 0.015522
5 | 0.015349 | 0.0038468
6 | 0.0046386 | 0.0011625
7 | 0.0097902 | 0.0024536
8 | 0.0049449 | 0.0012393
9 | 0.002678 | 0.00067118
10 | 0.051311 | 0.01286
11 | 0.033644 | 0.008432
12 | 0.024237 | 0.0060743
13 | 0.0037644 | 0.00094344
14 | 0.0019864 | 0.00049785
15 | 0.0048999 | 0.001228
16 | 0.029378 | 0.0073628
17 | 0.010506 | 0.002633
18 | 0.023952 | 0.006003
19 | 0.047138 | 0.011814
20 | 0.00837 | 0.0020977
21 | 0.0074567 | 0.0018688
22 | 0.005726 | 0.0014351
23 | 0.0037949 | 0.0009511
24 | 0.013307 | 0.003335
25 | 0.0041324 | 0.0010357
26 | 0.0051657 | 0.0012946
27 | 0.015286 | 0.003831
28 | 0.0052436 | 0.0013142
29 | 0.0039988 | 0.0010022
30 | 0.0049297 | 0.0012355
31 | 0.010231 | 0.0025641

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1