## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-62_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-62_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-62_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-62_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_230-62_0_6_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_230-62_0_6_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_230-62_0_6_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_230-62_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_230-62_0_6_node_113 | 0.4 | n |  | TRUE
9 | bus_LV_230-62_0_6_node_94 | 0.4 | n |  | TRUE
10 | bus_LV_230-62_0_6_node_112 | 0.4 | n |  | TRUE
11 | bus_LV_230-62_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_230-62_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_230-62_0_6_node_93 | 0.4 | n |  | TRUE
14 | bus_LV_230-62_0_6_node_118 | 0.4 | n |  | TRUE
15 | bus_LV_230-62_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_230-62_0_6_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_230-62_0_6_node_146 | 0.4 | n |  | TRUE
18 | bus_LV_230-62_0_6_node_90 | 0.4 | n |  | TRUE
19 | bus_LV_230-62_0_6_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_230-62_0_6_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_230-62_0_6_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_230-62_0_6_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_230-62_0_6_node_124 | 0.4 | n |  | TRUE
24 | bus_LV_230-62_0_6_node_122 | 0.4 | n |  | TRUE
25 | bus_LV_230-62_0_6_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_230-62_0_6_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_230-62_0_6_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_230-62_0_6_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_230-62_0_6_node_128 | 0.4 | n |  | TRUE
30 | bus_LV_230-62_0_6_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_230-62_0_6_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_230-62_0_6_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_230-62_0_6_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_230-62_0_6_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_230-62_0_6_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_230-62_0_6_node_129 | 0.4 | n |  | TRUE
37 | bus_LV_230-62_0_6_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_230-62_0_6_node_60 | 0.4 | n |  | TRUE
39 | bus_LV_230-62_0_6_node_61 | 0.4 | n |  | TRUE
40 | bus_LV_230-62_0_6_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_230-62_0_6_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_230-62_0_6_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_230-62_0_6_node_123 | 0.4 | n |  | TRUE
44 | bus_LV_230-62_0_6_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_230-62_0_6_node_126 | 0.4 | n |  | TRUE
46 | bus_LV_230-62_0_6_node_125 | 0.4 | n |  | TRUE
47 | bus_LV_230-62_0_6_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_230-62_0_6_node_18 | 0.4 | n |  | TRUE
49 | bus_LV_230-62_0_6_node_19 | 0.4 | n |  | TRUE
50 | bus_LV_230-62_0_6_node_17 | 0.4 | n |  | TRUE
51 | bus_LV_230-62_0_6_node_16 | 0.4 | n |  | TRUE
52 | bus_LV_230-62_0_6_node_133 | 0.4 | n |  | TRUE
53 | bus_LV_230-62_0_6_node_109 | 0.4 | n |  | TRUE
54 | bus_LV_230-62_0_6_node_121 | 0.4 | n |  | TRUE
55 | bus_LV_230-62_0_6_node_97 | 0.4 | n |  | TRUE
56 | bus_LV_230-62_0_6_node_68 | 0.4 | n |  | TRUE
57 | bus_LV_230-62_0_6_node_66 | 0.4 | n |  | TRUE
58 | bus_LV_230-62_0_6_node_127 | 0.4 | n |  | TRUE
59 | bus_LV_230-62_0_6_node_89 | 0.4 | n |  | TRUE
60 | bus_LV_230-62_0_6_node_20 | 0.4 | n |  | TRUE
61 | bus_LV_230-62_0_6_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_230-62_0_6_node_69 | 0.4 | n |  | TRUE
63 | bus_LV_230-62_0_6_node_21 | 0.4 | n |  | TRUE
64 | bus_LV_230-62_0_6_node_31 | 0.4 | n |  | TRUE
65 | bus_LV_230-62_0_6_node_85 | 0.4 | n |  | TRUE
66 | bus_LV_230-62_0_6_node_137 | 0.4 | n |  | TRUE
67 | bus_LV_230-62_0_6_node_147 | 0.4 | n |  | TRUE
68 | bus_LV_230-62_0_6_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_230-62_0_6_node_145 | 0.4 | n |  | TRUE
70 | bus_LV_230-62_0_6_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_230-62_0_6_node_120 | 0.4 | n |  | TRUE
72 | bus_LV_230-62_0_6_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_230-62_0_6_node_115 | 0.4 | n |  | TRUE
74 | bus_LV_230-62_0_6_node_135 | 0.4 | n |  | TRUE
75 | bus_LV_230-62_0_6_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_230-62_0_6_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_230-62_0_6_node_62 | 0.4 | n |  | TRUE
78 | bus_LV_230-62_0_6_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_230-62_0_6_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_230-62_0_6_node_48 | 0.4 | n |  | TRUE
81 | bus_LV_230-62_0_6_node_130 | 0.4 | n |  | TRUE
82 | bus_LV_230-62_0_6_node_42 | 0.4 | n |  | TRUE
83 | bus_LV_230-62_0_6_node_43 | 0.4 | n |  | TRUE
84 | bus_LV_230-62_0_6_node_45 | 0.4 | n |  | TRUE
85 | bus_LV_230-62_0_6_node_47 | 0.4 | n |  | TRUE
86 | bus_LV_230-62_0_6_node_50 | 0.4 | n |  | TRUE
87 | bus_LV_230-62_0_6_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_230-62_0_6_node_98 | 0.4 | n |  | TRUE
89 | bus_LV_230-62_0_6_node_99 | 0.4 | n |  | TRUE
90 | bus_LV_230-62_0_6_node_95 | 0.4 | n |  | TRUE
91 | bus_LV_230-62_0_6_node_100 | 0.4 | n |  | TRUE
92 | bus_LV_230-62_0_6_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_230-62_0_6_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_230-62_0_6_node_144 | 0.4 | n |  | TRUE
95 | bus_LV_230-62_0_6_node_56 | 0.4 | n |  | TRUE
96 | bus_LV_230-62_0_6_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_230-62_0_6_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_230-62_0_6_node_64 | 0.4 | n |  | TRUE
99 | bus_LV_230-62_0_6_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_230-62_0_6_node_73 | 0.4 | n |  | TRUE
101 | bus_LV_230-62_0_6_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_230-62_0_6_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_230-62_0_6_node_76 | 0.4 | n |  | TRUE
104 | bus_LV_230-62_0_6_node_77 | 0.4 | n |  | TRUE
105 | bus_LV_230-62_0_6_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_230-62_0_6_node_78 | 0.4 | n |  | TRUE
107 | bus_LV_230-62_0_6_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_230-62_0_6_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_230-62_0_6_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_230-62_0_6_node_87 | 0.4 | n |  | TRUE
111 | bus_LV_230-62_0_6_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_230-62_0_6_node_81 | 0.4 | n |  | TRUE
113 | bus_LV_230-62_0_6_node_83 | 0.4 | n |  | TRUE
114 | bus_LV_230-62_0_6_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_230-62_0_6_node_114 | 0.4 | n |  | TRUE
116 | bus_LV_230-62_0_6_node_92 | 0.4 | n |  | TRUE
117 | bus_LV_230-62_0_6_node_91 | 0.4 | n |  | TRUE
118 | bus_LV_230-62_0_6_node_101 | 0.4 | n |  | TRUE
119 | bus_LV_230-62_0_6_node_102 | 0.4 | n |  | TRUE
120 | bus_LV_230-62_0_6_node_103 | 0.4 | n |  | TRUE
121 | bus_LV_230-62_0_6_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_230-62_0_6_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_230-62_0_6_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_230-62_0_6_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_230-62_0_6_node_106 | 0.4 | n |  | TRUE
126 | bus_LV_230-62_0_6_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_230-62_0_6_node_134 | 0.4 | n |  | TRUE
128 | bus_LV_230-62_0_6_node_132 | 0.4 | n |  | TRUE
129 | bus_LV_230-62_0_6_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_230-62_0_6_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_230-62_0_6_node_136 | 0.4 | n |  | TRUE
132 | bus_LV_230-62_0_6_node_138 | 0.4 | n |  | TRUE
133 | bus_LV_230-62_0_6_node_139 | 0.4 | n |  | TRUE
134 | bus_LV_230-62_0_6_node_140 | 0.4 | n |  | TRUE
135 | bus_LV_230-62_0_6_node_141 | 0.4 | n |  | TRUE
136 | bus_LV_230-62_0_6_node_142 | 0.4 | n |  | TRUE
137 | bus_LV_230-62_0_6_node_143 | 0.4 | n |  | TRUE
138 | bus_MV_369_1_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-62_0_6_load_0 | 0 | 0.0071879 | 0.0018015 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-62_0_6_load_1 | 1 | 0.0038642 | 0.00096847 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-62_0_6_load_4 | 3 | 0.0033598 | 0.00084204 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-62_0_6_load_15 | 6 | 0.0040798 | 0.0010225 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-62_0_6_load_113 | 8 | 0.0024823 | 0.00062213 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-62_0_6_load_94 | 9 | 0.0029907 | 0.00074954 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-62_0_6_load_112 | 10 | 0.0055685 | 0.0013956 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-62_0_6_load_93 | 13 | 0.0043059 | 0.0010792 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-62_0_6_load_118 | 14 | 0.0042969 | 0.0010769 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-62_0_6_load_146 | 17 | 0.0023514 | 0.00058932 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-62_0_6_load_90 | 18 | 0.0040998 | 0.0010275 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-62_0_6_load_22 | 21 | 0.0058252 | 0.0014599 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-62_0_6_load_124 | 23 | 0.0029709 | 0.00074457 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-62_0_6_load_122 | 24 | 0.0033615 | 0.00084248 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-62_0_6_load_59 | 26 | 0.014832 | 0.0037172 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-62_0_6_load_128 | 29 | 0.0025728 | 0.0006448 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-62_0_6_load_72 | 32 | 0.011692 | 0.0029302 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-62_0_6_load_46 | 35 | 0.0031722 | 0.00079504 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-62_0_6_load_129 | 36 | 0.0026044 | 0.00065272 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-62_0_6_load_61 | 39 | 0.010003 | 0.0025069 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-62_0_6_load_54 | 42 | 0.0088079 | 0.0022075 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-62_0_6_load_123 | 43 | 0.0018984 | 0.00047579 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-62_0_6_load_126 | 45 | 0.005739 | 0.0014383 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-62_0_6_load_125 | 46 | 0.005739 | 0.0014383 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-62_0_6_load_41 | 47 | 0.0075846 | 0.0019009 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-62_0_6_load_18 | 48 | 0.0017209 | 0.00043131 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-62_0_6_load_19 | 49 | 0.0025779 | 0.00064609 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-62_0_6_load_16 | 51 | 0.068717 | 0.017222 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-62_0_6_load_133 | 52 | 0.0024858 | 0.00062301 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-62_0_6_load_121 | 54 | 0.013175 | 0.0033019 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-62_0_6_load_68 | 56 | 0.0059567 | 0.0014929 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-62_0_6_load_89 | 59 | 0.020745 | 0.0051992 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-62_0_6_load_20 | 60 | 0.0017285 | 0.00043321 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-62_0_6_load_69 | 62 | 0.0063655 | 0.0015953 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-62_0_6_load_21 | 63 | 0.0055538 | 0.0013919 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-62_0_6_load_137 | 66 | 0.0022299 | 0.00055886 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-62_0_6_load_147 | 67 | 0.0042778 | 0.0010721 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-62_0_6_load_145 | 69 | 0.003249 | 0.00081427 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-62_0_6_load_55 | 70 | 0.0066129 | 0.0016573 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-62_0_6_load_120 | 71 | 0.0062917 | 0.0015768 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-62_0_6_load_115 | 73 | 0.003247 | 0.00081377 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-62_0_6_load_135 | 74 | 0.0030741 | 0.00077044 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-62_0_6_load_62 | 77 | 0.0022722 | 0.00056946 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-62_0_6_load_52 | 78 | 0.014087 | 0.0035304 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-62_0_6_load_49 | 79 | 0.030064 | 0.0075348 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-62_0_6_load_48 | 80 | 0.032593 | 0.0081686 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-62_0_6_load_130 | 81 | 0.0047406 | 0.0011881 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-62_0_6_load_42 | 82 | 0.0036591 | 0.00091705 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-62_0_6_load_43 | 83 | 0.0032298 | 0.00080947 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-62_0_6_load_45 | 84 | 0.0046565 | 0.001167 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-62_0_6_load_47 | 85 | 0.0036745 | 0.00092093 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-62_0_6_load_50 | 86 | 0.015065 | 0.0037755 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-62_0_6_load_98 | 88 | 0.0012563 | 0.00031486 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-62_0_6_load_99 | 89 | 0.0014768 | 0.00037012 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-62_0_6_load_95 | 90 | 0.0028229 | 0.00070748 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-62_0_6_load_100 | 91 | 0.0046184 | 0.0011575 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-62_0_6_load_86 | 92 | 0.0043983 | 0.0011023 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-62_0_6_load_96 | 93 | 0.0026926 | 0.00067484 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-62_0_6_load_144 | 94 | 0.0030737 | 0.00077035 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-62_0_6_load_56 | 95 | 0.0077425 | 0.0019405 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-62_0_6_load_58 | 96 | 0.0066108 | 0.0016568 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-62_0_6_load_64 | 98 | 0.018397 | 0.0046107 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-62_0_6_load_70 | 99 | 0.011465 | 0.0028735 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-62_0_6_load_73 | 100 | 0.0026916 | 0.00067458 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-62_0_6_load_74 | 101 | 0.0021768 | 0.00054555 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-62_0_6_load_75 | 102 | 0.0023631 | 0.00059224 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-62_0_6_load_76 | 103 | 0.0022455 | 0.00056277 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-62_0_6_load_77 | 104 | 0.0049777 | 0.0012475 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-62_0_6_load_84 | 105 | 0.0021749 | 0.00054507 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-62_0_6_load_78 | 106 | 0.0014708 | 0.00036862 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-62_0_6_load_82 | 107 | 0.0034124 | 0.00085522 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-62_0_6_load_79 | 108 | 0.0084451 | 0.0021165 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-62_0_6_load_80 | 109 | 0.0040727 | 0.0010207 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-62_0_6_load_87 | 110 | 0.0016623 | 0.00041662 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-62_0_6_load_88 | 111 | 0.0016638 | 0.00041698 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-62_0_6_load_81 | 112 | 0.0057843 | 0.0014497 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-62_0_6_load_116 | 114 | 0.0028411 | 0.00071204 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-62_0_6_load_114 | 115 | 0.0054932 | 0.0013767 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-62_0_6_load_92 | 116 | 0.0050119 | 0.0012561 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-62_0_6_load_91 | 117 | 0.0030064 | 0.00075347 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-62_0_6_load_101 | 118 | 0.0012078 | 0.00030271 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-62_0_6_load_102 | 119 | 0.0027612 | 0.00069203 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-62_0_6_load_103 | 120 | 0.0021036 | 0.00052721 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-62_0_6_load_104 | 121 | 0.0018451 | 0.00046242 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-62_0_6_load_111 | 122 | 0.001933 | 0.00048445 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-62_0_6_load_105 | 124 | 0.0031618 | 0.00079243 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-62_0_6_load_106 | 125 | 0.0020408 | 0.00051147 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-62_0_6_load_110 | 126 | 0.0025231 | 0.00063235 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-62_0_6_load_134 | 127 | 0.003625 | 0.0009085 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-62_0_6_load_132 | 128 | 0.0029258 | 0.00073328 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_230-62_0_6_load_131 | 129 | 0.0029249 | 0.00073305 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_230-62_0_6_load_117 | 130 | 0.0041654 | 0.0010439 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_230-62_0_6_load_136 | 131 | 0.002786 | 0.00069825 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_230-62_0_6_load_139 | 133 | 0.0027886 | 0.00069888 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_230-62_0_6_load_140 | 134 | 0.0030711 | 0.00076968 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_230-62_0_6_load_141 | 135 | 0.0038766 | 0.00097156 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_230-62_0_6_load_142 | 136 | 0.0033204 | 0.00083218 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_230-62_0_6_load_143 | 137 | 0.0046957 | 0.0011769 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 93 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-62_0_6_line_0 |  | 0 | 1 | 0.019057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-62_0_6_line_1 |  | 0 | 2 | 0.013512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-62_0_6_line_2 |  | 2 | 3 | 0.02455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-62_0_6_line_3 |  | 3 | 4 | 0.014176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-62_0_6_line_4 |  | 4 | 5 | 0.017387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-62_0_6_line_5 |  | 4 | 6 | 0.015993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-62_0_6_line_6 |  | 5 | 50 | 0.037763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-62_0_6_line_7 |  | 5 | 51 | 0.026152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-62_0_6_line_8 |  | 7 | 8 | 0.019303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-62_0_6_line_9 |  | 7 | 9 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-62_0_6_line_10 |  | 7 | 10 | 0.01759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-62_0_6_line_11 |  | 8 | 52 | 0.0094493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-62_0_6_line_12 |  | 9 | 13 | 0.0081696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-62_0_6_line_13 |  | 11 | 12 | 0.13872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-62_0_6_line_14 |  | 11 | 13 | 0.0081831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-62_0_6_line_15 |  | 12 | 14 | 0.030233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-62_0_6_line_16 |  | 15 | 16 | 0.003588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-62_0_6_line_17 |  | 15 | 17 | 0.024522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-62_0_6_line_18 |  | 16 | 18 | 0.0090322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-62_0_6_line_19 |  | 17 | 58 | 0.020687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-62_0_6_line_20 |  | 18 | 59 | 0.016197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-62_0_6_line_21 |  | 19 | 20 | 0.013108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-62_0_6_line_22 |  | 19 | 21 | 0.0083702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-62_0_6_line_23 |  | 20 | 25 | 0.012453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_230-62_0_6_line_24 |  | 20 | 26 | 0.00092227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_230-62_0_6_line_25 |  | 21 | 63 | 0.023219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-62_0_6_line_26 |  | 22 | 23 | 0.011624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-62_0_6_line_27 |  | 22 | 24 | 0.010707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-62_0_6_line_28 |  | 23 | 27 | 0.028068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-62_0_6_line_29 |  | 24 | 43 | 0.012158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-62_0_6_line_30 |  | 25 | 33 | 0.003709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_230-62_0_6_line_31 |  | 26 | 37 | 0.031465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_230-62_0_6_line_32 |  | 27 | 28 | 0.037188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-62_0_6_line_33 |  | 27 | 29 | 0.037717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-62_0_6_line_34 |  | 28 | 47 | 0.013865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-62_0_6_line_35 |  | 29 | 36 | 0.009759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-62_0_6_line_36 |  | 30 | 31 | 0.019672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-62_0_6_line_37 |  | 30 | 32 | 0.017591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-62_0_6_line_38 |  | 31 | 39 | 0.016986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-62_0_6_line_39 |  | 32 | 61 | 0.037696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-62_0_6_line_40 |  | 33 | 70 | 0.030371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_230-62_0_6_line_41 |  | 33 | 40 | 0.010362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-62_0_6_line_42 |  | 34 | 35 | 0.012304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-62_0_6_line_43 |  | 34 | 36 | 0.010773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-62_0_6_line_44 |  | 35 | 75 | 0.0091702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-62_0_6_line_45 |  | 37 | 38 | 0.006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-62_0_6_line_46 |  | 37 | 39 | 0.025591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_230-62_0_6_line_47 |  | 38 | 76 | 0.012833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-62_0_6_line_48 |  | 38 | 77 | 0.017294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-62_0_6_line_49 |  | 40 | 41 | 0.023045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-62_0_6_line_50 |  | 40 | 42 | 0.0021592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-62_0_6_line_51 |  | 41 | 43 | 0.015935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-62_0_6_line_52 |  | 42 | 78 | 0.028498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-62_0_6_line_53 |  | 44 | 45 | 0.0095382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-62_0_6_line_54 |  | 44 | 46 | 0.018863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-62_0_6_line_55 |  | 45 | 81 | 0.002233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-62_0_6_line_56 |  | 48 | 49 | 0.0087608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-62_0_6_line_57 |  | 49 | 60 | 0.008545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-62_0_6_line_58 |  | 50 | 60 | 0.0019582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-62_0_6_line_59 |  | 50 | 61 | 0.022341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-62_0_6_line_60 |  | 52 | 129 | 0.008165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-62_0_6_line_61 |  | 53 | 54 | 0.011598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-62_0_6_line_62 |  | 53 | 55 | 0.003377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-62_0_6_line_63 |  | 54 | 72 | 0.019151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-62_0_6_line_64 |  | 55 | 93 | 0.020342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_230-62_0_6_line_65 |  | 55 | 96 | 0.015057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_230-62_0_6_line_66 |  | 56 | 57 | 0.049642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-62_0_6_line_67 |  | 57 | 98 | 0.017029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-62_0_6_line_68 |  | 58 | 67 | 0.011337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-62_0_6_line_69 |  | 59 | 117 | 0.0053891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-62_0_6_line_70 |  | 61 | 62 | 0.029246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-62_0_6_line_71 |  | 62 | 99 | 0.01202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-62_0_6_line_72 |  | 64 | 65 | 0.031544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-62_0_6_line_73 |  | 64 | 66 | 0.041386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-62_0_6_line_74 |  | 65 | 73 | 0.014165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-62_0_6_line_75 |  | 66 | 74 | 0.0086195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-62_0_6_line_76 |  | 67 | 68 | 0.023499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-62_0_6_line_77 |  | 68 | 69 | 0.018159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-62_0_6_line_78 |  | 69 | 94 | 0.0044531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-62_0_6_line_79 |  | 70 | 95 | 0.018517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_230-62_0_6_line_80 |  | 71 | 72 | 0.013389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-62_0_6_line_81 |  | 73 | 114 | 0.010561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-62_0_6_line_82 |  | 74 | 131 | 0.015295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_230-62_0_6_line_83 |  | 75 | 85 | 0.010184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-62_0_6_line_84 |  | 75 | 82 | 0.010721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-62_0_6_line_85 |  | 76 | 97 | 0.005682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-62_0_6_line_86 |  | 79 | 80 | 0.00022245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-62_0_6_line_87 |  | 80 | 86 | 0.0070562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-62_0_6_line_88 |  | 81 | 85 | 0.017794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-62_0_6_line_89 |  | 82 | 83 | 0.018398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-62_0_6_line_90 |  | 83 | 84 | 0.01062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-62_0_6_line_91 |  | 86 | 87 | 0.022799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-62_0_6_line_92 |  | 87 | 88 | 0.019219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-62_0_6_line_93 |  | 87 | 89 | 0.020248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_230-62_0_6_line_94 |  | 87 | 90 | 0.016744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_230-62_0_6_line_95 |  | 88 | 91 | 0.011906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-62_0_6_line_96 |  | 89 | 92 | 0.015398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_230-62_0_6_line_97 |  | 90 | 93 | 0.01891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_230-62_0_6_line_98 |  | 91 | 118 | 0.0066555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-62_0_6_line_99 |  | 92 | 113 | 0.028561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_230-62_0_6_line_100 |  | 94 | 134 | 0.008139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_230-62_0_6_line_101 |  | 95 | 96 | 0.019432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_230-62_0_6_line_102 |  | 97 | 98 | 0.018968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-62_0_6_line_103 |  | 100 | 101 | 0.0034911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-62_0_6_line_104 |  | 100 | 102 | 0.013856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-62_0_6_line_105 |  | 101 | 103 | 0.0029908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-62_0_6_line_106 |  | 102 | 104 | 0.010296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-62_0_6_line_107 |  | 103 | 105 | 0.0052469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-62_0_6_line_108 |  | 104 | 106 | 0.00078845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-62_0_6_line_109 |  | 105 | 107 | 0.017475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-62_0_6_line_110 |  | 106 | 108 | 0.018666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-62_0_6_line_111 |  | 107 | 112 | 0.0043429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_230-62_0_6_line_112 |  | 108 | 109 | 0.0016559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_230-62_0_6_line_113 |  | 109 | 110 | 0.018613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-62_0_6_line_114 |  | 110 | 111 | 0.00020726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-62_0_6_line_115 |  | 111 | 115 | 0.0025909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-62_0_6_line_116 |  | 112 | 113 | 0.015489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-62_0_6_line_117 |  | 114 | 130 | 0.018268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-62_0_6_line_118 |  | 115 | 116 | 0.01575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_230-62_0_6_line_119 |  | 116 | 117 | 0.0078506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-62_0_6_line_120 |  | 118 | 119 | 0.013216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-62_0_6_line_121 |  | 119 | 120 | 0.0029986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-62_0_6_line_122 |  | 120 | 121 | 0.012055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-62_0_6_line_123 |  | 121 | 122 | 0.0097082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-62_0_6_line_124 |  | 122 | 123 | 0.0076007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-62_0_6_line_125 |  | 123 | 126 | 0.013086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_230-62_0_6_line_126 |  | 123 | 125 | 0.013738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-62_0_6_line_127 |  | 124 | 125 | 0.0020387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-62_0_6_line_128 |  | 126 | 127 | 0.01366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_230-62_0_6_line_129 |  | 127 | 128 | 0.0011998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_230-62_0_6_line_130 |  | 128 | 129 | 0.010549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_230-62_0_6_line_131 |  | 131 | 132 | 0.017108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_230-62_0_6_line_132 |  | 132 | 133 | 0.010853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_230-62_0_6_line_133 |  | 132 | 134 | 0.026077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_230-62_0_6_line_134 |  | 133 | 135 | 0.0089026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-62_0_6_line_135 |  | 135 | 136 | 0.0080446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-62_0_6_line_136 |  | 136 | 137 | 0.0052603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-62_0_6_trafo_96 | 0.63 MVA 20/0.4 kV | 138 | 93 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2696531.5752 | 1262378.7321 | 2696524.9432 | 1262360.866
1 | 2696536.9473 | 1262390.8433 | 2696535.8206 | 1262390.1688 | 2696531.5752 | 1262378.7321
2 | 2696536.9473 | 1262390.8433 | 2696525.1838 | 1262412.3918
3 | 2696518.391 | 1262424.8348 | 2696525.1838 | 1262412.3918
4 | 2696518.391 | 1262424.8348 | 2696504.2559 | 1262414.6515
5 | 2696518.391 | 1262424.8348 | 2696510.7979 | 1262438.9107
6 | 2696467.8429 | 1262425.0438 | 2696504.2559 | 1262414.6515
7 | 2696504.2559 | 1262414.6515 | 2696497.0898 | 1262389.5003
8 | 2696399.0321 | 1262645.9463 | 2696395.335 | 1262643.9511 | 2696388.7155 | 1262630.3771
9 | 2696399.0321 | 1262645.9463 | 2696392.575 | 1262657.9509 | 2696390.0872 | 1262658.0326 | 2696388.3755 | 1262661.2
10 | 2696399.0321 | 1262645.9463 | 2696407.3627 | 1262630.4535
11 | 2696388.7155 | 1262630.3771 | 2696384.5737 | 1262621.8839
12 | 2696384.4913 | 1262668.3872 | 2696388.3755 | 1262661.2
13 | 2696433.6949 | 1262731.6478 | 2696363.7361 | 1262731.6521 | 2696369.1364 | 1262721.1427 | 2696385.8956 | 1262690.98 | 2696389.9934 | 1262683.652 | 2696391.9444 | 1262679.9808 | 2696386.9828 | 1262677.4423 | 2696383.1419 | 1262675.4892
14 | 2696383.1419 | 1262675.4892 | 2696385.4883 | 1262671.135 | 2696384.1361 | 1262669.0446 | 2696384.4913 | 1262668.3872
15 | 2696433.6949 | 1262731.6478 | 2696433.9098 | 1262701.4156
16 | 2696333.6541 | 1262691.674 | 2696333.0411 | 1262688.1389
17 | 2696333.6541 | 1262691.674 | 2696310.072 | 1262698.3978
18 | 2696333.0411 | 1262688.1389 | 2696331.1993 | 1262679.2965
19 | 2696289.5959 | 1262699.2628 | 2696297.9599 | 1262700.1553 | 2696307.0916 | 1262699.2476 | 2696310.072 | 1262698.3978
20 | 2696327.8966 | 1262663.4398 | 2696331.1993 | 1262679.2965
21 | 2696356.7922 | 1262384.8344 | 2696359.9872 | 1262390.8358 | 2696363.0013 | 1262396.3783
22 | 2696356.7922 | 1262384.8344 | 2696364.1138 | 1262380.7779
23 | 2696363.0013 | 1262396.3783 | 2696351.98 | 1262402.2368
24 | 2696363.8026 | 1262395.9217 | 2696363.0013 | 1262396.3783
25 | 2696384.424 | 1262369.525 | 2696364.1138 | 1262380.7779
26 | 2696333.7442 | 1262376.8747 | 2696328.7428 | 1262366.382
27 | 2696333.7442 | 1262376.8747 | 2696324.0473 | 1262381.4137
28 | 2696316.6659 | 1262341.0453 | 2696328.7428 | 1262366.382
29 | 2696324.0473 | 1262381.4137 | 2696316.1817 | 1262385.0954 | 2696317.6609 | 1262388.2378
30 | 2696348.6818 | 1262403.9512 | 2696351.98 | 1262402.2368
31 | 2696391.1423 | 1262380.3459 | 2696363.8026 | 1262395.9217
32 | 2696316.6659 | 1262341.0453 | 2696315.0411 | 1262337.6383 | 2696320.1152 | 1262335.1411 | 2696323.9725 | 1262333.3357 | 2696334.0096 | 1262354.5831
33 | 2696316.6659 | 1262341.0453 | 2696282.633 | 1262357.3039
34 | 2696334.0096 | 1262354.5831 | 2696346.5031 | 1262348.5709
35 | 2696282.633 | 1262357.3039 | 2696273.8272 | 1262361.5107
36 | 2696428.5832 | 1262360.073 | 2696445.8945 | 1262350.6364
37 | 2696445.8945 | 1262350.6364 | 2696447.7867 | 1262354.7373 | 2696451.3926 | 1262367.3047
38 | 2696428.5832 | 1262360.073 | 2696413.6464 | 1262368.1607
39 | 2696461.7891 | 1262403.5386 | 2696451.3926 | 1262367.3047
40 | 2696348.6818 | 1262403.9512 | 2696359.953 | 1262432.1536
41 | 2696339.5004 | 1262408.8056 | 2696348.6818 | 1262403.9512
42 | 2696264.1066 | 1262366.1546 | 2696266.9783 | 1262372.1173 | 2696269.4471 | 1262377.2391
43 | 2696264.1066 | 1262366.1546 | 2696273.8272 | 1262361.5107
44 | 2696273.4288 | 1262385.4998 | 2696269.4471 | 1262377.2391
45 | 2696391.1423 | 1262380.3459 | 2696393.7593 | 1262385.7485
46 | 2696391.1423 | 1262380.3459 | 2696413.6464 | 1262368.1607
47 | 2696398.9098 | 1262397.5087 | 2696393.7593 | 1262385.7485
48 | 2696393.7593 | 1262385.7485 | 2696386.7585 | 1262389.026 | 2696385.0303 | 1262392.8899 | 2696385.6293 | 1262394.045 | 2696387.428 | 1262397.6519
49 | 2696324.4478 | 1262402.6554 | 2696333.5264 | 1262397.6325 | 2696336.6488 | 1262403.4659 | 2696339.5004 | 1262408.8056
50 | 2696339.5004 | 1262408.8056 | 2696337.6085 | 1262409.8461
51 | 2696324.4478 | 1262402.6554 | 2696317.6609 | 1262388.2378
52 | 2696314.4529 | 1262425.3984 | 2696324.5624 | 1262420.1271 | 2696327.5026 | 1262415.4044 | 2696337.6085 | 1262409.8461
53 | 2696290.8556 | 1262421.2236 | 2696286.5486 | 1262412.7133 | 2696286.5486 | 1262412.7133
54 | 2696290.8556 | 1262421.2236 | 2696273.9795 | 1262429.6506
55 | 2696286.5486 | 1262412.7133 | 2696285.5789 | 1262410.7018
56 | 2696473.1545 | 1262443.561 | 2696470.7389 | 1262435.1398
57 | 2696470.7389 | 1262435.1398 | 2696468.3828 | 1262426.926
58 | 2696467.8429 | 1262425.0438 | 2696468.3828 | 1262426.926
59 | 2696461.7891 | 1262403.5386 | 2696465.0916 | 1262415.4133 | 2696467.8429 | 1262425.0438
60 | 2696380.9949 | 1262614.545 | 2696384.5737 | 1262621.8839
61 | 2696382.7133 | 1262479.9897 | 2696378.4498 | 1262469.2034
62 | 2696382.7133 | 1262479.9897 | 2696379.624 | 1262481.3738
63 | 2696371.41 | 1262451.3934 | 2696378.4498 | 1262469.2034
64 | 2696379.624 | 1262481.3738 | 2696361.1018 | 1262489.784
65 | 2696379.624 | 1262481.3738 | 2696374.0363 | 1262467.3924
66 | 2696410.5242 | 1262437.5194 | 2696437.3432 | 1262430.006 | 2696443.5568 | 1262450.8919
67 | 2696410.5242 | 1262437.5194 | 2696405.969 | 1262421.1111
68 | 2696289.5959 | 1262699.2628 | 2696278.6589 | 1262696.2763
69 | 2696327.8966 | 1262663.4398 | 2696326.7977 | 1262658.1638
70 | 2696461.7891 | 1262403.5386 | 2696457.5274 | 1262404.7368 | 2696439.7464 | 1262409.7176 | 2696438.099 | 1262403.5814
71 | 2696438.099 | 1262403.5814 | 2696434.9822 | 1262391.9721
72 | 2696228.5326 | 1262549.9475 | 2696199.7476 | 1262563.0344
73 | 2696199.7476 | 1262563.0344 | 2696217.0796 | 1262600.6164
74 | 2696228.5326 | 1262549.9475 | 2696234.4548 | 1262562.8151
75 | 2696220.6894 | 1262608.4436 | 2696217.0796 | 1262600.6164
76 | 2696255.9902 | 1262690.0862 | 2696278.6589 | 1262696.2763
77 | 2696255.9902 | 1262690.0862 | 2696254.8845 | 1262682.5732 | 2696250.4585 | 1262672.9798
78 | 2696248.5929 | 1262668.9363 | 2696250.4585 | 1262672.9798
79 | 2696359.953 | 1262432.1536 | 2696366.8248 | 1262449.3481
80 | 2696371.41 | 1262451.3934 | 2696366.4881 | 1262438.9414
81 | 2696234.4548 | 1262562.8151 | 2696238.8703 | 1262572.4092
82 | 2696220.6894 | 1262608.4436 | 2696227.0947 | 1262622.3327
83 | 2696273.4288 | 1262385.4998 | 2696277.8516 | 1262394.6738
84 | 2696273.4288 | 1262385.4998 | 2696283.1508 | 1262380.9809
85 | 2696398.9098 | 1262397.5087 | 2696400.8951 | 1262402.8343
86 | 2696316.3635 | 1262477.0571 | 2696316.4542 | 1262477.2602
87 | 2696316.4542 | 1262477.2602 | 2696319.3331 | 1262483.7025
88 | 2696277.8516 | 1262394.6738 | 2696285.5789 | 1262410.7018
89 | 2696295.7794 | 1262384.3698 | 2696292.2203 | 1262376.7652 | 2696283.1508 | 1262380.9809
90 | 2696300.281 | 1262393.9882 | 2696295.7794 | 1262384.3698
91 | 2696328.6348 | 1262504.5176 | 2696319.3331 | 1262483.7025
92 | 2696328.6348 | 1262504.5176 | 2696336.8168 | 1262521.9084
93 | 2696328.6348 | 1262504.5176 | 2696310.1975 | 1262512.8859
94 | 2696328.6348 | 1262504.5176 | 2696343.8824 | 1262497.5985
95 | 2696341.8855 | 1262532.6818 | 2696336.8168 | 1262521.9084
96 | 2696310.1975 | 1262512.8859 | 2696296.176 | 1262519.25
97 | 2696343.8824 | 1262497.5985 | 2696358.7484 | 1262490.8525 | 2696361.1018 | 1262489.784
98 | 2696341.8855 | 1262532.6818 | 2696344.7189 | 1262538.704
99 | 2696270.1689 | 1262531.0541 | 2696296.176 | 1262519.25
100 | 2696245.1833 | 1262661.546 | 2696248.5929 | 1262668.9363
101 | 2696366.8248 | 1262449.3481 | 2696374.0363 | 1262467.3924
102 | 2696400.8951 | 1262402.8343 | 2696405.969 | 1262421.1111
103 | 2696290.6533 | 1262575.6063 | 2696289.1949 | 1262572.4345
104 | 2696290.6533 | 1262575.6063 | 2696296.4418 | 1262588.1958
105 | 2696289.1949 | 1262572.4345 | 2696287.9455 | 1262569.7171
106 | 2696296.4418 | 1262588.1958 | 2696300.7429 | 1262597.5506
107 | 2696285.7537 | 1262564.9499 | 2696287.9455 | 1262569.7171
108 | 2696300.7429 | 1262597.5506 | 2696301.0723 | 1262598.267
109 | 2696278.4534 | 1262549.0724 | 2696285.7537 | 1262564.9499
110 | 2696301.0723 | 1262598.267 | 2696304.4725 | 1262605.6621 | 2696308.9601 | 1262615.1844
111 | 2696276.6392 | 1262545.1267 | 2696278.4534 | 1262549.0724
112 | 2696309.666 | 1262616.6823 | 2696308.9601 | 1262615.1844
113 | 2696309.666 | 1262616.6823 | 2696317.6007 | 1262633.5189
114 | 2696317.6007 | 1262633.5189 | 2696317.689 | 1262633.7064
115 | 2696318.7935 | 1262636.0501 | 2696317.689 | 1262633.7064
116 | 2696270.1689 | 1262531.0541 | 2696276.6392 | 1262545.1267
117 | 2696248.5887 | 1262587.5266 | 2696243.6258 | 1262582.742 | 2696238.8703 | 1262572.4092
118 | 2696318.7935 | 1262636.0501 | 2696321.9005 | 1262642.6427 | 2696324.8141 | 1262650.5876
119 | 2696326.7977 | 1262658.1638 | 2696325.7528 | 1262653.1473 | 2696324.8141 | 1262650.5876
120 | 2696350.3451 | 1262550.6625 | 2696344.7189 | 1262538.704
121 | 2696350.3451 | 1262550.6625 | 2696351.6217 | 1262553.3758
122 | 2696356.7537 | 1262564.2839 | 2696351.6217 | 1262553.3758
123 | 2696356.7537 | 1262564.2839 | 2696360.8867 | 1262573.0684
124 | 2696364.1225 | 1262579.946 | 2696360.8867 | 1262573.0684
125 | 2696364.1225 | 1262579.946 | 2696369.8583 | 1262591.7079
126 | 2696364.1225 | 1262579.946 | 2696376.7057 | 1262574.4336
127 | 2696378.5731 | 1262573.6156 | 2696376.7057 | 1262574.4336
128 | 2696369.8583 | 1262591.7079 | 2696375.8454 | 1262603.9854
129 | 2696376.3713 | 1262605.0638 | 2696375.8454 | 1262603.9854
130 | 2696380.9949 | 1262614.545 | 2696376.3713 | 1262605.0638
131 | 2696234.2592 | 1262637.8678 | 2696227.0947 | 1262622.3327
132 | 2696234.2592 | 1262637.8678 | 2696244.0634 | 1262633.2123
133 | 2696234.2592 | 1262637.8678 | 2696245.1833 | 1262661.546
134 | 2696244.0634 | 1262633.2123 | 2696252.1054 | 1262629.3937
135 | 2696252.1054 | 1262629.3937 | 2696259.3724 | 1262625.943
136 | 2696264.1242 | 1262623.6867 | 2696259.3724 | 1262625.943

## bus_geodata
| x | y | coords
0 | 2696531.5752 | 1262378.7321
1 | 2696524.9432 | 1262360.866
2 | 2696536.9473 | 1262390.8433
3 | 2696525.1838 | 1262412.3918
4 | 2696518.391 | 1262424.8348
5 | 2696504.2559 | 1262414.6515
6 | 2696510.7979 | 1262438.9107
7 | 2696399.0321 | 1262645.9463
8 | 2696388.7155 | 1262630.3771
9 | 2696388.3755 | 1262661.2
10 | 2696407.3627 | 1262630.4535
11 | 2696383.1419 | 1262675.4892
12 | 2696433.6949 | 1262731.6478
13 | 2696384.4913 | 1262668.3872
14 | 2696433.9098 | 1262701.4156
15 | 2696333.6541 | 1262691.674
16 | 2696333.0411 | 1262688.1389
17 | 2696310.072 | 1262698.3978
18 | 2696331.1993 | 1262679.2965
19 | 2696356.7922 | 1262384.8344
20 | 2696363.0013 | 1262396.3783
21 | 2696364.1138 | 1262380.7779
22 | 2696333.7442 | 1262376.8747
23 | 2696328.7428 | 1262366.382
24 | 2696324.0473 | 1262381.4137
25 | 2696351.98 | 1262402.2368
26 | 2696363.8026 | 1262395.9217
27 | 2696316.6659 | 1262341.0453
28 | 2696334.0096 | 1262354.5831
29 | 2696282.633 | 1262357.3039
30 | 2696445.8945 | 1262350.6364
31 | 2696428.5832 | 1262360.073
32 | 2696451.3926 | 1262367.3047
33 | 2696348.6818 | 1262403.9512
34 | 2696264.1066 | 1262366.1546
35 | 2696269.4471 | 1262377.2391
36 | 2696273.8272 | 1262361.5107
37 | 2696391.1423 | 1262380.3459
38 | 2696393.7593 | 1262385.7485
39 | 2696413.6464 | 1262368.1607
40 | 2696339.5004 | 1262408.8056
41 | 2696324.4478 | 1262402.6554
42 | 2696337.6085 | 1262409.8461
43 | 2696317.6609 | 1262388.2378
44 | 2696290.8556 | 1262421.2236
45 | 2696286.5486 | 1262412.7133
46 | 2696273.9795 | 1262429.6506
47 | 2696346.5031 | 1262348.5709
48 | 2696473.1545 | 1262443.561
49 | 2696470.7389 | 1262435.1398
50 | 2696467.8429 | 1262425.0438
51 | 2696497.0898 | 1262389.5003
52 | 2696384.5737 | 1262621.8839
53 | 2696382.7133 | 1262479.9897
54 | 2696378.4498 | 1262469.2034
55 | 2696379.624 | 1262481.3738
56 | 2696443.5568 | 1262450.8919
57 | 2696410.5242 | 1262437.5194
58 | 2696289.5959 | 1262699.2628
59 | 2696327.8966 | 1262663.4398
60 | 2696468.3828 | 1262426.926
61 | 2696461.7891 | 1262403.5386
62 | 2696438.099 | 1262403.5814
63 | 2696384.424 | 1262369.525
64 | 2696199.7476 | 1262563.0344
65 | 2696228.5326 | 1262549.9475
66 | 2696217.0796 | 1262600.6164
67 | 2696278.6589 | 1262696.2763
68 | 2696255.9902 | 1262690.0862
69 | 2696250.4585 | 1262672.9798
70 | 2696359.953 | 1262432.1536
71 | 2696366.4881 | 1262438.9414
72 | 2696371.41 | 1262451.3934
73 | 2696234.4548 | 1262562.8151
74 | 2696220.6894 | 1262608.4436
75 | 2696273.4288 | 1262385.4998
76 | 2696398.9098 | 1262397.5087
77 | 2696387.428 | 1262397.6519
78 | 2696314.4529 | 1262425.3984
79 | 2696316.3635 | 1262477.0571
80 | 2696316.4542 | 1262477.2602
81 | 2696285.5789 | 1262410.7018
82 | 2696283.1508 | 1262380.9809
83 | 2696295.7794 | 1262384.3698
84 | 2696300.281 | 1262393.9882
85 | 2696277.8516 | 1262394.6738
86 | 2696319.3331 | 1262483.7025
87 | 2696328.6348 | 1262504.5176
88 | 2696336.8168 | 1262521.9084
89 | 2696310.1975 | 1262512.8859
90 | 2696343.8824 | 1262497.5985
91 | 2696341.8855 | 1262532.6818
92 | 2696296.176 | 1262519.25
93 | 2696361.1018 | 1262489.784
94 | 2696248.5929 | 1262668.9363
95 | 2696366.8248 | 1262449.3481
96 | 2696374.0363 | 1262467.3924
97 | 2696400.8951 | 1262402.8343
98 | 2696405.969 | 1262421.1111
99 | 2696434.9822 | 1262391.9721
100 | 2696290.6533 | 1262575.6063
101 | 2696289.1949 | 1262572.4345
102 | 2696296.4417 | 1262588.1958
103 | 2696287.9455 | 1262569.7171
104 | 2696300.7429 | 1262597.5506
105 | 2696285.7537 | 1262564.9499
106 | 2696301.0723 | 1262598.267
107 | 2696278.4534 | 1262549.0724
108 | 2696308.9601 | 1262615.1844
109 | 2696309.666 | 1262616.6823
110 | 2696317.6007 | 1262633.5189
111 | 2696317.689 | 1262633.7064
112 | 2696276.6392 | 1262545.1267
113 | 2696270.1689 | 1262531.0541
114 | 2696238.8703 | 1262572.4092
115 | 2696318.7935 | 1262636.0501
116 | 2696324.8141 | 1262650.5876
117 | 2696326.7977 | 1262658.1638
118 | 2696344.7189 | 1262538.704
119 | 2696350.3451 | 1262550.6625
120 | 2696351.6217 | 1262553.3758
121 | 2696356.7537 | 1262564.2839
122 | 2696360.8867 | 1262573.0684
123 | 2696364.1225 | 1262579.946
124 | 2696378.5731 | 1262573.6156
125 | 2696376.7057 | 1262574.4336
126 | 2696369.8583 | 1262591.7079
127 | 2696375.8454 | 1262603.9854
128 | 2696376.3713 | 1262605.0638
129 | 2696380.9949 | 1262614.545
130 | 2696248.5887 | 1262587.5267
131 | 2696227.0947 | 1262622.3327
132 | 2696234.2592 | 1262637.8678
133 | 2696244.0634 | 1262633.2123
134 | 2696245.1833 | 1262661.546
135 | 2696252.1054 | 1262629.3937
136 | 2696259.3724 | 1262625.943
137 | 2696264.1242 | 1262623.6867
138 | 2696379.624 | 1262481.3738

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97092 | -0.56077 | 0.0071879 | 0.0018015
1 | 0.97085 | -0.56213 | 0.0038642 | 0.00096847
2 | 0.97106 | -0.558 | 0 | 0
3 | 0.97131 | -0.55299 | 0.0033598 | 0.00084204
4 | 0.9715 | -0.54922 | 0 | 0
5 | 0.9718 | -0.54328 | 0 | 0
6 | 0.97144 | -0.55042 | 0.0040798 | 0.0010225
7 | 0.99166 | -0.16008 | 0 | 0
8 | 0.99196 | -0.15421 | 0.0024823 | 0.00062213
9 | 0.99145 | -0.16414 | 0.0029907 | 0.00074954
10 | 0.99157 | -0.16182 | 0.0055685 | 0.0013956
11 | 0.99136 | -0.16601 | 0 | 0
12 | 0.99081 | -0.17659 | 0 | 0
13 | 0.99139 | -0.16538 | 0.0043059 | 0.0010792
14 | 0.99069 | -0.1789 | 0.0042969 | 0.0010769
15 | 0.97839 | -0.41528 | 0 | 0
16 | 0.97856 | -0.41207 | 0 | 0
17 | 0.97727 | -0.43721 | 0.0023514 | 0.00058932
18 | 0.97897 | -0.40401 | 0.0040998 | 0.0010275
19 | 0.99001 | -0.19004 | 0 | 0
20 | 0.99014 | -0.18738 | 0 | 0
21 | 0.98992 | -0.19173 | 0.0058252 | 0.0014599
22 | 0.98723 | -0.24397 | 0 | 0
23 | 0.98669 | -0.25444 | 0.0029709 | 0.00074457
24 | 0.98772 | -0.23433 | 0.0033615 | 0.00084248
25 | 0.99086 | -0.1737 | 0 | 0
26 | 0.99009 | -0.18834 | 0.014832 | 0.0037172
27 | 0.98546 | -0.27828 | 0 | 0
28 | 0.9852 | -0.28334 | 0 | 0
29 | 0.98407 | -0.30526 | 0.0025728 | 0.0006448
30 | 0.98275 | -0.32933 | 0 | 0
31 | 0.98501 | -0.28585 | 0 | 0
32 | 0.98074 | -0.36838 | 0.011692 | 0.0029302
33 | 0.99107 | -0.16962 | 0 | 0
34 | 0.9834 | -0.31851 | 0 | 0
35 | 0.983 | -0.32619 | 0.0031722 | 0.00079504
36 | 0.98374 | -0.31179 | 0.0026044 | 0.00065272
37 | 0.98854 | -0.21811 | 0 | 0
38 | 0.98839 | -0.22096 | 0 | 0
39 | 0.98695 | -0.24846 | 0.010003 | 0.0025069
40 | 0.99032 | -0.18407 | 0 | 0
41 | 0.98914 | -0.20687 | 0 | 0
42 | 0.99028 | -0.18495 | 0.0088079 | 0.0022075
43 | 0.98833 | -0.22267 | 0.0018984 | 0.00047579
44 | 0.98221 | -0.34172 | 0 | 0
45 | 0.98226 | -0.34073 | 0.005739 | 0.0014383
46 | 0.98211 | -0.34367 | 0.005739 | 0.0014383
47 | 0.9851 | -0.28523 | 0.0075846 | 0.0019009
48 | 0.97482 | -0.48386 | 0.0017209 | 0.00043131
49 | 0.97484 | -0.48358 | 0.0025779 | 0.00064609
50 | 0.97488 | -0.48269 | 0 | 0
51 | 0.97012 | -0.5765 | 0.068717 | 0.017222
52 | 0.99213 | -0.15092 | 0.0024858 | 0.00062301
53 | 0.99803 | -0.037215 | 0 | 0
54 | 0.99783 | -0.041167 | 0.013175 | 0.0033019
55 | 0.99809 | -0.036065 | 0 | 0
56 | 0.98719 | -0.24436 | 0.0059567 | 0.0014929
57 | 0.98746 | -0.23908 | 0 | 0
58 | 0.97637 | -0.45486 | 0 | 0
59 | 0.97977 | -0.38837 | 0.020745 | 0.0051992
60 | 0.97487 | -0.48291 | 0.0017285 | 0.00043321
61 | 0.97683 | -0.44456 | 0 | 0
62 | 0.97634 | -0.45409 | 0.0063655 | 0.0015953
63 | 0.9898 | -0.19402 | 0.0055538 | 0.0013919
64 | 0.97198 | -0.54137 | 0 | 0
65 | 0.97168 | -0.54734 | 0 | 0
66 | 0.97238 | -0.53354 | 0.0022299 | 0.00055886
67 | 0.97588 | -0.46454 | 0.0042778 | 0.0010721
68 | 0.97495 | -0.48281 | 0 | 0
69 | 0.97423 | -0.49694 | 0.003249 | 0.00081427
70 | 0.99355 | -0.12229 | 0.0066129 | 0.0016573
71 | 0.99764 | -0.044752 | 0.0062917 | 0.0015768
72 | 0.99772 | -0.043276 | 0 | 0
73 | 0.97154 | -0.55002 | 0.003247 | 0.00081377
74 | 0.97248 | -0.53156 | 0.0030741 | 0.00077044
75 | 0.98274 | -0.33139 | 0 | 0
76 | 0.98811 | -0.22654 | 0 | 0
77 | 0.98836 | -0.22166 | 0.0022722 | 0.00056946
78 | 0.98991 | -0.19209 | 0.014087 | 0.0035304
79 | 0.99502 | -0.095263 | 0.030064 | 0.0075348
80 | 0.99502 | -0.095145 | 0.032593 | 0.0081686
81 | 0.98228 | -0.34026 | 0.0047406 | 0.0011881
82 | 0.98262 | -0.33363 | 0.0036591 | 0.00091705
83 | 0.98249 | -0.33625 | 0.0032298 | 0.00080947
84 | 0.98244 | -0.33714 | 0.0046565 | 0.001167
85 | 0.98255 | -0.33505 | 0.0036745 | 0.00092093
86 | 0.99543 | -0.087365 | 0.015065 | 0.0037755
87 | 0.99704 | -0.056246 | 0 | 0
88 | 0.99608 | -0.074821 | 0.0012563 | 0.00031486
89 | 0.99619 | -0.072406 | 0.0014768 | 0.00037012
90 | 0.99842 | -0.029936 | 0.0028229 | 0.00070748
91 | 0.99549 | -0.086083 | 0.0046184 | 0.0011575
92 | 0.99555 | -0.08458 | 0.0043983 | 0.0011023
93 | 1 | 0 | -0.58646 | -0.14975
94 | 0.97407 | -0.50015 | 0.0030737 | 0.00077035
95 | 0.9951 | -0.092831 | 0.0077425 | 0.0019405
96 | 0.99677 | -0.061133 | 0.0066108 | 0.0016568
97 | 0.98798 | -0.22901 | 0 | 0
98 | 0.98755 | -0.23726 | 0.018397 | 0.0046107
99 | 0.97622 | -0.45661 | 0.011465 | 0.0028735
100 | 0.9882 | -0.22499 | 0.0026916 | 0.00067458
101 | 0.98857 | -0.21784 | 0.0021768 | 0.00054555
102 | 0.98676 | -0.25274 | 0.0023631 | 0.00059224
103 | 0.9889 | -0.2116 | 0.0022455 | 0.00056277
104 | 0.98571 | -0.27298 | 0.0049777 | 0.0012475
105 | 0.98948 | -0.20046 | 0.0021749 | 0.00054507
106 | 0.98564 | -0.27447 | 0.0014708 | 0.00036862
107 | 0.99144 | -0.16278 | 0.0034124 | 0.00085522
108 | 0.98385 | -0.30911 | 0.0084451 | 0.0021165
109 | 0.9837 | -0.31194 | 0.0040727 | 0.0010207
110 | 0.98213 | -0.34241 | 0.0016623 | 0.00041662
111 | 0.98211 | -0.34274 | 0.0016638 | 0.00041698
112 | 0.99195 | -0.15318 | 0.0057843 | 0.0014497
113 | 0.99382 | -0.11742 | 0 | 0
114 | 0.97147 | -0.55139 | 0.0028411 | 0.00071204
115 | 0.9819 | -0.34683 | 0.0054932 | 0.0013767
116 | 0.9807 | -0.37019 | 0.0050119 | 0.0012561
117 | 0.98014 | -0.38114 | 0.0030064 | 0.00075347
118 | 0.99519 | -0.091843 | 0.0012078 | 0.00030271
119 | 0.99461 | -0.10301 | 0.0027612 | 0.00069203
120 | 0.99449 | -0.1054 | 0.0021036 | 0.00052721
121 | 0.99401 | -0.11457 | 0.0018451 | 0.00046242
122 | 0.99365 | -0.12164 | 0.001933 | 0.00048445
123 | 0.99337 | -0.12692 | 0 | 0
124 | 0.9933 | -0.12829 | 0.0031618 | 0.00079243
125 | 0.99331 | -0.12818 | 0.0020408 | 0.00051147
126 | 0.99297 | -0.13481 | 0.0025231 | 0.00063235
127 | 0.99257 | -0.14245 | 0.003625 | 0.0009085
128 | 0.99254 | -0.14304 | 0.0029258 | 0.00073328
129 | 0.9923 | -0.14772 | 0.0029249 | 0.00073305
130 | 0.9714 | -0.55279 | 0.0041654 | 0.0010439
131 | 0.9727 | -0.52717 | 0.002786 | 0.00069825
132 | 0.97299 | -0.52139 | 0 | 0
133 | 0.97284 | -0.52433 | 0.0027886 | 0.00069888
134 | 0.9738 | -0.50555 | 0.0030711 | 0.00076968
135 | 0.97274 | -0.52628 | 0.0038766 | 0.00097156
136 | 0.97268 | -0.52746 | 0.0033204 | 0.00083218
137 | 0.97266 | -0.52792 | 0.0046957 | 0.0011769
138 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0038645 | 0.00096839 | -0.0038642 | -0.00096847 | 2.5068e-07 | -7.5235e-08 | 0.0059226 | 0.0059227 | 0.0059227 | 0.97092 | -0.56077 | 0.97085 | -0.56213 | 1.6271
1 | -0.011052 | -0.0027699 | 0.011054 | 0.0027706 | 1.4539e-06 | 7.6333e-07 | 0.016939 | 0.016939 | 0.016939 | 0.97092 | -0.56077 | 0.97106 | -0.558 | 4.6535
2 | -0.011054 | -0.0027706 | 0.011056 | 0.002772 | 2.6414e-06 | 1.3867e-06 | 0.016939 | 0.016938 | 0.016939 | 0.97106 | -0.558 | 0.97131 | -0.55299 | 4.6535
3 | -0.014416 | -0.003614 | 0.014419 | 0.0036155 | 2.5931e-06 | 1.4841e-06 | 0.022086 | 0.022085 | 0.022086 | 0.97131 | -0.55299 | 0.9715 | -0.54922 | 6.0675
4 | -0.018499 | -0.004638 | 0.018504 | 0.0046411 | 5.2347e-06 | 3.1348e-06 | 0.028335 | 0.028335 | 0.028335 | 0.9715 | -0.54922 | 0.9718 | -0.54328 | 7.7843
5 | 0.00408 | 0.0010224 | -0.0040798 | -0.0010225 | 2.3422e-07 | -4.8121e-08 | 0.0062492 | 0.0062492 | 0.0062492 | 0.9715 | -0.54922 | 0.97144 | -0.55042 | 1.7168
6 | -0.08733 | -0.021933 | 0.087583 | 0.022094 | 0.00025327 | 0.00016163 | 0.13374 | 0.13374 | 0.13374 | 0.9718 | -0.54328 | 0.97488 | -0.48269 | 36.7405
7 | 0.068826 | 0.017292 | -0.068717 | -0.017222 | 0.00010895 | 6.9405e-05 | 0.1054 | 0.1054 | 0.1054 | 0.9718 | -0.54328 | 0.97012 | -0.5765 | 28.9563
8 | -0.017168 | -0.0043022 | 0.017173 | 0.004305 | 4.8037e-06 | 2.8253e-06 | 0.025761 | 0.025761 | 0.025761 | 0.99166 | -0.16008 | 0.99196 | -0.15421 | 7.0772
9 | 0.011599 | 0.0029065 | -0.011597 | -0.0029053 | 2.2401e-06 | 1.1793e-06 | 0.017405 | 0.017405 | 0.017405 | 0.99166 | -0.16008 | 0.99145 | -0.16414 | 4.7815
10 | 0.0055689 | 0.0013957 | -0.0055685 | -0.0013956 | 4.6062e-07 | 6.7876e-08 | 0.0083563 | 0.0083564 | 0.0083564 | 0.99166 | -0.16008 | 0.99157 | -0.16182 | 2.2957
11 | -0.019655 | -0.0049271 | 0.019658 | 0.004929 | 3.0805e-06 | 1.8495e-06 | 0.029484 | 0.029484 | 0.029484 | 0.99196 | -0.15421 | 0.99213 | -0.15092 | 8.1001
12 | 0.0086061 | 0.0021558 | -0.0086056 | -0.0021556 | 5.1108e-07 | 2.2175e-07 | 0.012916 | 0.012916 | 0.012916 | 0.99145 | -0.16414 | 0.99139 | -0.16538 | 3.5484
13 | 0.0042996 | 0.0010764 | -0.0042974 | -0.0010768 | 2.1665e-06 | -4.0099e-07 | 0.0064532 | 0.0064539 | 0.0064539 | 0.99136 | -0.16601 | 0.99081 | -0.17659 | 1.773
14 | -0.0042996 | -0.0010764 | 0.0042997 | 0.0010764 | 1.2779e-07 | -2.3725e-08 | 0.0064532 | 0.0064532 | 0.0064532 | 0.99136 | -0.16601 | 0.99139 | -0.16538 | 1.7729
15 | 0.0042974 | 0.0010768 | -0.0042969 | -0.0010769 | 4.7224e-07 | -8.7099e-08 | 0.0064539 | 0.006454 | 0.006454 | 0.99081 | -0.17659 | 0.99069 | -0.1789 | 1.7731
16 | -0.049289 | -0.012443 | 0.049296 | 0.012448 | 7.5673e-06 | 4.798e-06 | 0.074994 | 0.074994 | 0.074994 | 0.97839 | -0.41528 | 0.97856 | -0.41207 | 20.6029
17 | 0.049289 | 0.012443 | -0.049237 | -0.01241 | 5.1718e-05 | 3.2792e-05 | 0.074994 | 0.074995 | 0.074995 | 0.97839 | -0.41528 | 0.97727 | -0.43721 | 20.6029
18 | -0.049296 | -0.012448 | 0.049315 | 0.01246 | 1.9049e-05 | 1.2078e-05 | 0.074994 | 0.074994 | 0.074994 | 0.97856 | -0.41207 | 0.97897 | -0.40401 | 20.6029
19 | 0.046886 | 0.011821 | -0.046846 | -0.011796 | 3.9565e-05 | 2.5062e-05 | 0.071414 | 0.071414 | 0.071414 | 0.97727 | -0.43721 | 0.97637 | -0.45486 | 19.6193
20 | -0.053415 | -0.013487 | 0.053455 | 0.013513 | 4.0073e-05 | 2.5443e-05 | 0.081226 | 0.081226 | 0.081226 | 0.97897 | -0.40401 | 0.97977 | -0.38837 | 22.3148
21 | -0.01138 | -0.0028524 | 0.011382 | 0.0028532 | 1.4382e-06 | 7.5189e-07 | 0.017105 | 0.017105 | 0.017105 | 0.99001 | -0.19004 | 0.99014 | -0.18738 | 4.6993
22 | 0.01138 | 0.0028524 | -0.01138 | -0.0028519 | 9.184e-07 | 4.8016e-07 | 0.017105 | 0.017105 | 0.017105 | 0.99001 | -0.19004 | 0.98992 | -0.19173 | 4.6993
23 | -0.18775 | -0.047882 | 0.18787 | 0.04796 | 0.00012418 | 7.8994e-05 | 0.28245 | 0.28244 | 0.28245 | 0.99014 | -0.18738 | 0.99086 | -0.1737 | 25.8649
24 | 0.17636 | 0.045028 | -0.17636 | -0.045023 | 8.1166e-06 | 5.159e-06 | 0.26534 | 0.26534 | 0.26534 | 0.99014 | -0.18738 | 0.99009 | -0.18834 | 24.2985
25 | 0.0055544 | 0.001392 | -0.0055538 | -0.0013919 | 6.0697e-07 | 8.9986e-08 | 0.0083491 | 0.0083492 | 0.0083492 | 0.98992 | -0.19173 | 0.9898 | -0.19402 | 2.2937
26 | 0.050531 | 0.012734 | -0.050506 | -0.012718 | 2.5302e-05 | 1.6045e-05 | 0.076188 | 0.076188 | 0.076188 | 0.98723 | -0.24397 | 0.98669 | -0.25444 | 20.9309
27 | -0.050531 | -0.012734 | 0.050554 | 0.012749 | 2.3306e-05 | 1.4779e-05 | 0.076188 | 0.076188 | 0.076188 | 0.98723 | -0.24397 | 0.98772 | -0.23433 | 20.9309
28 | 0.047535 | 0.011973 | -0.047481 | -0.011939 | 5.4122e-05 | 3.428e-05 | 0.071708 | 0.071708 | 0.071708 | 0.98669 | -0.25444 | 0.98546 | -0.27828 | 19.7001
29 | -0.053916 | -0.013591 | 0.053946 | 0.01361 | 3.01e-05 | 1.9108e-05 | 0.081253 | 0.081252 | 0.081253 | 0.98772 | -0.23433 | 0.98833 | -0.22267 | 22.3221
30 | -0.18787 | -0.04796 | 0.18791 | 0.047984 | 3.6986e-05 | 2.3528e-05 | 0.28244 | 0.28244 | 0.28244 | 0.99086 | -0.1737 | 0.99107 | -0.16962 | 25.8649
31 | 0.16152 | 0.041306 | -0.16129 | -0.041159 | 0.00023234 | 0.00014749 | 0.24305 | 0.24305 | 0.24305 | 0.99009 | -0.18834 | 0.98854 | -0.21811 | 22.2573
32 | 0.0075871 | 0.0019018 | -0.0075852 | -0.0019011 | 1.8303e-06 | 6.9775e-07 | 0.011456 | 0.011457 | 0.011457 | 0.98546 | -0.27828 | 0.9852 | -0.28334 | 3.1474
33 | 0.039893 | 0.010037 | -0.039842 | -0.010005 | 5.1347e-05 | 3.2382e-05 | 0.060252 | 0.060252 | 0.060252 | 0.98546 | -0.27828 | 0.98407 | -0.30526 | 16.5527
34 | 0.0075852 | 0.0019011 | -0.0075846 | -0.0019009 | 6.8243e-07 | 2.6022e-07 | 0.011457 | 0.011457 | 0.011457 | 0.9852 | -0.28334 | 0.9851 | -0.28523 | 3.1474
35 | 0.037269 | 0.0093599 | -0.037258 | -0.0093526 | 1.1625e-05 | 7.3163e-06 | 0.056362 | 0.056362 | 0.056362 | 0.98407 | -0.30526 | 0.98374 | -0.31179 | 15.484
36 | -0.12396 | -0.031529 | 0.12422 | 0.031695 | 0.00026032 | 0.00016636 | 0.18785 | 0.18785 | 0.18785 | 0.98275 | -0.32933 | 0.98501 | -0.28585 | 51.6076
37 | 0.12396 | 0.031529 | -0.12372 | -0.03138 | 0.00023278 | 0.00014876 | 0.18785 | 0.18785 | 0.18785 | 0.98275 | -0.32933 | 0.98074 | -0.36838 | 51.6076
38 | -0.12422 | -0.031695 | 0.12444 | 0.031839 | 0.00022477 | 0.00014364 | 0.18785 | 0.18785 | 0.18785 | 0.98501 | -0.28585 | 0.98695 | -0.24846 | 51.6075
39 | 0.11203 | 0.02845 | -0.11162 | -0.028188 | 0.00040907 | 0.00026133 | 0.17011 | 0.17011 | 0.17011 | 0.98074 | -0.36838 | 0.97683 | -0.44456 | 46.7343
40 | -0.26681 | -0.067912 | 0.26742 | 0.068301 | 0.00061036 | 0.00038945 | 0.40096 | 0.40096 | 0.40096 | 0.99107 | -0.16962 | 0.99355 | -0.12229 | 36.7184
41 | 0.078902 | 0.019928 | -0.078848 | -0.019893 | 5.4583e-05 | 3.48e-05 | 0.11852 | 0.11852 | 0.11852 | 0.99107 | -0.16962 | 0.99032 | -0.18407 | 32.5604
42 | 0.034642 | 0.0086929 | -0.034629 | -0.0086849 | 1.268e-05 | 7.959e-06 | 0.052422 | 0.052422 | 0.052422 | 0.9834 | -0.31851 | 0.983 | -0.32619 | 14.4018
43 | -0.034642 | -0.0086929 | 0.034653 | 0.0086998 | 1.1102e-05 | 6.9685e-06 | 0.052422 | 0.052422 | 0.052422 | 0.9834 | -0.31851 | 0.98374 | -0.31179 | 14.4017
44 | 0.031457 | 0.0078899 | -0.031449 | -0.007885 | 7.7983e-06 | 4.8747e-06 | 0.04762 | 0.04762 | 0.04762 | 0.983 | -0.32619 | 0.98274 | -0.33139 | 13.0825
45 | 0.02665 | 0.0066872 | -0.026647 | -0.0066849 | 3.6214e-06 | 2.2408e-06 | 0.040119 | 0.040119 | 0.040119 | 0.98854 | -0.21811 | 0.98839 | -0.22096 | 11.0217
46 | 0.13464 | 0.034471 | -0.13444 | -0.034346 | 0.0001976 | 0.00012581 | 0.20293 | 0.20293 | 0.20293 | 0.98854 | -0.21811 | 0.98695 | -0.24846 | 27.8753
47 | 0.024375 | 0.0061157 | -0.024368 | -0.0061117 | 6.4811e-06 | 3.9835e-06 | 0.036698 | 0.036698 | 0.036698 | 0.98839 | -0.22096 | 0.98811 | -0.22654 | 10.0819
48 | 0.0022722 | 0.00056928 | -0.0022722 | -0.00056946 | 7.5892e-08 | -1.7308e-07 | 0.0034208 | 0.0034208 | 0.0034208 | 0.98839 | -0.22096 | 0.98836 | -0.22166 | 0.93979
49 | 0.055948 | 0.014152 | -0.055886 | -0.014113 | 6.1139e-05 | 3.8833e-05 | 0.084111 | 0.084111 | 0.084111 | 0.99032 | -0.18407 | 0.98914 | -0.20687 | 23.1073
50 | 0.0229 | 0.0057412 | -0.022899 | -0.0057406 | 9.5868e-07 | 5.8578e-07 | 0.03441 | 0.03441 | 0.03441 | 0.99032 | -0.18407 | 0.99028 | -0.18495 | 9.4532
51 | 0.055886 | 0.014113 | -0.055844 | -0.014086 | 4.2276e-05 | 2.6852e-05 | 0.084111 | 0.084111 | 0.084111 | 0.98914 | -0.20687 | 0.98833 | -0.22267 | 23.1073
52 | 0.014091 | 0.0035331 | -0.014087 | -0.0035304 | 4.7916e-06 | 2.7001e-06 | 0.021175 | 0.021175 | 0.021175 | 0.99028 | -0.18495 | 0.98991 | -0.19209 | 5.8172
53 | -0.0057395 | -0.0014384 | 0.0057398 | 0.0014385 | 2.7042e-07 | 5.2345e-08 | 0.0086951 | 0.0086951 | 0.0086951 | 0.98221 | -0.34172 | 0.98226 | -0.34073 | 2.3888
54 | 0.0057395 | 0.0014384 | -0.005739 | -0.0014383 | 5.3481e-07 | 1.0356e-07 | 0.0086951 | 0.0086952 | 0.0086952 | 0.98221 | -0.34172 | 0.98211 | -0.34367 | 2.3888
55 | -0.011479 | -0.0028768 | 0.011479 | 0.0028769 | 2.532e-07 | 1.3378e-07 | 0.017389 | 0.017389 | 0.017389 | 0.98226 | -0.34073 | 0.98228 | -0.34026 | 4.7772
56 | -0.0017209 | -0.00043131 | 0.001721 | 0.00043121 | 2.2671e-08 | -9.4713e-08 | 0.0026269 | 0.0026269 | 0.0026269 | 0.97482 | -0.48386 | 0.97484 | -0.48358 | 0.72168
57 | -0.0042989 | -0.0010773 | 0.004299 | 0.0010773 | 1.3797e-07 | -1.8233e-08 | 0.0065619 | 0.0065619 | 0.0065619 | 0.97484 | -0.48358 | 0.97487 | -0.48291 | 1.8027
58 | 0.0060276 | 0.0015105 | -0.0060275 | -0.0015105 | 6.2155e-08 | 1.5364e-08 | 0.0092002 | 0.0092002 | 0.0092002 | 0.97488 | -0.48269 | 0.97487 | -0.48291 | 2.5275
59 | -0.093611 | -0.023605 | 0.093782 | 0.023714 | 0.00017117 | 0.00010927 | 0.14294 | 0.14294 | 0.14294 | 0.97488 | -0.48269 | 0.97683 | -0.44456 | 39.268
60 | -0.022144 | -0.005552 | 0.022147 | 0.005554 | 3.3775e-06 | 2.0561e-06 | 0.033213 | 0.033213 | 0.033213 | 0.99213 | -0.15092 | 0.9923 | -0.14772 | 9.1244
61 | 0.019471 | 0.0048812 | -0.019468 | -0.004879 | 3.6657e-06 | 2.1945e-06 | 0.029031 | 0.029031 | 0.029031 | 0.99803 | -0.037215 | 0.99783 | -0.041167 | 7.9756
62 | -0.019471 | -0.0048812 | 0.019472 | 0.0048819 | 1.0673e-06 | 6.3895e-07 | 0.029031 | 0.029031 | 0.029031 | 0.99803 | -0.037215 | 0.99809 | -0.036065 | 7.9756
63 | 0.0062927 | 0.0015771 | -0.0062921 | -0.0015769 | 6.3243e-07 | 1.5463e-07 | 0.0093841 | 0.0093842 | 0.0093842 | 0.99783 | -0.041167 | 0.99772 | -0.043276 | 2.5781
64 | -0.30903 | -0.079188 | 0.30958 | 0.079534 | 0.0005412 | 0.00034557 | 0.46134 | 0.46134 | 0.46134 | 0.99809 | -0.036065 | 1 | 0 | 42.2477
65 | 0.28956 | 0.074306 | -0.28921 | -0.074082 | 0.00035175 | 0.00022453 | 0.43231 | 0.43231 | 0.43231 | 0.99809 | -0.036065 | 0.99677 | -0.061133 | 39.5892
66 | -0.0059567 | -0.0014929 | 0.0059582 | 0.0014932 | 1.5007e-06 | 3.256e-07 | 0.0089787 | 0.0089785 | 0.0089787 | 0.98719 | -0.24436 | 0.98746 | -0.23908 | 2.4667
67 | -0.0059582 | -0.0014932 | 0.0059588 | 0.0014933 | 5.1478e-07 | 1.116e-07 | 0.0089785 | 0.0089784 | 0.0089785 | 0.98746 | -0.23908 | 0.98755 | -0.23726 | 2.4666
68 | 0.046846 | 0.011796 | -0.046824 | -0.011782 | 2.1683e-05 | 1.3735e-05 | 0.071414 | 0.071414 | 0.071414 | 0.97637 | -0.45486 | 0.97588 | -0.46454 | 19.6193
69 | -0.0742 | -0.018712 | 0.074226 | 0.018728 | 2.5683e-05 | 1.6369e-05 | 0.11273 | 0.11273 | 0.11273 | 0.97977 | -0.38837 | 0.98014 | -0.38114 | 30.9703
70 | 0.01784 | 0.0044744 | -0.017832 | -0.0044695 | 8.1006e-06 | 4.8185e-06 | 0.027177 | 0.027178 | 0.027178 | 0.97683 | -0.44456 | 0.97634 | -0.45409 | 7.4664
71 | 0.011467 | 0.0028742 | -0.011465 | -0.0028735 | 1.3767e-06 | 7.3079e-07 | 0.017476 | 0.017476 | 0.017476 | 0.97634 | -0.45409 | 0.97622 | -0.45661 | 4.8012
72 | 0.010258 | 0.002572 | -0.010255 | -0.0025705 | 2.9176e-06 | 1.4764e-06 | 0.015705 | 0.015705 | 0.015705 | 0.97198 | -0.54137 | 0.97168 | -0.54734 | 4.3146
73 | -0.010258 | -0.002572 | 0.010262 | 0.0025739 | 3.8279e-06 | 1.9367e-06 | 0.015705 | 0.015705 | 0.015705 | 0.97198 | -0.54137 | 0.97238 | -0.53354 | 4.3146
74 | 0.010255 | 0.0025705 | -0.010254 | -0.0025699 | 1.3102e-06 | 6.6308e-07 | 0.015705 | 0.015705 | 0.015705 | 0.97168 | -0.54734 | 0.97154 | -0.55002 | 4.3146
75 | -0.012492 | -0.0031328 | 0.012493 | 0.0031334 | 1.1813e-06 | 6.491e-07 | 0.019117 | 0.019117 | 0.019117 | 0.97238 | -0.53354 | 0.97248 | -0.53156 | 5.252
76 | 0.042547 | 0.01071 | -0.042509 | -0.010686 | 3.7107e-05 | 2.3455e-05 | 0.064892 | 0.064892 | 0.064892 | 0.97588 | -0.46454 | 0.97495 | -0.48281 | 17.8274
77 | 0.042509 | 0.010686 | -0.042481 | -0.010668 | 2.8675e-05 | 1.8126e-05 | 0.064892 | 0.064892 | 0.064892 | 0.97495 | -0.48281 | 0.97423 | -0.49694 | 17.8274
78 | 0.039232 | 0.0098538 | -0.039226 | -0.00985 | 5.9976e-06 | 3.783e-06 | 0.059929 | 0.059929 | 0.059929 | 0.97423 | -0.49694 | 0.97407 | -0.50015 | 16.4641
79 | -0.27403 | -0.069958 | 0.27442 | 0.070208 | 0.00039073 | 0.00024935 | 0.41087 | 0.41087 | 0.41087 | 0.99355 | -0.12229 | 0.9951 | -0.092831 | 37.6253
80 | -0.0062917 | -0.0015768 | 0.0062921 | 0.0015769 | 4.4217e-07 | 1.0814e-07 | 0.0093842 | 0.0093842 | 0.0093842 | 0.99764 | -0.044752 | 0.99772 | -0.043276 | 2.5781
81 | 0.0070072 | 0.0017561 | -0.0070067 | -0.0017559 | 4.5617e-07 | 1.6118e-07 | 0.010732 | 0.010732 | 0.010732 | 0.97154 | -0.55002 | 0.97147 | -0.55139 | 2.9484
82 | -0.015567 | -0.0039039 | 0.015571 | 0.0039058 | 3.2546e-06 | 1.8931e-06 | 0.023821 | 0.023821 | 0.023821 | 0.97248 | -0.53156 | 0.9727 | -0.52717 | 6.5442
83 | 0.019902 | 0.0049904 | -0.019898 | -0.0049883 | 3.4683e-06 | 2.0907e-06 | 0.030135 | 0.030135 | 0.030135 | 0.98274 | -0.33139 | 0.98255 | -0.33505 | 8.2789
84 | 0.011548 | 0.0028946 | -0.011547 | -0.0028939 | 1.2292e-06 | 6.5085e-07 | 0.017485 | 0.017485 | 0.017485 | 0.98274 | -0.33139 | 0.98262 | -0.33363 | 4.8037
85 | 0.024368 | 0.0061117 | -0.024365 | -0.0061099 | 2.8696e-06 | 1.7638e-06 | 0.036698 | 0.036698 | 0.036698 | 0.98811 | -0.22654 | 0.98798 | -0.22901 | 10.0819
86 | -0.030064 | -0.0075348 | 0.030065 | 0.0075349 | 1.6862e-07 | 1.0503e-07 | 0.04496 | 0.04496 | 0.04496 | 0.99502 | -0.095263 | 0.99502 | -0.095145 | 12.3517
87 | -0.062657 | -0.015704 | 0.062681 | 0.015718 | 2.3233e-05 | 1.4777e-05 | 0.093702 | 0.093702 | 0.093702 | 0.99502 | -0.095145 | 0.99543 | -0.087365 | 25.7422
88 | -0.01622 | -0.004065 | 0.016224 | 0.0040674 | 4.0282e-06 | 2.3528e-06 | 0.02457 | 0.02457 | 0.02457 | 0.98228 | -0.34026 | 0.98255 | -0.33505 | 6.7501
89 | 0.0078875 | 0.0019769 | -0.0078865 | -0.0019765 | 9.8429e-07 | 3.9693e-07 | 0.011944 | 0.011944 | 0.011944 | 0.98262 | -0.33363 | 0.98249 | -0.33625 | 3.2814
90 | 0.0046567 | 0.001167 | -0.0046565 | -0.001167 | 1.9809e-07 | -7.7029e-09 | 0.0070527 | 0.0070528 | 0.0070528 | 0.98249 | -0.33625 | 0.98244 | -0.33714 | 1.9376
91 | -0.077745 | -0.019494 | 0.077861 | 0.019567 | 0.00011548 | 7.3611e-05 | 0.11622 | 0.11622 | 0.11622 | 0.99543 | -0.087365 | 0.99704 | -0.056246 | 31.9288
92 | 0.055271 | 0.01393 | -0.055221 | -0.013899 | 4.9072e-05 | 3.1156e-05 | 0.082515 | 0.082515 | 0.082515 | 0.99704 | -0.056246 | 0.99608 | -0.074821 | 22.669
93 | 0.13854 | 0.035538 | -0.13843 | -0.03547 | 0.0001085 | 6.865e-05 | 0.20705 | 0.20705 | 0.20705 | 0.99704 | -0.056246 | 0.99619 | -0.072406 | 18.9608
94 | -0.27167 | -0.069036 | 0.27202 | 0.069256 | 0.00034464 | 0.00021991 | 0.40579 | 0.40579 | 0.40579 | 0.99704 | -0.056246 | 0.99842 | -0.029936 | 37.1599
95 | 0.053965 | 0.013584 | -0.053936 | -0.013566 | 2.9033e-05 | 1.8426e-05 | 0.080638 | 0.080638 | 0.080638 | 0.99608 | -0.074821 | 0.99549 | -0.086083 | 22.1534
96 | 0.13695 | 0.0351 | -0.13687 | -0.035048 | 8.0767e-05 | 5.109e-05 | 0.20485 | 0.20485 | 0.20485 | 0.99619 | -0.072406 | 0.99555 | -0.08458 | 18.7588
97 | -0.27484 | -0.069963 | 0.27524 | 0.070217 | 0.00039732 | 0.00025354 | 0.40999 | 0.40999 | 0.40999 | 0.99842 | -0.029936 | 1 | 0 | 37.5451
98 | 0.049318 | 0.012408 | -0.049304 | -0.0124 | 1.3569e-05 | 8.5979e-06 | 0.073735 | 0.073735 | 0.073735 | 0.99549 | -0.086083 | 0.99519 | -0.091843 | 20.2569
99 | 0.13248 | 0.033946 | -0.13226 | -0.033812 | 0.00021052 | 0.00013399 | 0.19827 | 0.19827 | 0.19827 | 0.99555 | -0.08458 | 0.99382 | -0.11742 | 27.2352
100 | 0.036152 | 0.0090797 | -0.036143 | -0.0090738 | 9.3113e-06 | 5.858e-06 | 0.055234 | 0.055234 | 0.055234 | 0.97407 | -0.50015 | 0.9738 | -0.50555 | 15.1741
101 | -0.28217 | -0.072148 | 0.2826 | 0.072425 | 0.00043348 | 0.00027667 | 0.42245 | 0.42245 | 0.42245 | 0.9951 | -0.092831 | 0.99677 | -0.061133 | 38.6855
102 | 0.024365 | 0.0061099 | -0.024356 | -0.006104 | 9.5795e-06 | 5.8881e-06 | 0.036698 | 0.036698 | 0.036698 | 0.98798 | -0.22901 | 0.98755 | -0.23726 | 10.0819
103 | -0.11582 | -0.029439 | 0.11586 | 0.029464 | 3.9886e-05 | 2.5483e-05 | 0.17455 | 0.17455 | 0.17455 | 0.9882 | -0.22499 | 0.98857 | -0.21784 | 47.9529
104 | 0.11313 | 0.028764 | -0.11298 | -0.028668 | 0.00015105 | 9.6492e-05 | 0.1705 | 0.1705 | 0.1705 | 0.9882 | -0.22499 | 0.98676 | -0.25274 | 46.8395
105 | -0.11804 | -0.03001 | 0.11807 | 0.030032 | 3.5466e-05 | 2.266e-05 | 0.17783 | 0.17783 | 0.17783 | 0.98857 | -0.21784 | 0.9889 | -0.2116 | 48.853
106 | 0.11062 | 0.028075 | -0.11051 | -0.028007 | 0.00010759 | 6.8729e-05 | 0.16693 | 0.16693 | 0.16693 | 0.98676 | -0.25274 | 0.98571 | -0.27298 | 45.8605
107 | -0.12032 | -0.030595 | 0.12038 | 0.030636 | 6.4606e-05 | 4.128e-05 | 0.1812 | 0.1812 | 0.1812 | 0.9889 | -0.2116 | 0.98948 | -0.20046 | 49.7813
108 | 0.10553 | 0.026759 | -0.10552 | -0.026754 | 7.5142e-06 | 4.799e-06 | 0.15942 | 0.15942 | 0.15942 | 0.98571 | -0.27298 | 0.98564 | -0.27447 | 43.7962
109 | -0.12256 | -0.031181 | 0.12278 | 0.031324 | 0.00022301 | 0.0001425 | 0.18447 | 0.18447 | 0.18447 | 0.98948 | -0.20046 | 0.99144 | -0.16278 | 50.6798
110 | 0.10405 | 0.026386 | -0.10388 | -0.026275 | 0.00017297 | 0.00011046 | 0.1572 | 0.1572 | 0.1572 | 0.98564 | -0.27447 | 0.98385 | -0.30911 | 43.1862
111 | -0.12619 | -0.032179 | 0.12625 | 0.032217 | 5.8542e-05 | 3.7411e-05 | 0.1896 | 0.1896 | 0.1896 | 0.99144 | -0.16278 | 0.99195 | -0.15318 | 52.0867
112 | 0.095434 | 0.024159 | -0.095421 | -0.02415 | 1.2953e-05 | 8.2687e-06 | 0.14442 | 0.14442 | 0.14442 | 0.98385 | -0.30911 | 0.9837 | -0.31194 | 39.6772
113 | 0.091348 | 0.02313 | -0.091215 | -0.023044 | 0.00013343 | 8.516e-05 | 0.13826 | 0.13826 | 0.13826 | 0.9837 | -0.31194 | 0.98213 | -0.34241 | 37.9847
114 | 0.089552 | 0.022628 | -0.089551 | -0.022627 | 1.4322e-06 | 9.1396e-07 | 0.13575 | 0.13575 | 0.13575 | 0.98213 | -0.34241 | 0.98211 | -0.34274 | 37.2928
115 | 0.087887 | 0.02221 | -0.08787 | -0.022199 | 1.7244e-05 | 1.1004e-05 | 0.13323 | 0.13323 | 0.13323 | 0.98211 | -0.34274 | 0.9819 | -0.34683 | 36.6003
116 | -0.13204 | -0.033666 | 0.13226 | 0.033812 | 0.00022834 | 0.00014593 | 0.19827 | 0.19827 | 0.19827 | 0.99195 | -0.15318 | 0.99382 | -0.11742 | 54.4705
117 | 0.0041657 | 0.0010439 | -0.0041654 | -0.0010439 | 2.789e-07 | -4.7676e-08 | 0.0063805 | 0.0063806 | 0.0063806 | 0.97147 | -0.55139 | 0.9714 | -0.55279 | 1.7529
118 | 0.082377 | 0.020822 | -0.082285 | -0.020763 | 9.2141e-05 | 5.8771e-05 | 0.1249 | 0.1249 | 0.1249 | 0.9819 | -0.34683 | 0.9807 | -0.37019 | 34.3133
119 | 0.077273 | 0.019507 | -0.077232 | -0.019482 | 4.0504e-05 | 2.5824e-05 | 0.1173 | 0.1173 | 0.1173 | 0.9807 | -0.37019 | 0.98014 | -0.38114 | 32.2242
120 | 0.048096 | 0.012097 | -0.048071 | -0.012081 | 2.5641e-05 | 1.6239e-05 | 0.071929 | 0.071929 | 0.071929 | 0.99519 | -0.091843 | 0.99461 | -0.10301 | 19.7608
121 | 0.045309 | 0.011389 | -0.045304 | -0.011385 | 5.1687e-06 | 3.2691e-06 | 0.067798 | 0.067798 | 0.067798 | 0.99461 | -0.10301 | 0.99449 | -0.1054 | 18.6259
122 | 0.043201 | 0.010858 | -0.043182 | -0.010846 | 1.8895e-05 | 1.1936e-05 | 0.064651 | 0.064651 | 0.064651 | 0.99449 | -0.1054 | 0.99401 | -0.11457 | 17.7612
123 | 0.041337 | 0.010384 | -0.041323 | -0.010375 | 1.3944e-05 | 8.7984e-06 | 0.061889 | 0.061889 | 0.061889 | 0.99401 | -0.11457 | 0.99365 | -0.12164 | 17.0024
124 | 0.03939 | 0.0098906 | -0.03938 | -0.0098843 | 9.9198e-06 | 6.2502e-06 | 0.058994 | 0.058994 | 0.058994 | 0.99365 | -0.12164 | 0.99337 | -0.12692 | 16.2072
125 | 0.034177 | 0.0085804 | -0.034164 | -0.0085723 | 1.2864e-05 | 8.0638e-06 | 0.0512 | 0.0512 | 0.0512 | 0.99337 | -0.12692 | 0.99297 | -0.13481 | 14.066
126 | 0.005203 | 0.0013039 | -0.0052026 | -0.0013039 | 3.1292e-07 | 2.2434e-08 | 0.0077937 | 0.0077938 | 0.0077938 | 0.99337 | -0.12692 | 0.99331 | -0.12818 | 2.1411
127 | -0.0031618 | -0.00079243 | 0.0031618 | 0.00079241 | 1.7152e-08 | -1.5412e-08 | 0.0047366 | 0.0047366 | 0.0047366 | 0.9933 | -0.12829 | 0.99331 | -0.12818 | 1.3013
128 | 0.031641 | 0.00794 | -0.031629 | -0.0079328 | 1.1518e-05 | 7.1949e-06 | 0.047419 | 0.047419 | 0.047419 | 0.99297 | -0.13481 | 0.99257 | -0.14245 | 13.0273
129 | 0.028005 | 0.0070243 | -0.028004 | -0.0070238 | 7.931e-07 | 4.9208e-07 | 0.041985 | 0.041985 | 0.041985 | 0.99257 | -0.14245 | 0.99254 | -0.14304 | 11.5344
130 | 0.025078 | 0.0062905 | -0.025072 | -0.0062871 | 5.592e-06 | 3.4426e-06 | 0.037599 | 0.037599 | 0.037599 | 0.99254 | -0.14304 | 0.9923 | -0.14772 | 10.3293
131 | -0.018357 | -0.004604 | 0.018362 | 0.0046071 | 5.0594e-06 | 3.0256e-06 | 0.028083 | 0.028083 | 0.028083 | 0.9727 | -0.52717 | 0.97299 | -0.52139 | 7.7151
132 | 0.014685 | 0.0036814 | -0.014683 | -0.0036803 | 2.0529e-06 | 1.179e-06 | 0.022458 | 0.022458 | 0.022458 | 0.97299 | -0.52139 | 0.97284 | -0.52433 | 6.1699
133 | -0.033047 | -0.0082885 | 0.033072 | 0.0083042 | 2.4979e-05 | 1.5662e-05 | 0.050541 | 0.050541 | 0.050541 | 0.97299 | -0.52139 | 0.9738 | -0.50555 | 13.885
134 | 0.011894 | 0.0029814 | -0.011893 | -0.0029808 | 1.105e-06 | 5.9668e-07 | 0.018193 | 0.018193 | 0.018193 | 0.97284 | -0.52433 | 0.97274 | -0.52628 | 4.9981
135 | 0.0080167 | 0.0020092 | -0.0080162 | -0.002009 | 4.5368e-07 | 1.9049e-07 | 0.012263 | 0.012263 | 0.012263 | 0.97274 | -0.52628 | 0.97268 | -0.52746 | 3.369
136 | 0.0046958 | 0.0011769 | -0.0046957 | -0.0011769 | 1.018e-07 | -1.4184e-10 | 0.0071836 | 0.0071836 | 0.0071836 | 0.97268 | -0.52746 | 0.97266 | -0.52792 | 1.9735

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58915 | 0.15043

## res_load
| p_mw | q_mvar
0 | 0.0071879 | 0.0018015
1 | 0.0038642 | 0.00096847
2 | 0.0033598 | 0.00084204
3 | 0.0040798 | 0.0010225
4 | 0.0024823 | 0.00062213
5 | 0.0029907 | 0.00074954
6 | 0.0055685 | 0.0013956
7 | 0.0043059 | 0.0010792
8 | 0.0042969 | 0.0010769
9 | 0.0023514 | 0.00058932
10 | 0.0040998 | 0.0010275
11 | 0.0058252 | 0.0014599
12 | 0.0029709 | 0.00074457
13 | 0.0033615 | 0.00084248
14 | 0.014832 | 0.0037172
15 | 0.0025728 | 0.0006448
16 | 0.011692 | 0.0029302
17 | 0.0031722 | 0.00079504
18 | 0.0026044 | 0.00065272
19 | 0.010003 | 0.0025069
20 | 0.0088079 | 0.0022075
21 | 0.0018984 | 0.00047579
22 | 0.005739 | 0.0014383
23 | 0.005739 | 0.0014383
24 | 0.0075846 | 0.0019009
25 | 0.0017209 | 0.00043131
26 | 0.0025779 | 0.00064609
27 | 0.068717 | 0.017222
28 | 0.0024858 | 0.00062301
29 | 0.013175 | 0.0033019
30 | 0.0059567 | 0.0014929
31 | 0.020745 | 0.0051992
32 | 0.0017285 | 0.00043321
33 | 0.0063655 | 0.0015953
34 | 0.0055538 | 0.0013919
35 | 0.0022299 | 0.00055886
36 | 0.0042778 | 0.0010721
37 | 0.003249 | 0.00081427
38 | 0.0066129 | 0.0016573
39 | 0.0062917 | 0.0015768
40 | 0.003247 | 0.00081377
41 | 0.0030741 | 0.00077044
42 | 0.0022722 | 0.00056946
43 | 0.014087 | 0.0035304
44 | 0.030064 | 0.0075348
45 | 0.032593 | 0.0081686
46 | 0.0047406 | 0.0011881
47 | 0.0036591 | 0.00091705
48 | 0.0032298 | 0.00080947
49 | 0.0046565 | 0.001167
50 | 0.0036745 | 0.00092093
51 | 0.015065 | 0.0037755
52 | 0.0012563 | 0.00031486
53 | 0.0014768 | 0.00037012
54 | 0.0028229 | 0.00070748
55 | 0.0046184 | 0.0011575
56 | 0.0043983 | 0.0011023
57 | 0.0026926 | 0.00067484
58 | 0.0030737 | 0.00077035
59 | 0.0077425 | 0.0019405
60 | 0.0066108 | 0.0016568
61 | 0.018397 | 0.0046107
62 | 0.011465 | 0.0028735
63 | 0.0026916 | 0.00067458
64 | 0.0021768 | 0.00054555
65 | 0.0023631 | 0.00059224
66 | 0.0022455 | 0.00056277
67 | 0.0049777 | 0.0012475
68 | 0.0021749 | 0.00054507
69 | 0.0014708 | 0.00036862
70 | 0.0034124 | 0.00085522
71 | 0.0084451 | 0.0021165
72 | 0.0040727 | 0.0010207
73 | 0.0016623 | 0.00041662
74 | 0.0016638 | 0.00041698
75 | 0.0057843 | 0.0014497
76 | 0.0028411 | 0.00071204
77 | 0.0054932 | 0.0013767
78 | 0.0050119 | 0.0012561
79 | 0.0030064 | 0.00075347
80 | 0.0012078 | 0.00030271
81 | 0.0027612 | 0.00069203
82 | 0.0021036 | 0.00052721
83 | 0.0018451 | 0.00046242
84 | 0.001933 | 0.00048445
85 | 0.0031618 | 0.00079243
86 | 0.0020408 | 0.00051147
87 | 0.0025231 | 0.00063235
88 | 0.003625 | 0.0009085
89 | 0.0029258 | 0.00073328
90 | 0.0029249 | 0.00073305
91 | 0.0041654 | 0.0010439
92 | 0.002786 | 0.00069825
93 | 0.0027886 | 0.00069888
94 | 0.0030711 | 0.00076968
95 | 0.0038766 | 0.00097156
96 | 0.0033204 | 0.00083218
97 | 0.0046957 | 0.0011769

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1