## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-70_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-70_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-70_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-70_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-70_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-70_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_230-70_0_5_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_230-70_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_230-70_0_5_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_230-70_0_5_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_230-70_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_230-70_0_5_node_56 | 0.4 | n |  | TRUE
12 | bus_LV_230-70_0_5_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_230-70_0_5_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_230-70_0_5_node_55 | 0.4 | n |  | TRUE
15 | bus_LV_230-70_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_230-70_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_230-70_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_230-70_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_230-70_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_230-70_0_5_node_89 | 0.4 | n |  | TRUE
21 | bus_LV_230-70_0_5_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_230-70_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_230-70_0_5_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_230-70_0_5_node_73 | 0.4 | n |  | TRUE
25 | bus_LV_230-70_0_5_node_76 | 0.4 | n |  | TRUE
26 | bus_LV_230-70_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_230-70_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_230-70_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_230-70_0_5_node_113 | 0.4 | n |  | TRUE
30 | bus_LV_230-70_0_5_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_230-70_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_230-70_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_230-70_0_5_node_128 | 0.4 | n |  | TRUE
34 | bus_LV_230-70_0_5_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_230-70_0_5_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_230-70_0_5_node_130 | 0.4 | n |  | TRUE
37 | bus_LV_230-70_0_5_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_230-70_0_5_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_230-70_0_5_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_230-70_0_5_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_230-70_0_5_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_230-70_0_5_node_106 | 0.4 | n |  | TRUE
43 | bus_LV_230-70_0_5_node_103 | 0.4 | n |  | TRUE
44 | bus_LV_230-70_0_5_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_230-70_0_5_node_87 | 0.4 | n |  | TRUE
46 | bus_LV_230-70_0_5_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_230-70_0_5_node_86 | 0.4 | n |  | TRUE
48 | bus_LV_230-70_0_5_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_230-70_0_5_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_230-70_0_5_node_84 | 0.4 | n |  | TRUE
51 | bus_LV_230-70_0_5_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_230-70_0_5_node_116 | 0.4 | n |  | TRUE
53 | bus_LV_230-70_0_5_node_115 | 0.4 | n |  | TRUE
54 | bus_LV_230-70_0_5_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_230-70_0_5_node_83 | 0.4 | n |  | TRUE
56 | bus_LV_230-70_0_5_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_230-70_0_5_node_78 | 0.4 | n |  | TRUE
58 | bus_LV_230-70_0_5_node_121 | 0.4 | n |  | TRUE
59 | bus_LV_230-70_0_5_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_230-70_0_5_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_230-70_0_5_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_230-70_0_5_node_30 | 0.4 | n |  | TRUE
63 | bus_LV_230-70_0_5_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_230-70_0_5_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_230-70_0_5_node_85 | 0.4 | n |  | TRUE
66 | bus_LV_230-70_0_5_node_81 | 0.4 | n |  | TRUE
67 | bus_LV_230-70_0_5_node_129 | 0.4 | n |  | TRUE
68 | bus_LV_230-70_0_5_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_230-70_0_5_node_35 | 0.4 | n |  | TRUE
70 | bus_LV_230-70_0_5_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_230-70_0_5_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_230-70_0_5_node_36 | 0.4 | n |  | TRUE
73 | bus_LV_230-70_0_5_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_230-70_0_5_node_37 | 0.4 | n |  | TRUE
75 | bus_LV_230-70_0_5_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_230-70_0_5_node_124 | 0.4 | n |  | TRUE
77 | bus_LV_230-70_0_5_node_127 | 0.4 | n |  | TRUE
78 | bus_LV_230-70_0_5_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_230-70_0_5_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_230-70_0_5_node_92 | 0.4 | n |  | TRUE
81 | bus_LV_230-70_0_5_node_110 | 0.4 | n |  | TRUE
82 | bus_LV_230-70_0_5_node_90 | 0.4 | n |  | TRUE
83 | bus_LV_230-70_0_5_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_230-70_0_5_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_230-70_0_5_node_112 | 0.4 | n |  | TRUE
86 | bus_LV_230-70_0_5_node_50 | 0.4 | n |  | TRUE
87 | bus_LV_230-70_0_5_node_107 | 0.4 | n |  | TRUE
88 | bus_LV_230-70_0_5_node_104 | 0.4 | n |  | TRUE
89 | bus_LV_230-70_0_5_node_126 | 0.4 | n |  | TRUE
90 | bus_LV_230-70_0_5_node_117 | 0.4 | n |  | TRUE
91 | bus_LV_230-70_0_5_node_114 | 0.4 | n |  | TRUE
92 | bus_LV_230-70_0_5_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_230-70_0_5_node_120 | 0.4 | n |  | TRUE
94 | bus_LV_230-70_0_5_node_75 | 0.4 | n |  | TRUE
95 | bus_LV_230-70_0_5_node_53 | 0.4 | n |  | TRUE
96 | bus_LV_230-70_0_5_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_230-70_0_5_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_230-70_0_5_node_125 | 0.4 | n |  | TRUE
99 | bus_LV_230-70_0_5_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_230-70_0_5_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_230-70_0_5_node_69 | 0.4 | n |  | TRUE
102 | bus_LV_230-70_0_5_node_46 | 0.4 | n |  | TRUE
103 | bus_LV_230-70_0_5_node_48 | 0.4 | n |  | TRUE
104 | bus_LV_230-70_0_5_node_58 | 0.4 | n |  | TRUE
105 | bus_LV_230-70_0_5_node_59 | 0.4 | n |  | TRUE
106 | bus_LV_230-70_0_5_node_74 | 0.4 | n |  | TRUE
107 | bus_LV_230-70_0_5_node_131 | 0.4 | n |  | TRUE
108 | bus_LV_230-70_0_5_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_230-70_0_5_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_230-70_0_5_node_93 | 0.4 | n |  | TRUE
111 | bus_LV_230-70_0_5_node_94 | 0.4 | n |  | TRUE
112 | bus_LV_230-70_0_5_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_230-70_0_5_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_230-70_0_5_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_230-70_0_5_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_230-70_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_230-70_0_5_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_230-70_0_5_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_230-70_0_5_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_230-70_0_5_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_230-70_0_5_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_230-70_0_5_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_230-70_0_5_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_230-70_0_5_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_230-70_0_5_node_119 | 0.4 | n |  | TRUE
126 | bus_MV_371_0_node_152 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-70_0_5_load_0 | 0 | 0.00040073 | 0.00010043 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-70_0_5_load_1 | 1 | 0.0011182 | 0.00028025 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-70_0_5_load_2 | 2 | 0.00054666 | 0.00013701 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-70_0_5_load_3 | 3 | 0.00084554 | 0.00021191 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-70_0_5_load_8 | 5 | 0.00053943 | 0.00013519 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-70_0_5_load_54 | 6 | 0.00056713 | 0.00014214 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-70_0_5_load_47 | 8 | 0.0015447 | 0.00038714 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-70_0_5_load_57 | 9 | 0.0014183 | 0.00035546 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-70_0_5_load_56 | 11 | 0.0015128 | 0.00037915 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-70_0_5_load_49 | 12 | 0.0006199 | 0.00015536 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-70_0_5_load_45 | 13 | 0.0013384 | 0.00033544 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-70_0_5_load_55 | 14 | 0.00074774 | 0.0001874 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-70_0_5_load_9 | 15 | 0.0027602 | 0.00069178 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-70_0_5_load_89 | 20 | 0.0011451 | 0.00028698 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-70_0_5_load_44 | 21 | 0.0027501 | 0.00068925 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-70_0_5_load_73 | 24 | 0.017055 | 0.0042743 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-70_0_5_load_76 | 25 | 0.04317 | 0.010819 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-70_0_5_load_113 | 29 | 0.0020156 | 0.00050515 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-70_0_5_load_128 | 33 | 0.0089092 | 0.0022329 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-70_0_5_load_41 | 35 | 0.0016103 | 0.00040358 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-70_0_5_load_130 | 36 | 0.0092455 | 0.0023172 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-70_0_5_load_64 | 38 | 0.00088589 | 0.00022203 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-70_0_5_load_63 | 40 | 0.0059369 | 0.0014879 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-70_0_5_load_106 | 42 | 0.0011474 | 0.00028756 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-70_0_5_load_103 | 43 | 0.0011545 | 0.00028936 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-70_0_5_load_86 | 47 | 0.0064484 | 0.0016161 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-70_0_5_load_88 | 48 | 0.0043787 | 0.0010974 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-70_0_5_load_84 | 50 | 0.021354 | 0.0053517 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-70_0_5_load_116 | 52 | 0.0019236 | 0.00048209 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-70_0_5_load_115 | 53 | 0.0019189 | 0.00048093 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-70_0_5_load_83 | 55 | 0.00258 | 0.00064661 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-70_0_5_load_121 | 58 | 0.021317 | 0.0053426 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-70_0_5_load_61 | 63 | 0.0004646 | 0.00011644 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-70_0_5_load_60 | 64 | 0.00040806 | 0.00010227 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-70_0_5_load_85 | 65 | 0.0007251 | 0.00018173 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-70_0_5_load_81 | 66 | 0.0017293 | 0.0004334 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-70_0_5_load_129 | 67 | 0.0063534 | 0.0015923 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-70_0_5_load_67 | 71 | 0.0052519 | 0.0013163 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-70_0_5_load_62 | 73 | 0.00044439 | 0.00011137 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-70_0_5_load_66 | 75 | 0.0035871 | 0.00089902 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-70_0_5_load_124 | 76 | 0.0097164 | 0.0024352 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-70_0_5_load_127 | 77 | 0.043283 | 0.010848 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-70_0_5_load_68 | 79 | 0.0017269 | 0.00043279 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-70_0_5_load_92 | 80 | 0.0011529 | 0.00028895 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-70_0_5_load_110 | 81 | 0.0011551 | 0.00028949 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-70_0_5_load_90 | 82 | 0.001144 | 0.00028671 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-70_0_5_load_72 | 83 | 0.019302 | 0.0048374 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-70_0_5_load_77 | 84 | 0.019949 | 0.0049997 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-70_0_5_load_112 | 85 | 0.0011912 | 0.00029854 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-70_0_5_load_50 | 86 | 0.00064899 | 0.00016265 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-70_0_5_load_107 | 87 | 0.0011498 | 0.00028816 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-70_0_5_load_104 | 88 | 0.0011538 | 0.00028916 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-70_0_5_load_126 | 89 | 0.004456 | 0.0011168 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-70_0_5_load_117 | 90 | 0.0019171 | 0.00048047 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-70_0_5_load_114 | 91 | 0.001145 | 0.00028698 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-70_0_5_load_70 | 92 | 0.00063905 | 0.00016016 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-70_0_5_load_75 | 94 | 0.030113 | 0.007547 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-70_0_5_load_53 | 95 | 0.00059047 | 0.00014798 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-70_0_5_load_65 | 97 | 0.0025694 | 0.00064396 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-70_0_5_load_125 | 98 | 0.003714 | 0.00093082 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-70_0_5_load_122 | 99 | 0.0096525 | 0.0024192 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-70_0_5_load_123 | 100 | 0.009642 | 0.0024165 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-70_0_5_load_69 | 101 | 0.0024582 | 0.00061608 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-70_0_5_load_46 | 102 | 0.001201 | 0.00030099 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-70_0_5_load_48 | 103 | 0.0039632 | 0.00099326 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-70_0_5_load_58 | 104 | 0.0014431 | 0.00036167 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-70_0_5_load_59 | 105 | 0.0014995 | 0.00037581 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-70_0_5_load_74 | 106 | 0.018013 | 0.0045144 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-70_0_5_load_131 | 107 | 0.0056117 | 0.0014064 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-70_0_5_load_79 | 108 | 0.0017641 | 0.00044213 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-70_0_5_load_91 | 109 | 0.0011451 | 0.00028698 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-70_0_5_load_93 | 110 | 0.0011448 | 0.00028691 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-70_0_5_load_94 | 111 | 0.0011443 | 0.00028678 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-70_0_5_load_105 | 112 | 0.0011548 | 0.00028943 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-70_0_5_load_102 | 113 | 0.0011355 | 0.00028457 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-70_0_5_load_100 | 114 | 0.0011344 | 0.0002843 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-70_0_5_load_95 | 115 | 0.0011344 | 0.0002843 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-70_0_5_load_96 | 116 | 0.0011355 | 0.00028458 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-70_0_5_load_97 | 117 | 0.0011346 | 0.00028436 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-70_0_5_load_99 | 119 | 0.0011917 | 0.00029868 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-70_0_5_load_101 | 120 | 0.0011481 | 0.00028775 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-70_0_5_load_111 | 121 | 0.0011904 | 0.00029834 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-70_0_5_load_109 | 123 | 0.0011327 | 0.00028389 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-70_0_5_load_118 | 124 | 0.0019167 | 0.00048036 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-70_0_5_load_119 | 125 | 0.0019167 | 0.00048036 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-70_0_5_line_0 |  | 0 | 1 | 0.026666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-70_0_5_line_1 |  | 0 | 2 | 0.093992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-70_0_5_line_2 |  | 1 | 3 | 0.036895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-70_0_5_line_3 |  | 2 | 4 | 0.036739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-70_0_5_line_4 |  | 4 | 5 | 0.1385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-70_0_5_line_5 |  | 5 | 6 | 0.019752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-70_0_5_line_6 |  | 6 | 14 | 0.036796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-70_0_5_line_7 |  | 7 | 8 | 0.055793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-70_0_5_line_8 |  | 7 | 9 | 0.0231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-70_0_5_line_9 |  | 8 | 12 | 0.031535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-70_0_5_line_10 |  | 8 | 13 | 0.022259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-70_0_5_line_11 |  | 9 | 10 | 0.045407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-70_0_5_line_12 |  | 10 | 11 | 0.020479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-70_0_5_line_13 |  | 12 | 60 | 0.02214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-70_0_5_line_14 |  | 13 | 102 | 0.002779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-70_0_5_line_15 |  | 14 | 95 | 0.017269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-70_0_5_line_16 |  | 15 | 16 | 0.012243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_230-70_0_5_line_17 |  | 15 | 17 | 0.0039818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_230-70_0_5_line_18 |  | 16 | 18 | 0.022474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_230-70_0_5_line_19 |  | 17 | 19 | 0.032733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_230-70_0_5_line_20 |  | 18 | 20 | 0.0095524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_230-70_0_5_line_21 |  | 19 | 21 | 0.021558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_230-70_0_5_line_22 |  | 20 | 82 | 0.0059727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_230-70_0_5_line_23 |  | 21 | 39 | 0.057222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_230-70_0_5_line_24 |  | 22 | 23 | 0.015075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_230-70_0_5_line_25 |  | 22 | 24 | 0.014428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_230-70_0_5_line_26 |  | 22 | 25 | 0.016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-70_0_5_line_27 |  | 23 | 68 | 0.026508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_230-70_0_5_line_28 |  | 23 | 36 | 0.022108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-70_0_5_line_29 |  | 24 | 83 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_230-70_0_5_line_30 |  | 25 | 84 | 0.020734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-70_0_5_line_31 |  | 26 | 27 | 0.066406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_230-70_0_5_line_32 |  | 26 | 28 | 0.046142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-70_0_5_line_33 |  | 26 | 29 | 0.0072103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_230-70_0_5_line_34 |  | 27 | 34 | 0.04085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_230-70_0_5_line_35 |  | 27 | 35 | 0.018677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-70_0_5_line_36 |  | 28 | 48 | 0.024203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-70_0_5_line_37 |  | 29 | 85 | 0.0062173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_230-70_0_5_line_38 |  | 30 | 31 | 0.064036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-70_0_5_line_39 |  | 30 | 32 | 0.10089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-70_0_5_line_40 |  | 30 | 33 | 0.024525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-70_0_5_line_41 |  | 31 | 36 | 0.039052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-70_0_5_line_42 |  | 32 | 65 | 0.069574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-70_0_5_line_43 |  | 32 | 66 | 0.11987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-70_0_5_line_44 |  | 34 | 54 | 0.03742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-70_0_5_line_45 |  | 34 | 55 | 0.065882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_230-70_0_5_line_46 |  | 35 | 59 | 0.016852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-70_0_5_line_47 |  | 37 | 38 | 0.027267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-70_0_5_line_48 |  | 37 | 39 | 0.049712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_230-70_0_5_line_49 |  | 37 | 40 | 0.02854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_230-70_0_5_line_50 |  | 40 | 73 | 0.026963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_230-70_0_5_line_51 |  | 41 | 42 | 0.0062138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-70_0_5_line_52 |  | 41 | 43 | 0.0011659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-70_0_5_line_53 |  | 42 | 87 | 0.0061002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-70_0_5_line_54 |  | 43 | 88 | 0.0061153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-70_0_5_line_55 |  | 44 | 45 | 0.023084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-70_0_5_line_56 |  | 44 | 46 | 0.026231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-70_0_5_line_57 |  | 44 | 47 | 0.04664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-70_0_5_line_58 |  | 45 | 89 | 0.022535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-70_0_5_line_59 |  | 46 | 76 | 0.01884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-70_0_5_line_60 |  | 46 | 49 | 0.043276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-70_0_5_line_61 |  | 48 | 74 | 0.0056674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-70_0_5_line_62 |  | 49 | 50 | 0.026656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-70_0_5_line_63 |  | 51 | 52 | 0.0062526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-70_0_5_line_64 |  | 51 | 53 | 0.0012075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-70_0_5_line_65 |  | 52 | 90 | 0.005964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-70_0_5_line_66 |  | 53 | 91 | 0.0062781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-70_0_5_line_67 |  | 54 | 86 | 0.010864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-70_0_5_line_68 |  | 55 | 92 | 0.016023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_230-70_0_5_line_69 |  | 56 | 57 | 0.010984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_230-70_0_5_line_70 |  | 56 | 58 | 0.010521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_230-70_0_5_line_71 |  | 57 | 93 | 0.16878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-70_0_5_line_72 |  | 58 | 94 | 0.012341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_230-70_0_5_line_73 |  | 59 | 60 | 0.026803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-70_0_5_line_74 |  | 59 | 61 | 0.15168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-70_0_5_line_75 |  | 60 | 95 | 0.043892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-70_0_5_line_76 |  | 61 | 67 | 0.016369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-70_0_5_line_77 |  | 62 | 63 | 0.021328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-70_0_5_line_78 |  | 62 | 64 | 0.008329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-70_0_5_line_79 |  | 64 | 72 | 0.023274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-70_0_5_line_80 |  | 66 | 96 | 0.04529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-70_0_5_line_81 |  | 68 | 78 | 0.031432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-70_0_5_line_82 |  | 68 | 79 | 0.023585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_230-70_0_5_line_83 |  | 69 | 70 | 0.052375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-70_0_5_line_84 |  | 69 | 71 | 0.018505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-70_0_5_line_85 |  | 70 | 77 | 0.068921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-70_0_5_line_86 |  | 70 | 72 | 0.079183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_230-70_0_5_line_87 |  | 72 | 73 | 0.038449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_230-70_0_5_line_88 |  | 74 | 75 | 0.018358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-70_0_5_line_89 |  | 75 | 97 | 0.019699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-70_0_5_line_90 |  | 76 | 100 | 0.028152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-70_0_5_line_91 |  | 78 | 98 | 0.017127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-70_0_5_line_92 |  | 78 | 99 | 0.01457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-70_0_5_line_93 |  | 79 | 101 | 0.033697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_230-70_0_5_line_94 |  | 80 | 81 | 0.0051411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-70_0_5_line_95 |  | 81 | 112 | 0.0061205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-70_0_5_line_96 |  | 82 | 109 | 0.0059735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_230-70_0_5_line_97 |  | 83 | 106 | 0.0086186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_230-70_0_5_line_98 |  | 85 | 121 | 0.0062141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_230-70_0_5_line_99 |  | 87 | 122 | 0.010576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-70_0_5_line_100 |  | 88 | 112 | 0.0061161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_230-70_0_5_line_101 |  | 90 | 124 | 0.0059526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_230-70_0_5_line_102 |  | 91 | 123 | 0.0062749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-70_0_5_line_103 |  | 92 | 101 | 0.007159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_230-70_0_5_line_104 |  | 93 | 107 | 0.063902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-70_0_5_line_105 |  | 94 | 106 | 0.019157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_230-70_0_5_line_106 |  | 96 | 108 | 0.029777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-70_0_5_line_107 |  | 99 | 100 | 0.028024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-70_0_5_line_108 |  | 102 | 103 | 0.018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-70_0_5_line_109 |  | 103 | 104 | 0.024947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-70_0_5_line_110 |  | 104 | 105 | 0.0087983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-70_0_5_line_111 |  | 109 | 110 | 0.005972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_230-70_0_5_line_112 |  | 110 | 111 | 0.0059712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_230-70_0_5_line_113 |  | 111 | 113 | 0.015467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_230-70_0_5_line_114 |  | 113 | 114 | 0.0059192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_230-70_0_5_line_115 |  | 114 | 118 | 0.0047061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_230-70_0_5_line_116 |  | 115 | 116 | 0.0059199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_230-70_0_5_line_117 |  | 115 | 117 | 0.0059185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_230-70_0_5_line_118 |  | 116 | 118 | 0.0012123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_230-70_0_5_line_119 |  | 117 | 119 | 0.015962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_230-70_0_5_line_120 |  | 118 | 120 | 0.019672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-70_0_5_line_121 |  | 119 | 121 | 0.006216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_230-70_0_5_line_122 |  | 120 | 122 | 0.0064059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-70_0_5_line_123 |  | 122 | 123 | 0.0079695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-70_0_5_line_124 |  | 124 | 125 | 0.0010327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-70_0_5_trafo_78 | 0.63 MVA 20/0.4 kV | 126 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2693615.3507 | 1262131.2387 | 2693617.3808 | 1262129.4624 | 2693626.6088 | 1262122.9699 | 2693638.4987 | 1262118.5494
1 | 2693615.3507 | 1262131.2387 | 2693604.1616 | 1262141.0292 | 2693583.3839 | 1262161.2167 | 2693568.408 | 1262169.998 | 2693537.4474 | 1262180.8101
2 | 2693638.4987 | 1262118.5494 | 2693642.3295 | 1262117.1251 | 2693659.4587 | 1262113.2265 | 2693672.308 | 1262111.6954 | 2693674.2584 | 1262110.4756
3 | 2693503.5932 | 1262195.06 | 2693533.8642 | 1262182.0615 | 2693537.4474 | 1262180.8101
4 | 2693503.5932 | 1262195.06 | 2693518.4349 | 1262201.889 | 2693539.9914 | 1262203.42 | 2693562.7775 | 1262202.4796 | 2693599.002 | 1262196.103 | 2693609.5704 | 1262196.793 | 2693621.5445 | 1262201.5086 | 2693630.9468 | 1262208.741 | 2693634.3983 | 1262213.2109
5 | 2693646.4703 | 1262228.8447 | 2693634.3983 | 1262213.2109
6 | 2693646.4703 | 1262228.8447 | 2693647.2721 | 1262229.8831 | 2693663.6998 | 1262261.3357
7 | 2693752.9832 | 1262231.7257 | 2693747.0698 | 1262235.4238 | 2693732.1841 | 1262252.7686 | 2693715.8358 | 1262273.0259
8 | 2693752.9832 | 1262231.7257 | 2693761.1117 | 1262229.4749 | 2693769.2872 | 1262230.4275 | 2693775.6541 | 1262231.3622
9 | 2693715.8358 | 1262273.0259 | 2693697.8356 | 1262298.919
10 | 2693715.8358 | 1262273.0259 | 2693734.9988 | 1262284.3498
11 | 2693820.5799 | 1262237.9579 | 2693775.6541 | 1262231.3622
12 | 2693820.5799 | 1262237.9579 | 2693827.883 | 1262241.6545 | 2693836.2101 | 1262242.554 | 2693840.1126 | 1262242.2025
13 | 2693686.6255 | 1262317.9884 | 2693694.9007 | 1262303.1408 | 2693697.8356 | 1262298.919
14 | 2693736.9747 | 1262282.3957 | 2693734.9988 | 1262284.3498 | 2693734.9988 | 1262284.3498
15 | 2693670.7832 | 1262277.0552 | 2693667.559 | 1262268.7245 | 2693663.6998 | 1262261.3357
16 | 2693608.0509 | 1262482.099 | 2693598.4137 | 1262489.6493
17 | 2693595.2792 | 1262492.105 | 2693598.4137 | 1262489.6493
18 | 2693608.0509 | 1262482.099 | 2693618.4041 | 1262473.9896 | 2693627.5652 | 1262475.9696
19 | 2693595.2792 | 1262492.105 | 2693583.7816 | 1262501.1192 | 2693573.6878 | 1262509.0326 | 2693574.5361 | 1262510.1803 | 2693576.8148 | 1262513.3077
20 | 2693627.5652 | 1262475.9696 | 2693635.0149 | 1262469.9904
21 | 2693576.8148 | 1262513.3077 | 2693593.6012 | 1262499.7811
22 | 2693635.0149 | 1262469.9904 | 2693639.6729 | 1262466.2519
23 | 2693636.897 | 1262507.5984 | 2693632.7996 | 1262502.7518 | 2693623.2085 | 1262490.8126 | 2693619.0617 | 1262487.6555 | 2693615.4749 | 1262486.2421 | 2693612.077 | 1262486.2216 | 2693609.4879 | 1262486.9924 | 2693595.857 | 1262497.9633 | 2693593.6012 | 1262499.7811
24 | 2693899.9873 | 1262402.395 | 2693893.0885 | 1262405.9884 | 2693886.7691 | 1262409.6355
25 | 2693886.7691 | 1262409.6355 | 2693885.5447 | 1262407.5032 | 2693883.7557 | 1262404.3834 | 2693881.8902 | 1262402.2854 | 2693879.2027 | 1262400.7082 | 2693876.8899 | 1262399.9004
26 | 2693886.7691 | 1262409.6355 | 2693876.3154 | 1262414.0843 | 2693871.0331 | 1262415.5212
27 | 2693899.9873 | 1262402.395 | 2693899.5429 | 1262399.5412 | 2693899.4633 | 1262396.9601 | 2693899.8079 | 1262394.7193 | 2693900.8933 | 1262392.3235 | 2693902.7191 | 1262389.806 | 2693899.4459 | 1262384.3051 | 2693896.3973 | 1262378.4187
28 | 2693899.9873 | 1262402.395 | 2693901.098 | 1262405.0481 | 2693903.228 | 1262407.5728 | 2693907.3509 | 1262412.2309 | 2693911.8999 | 1262415.2056 | 2693915.6032 | 1262417.337
29 | 2693865.229 | 1262399.4802 | 2693873.3654 | 1262398.6695 | 2693876.8899 | 1262399.9004
30 | 2693871.0331 | 1262415.5212 | 2693861.0591 | 1262418.2344 | 2693850.7674 | 1262419.7165
31 | 2693712.1932 | 1262407.7213 | 2693699.9731 | 1262392.8935 | 2693726.7478 | 1262371.7895 | 2693731.0684 | 1262368.2663 | 2693725.1288 | 1262363.6462
32 | 2693712.1932 | 1262407.7213 | 2693724.6925 | 1262422.5201 | 2693731.8803 | 1262431.1076 | 2693735.8808 | 1262435.886 | 2693738.4322 | 1262437.9725 | 2693734.4421 | 1262442.513
33 | 2693712.1932 | 1262407.7213 | 2693706.571 | 1262412.2355
34 | 2693725.1288 | 1262363.6462 | 2693731.0684 | 1262368.2663 | 2693753.8084 | 1262386.3523 | 2693756.4982 | 1262383.0367
35 | 2693725.1288 | 1262363.6462 | 2693719.3841 | 1262359.0848 | 2693710.5627 | 1262351.9556
36 | 2693734.4421 | 1262442.513 | 2693738.4006 | 1262444.2437 | 2693740.1049 | 1262446.05 | 2693740.1491 | 1262448.9642 | 2693737.9723 | 1262463.2847
37 | 2693706.571 | 1262412.2355 | 2693701.723 | 1262416.128
38 | 2693949.5114 | 1262436.709 | 2693980.4018 | 1262454.8811 | 2693995.1001 | 1262463.5438 | 2693998.2088 | 1262452.8513
39 | 2693933.5559 | 1262502.8757 | 2693941.8292 | 1262498.6037 | 2693955.1662 | 1262487.6733 | 2693960.9431 | 1262478.8135 | 2693966.7585 | 1262469.8987 | 2693970.6125 | 1262461.6088 | 2693973.5828 | 1262456.7743 | 2693977.6705 | 1262459.3746 | 2693980.4018 | 1262454.8811 | 2693995.1001 | 1262463.5438 | 2693998.2088 | 1262452.8513
40 | 2693998.2088 | 1262452.8513 | 2694005.4725 | 1262429.4266
41 | 2693949.5114 | 1262436.709 | 2693930.9547 | 1262426.1725 | 2693915.6032 | 1262417.337
42 | 2693933.5559 | 1262502.8757 | 2693909.4526 | 1262515.6478 | 2693871.4609 | 1262534.2376
43 | 2693933.5559 | 1262502.8757 | 2693977.5528 | 1262577.6683 | 2693983.9523 | 1262595.9848 | 2693992.2632 | 1262606.8726
44 | 2693767.0516 | 1262347.1306 | 2693756.4982 | 1262383.0367
45 | 2693756.4982 | 1262383.0367 | 2693760.1004 | 1262386.3298 | 2693764.0521 | 1262388.9612 | 2693768.4135 | 1262391.4213 | 2693771.3553 | 1262392.6467 | 2693796.4274 | 1262398.6045 | 2693806.793 | 1262398.7579 | 2693809.3748 | 1262398.4541 | 2693818.636 | 1262397.3839
46 | 2693696.4096 | 1262342.9523 | 2693705.0405 | 1262347.4927 | 2693710.5627 | 1262351.9556
47 | 2693658.0061 | 1262506.3871 | 2693656.5359 | 1262504.5401 | 2693667.1861 | 1262496.2354 | 2693676.7367 | 1262490.0096
48 | 2693636.897 | 1262507.5984 | 2693643.1535 | 1262512.6682 | 2693641.8942 | 1262515.5839 | 2693640.4369 | 1262518.63 | 2693638.1023 | 1262521.8845 | 2693641.4054 | 1262525.9846 | 2693654.2474 | 1262509.1632 | 2693658.0061 | 1262506.3871
49 | 2693658.0061 | 1262506.3871 | 2693667.2965 | 1262499.7289 | 2693675.2177 | 1262508.15 | 2693678.8844 | 1262512.3152
50 | 2693696.7006 | 1262532.5539 | 2693678.8844 | 1262512.3152
51 | 2693672.2359 | 1262477.1222 | 2693677.0717 | 1262473.2202
52 | 2693672.2359 | 1262477.1222 | 2693671.2436 | 1262477.7343
53 | 2693677.0717 | 1262473.2202 | 2693681.8192 | 1262469.3895
54 | 2693671.2436 | 1262477.7343 | 2693666.039 | 1262480.9451
55 | 2693999.3133 | 1262310.4316 | 2694021.2881 | 1262303.1639
56 | 2693994.0382 | 1262328.4735 | 2693997.2064 | 1262326.8336 | 2694005.268 | 1262322.625 | 2693999.3133 | 1262310.4316
57 | 2693999.3133 | 1262310.4316 | 2693992.6218 | 1262296.7142 | 2693991.0351 | 1262283.723 | 2694009.1923 | 1262281.5226
58 | 2694021.2881 | 1262303.1639 | 2694042.6817 | 1262296.0838
59 | 2693994.0382 | 1262328.4735 | 2693991.5171 | 1262323.5405 | 2693979.6258 | 1262329.4984
60 | 2693992.2281 | 1262342.3225 | 2693991.149 | 1262335.789 | 2693996.2919 | 1262333.1686 | 2693999.5356 | 1262331.5188 | 2694007.6905 | 1262327.6008 | 2694005.268 | 1262322.625 | 2693997.2064 | 1262326.8336 | 2693994.0382 | 1262328.4735
61 | 2693737.1206 | 1262468.8878 | 2693737.9723 | 1262463.2847
62 | 2693992.2281 | 1262342.3225 | 2693992.4961 | 1262343.9503 | 2693985.523 | 1262367.9643
63 | 2693707.089 | 1262449.2628 | 2693711.3594 | 1262444.6957
64 | 2693707.089 | 1262449.2628 | 2693706.1422 | 1262450.0122
65 | 2693711.3594 | 1262444.6957 | 2693715.4327 | 1262440.3394
66 | 2693701.2194 | 1262453.9083 | 2693706.1422 | 1262450.0122
67 | 2693767.0516 | 1262347.1306 | 2693770.5902 | 1262340.6593 | 2693772.6296 | 1262337.829
68 | 2693834.4587 | 1262394.9037 | 2693824.2233 | 1262396.7327 | 2693821.5585 | 1262397.0462 | 2693818.636 | 1262397.3839
69 | 2693815.3376 | 1262407.3003 | 2693813.3277 | 1262418.0994
70 | 2693815.3376 | 1262407.3003 | 2693823.6987 | 1262404.6196 | 2693825.4211 | 1262404.3673
71 | 2693776.7477 | 1262574.2231 | 2693775.9222 | 1262567.8382 | 2693777.1847 | 1262553.8025 | 2693781.5204 | 1262546.4764 | 2693789.6931 | 1262539.0333 | 2693801.7568 | 1262531.8744 | 2693803.7897 | 1262525.3235 | 2693807.7273 | 1262448.1348 | 2693812.2323 | 1262423.9756 | 2693813.3277 | 1262418.0994
72 | 2693837.6322 | 1262402.5783 | 2693825.4211 | 1262404.3673
73 | 2693686.6255 | 1262317.9884 | 2693696.4096 | 1262342.9523
74 | 2693696.4096 | 1262342.9523 | 2693692.846 | 1262341.9729 | 2693681.9846 | 1262342.1899 | 2693571.8476 | 1262358.7379 | 2693562.1443 | 1262359.1069 | 2693561.2727 | 1262364.6643 | 2693559.3976 | 1262366.0246 | 2693564.5354 | 1262372.2776
75 | 2693686.6255 | 1262317.9884 | 2693670.7832 | 1262277.0552
76 | 2693564.5354 | 1262372.2776 | 2693574.9273 | 1262384.925
77 | 2693712.7661 | 1262514.1607 | 2693722.714 | 1262525.4385 | 2693726.896 | 1262530.1752
78 | 2693726.896 | 1262530.1752 | 2693725.6336 | 1262538.408
79 | 2693722.1058 | 1262561.4134 | 2693725.6336 | 1262538.408
80 | 2693978.7984 | 1262644.3309 | 2693998.2417 | 1262614.7048 | 2693992.2632 | 1262606.8726
81 | 2693896.3973 | 1262378.4187 | 2693918.918 | 1262366.6444 | 2693916.375 | 1262361.1886
82 | 2693896.3973 | 1262378.4187 | 2693885.0305 | 1262383.8982 | 2693876.7583 | 1262386.6692 | 2693874.564 | 1262387.1333
83 | 2693701.2309 | 1262624.8673 | 2693695.4522 | 1262628.6455 | 2693666.9233 | 1262658.7735 | 2693669.8416 | 1262661.4775
84 | 2693669.8416 | 1262661.4775 | 2693683.4245 | 1262674.0456
85 | 2693701.2309 | 1262624.8673 | 2693702.1675 | 1262617.5874 | 2693697.455 | 1262612.5753 | 2693661.8975 | 1262571.0065
86 | 2693701.2309 | 1262624.8673 | 2693706.8498 | 1262624.0334 | 2693711.8122 | 1262625.6467 | 2693715.2064 | 1262619.7179 | 2693719.0709 | 1262611.6837 | 2693722.0024 | 1262601.1995 | 2693726.4682 | 1262566.6535 | 2693722.1058 | 1262561.4134
87 | 2693722.1058 | 1262561.4134 | 2693696.7006 | 1262532.5539
88 | 2693737.1206 | 1262468.8878 | 2693723.4302 | 1262481.118
89 | 2693708.7394 | 1262494.2419 | 2693723.4302 | 1262481.118
90 | 2693979.6258 | 1262329.4984 | 2693954.4558 | 1262342.1091
91 | 2693904.659 | 1262358.2891 | 2693908.1553 | 1262365.3948 | 2693916.375 | 1262361.1886
92 | 2693916.375 | 1262361.1886 | 2693929.4011 | 1262354.6621
93 | 2693874.564 | 1262387.1333 | 2693856.1715 | 1262391.0238 | 2693841.506 | 1262393.6444
94 | 2693655.6248 | 1262487.3699 | 2693653.7836 | 1262488.5058 | 2693651.4857 | 1262490.3996
95 | 2693655.6248 | 1262487.3699 | 2693660.8338 | 1262484.1564
96 | 2693639.6729 | 1262466.2519 | 2693644.3315 | 1262462.5129
97 | 2693865.229 | 1262399.4802 | 2693856.6529 | 1262400.3347
98 | 2693696.8775 | 1262420.0185 | 2693701.723 | 1262416.128
99 | 2693690.05 | 1262462.7482 | 2693681.8192 | 1262469.3895
100 | 2693660.8338 | 1262484.1564 | 2693666.039 | 1262480.9451
101 | 2693715.4327 | 1262440.3394 | 2693719.4982 | 1262435.9914
102 | 2693696.2991 | 1262457.8024 | 2693701.2194 | 1262453.9083
103 | 2693834.4587 | 1262394.9037 | 2693841.506 | 1262393.6444
104 | 2693776.7477 | 1262574.2231 | 2693812.2853 | 1262599.6071 | 2693812.2681 | 1262619.8371
105 | 2693837.6322 | 1262402.5783 | 2693845.0647 | 1262401.4894 | 2693856.6529 | 1262400.3347
106 | 2693978.7984 | 1262644.3309 | 2693962.8202 | 1262631.3666 | 2693955.6721 | 1262625.5729
107 | 2693929.4011 | 1262354.6621 | 2693954.4558 | 1262342.1091
108 | 2693749.9159 | 1262269.5976 | 2693736.9747 | 1262282.3957
109 | 2693749.9159 | 1262269.5976 | 2693767.6542 | 1262252.0554
110 | 2693773.91 | 1262245.8688 | 2693767.6542 | 1262252.0554
111 | 2693644.3315 | 1262462.5129 | 2693648.9889 | 1262458.7748
112 | 2693648.9889 | 1262458.7748 | 2693653.6457 | 1262455.0373
113 | 2693653.6457 | 1262455.0373 | 2693655.9481 | 1262453.1894 | 2693657.6626 | 1262455.3071 | 2693665.2971 | 1262449.1783
114 | 2693669.913 | 1262445.4728 | 2693665.2971 | 1262449.1783
115 | 2693673.5828 | 1262442.5267 | 2693669.913 | 1262445.4728
116 | 2693679.1442 | 1262438.0613 | 2693674.5281 | 1262441.7677
117 | 2693679.1442 | 1262438.0613 | 2693683.7592 | 1262434.3559
118 | 2693673.5828 | 1262442.5267 | 2693674.5281 | 1262441.7677
119 | 2693692.0305 | 1262423.9103 | 2693688.0455 | 1262427.11 | 2693689.9077 | 1262429.4191 | 2693683.7592 | 1262434.3559
120 | 2693673.5828 | 1262442.5267 | 2693686.005 | 1262457.781
121 | 2693692.0305 | 1262423.9103 | 2693696.8775 | 1262420.0185
122 | 2693690.05 | 1262462.7482 | 2693686.005 | 1262457.781
123 | 2693690.05 | 1262462.7482 | 2693696.2991 | 1262457.8024
124 | 2693720.2036 | 1262435.237 | 2693719.4982 | 1262435.9914

## bus_geodata
| x | y | coords
0 | 2693615.3507 | 1262131.2387
1 | 2693638.4987 | 1262118.5494
2 | 2693537.4474 | 1262180.8101
3 | 2693674.2584 | 1262110.4756
4 | 2693503.5932 | 1262195.06
5 | 2693634.3983 | 1262213.2109
6 | 2693646.4703 | 1262228.8447
7 | 2693752.9832 | 1262231.7257
8 | 2693715.8358 | 1262273.0259
9 | 2693775.6541 | 1262231.3622
10 | 2693820.5799 | 1262237.9579
11 | 2693840.1126 | 1262242.2025
12 | 2693697.8356 | 1262298.919
13 | 2693734.9988 | 1262284.3498
14 | 2693663.6998 | 1262261.3357
15 | 2693598.4137 | 1262489.6493
16 | 2693608.0509 | 1262482.099
17 | 2693595.2792 | 1262492.105
18 | 2693627.5652 | 1262475.9696
19 | 2693576.8148 | 1262513.3077
20 | 2693635.0149 | 1262469.9904
21 | 2693593.6012 | 1262499.7811
22 | 2693886.7691 | 1262409.6355
23 | 2693899.9873 | 1262402.395
24 | 2693876.8899 | 1262399.9004
25 | 2693871.0331 | 1262415.5212
26 | 2693712.1932 | 1262407.7213
27 | 2693725.1288 | 1262363.6462
28 | 2693734.4421 | 1262442.513
29 | 2693706.571 | 1262412.2355
30 | 2693998.2088 | 1262452.8513
31 | 2693949.5114 | 1262436.709
32 | 2693933.5559 | 1262502.8757
33 | 2694005.4725 | 1262429.4266
34 | 2693756.4982 | 1262383.0367
35 | 2693710.5627 | 1262351.9556
36 | 2693915.6032 | 1262417.337
37 | 2693658.0061 | 1262506.3871
38 | 2693676.7367 | 1262490.0096
39 | 2693636.897 | 1262507.5984
40 | 2693678.8844 | 1262512.3152
41 | 2693672.2359 | 1262477.1222
42 | 2693677.0717 | 1262473.2202
43 | 2693671.2436 | 1262477.7343
44 | 2693999.3133 | 1262310.4316
45 | 2694021.2881 | 1262303.1639
46 | 2693994.0382 | 1262328.4735
47 | 2694009.1923 | 1262281.5226
48 | 2693737.9723 | 1262463.2847
49 | 2693992.2281 | 1262342.3225
50 | 2693985.523 | 1262367.9643
51 | 2693707.089 | 1262449.2628
52 | 2693711.3594 | 1262444.6957
53 | 2693706.1422 | 1262450.0122
54 | 2693767.0516 | 1262347.1306
55 | 2693818.636 | 1262397.3839
56 | 2693815.3376 | 1262407.3003
57 | 2693813.3277 | 1262418.0994
58 | 2693825.4211 | 1262404.3673
59 | 2693696.4096 | 1262342.9523
60 | 2693686.6255 | 1262317.9884
61 | 2693564.5354 | 1262372.2776
62 | 2693726.896 | 1262530.1752
63 | 2693712.7661 | 1262514.1607
64 | 2693725.6336 | 1262538.408
65 | 2693871.4609 | 1262534.2376
66 | 2693992.2632 | 1262606.8726
67 | 2693574.9273 | 1262384.925
68 | 2693896.3973 | 1262378.4187
69 | 2693669.8416 | 1262661.4775
70 | 2693701.2309 | 1262624.8673
71 | 2693683.4245 | 1262674.0456
72 | 2693722.1058 | 1262561.4134
73 | 2693696.7006 | 1262532.5539
74 | 2693737.1206 | 1262468.8878
75 | 2693723.4302 | 1262481.118
76 | 2693979.6258 | 1262329.4984
77 | 2693661.8975 | 1262571.0065
78 | 2693916.375 | 1262361.1886
79 | 2693874.564 | 1262387.1333
80 | 2693651.4857 | 1262490.3996
81 | 2693655.6248 | 1262487.3699
82 | 2693639.6729 | 1262466.2519
83 | 2693865.229 | 1262399.4802
84 | 2693850.7674 | 1262419.7165
85 | 2693701.723 | 1262416.128
86 | 2693772.6296 | 1262337.829
87 | 2693681.8192 | 1262469.3895
88 | 2693666.0391 | 1262480.9451
89 | 2694042.6817 | 1262296.0838
90 | 2693715.4327 | 1262440.3394
91 | 2693701.2194 | 1262453.9083
92 | 2693834.4587 | 1262394.9037
93 | 2693776.7477 | 1262574.2231
94 | 2693837.6322 | 1262402.5783
95 | 2693670.7832 | 1262277.0552
96 | 2693978.7984 | 1262644.3309
97 | 2693708.7394 | 1262494.2419
98 | 2693904.659 | 1262358.2891
99 | 2693929.4011 | 1262354.6621
100 | 2693954.4558 | 1262342.1091
101 | 2693841.506 | 1262393.6444
102 | 2693736.9747 | 1262282.3957
103 | 2693749.9159 | 1262269.5976
104 | 2693767.6542 | 1262252.0554
105 | 2693773.91 | 1262245.8688
106 | 2693856.6529 | 1262400.3347
107 | 2693812.2681 | 1262619.8371
108 | 2693955.6721 | 1262625.5729
109 | 2693644.3315 | 1262462.5129
110 | 2693648.9889 | 1262458.7748
111 | 2693653.6457 | 1262455.0373
112 | 2693660.8338 | 1262484.1564
113 | 2693665.2972 | 1262449.1783
114 | 2693669.913 | 1262445.4728
115 | 2693679.1442 | 1262438.0613
116 | 2693674.5281 | 1262441.7677
117 | 2693683.7592 | 1262434.3559
118 | 2693673.5829 | 1262442.5267
119 | 2693692.0306 | 1262423.9103
120 | 2693686.005 | 1262457.781
121 | 2693696.8775 | 1262420.0185
122 | 2693690.05 | 1262462.7482
123 | 2693696.2991 | 1262457.8024
124 | 2693719.4982 | 1262435.9914
125 | 2693720.2036 | 1262435.237
126 | 2693815.3376 | 1262407.3003

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98206 | -0.34497 | 0.00040073 | 0.00010043
1 | 0.98201 | -0.34591 | 0.0011182 | 0.00028025
2 | 0.98227 | -0.34094 | 0.00054666 | 0.00013701
3 | 0.98198 | -0.34648 | 0.00084554 | 0.00021191
4 | 0.98236 | -0.33901 | 0 | 0
5 | 0.98274 | -0.33171 | 0.00053943 | 0.00013519
6 | 0.9828 | -0.33047 | 0.00056713 | 0.00014214
7 | 0.98237 | -0.33875 | 0 | 0
8 | 0.98253 | -0.3358 | 0.0015447 | 0.00038714
9 | 0.98231 | -0.33998 | 0.0014183 | 0.00035546
10 | 0.98225 | -0.34122 | 0 | 0
11 | 0.98222 | -0.34178 | 0.0015128 | 0.00037915
12 | 0.98293 | -0.32787 | 0.0006199 | 0.00015536
13 | 0.98233 | -0.33959 | 0.0013384 | 0.00033544
14 | 0.98294 | -0.3278 | 0.00074774 | 0.0001874
15 | 0.98026 | -0.37962 | 0.0027602 | 0.00069178
16 | 0.98044 | -0.37616 | 0 | 0
17 | 0.98021 | -0.38069 | 0 | 0
18 | 0.98076 | -0.36982 | 0 | 0
19 | 0.97975 | -0.38952 | 0 | 0
20 | 0.9809 | -0.36713 | 0.0011451 | 0.00028698
21 | 0.97945 | -0.39534 | 0.0027501 | 0.00068925
22 | 0.99286 | -0.13619 | 0 | 0
23 | 0.99205 | -0.15181 | 0 | 0
24 | 0.99385 | -0.11724 | 0.017055 | 0.0042743
25 | 0.99189 | -0.155 | 0.04317 | 0.010819
26 | 0.9829 | -0.32824 | 0 | 0
27 | 0.98461 | -0.29509 | 0 | 0
28 | 0.98245 | -0.33702 | 0 | 0
29 | 0.98273 | -0.33151 | 0.0020156 | 0.00050515
30 | 0.99035 | -0.18463 | 0 | 0
31 | 0.99112 | -0.16968 | 0 | 0
32 | 0.98996 | -0.19221 | 0 | 0
33 | 0.99015 | -0.18851 | 0.0089092 | 0.0022329
34 | 0.98592 | -0.26965 | 0 | 0
35 | 0.98413 | -0.30446 | 0.0016103 | 0.00040358
36 | 0.99159 | -0.16058 | 0.0092455 | 0.0023172
37 | 0.97804 | -0.42293 | 0 | 0
38 | 0.97802 | -0.42337 | 0.00088589 | 0.00022203
39 | 0.9787 | -0.41009 | 0 | 0
40 | 0.97767 | -0.43018 | 0.0059369 | 0.0014879
41 | 0.98103 | -0.36477 | 0 | 0
42 | 0.98106 | -0.36412 | 0.0011474 | 0.00028756
43 | 0.98102 | -0.36489 | 0.0011545 | 0.00028936
44 | 0.9848 | -0.29207 | 0 | 0
45 | 0.98471 | -0.29392 | 0 | 0
46 | 0.98507 | -0.28693 | 0 | 0
47 | 0.98453 | -0.29748 | 0.0064484 | 0.0016161
48 | 0.98222 | -0.34163 | 0.0043787 | 0.0010974
49 | 0.98421 | -0.30355 | 0 | 0
50 | 0.98369 | -0.31379 | 0.021354 | 0.0053517
51 | 0.98097 | -0.366 | 0 | 0
52 | 0.98092 | -0.36687 | 0.0019236 | 0.00048209
53 | 0.98097 | -0.36583 | 0.0019189 | 0.00048093
54 | 0.9859 | -0.27009 | 0 | 0
55 | 0.98805 | -0.22856 | 0.00258 | 0.00064661
56 | 0.99898 | -0.019316 | 0 | 0
57 | 1 | 0 | -0.41509 | -0.10543
58 | 0.99801 | -0.037854 | 0.021317 | 0.0053426
59 | 0.98372 | -0.31244 | 0 | 0
60 | 0.98323 | -0.32206 | 0 | 0
61 | 0.98283 | -0.32982 | 0 | 0
62 | 0.97689 | -0.44543 | 0 | 0
63 | 0.97688 | -0.44561 | 0.0004646 | 0.00011644
64 | 0.9769 | -0.44536 | 0.00040806 | 0.00010227
65 | 0.98992 | -0.19311 | 0.0007251 | 0.00018173
66 | 0.98958 | -0.19967 | 0.0017293 | 0.0004334
67 | 0.98274 | -0.3317 | 0.0063534 | 0.0015923
68 | 0.99075 | -0.17671 | 0 | 0
69 | 0.97487 | -0.4852 | 0 | 0
70 | 0.97512 | -0.48015 | 0 | 0
71 | 0.97478 | -0.48698 | 0.0052519 | 0.0013163
72 | 0.97692 | -0.44499 | 0 | 0
73 | 0.97736 | -0.43632 | 0.00044439 | 0.00011137
74 | 0.98218 | -0.34226 | 0 | 0
75 | 0.98208 | -0.3443 | 0.0035871 | 0.00089902
76 | 0.98563 | -0.27602 | 0.0097164 | 0.0024352
77 | 0.97234 | -0.53499 | 0.043283 | 0.010848
78 | 0.98887 | -0.21305 | 0 | 0
79 | 0.98995 | -0.19209 | 0.0017269 | 0.00043279
80 | 0.98096 | -0.36615 | 0.0011529 | 0.00028895
81 | 0.98096 | -0.36604 | 0.0011551 | 0.00028949
82 | 0.98099 | -0.36542 | 0.001144 | 0.00028671
83 | 0.99471 | -0.10074 | 0.019302 | 0.0048374
84 | 0.99151 | -0.16233 | 0.019949 | 0.0049997
85 | 0.98259 | -0.33427 | 0.0011912 | 0.00029854
86 | 0.98589 | -0.27021 | 0.00064899 | 0.00016265
87 | 0.9811 | -0.36336 | 0.0011498 | 0.00028816
88 | 0.981 | -0.3654 | 0.0011538 | 0.00028916
89 | 0.98462 | -0.29573 | 0.004456 | 0.0011168
90 | 0.98089 | -0.36749 | 0.0019171 | 0.00048047
91 | 0.98103 | -0.36474 | 0.001145 | 0.00028698
92 | 0.98858 | -0.21841 | 0.00063905 | 0.00016016
93 | 0.99914 | -0.016537 | 0 | 0
94 | 0.99692 | -0.058493 | 0.030113 | 0.007547
95 | 0.98301 | -0.32631 | 0.00059047 | 0.00014798
96 | 0.98951 | -0.20109 | 0 | 0
97 | 0.98203 | -0.34521 | 0.0025694 | 0.00064396
98 | 0.98881 | -0.21418 | 0.003714 | 0.00093082
99 | 0.98805 | -0.22897 | 0.0096525 | 0.0024192
100 | 0.98671 | -0.25484 | 0.009642 | 0.0024165
101 | 0.98881 | -0.21386 | 0.0024582 | 0.00061608
102 | 0.98231 | -0.34 | 0.001201 | 0.00030099
103 | 0.98219 | -0.34227 | 0.0039632 | 0.00099326
104 | 0.98213 | -0.3436 | 0.0014431 | 0.00036167
105 | 0.98211 | -0.34384 | 0.0014995 | 0.00037581
106 | 0.99537 | -0.088081 | 0.018013 | 0.0045144
107 | 0.99881 | -0.022801 | 0.0056117 | 0.0014064
108 | 0.98946 | -0.20203 | 0.0017641 | 0.00044213
109 | 0.98108 | -0.36367 | 0.0011451 | 0.00028698
110 | 0.98117 | -0.3619 | 0.0011448 | 0.00028691
111 | 0.98126 | -0.36009 | 0.0011443 | 0.00028678
112 | 0.98098 | -0.36579 | 0.0011548 | 0.00028943
113 | 0.98151 | -0.35534 | 0.0011355 | 0.00028457
114 | 0.9816 | -0.35349 | 0.0011344 | 0.0002843
115 | 0.98183 | -0.34902 | 0.0011344 | 0.0002843
116 | 0.98171 | -0.35149 | 0.0011355 | 0.00028458
117 | 0.98196 | -0.34651 | 0.0011346 | 0.00028436
118 | 0.98168 | -0.35199 | 0 | 0
119 | 0.98231 | -0.33968 | 0.0011917 | 0.00029868
120 | 0.9813 | -0.3595 | 0.0011481 | 0.00028775
121 | 0.98245 | -0.33699 | 0.0011904 | 0.00029834
122 | 0.98118 | -0.36181 | 0 | 0
123 | 0.98109 | -0.36352 | 0.0011327 | 0.00028389
124 | 0.98087 | -0.36791 | 0.0019167 | 0.00048036
125 | 0.98087 | -0.36794 | 0.0019167 | 0.00048036
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0019639 | 0.00049143 | -0.0019638 | -0.00049171 | 8.853e-08 | -2.8072e-07 | 0.0029754 | 0.0029755 | 0.0029755 | 0.98206 | -0.34497 | 0.98201 | -0.34591 | 0.81745
1 | -0.0023646 | -0.00059187 | 0.0023651 | 0.00059097 | 4.5234e-07 | -9.0002e-07 | 0.0035826 | 0.0035822 | 0.0035826 | 0.98206 | -0.34497 | 0.98227 | -0.34094 | 0.98423
2 | 0.00084556 | 0.00021146 | -0.00084554 | -0.00021191 | 2.271e-08 | -4.5223e-07 | 0.0012811 | 0.0012813 | 0.0012813 | 0.98201 | -0.34591 | 0.98198 | -0.34648 | 0.352
3 | -0.0029117 | -0.00072797 | 0.002912 | 0.00072768 | 2.6797e-07 | -2.936e-07 | 0.0044103 | 0.0044101 | 0.0044103 | 0.98227 | -0.34094 | 0.98236 | -0.33901 | 1.2116
4 | -0.002912 | -0.00072768 | 0.002913 | 0.00072657 | 1.01e-06 | -1.1078e-06 | 0.0044101 | 0.0044095 | 0.0044101 | 0.98236 | -0.33901 | 0.98274 | -0.33171 | 1.2116
5 | -0.0034524 | -0.00086177 | 0.0034526 | 0.00086164 | 2.0231e-07 | -1.208e-07 | 0.0052263 | 0.0052262 | 0.0052263 | 0.98274 | -0.33171 | 0.9828 | -0.33047 | 1.4358
6 | -0.0040198 | -0.0010038 | 0.0040203 | 0.0010036 | 5.1089e-07 | -1.3937e-07 | 0.0060849 | 0.0060847 | 0.0060849 | 0.9828 | -0.33047 | 0.98294 | -0.3278 | 1.6717
7 | -0.0029314 | -0.00073367 | 0.0029318 | 0.00073323 | 4.1241e-07 | -4.4256e-07 | 0.0044399 | 0.0044396 | 0.0044399 | 0.98237 | -0.33875 | 0.98253 | -0.3358 | 1.2197
8 | 0.0029314 | 0.00073367 | -0.0029312 | -0.00073385 | 1.7077e-07 | -1.8316e-07 | 0.0044399 | 0.00444 | 0.00444 | 0.98237 | -0.33875 | 0.98231 | -0.33998 | 1.2198
9 | -0.013924 | -0.0034884 | 0.01393 | 0.0034913 | 5.2588e-06 | 2.9661e-06 | 0.021088 | 0.021088 | 0.021088 | 0.98253 | -0.3358 | 0.98293 | -0.32787 | 5.7934
10 | 0.0094479 | 0.002368 | -0.0094462 | -0.0023672 | 1.709e-06 | 8.119e-07 | 0.014309 | 0.014309 | 0.014309 | 0.98253 | -0.3358 | 0.98233 | -0.33959 | 3.931
11 | 0.0015129 | 0.0003784 | -0.0015129 | -0.00037891 | 8.9424e-08 | -5.1756e-07 | 0.0022915 | 0.0022917 | 0.0022917 | 0.98231 | -0.33998 | 0.98225 | -0.34122 | 0.6296
12 | 0.0015129 | 0.00037891 | -0.0015128 | -0.00037915 | 4.0336e-08 | -2.334e-07 | 0.0022917 | 0.0022918 | 0.0022918 | 0.98225 | -0.34122 | 0.98222 | -0.34178 | 0.62963
13 | -0.01455 | -0.0036467 | 0.014554 | 0.003649 | 4.0279e-06 | 2.2971e-06 | 0.022026 | 0.022026 | 0.022026 | 0.98293 | -0.32787 | 0.98323 | -0.32206 | 6.0511
14 | 0.0081078 | 0.0020318 | -0.0081077 | -0.0020317 | 1.5719e-07 | 6.5419e-08 | 0.012281 | 0.012281 | 0.012281 | 0.98233 | -0.33959 | 0.98231 | -0.34 | 3.374
15 | -0.004768 | -0.001191 | 0.0047684 | 0.001191 | 3.3726e-07 | -3.0604e-09 | 0.0072167 | 0.0072166 | 0.0072167 | 0.98294 | -0.3278 | 0.98301 | -0.32631 | 1.9826
16 | -0.062557 | -0.015805 | 0.062568 | 0.015811 | 1.036e-05 | 6.0128e-06 | 0.095006 | 0.095006 | 0.095006 | 0.98026 | -0.37962 | 0.98044 | -0.37616 | 6.5252
17 | 0.059797 | 0.015114 | -0.059794 | -0.015112 | 3.0788e-06 | 1.7697e-06 | 0.090816 | 0.090817 | 0.090817 | 0.98026 | -0.37962 | 0.98021 | -0.38069 | 6.2374
18 | -0.062568 | -0.015811 | 0.062587 | 0.015823 | 1.9018e-05 | 1.1037e-05 | 0.095006 | 0.095006 | 0.095006 | 0.98044 | -0.37616 | 0.98076 | -0.36982 | 6.5252
19 | 0.059794 | 0.015112 | -0.059769 | -0.015097 | 2.531e-05 | 1.4549e-05 | 0.090817 | 0.090817 | 0.090817 | 0.98021 | -0.38069 | 0.97975 | -0.38952 | 6.2374
20 | -0.062587 | -0.015823 | 0.062595 | 0.015827 | 8.0832e-06 | 4.691e-06 | 0.095006 | 0.095006 | 0.095006 | 0.98076 | -0.36982 | 0.9809 | -0.36713 | 6.5251
21 | 0.059769 | 0.015097 | -0.059752 | -0.015088 | 1.6669e-05 | 9.5827e-06 | 0.090817 | 0.090818 | 0.090818 | 0.97975 | -0.38952 | 0.97945 | -0.39534 | 6.2375
22 | -0.06374 | -0.016114 | 0.063745 | 0.016117 | 5.2406e-06 | 3.0524e-06 | 0.096743 | 0.096743 | 0.096743 | 0.9809 | -0.36713 | 0.98099 | -0.36542 | 6.6444
23 | 0.057002 | 0.014399 | -0.056962 | -0.014376 | 4.0269e-05 | 2.2894e-05 | 0.086639 | 0.08664 | 0.08664 | 0.97945 | -0.39534 | 0.9787 | -0.41009 | 5.9506
24 | 0.23648 | 0.060139 | -0.2363 | -0.060026 | 0.00017783 | 0.00011303 | 0.35472 | 0.35472 | 0.35472 | 0.99286 | -0.13619 | 0.99205 | -0.15181 | 24.3627
25 | -0.29966 | -0.075998 | 0.29993 | 0.076172 | 0.00027321 | 0.00017411 | 0.44942 | 0.44942 | 0.44942 | 0.99286 | -0.13619 | 0.99385 | -0.11724 | 30.8669
26 | 0.063182 | 0.015859 | -0.063126 | -0.015823 | 5.6619e-05 | 3.6018e-05 | 0.094701 | 0.094701 | 0.094701 | 0.99286 | -0.13619 | 0.99189 | -0.155 | 26.0168
27 | 0.2139 | 0.054407 | -0.21364 | -0.054244 | 0.00025626 | 0.00016264 | 0.32112 | 0.32112 | 0.32112 | 0.99205 | -0.15181 | 0.99075 | -0.17671 | 22.0548
28 | 0.022402 | 0.0056192 | -0.022393 | -0.0056135 | 9.3619e-06 | 5.7063e-06 | 0.033604 | 0.033604 | 0.033604 | 0.99205 | -0.15181 | 0.99159 | -0.16058 | 9.2319
29 | -0.31699 | -0.080447 | 0.31724 | 0.080607 | 0.00025188 | 0.00016058 | 0.47496 | 0.47496 | 0.47496 | 0.99385 | -0.11724 | 0.99471 | -0.10074 | 32.6206
30 | 0.019956 | 0.0050039 | -0.019949 | -0.0049997 | 6.9692e-06 | 4.1928e-06 | 0.029938 | 0.029939 | 0.029939 | 0.99189 | -0.155 | 0.99151 | -0.16233 | 8.2249
31 | -0.11138 | -0.028117 | 0.11156 | 0.028227 | 0.00017717 | 0.00011002 | 0.1687 | 0.16869 | 0.1687 | 0.9829 | -0.32824 | 0.98461 | -0.29509 | 11.5863
32 | 0.010543 | 0.0026438 | -0.010538 | -0.0026416 | 4.4084e-06 | 2.2368e-06 | 0.015961 | 0.015962 | 0.015962 | 0.9829 | -0.32824 | 0.98245 | -0.33702 | 4.3851
33 | 0.10084 | 0.025473 | -0.10082 | -0.025463 | 1.5769e-05 | 9.7265e-06 | 0.15273 | 0.15273 | 0.15273 | 0.9829 | -0.32824 | 0.98273 | -0.33151 | 10.49
34 | -0.13948 | -0.035232 | 0.13965 | 0.035339 | 0.00017031 | 0.00010692 | 0.21088 | 0.21088 | 0.21088 | 0.98461 | -0.29509 | 0.98592 | -0.26965 | 14.4838
35 | 0.027915 | 0.0070051 | -0.027902 | -0.0069973 | 1.2467e-05 | 7.7416e-06 | 0.04219 | 0.04219 | 0.04219 | 0.98461 | -0.29509 | 0.98413 | -0.30446 | 11.5907
36 | 0.010538 | 0.0026416 | -0.010536 | -0.0026404 | 2.3124e-06 | 1.1735e-06 | 0.015962 | 0.015962 | 0.015962 | 0.98245 | -0.33702 | 0.98222 | -0.34163 | 4.3851
37 | 0.098809 | 0.024958 | -0.098796 | -0.02495 | 1.3059e-05 | 8.0428e-06 | 0.14968 | 0.14968 | 0.14968 | 0.98273 | -0.33151 | 0.98259 | -0.33427 | 10.2804
38 | -0.013132 | -0.0032881 | 0.013142 | 0.0032932 | 9.3479e-06 | 5.1581e-06 | 0.01973 | 0.01973 | 0.01973 | 0.99035 | -0.18463 | 0.99112 | -0.16968 | 5.4204
39 | 0.0042215 | 0.0010545 | -0.00422 | -0.0010548 | 1.5217e-06 | -3.2384e-07 | 0.0063416 | 0.0063421 | 0.0063421 | 0.99035 | -0.18463 | 0.98996 | -0.19221 | 1.7423
40 | 0.0089109 | 0.0022336 | -0.0089092 | -0.0022329 | 1.6486e-06 | 7.3962e-07 | 0.013389 | 0.013389 | 0.013389 | 0.99035 | -0.18463 | 0.99015 | -0.18851 | 3.6783
41 | -0.013142 | -0.0032932 | 0.013147 | 0.0032964 | 5.7007e-06 | 3.1449e-06 | 0.01973 | 0.01973 | 0.01973 | 0.99112 | -0.16968 | 0.99159 | -0.16058 | 5.4203
42 | 0.00072513 | 0.00018085 | -0.0007251 | -0.00018173 | 3.0986e-08 | -8.7466e-07 | 0.0010896 | 0.00109 | 0.00109 | 0.98996 | -0.19221 | 0.98992 | -0.19311 | 0.29944
43 | 0.0034948 | 0.00087395 | -0.0034936 | -0.00087469 | 1.2403e-06 | -7.4687e-07 | 0.0052524 | 0.005253 | 0.005253 | 0.98996 | -0.19221 | 0.98958 | -0.19967 | 1.4431
44 | 0.000649 | 0.00016205 | -0.00064899 | -0.00016252 | 1.346e-08 | -4.6857e-07 | 0.0009793 | 0.00097947 | 0.00097947 | 0.98592 | -0.26965 | 0.9859 | -0.27009 | 0.26909
45 | -0.14029 | -0.035501 | 0.14057 | 0.035675 | 0.00027723 | 0.00017406 | 0.21186 | 0.21186 | 0.21186 | 0.98592 | -0.26965 | 0.98805 | -0.22856 | 14.551
46 | 0.026292 | 0.0065937 | -0.026282 | -0.0065876 | 9.9882e-06 | 6.1784e-06 | 0.039755 | 0.039755 | 0.039755 | 0.98413 | -0.30446 | 0.98372 | -0.31244 | 10.9218
47 | 0.00088591 | 0.0002217 | -0.00088589 | -0.00022203 | 1.8574e-08 | -3.3029e-07 | 0.0013477 | 0.0013478 | 0.0013478 | 0.97804 | -0.42293 | 0.97802 | -0.42337 | 0.37029
48 | -0.056927 | -0.014356 | 0.056962 | 0.014376 | 3.4984e-05 | 1.9893e-05 | 0.086641 | 0.08664 | 0.086641 | 0.97804 | -0.42293 | 0.9787 | -0.41009 | 5.9506
49 | 0.056041 | 0.014134 | -0.056021 | -0.014123 | 1.9466e-05 | 1.1026e-05 | 0.085294 | 0.085294 | 0.085294 | 0.97804 | -0.42293 | 0.97767 | -0.43018 | 5.8581
50 | 0.050084 | 0.012635 | -0.05007 | -0.012627 | 1.47e-05 | 8.056e-06 | 0.076258 | 0.076259 | 0.076259 | 0.97767 | -0.43018 | 0.97736 | -0.43632 | 5.2375
51 | -0.0057714 | -0.0014462 | 0.0057716 | 0.0014463 | 1.7856e-07 | 3.5821e-08 | 0.0087539 | 0.0087539 | 0.0087539 | 0.98103 | -0.36477 | 0.98106 | -0.36412 | 2.4049
52 | 0.0057714 | 0.0014462 | -0.0057713 | -0.0014462 | 3.3504e-08 | 6.7216e-09 | 0.0087539 | 0.0087539 | 0.0087539 | 0.98103 | -0.36477 | 0.98102 | -0.36489 | 2.4049
53 | -0.0069189 | -0.0017338 | 0.0069192 | 0.0017339 | 2.5192e-07 | 8.4201e-08 | 0.010494 | 0.010494 | 0.010494 | 0.98106 | -0.36412 | 0.9811 | -0.36336 | 2.883
54 | 0.0046168 | 0.0011569 | -0.0046167 | -0.0011569 | 1.1246e-07 | -5.2385e-09 | 0.0070027 | 0.0070027 | 0.0070027 | 0.98102 | -0.36489 | 0.981 | -0.3654 | 1.9238
55 | 0.0044567 | 0.0011167 | -0.0044563 | -0.0011167 | 3.9254e-07 | -4.2455e-08 | 0.0067339 | 0.006734 | 0.006734 | 0.9848 | -0.29207 | 0.98471 | -0.29392 | 1.85
56 | -0.010907 | -0.0027333 | 0.010909 | 0.0027347 | 2.6715e-06 | 1.3759e-06 | 0.01648 | 0.01648 | 0.01648 | 0.9848 | -0.29207 | 0.98507 | -0.28693 | 4.5274
57 | 0.0064501 | 0.0016166 | -0.0064484 | -0.0016161 | 1.6613e-06 | 4.6997e-07 | 0.0097459 | 0.0097461 | 0.0097461 | 0.9848 | -0.29207 | 0.98453 | -0.29748 | 2.6775
58 | 0.0044563 | 0.0011167 | -0.004456 | -0.0011168 | 3.8321e-07 | -4.1383e-08 | 0.006734 | 0.0067341 | 0.0067341 | 0.98471 | -0.29392 | 0.98462 | -0.29573 | 1.85
59 | -0.03229 | -0.008103 | 0.032307 | 0.0081135 | 1.6812e-05 | 1.0519e-05 | 0.048781 | 0.048781 | 0.048781 | 0.98507 | -0.28693 | 0.98563 | -0.27602 | 13.4013
60 | 0.021381 | 0.0053683 | -0.021364 | -0.005358 | 1.6932e-05 | 1.0286e-05 | 0.032301 | 0.032301 | 0.032301 | 0.98507 | -0.28693 | 0.98421 | -0.30355 | 8.8739
61 | 0.0061575 | 0.001543 | -0.0061573 | -0.001543 | 1.8493e-07 | 4.6628e-08 | 0.0093282 | 0.0093282 | 0.0093282 | 0.98222 | -0.34163 | 0.98218 | -0.34226 | 2.5627
62 | 0.021364 | 0.005358 | -0.021354 | -0.0053517 | 1.0429e-05 | 6.3362e-06 | 0.032301 | 0.032301 | 0.032301 | 0.98421 | -0.30355 | 0.98369 | -0.31379 | 8.874
63 | 0.0076746 | 0.0019234 | -0.0076743 | -0.0019233 | 3.1777e-07 | 1.2444e-07 | 0.011641 | 0.011642 | 0.011642 | 0.98097 | -0.366 | 0.98092 | -0.36687 | 3.1982
64 | -0.0076746 | -0.0019234 | 0.0076747 | 0.0019234 | 6.1365e-08 | 2.403e-08 | 0.011641 | 0.011641 | 0.011641 | 0.98097 | -0.366 | 0.98097 | -0.36583 | 3.1982
65 | 0.0057507 | 0.0014412 | -0.0057505 | -0.0014412 | 1.702e-07 | 3.3643e-08 | 0.0087235 | 0.0087236 | 0.0087236 | 0.98092 | -0.36687 | 0.98089 | -0.36749 | 2.3966
66 | -0.0095936 | -0.0024044 | 0.0095941 | 0.0024046 | 4.9856e-07 | 2.3982e-07 | 0.014552 | 0.014552 | 0.014552 | 0.98097 | -0.36583 | 0.98103 | -0.36474 | 3.9979
67 | 0.00064899 | 0.00016252 | -0.00064899 | -0.00016265 | 3.9087e-09 | -1.3604e-07 | 0.00097947 | 0.00097952 | 0.00097952 | 0.9859 | -0.27009 | 0.98589 | -0.27021 | 0.2691
68 | -0.14315 | -0.036321 | 0.14322 | 0.036365 | 6.9919e-05 | 4.3927e-05 | 0.21575 | 0.21575 | 0.21575 | 0.98805 | -0.22856 | 0.98858 | -0.21841 | 14.8178
69 | -0.40744 | -0.10378 | 0.40782 | 0.10402 | 0.00038002 | 0.00024264 | 0.60749 | 0.60749 | 0.60749 | 0.99898 | -0.019316 | 1 | 0 | 41.7229
70 | 0.40744 | 0.10378 | -0.40708 | -0.10355 | 0.000364 | 0.00023241 | 0.60749 | 0.60749 | 0.60749 | 0.99898 | -0.019316 | 0.99801 | -0.037854 | 41.723
71 | 0.0056178 | 0.0014073 | -0.0056134 | -0.0014067 | 4.423e-06 | 6.1838e-07 | 0.0083592 | 0.00836 | 0.00836 | 1 | 0 | 0.99914 | -0.016537 | 2.2967
72 | 0.38576 | 0.098205 | -0.38538 | -0.09796 | 0.00038347 | 0.00024478 | 0.5757 | 0.5757 | 0.5757 | 0.99801 | -0.037854 | 0.99692 | -0.058493 | 39.5401
73 | 0.019923 | 0.0049937 | -0.019914 | -0.0049882 | 9.1283e-06 | 5.502e-06 | 0.030136 | 0.030136 | 0.030136 | 0.98372 | -0.31244 | 0.98323 | -0.32206 | 8.2792
74 | 0.0063592 | 0.0015939 | -0.006354 | -0.0015925 | 5.2635e-06 | 1.4447e-06 | 0.0096193 | 0.00962 | 0.00962 | 0.98372 | -0.31244 | 0.98283 | -0.32982 | 2.6429
75 | 0.0053599 | 0.0013392 | -0.0053588 | -0.001339 | 1.0827e-06 | 1.3634e-07 | 0.0081102 | 0.0081104 | 0.0081104 | 0.98323 | -0.32206 | 0.98301 | -0.32631 | 2.2281
76 | 0.006354 | 0.0015925 | -0.0063534 | -0.0015923 | 5.6808e-07 | 1.5615e-07 | 0.00962 | 0.0096201 | 0.0096201 | 0.98283 | -0.32982 | 0.98274 | -0.3317 | 2.6429
77 | 0.0004646 | 0.00011617 | -0.0004646 | -0.00011644 | 4.005e-09 | -2.6446e-07 | 0.00070759 | 0.00070769 | 0.00070769 | 0.97689 | -0.44543 | 0.97688 | -0.44561 | 0.19442
78 | -0.0004646 | -0.00011617 | 0.0004646 | 0.00011607 | 1.5637e-09 | -1.0328e-07 | 0.00070759 | 0.00070755 | 0.00070759 | 0.97689 | -0.44543 | 0.9769 | -0.44536 | 0.19439
79 | -0.00087267 | -0.00021834 | 0.00087268 | 0.00021806 | 1.5417e-08 | -2.8154e-07 | 0.0013291 | 0.001329 | 0.0013291 | 0.9769 | -0.44536 | 0.97692 | -0.44499 | 0.36514
80 | 0.0017643 | 0.00044129 | -0.0017642 | -0.0004418 | 1.1952e-07 | -5.0532e-07 | 0.0026527 | 0.0026529 | 0.0026529 | 0.98958 | -0.19967 | 0.98951 | -0.20109 | 0.72881
81 | 0.065299 | 0.016484 | -0.065185 | -0.016412 | 0.00011347 | 7.2217e-05 | 0.098116 | 0.098116 | 0.098116 | 0.99075 | -0.17671 | 0.98887 | -0.21305 | 26.9549
82 | 0.14834 | 0.03776 | -0.14823 | -0.037691 | 0.00010996 | 6.9161e-05 | 0.223 | 0.223 | 0.223 | 0.99075 | -0.17671 | 0.98995 | -0.19209 | 15.3162
83 | -0.0052524 | -0.0013163 | 0.0052537 | 0.0013165 | 1.2623e-06 | 1.5471e-07 | 0.0080171 | 0.0080169 | 0.0080171 | 0.97487 | -0.4852 | 0.97512 | -0.48015 | 2.2025
84 | 0.0052524 | 0.0013163 | -0.0052519 | -0.0013163 | 4.4604e-07 | 5.4757e-08 | 0.0080171 | 0.0080172 | 0.0080172 | 0.97487 | -0.4852 | 0.97478 | -0.48698 | 2.2025
85 | 0.043396 | 0.010919 | -0.043283 | -0.010848 | 0.0001134 | 7.1716e-05 | 0.066238 | 0.066238 | 0.066238 | 0.97512 | -0.48015 | 0.97234 | -0.53499 | 18.1972
86 | -0.04865 | -0.012236 | 0.048732 | 0.012286 | 8.1861e-05 | 5.0412e-05 | 0.074255 | 0.074254 | 0.074255 | 0.97512 | -0.48015 | 0.97692 | -0.44499 | 10.1998
87 | -0.049605 | -0.012504 | 0.049625 | 0.012516 | 2.0592e-05 | 1.1252e-05 | 0.075583 | 0.075582 | 0.075583 | 0.97692 | -0.44499 | 0.97736 | -0.43632 | 5.1911
88 | 0.0061573 | 0.001543 | -0.0061567 | -0.0015428 | 5.9904e-07 | 1.5107e-07 | 0.0093282 | 0.0093283 | 0.0093283 | 0.98218 | -0.34226 | 0.98208 | -0.3443 | 2.5627
89 | 0.0025695 | 0.00064378 | -0.0025694 | -0.00064396 | 1.1197e-07 | -1.7759e-07 | 0.0038932 | 0.0038933 | 0.0038933 | 0.98208 | -0.3443 | 0.98203 | -0.34521 | 1.0696
90 | -0.042024 | -0.010549 | 0.042066 | 0.010575 | 4.2501e-05 | 2.6842e-05 | 0.06345 | 0.063449 | 0.06345 | 0.98563 | -0.27602 | 0.98671 | -0.25484 | 17.4312
91 | 0.0037142 | 0.00093072 | -0.003714 | -0.00093082 | 2.0062e-07 | -9.1307e-08 | 0.005589 | 0.005589 | 0.005589 | 0.98887 | -0.21305 | 0.98881 | -0.21418 | 1.5355
92 | 0.061471 | 0.015481 | -0.061424 | -0.015452 | 4.6775e-05 | 2.9749e-05 | 0.092527 | 0.092527 | 0.092527 | 0.98887 | -0.21305 | 0.98805 | -0.22897 | 25.4195
93 | 0.1465 | 0.037258 | -0.14635 | -0.037161 | 0.00015347 | 9.6489e-05 | 0.22041 | 0.22041 | 0.22041 | 0.98995 | -0.19209 | 0.98881 | -0.21386 | 15.1379
94 | -0.0011529 | -0.00028895 | 0.0011529 | 0.00028888 | 5.8964e-09 | -6.113e-08 | 0.0017488 | 0.0017488 | 0.0017488 | 0.98096 | -0.36615 | 0.98096 | -0.36604 | 0.48045
95 | -0.002308 | -0.00057838 | 0.002308 | 0.00057832 | 2.8131e-08 | -5.9266e-08 | 0.003501 | 0.0035009 | 0.003501 | 0.98096 | -0.36604 | 0.98098 | -0.36579 | 0.9618
96 | -0.064889 | -0.016404 | 0.064895 | 0.016407 | 5.431e-06 | 3.1741e-06 | 0.098478 | 0.098478 | 0.098478 | 0.98099 | -0.36542 | 0.98108 | -0.36367 | 6.7636
97 | -0.33654 | -0.085445 | 0.33675 | 0.085576 | 0.0002051 | 0.00013082 | 0.50383 | 0.50383 | 0.50383 | 0.99471 | -0.10074 | 0.99537 | -0.088081 | 34.6037
98 | 0.097605 | 0.024651 | -0.097592 | -0.024644 | 1.274e-05 | 7.8387e-06 | 0.14788 | 0.14788 | 0.14788 | 0.98259 | -0.33427 | 0.98245 | -0.33699 | 10.1565
99 | -0.008069 | -0.0020221 | 0.0080696 | 0.0020223 | 5.9398e-07 | 2.4658e-07 | 0.012238 | 0.012238 | 0.012238 | 0.9811 | -0.36336 | 0.98118 | -0.36181 | 3.3621
100 | 0.0034629 | 0.00086771 | -0.0034629 | -0.00086775 | 6.328e-08 | -3.6717e-08 | 0.0052527 | 0.0052527 | 0.0052527 | 0.981 | -0.3654 | 0.98098 | -0.36579 | 1.443
101 | 0.0038334 | 0.00096069 | -0.0038334 | -0.00096072 | 7.549e-08 | -2.6822e-08 | 0.0058153 | 0.0058154 | 0.0058154 | 0.98089 | -0.36749 | 0.98087 | -0.36791 | 1.5976
102 | -0.010739 | -0.0026916 | 0.01074 | 0.0026919 | 6.2434e-07 | 3.2035e-07 | 0.016289 | 0.016289 | 0.016289 | 0.98103 | -0.36474 | 0.98109 | -0.36352 | 4.475
103 | -0.14386 | -0.036525 | 0.14389 | 0.036545 | 3.1519e-05 | 1.9805e-05 | 0.21671 | 0.21671 | 0.21671 | 0.98858 | -0.21841 | 0.98881 | -0.21386 | 14.8839
104 | 0.0056134 | 0.0014067 | -0.0056117 | -0.0014064 | 1.6748e-06 | 2.3526e-07 | 0.00836 | 0.0083603 | 0.0083603 | 0.99914 | -0.016537 | 0.99881 | -0.022801 | 2.2968
105 | 0.35526 | 0.090413 | -0.35476 | -0.09009 | 0.00050594 | 0.0003228 | 0.53076 | 0.53076 | 0.53076 | 0.99692 | -0.058493 | 0.99537 | -0.088081 | 36.4531
106 | 0.0017642 | 0.0004418 | -0.0017641 | -0.00044213 | 7.8591e-08 | -3.3219e-07 | 0.0026529 | 0.002653 | 0.002653 | 0.98951 | -0.20109 | 0.98946 | -0.20203 | 0.72885
107 | 0.051772 | 0.013033 | -0.051708 | -0.012992 | 6.3919e-05 | 4.055e-05 | 0.07799 | 0.07799 | 0.07799 | 0.98805 | -0.22897 | 0.98671 | -0.25484 | 21.4258
108 | 0.0069067 | 0.0017307 | -0.0069059 | -0.0017304 | 7.4709e-07 | 2.4776e-07 | 0.010462 | 0.010462 | 0.010462 | 0.98231 | -0.34 | 0.98219 | -0.34227 | 2.8743
109 | 0.0029428 | 0.00073718 | -0.0029426 | -0.00073738 | 1.8594e-07 | -1.9672e-07 | 0.0044582 | 0.0044583 | 0.0044583 | 0.98219 | -0.34227 | 0.98213 | -0.3436 | 1.2248
110 | 0.0014995 | 0.00037571 | -0.0014995 | -0.00037581 | 1.703e-08 | -1.0044e-07 | 0.0022719 | 0.0022719 | 0.0022719 | 0.98213 | -0.3436 | 0.98211 | -0.34384 | 0.62416
111 | -0.06604 | -0.016694 | 0.066045 | 0.016697 | 5.6228e-06 | 3.2969e-06 | 0.10021 | 0.10021 | 0.10021 | 0.98108 | -0.36367 | 0.98117 | -0.3619 | 6.8829
112 | -0.06719 | -0.016984 | 0.067196 | 0.016988 | 5.8185e-06 | 3.4221e-06 | 0.10195 | 0.10195 | 0.10195 | 0.98117 | -0.3619 | 0.98126 | -0.36009 | 7.0021
113 | -0.06834 | -0.017275 | 0.068356 | 0.017284 | 1.5589e-05 | 9.1953e-06 | 0.10369 | 0.10369 | 0.10369 | 0.98126 | -0.36009 | 0.98151 | -0.35534 | 7.1213
114 | -0.069491 | -0.017568 | 0.069497 | 0.017572 | 6.1655e-06 | 3.6467e-06 | 0.10541 | 0.10541 | 0.10541 | 0.98151 | -0.35534 | 0.9816 | -0.35349 | 7.2395
115 | -0.070632 | -0.017856 | 0.070637 | 0.017859 | 5.0632e-06 | 3.0025e-06 | 0.10713 | 0.10713 | 0.10713 | 0.9816 | -0.35349 | 0.98168 | -0.35199 | 7.3576
116 | 0.092886 | 0.023444 | -0.092875 | -0.023437 | 1.1008e-05 | 6.7455e-06 | 0.14083 | 0.14083 | 0.14083 | 0.98183 | -0.34902 | 0.98171 | -0.35149 | 9.6726
117 | -0.094021 | -0.023728 | 0.094032 | 0.023735 | 1.1275e-05 | 6.9167e-06 | 0.14255 | 0.14255 | 0.14255 | 0.98183 | -0.34902 | 0.98196 | -0.34651 | 9.7907
118 | 0.09174 | 0.023153 | -0.091738 | -0.023152 | 2.1994e-06 | 1.3463e-06 | 0.13911 | 0.13911 | 0.13911 | 0.98171 | -0.35149 | 0.98168 | -0.35199 | 9.5544
119 | -0.095167 | -0.02402 | 0.095198 | 0.024039 | 3.1148e-05 | 1.9126e-05 | 0.14427 | 0.14427 | 0.14427 | 0.98196 | -0.34651 | 0.98231 | -0.33968 | 9.9087
120 | 0.021101 | 0.0052923 | -0.021093 | -0.0052877 | 7.5475e-06 | 4.5818e-06 | 0.031986 | 0.031986 | 0.031986 | 0.98168 | -0.35199 | 0.9813 | -0.3595 | 8.7873
121 | -0.096389 | -0.024338 | 0.096402 | 0.024345 | 1.2435e-05 | 7.6435e-06 | 0.14608 | 0.14608 | 0.14608 | 0.98231 | -0.33968 | 0.98245 | -0.33699 | 10.0327
122 | 0.019945 | 0.0049999 | -0.019943 | -0.0049986 | 2.1974e-06 | 1.3254e-06 | 0.030245 | 0.030245 | 0.030245 | 0.9813 | -0.3595 | 0.98118 | -0.36181 | 8.309
123 | 0.011873 | 0.0029763 | -0.011872 | -0.0029758 | 9.6904e-07 | 5.1954e-07 | 0.018007 | 0.018007 | 0.018007 | 0.98118 | -0.36181 | 0.98109 | -0.36352 | 4.947
124 | 0.0019167 | 0.00048035 | -0.0019167 | -0.00048036 | 3.2742e-09 | -1.094e-08 | 0.0029077 | 0.0029077 | 0.0029077 | 0.98087 | -0.36791 | 0.98087 | -0.36794 | 0.79881

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41509 | 0.10543

## res_load
| p_mw | q_mvar
0 | 0.00040073 | 0.00010043
1 | 0.0011182 | 0.00028025
2 | 0.00054666 | 0.00013701
3 | 0.00084554 | 0.00021191
4 | 0.00053943 | 0.00013519
5 | 0.00056713 | 0.00014214
6 | 0.0015447 | 0.00038714
7 | 0.0014183 | 0.00035546
8 | 0.0015128 | 0.00037915
9 | 0.0006199 | 0.00015536
10 | 0.0013384 | 0.00033544
11 | 0.00074774 | 0.0001874
12 | 0.0027602 | 0.00069178
13 | 0.0011451 | 0.00028698
14 | 0.0027501 | 0.00068925
15 | 0.017055 | 0.0042743
16 | 0.04317 | 0.010819
17 | 0.0020156 | 0.00050515
18 | 0.0089092 | 0.0022329
19 | 0.0016103 | 0.00040358
20 | 0.0092455 | 0.0023172
21 | 0.00088589 | 0.00022203
22 | 0.0059369 | 0.0014879
23 | 0.0011474 | 0.00028756
24 | 0.0011545 | 0.00028936
25 | 0.0064484 | 0.0016161
26 | 0.0043787 | 0.0010974
27 | 0.021354 | 0.0053517
28 | 0.0019236 | 0.00048209
29 | 0.0019189 | 0.00048093
30 | 0.00258 | 0.00064661
31 | 0.021317 | 0.0053426
32 | 0.0004646 | 0.00011644
33 | 0.00040806 | 0.00010227
34 | 0.0007251 | 0.00018173
35 | 0.0017293 | 0.0004334
36 | 0.0063534 | 0.0015923
37 | 0.0052519 | 0.0013163
38 | 0.00044439 | 0.00011137
39 | 0.0035871 | 0.00089902
40 | 0.0097164 | 0.0024352
41 | 0.043283 | 0.010848
42 | 0.0017269 | 0.00043279
43 | 0.0011529 | 0.00028895
44 | 0.0011551 | 0.00028949
45 | 0.001144 | 0.00028671
46 | 0.019302 | 0.0048374
47 | 0.019949 | 0.0049997
48 | 0.0011912 | 0.00029854
49 | 0.00064899 | 0.00016265
50 | 0.0011498 | 0.00028816
51 | 0.0011538 | 0.00028916
52 | 0.004456 | 0.0011168
53 | 0.0019171 | 0.00048047
54 | 0.001145 | 0.00028698
55 | 0.00063905 | 0.00016016
56 | 0.030113 | 0.007547
57 | 0.00059047 | 0.00014798
58 | 0.0025694 | 0.00064396
59 | 0.003714 | 0.00093082
60 | 0.0096525 | 0.0024192
61 | 0.009642 | 0.0024165
62 | 0.0024582 | 0.00061608
63 | 0.001201 | 0.00030099
64 | 0.0039632 | 0.00099326
65 | 0.0014431 | 0.00036167
66 | 0.0014995 | 0.00037581
67 | 0.018013 | 0.0045144
68 | 0.0056117 | 0.0014064
69 | 0.0017641 | 0.00044213
70 | 0.0011451 | 0.00028698
71 | 0.0011448 | 0.00028691
72 | 0.0011443 | 0.00028678
73 | 0.0011548 | 0.00028943
74 | 0.0011355 | 0.00028457
75 | 0.0011344 | 0.0002843
76 | 0.0011344 | 0.0002843
77 | 0.0011355 | 0.00028458
78 | 0.0011346 | 0.00028436
79 | 0.0011917 | 0.00029868
80 | 0.0011481 | 0.00028775
81 | 0.0011904 | 0.00029834
82 | 0.0011327 | 0.00028389
83 | 0.0019167 | 0.00048036
84 | 0.0019167 | 0.00048036

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1