## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-71_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-71_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-71_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-71_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-71_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-71_0_6_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_230-71_0_6_node_84 | 0.4 | n |  | TRUE
7 | bus_LV_230-71_0_6_node_83 | 0.4 | n |  | TRUE
8 | bus_LV_230-71_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_230-71_0_6_node_85 | 0.4 | n |  | TRUE
10 | bus_LV_230-71_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_230-71_0_6_node_87 | 0.4 | n |  | TRUE
12 | bus_LV_230-71_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_230-71_0_6_node_86 | 0.4 | n |  | TRUE
14 | bus_LV_230-71_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_230-71_0_6_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_230-71_0_6_node_89 | 0.4 | n |  | TRUE
17 | bus_LV_230-71_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_230-71_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_230-71_0_6_node_94 | 0.4 | n |  | TRUE
20 | bus_LV_230-71_0_6_node_99 | 0.4 | n |  | TRUE
21 | bus_LV_230-71_0_6_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_230-71_0_6_node_92 | 0.4 | n |  | TRUE
23 | bus_LV_230-71_0_6_node_88 | 0.4 | n |  | TRUE
24 | bus_LV_230-71_0_6_node_93 | 0.4 | n |  | TRUE
25 | bus_LV_230-71_0_6_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_230-71_0_6_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_230-71_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_230-71_0_6_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_230-71_0_6_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_230-71_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_230-71_0_6_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_230-71_0_6_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_230-71_0_6_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_230-71_0_6_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_230-71_0_6_node_54 | 0.4 | n |  | TRUE
36 | bus_LV_230-71_0_6_node_53 | 0.4 | n |  | TRUE
37 | bus_LV_230-71_0_6_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_230-71_0_6_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_230-71_0_6_node_49 | 0.4 | n |  | TRUE
40 | bus_LV_230-71_0_6_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_230-71_0_6_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_230-71_0_6_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_230-71_0_6_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_230-71_0_6_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_230-71_0_6_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_230-71_0_6_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_230-71_0_6_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_230-71_0_6_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_230-71_0_6_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_230-71_0_6_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_230-71_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_230-71_0_6_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_230-71_0_6_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_230-71_0_6_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_230-71_0_6_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_230-71_0_6_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_230-71_0_6_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_230-71_0_6_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_230-71_0_6_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_230-71_0_6_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_230-71_0_6_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_230-71_0_6_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_230-71_0_6_node_68 | 0.4 | n |  | TRUE
64 | bus_LV_230-71_0_6_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_230-71_0_6_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_230-71_0_6_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_230-71_0_6_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_230-71_0_6_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_230-71_0_6_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_230-71_0_6_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_230-71_0_6_node_76 | 0.4 | n |  | TRUE
72 | bus_LV_230-71_0_6_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_230-71_0_6_node_78 | 0.4 | n |  | TRUE
74 | bus_LV_230-71_0_6_node_74 | 0.4 | n |  | TRUE
75 | bus_LV_230-71_0_6_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_230-71_0_6_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_230-71_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_230-71_0_6_node_91 | 0.4 | n |  | TRUE
79 | bus_LV_230-71_0_6_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_230-71_0_6_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_230-71_0_6_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_230-71_0_6_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_230-71_0_6_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_230-71_0_6_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_230-71_0_6_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_230-71_0_6_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_230-71_0_6_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_230-71_0_6_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_230-71_0_6_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_230-71_0_6_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_230-71_0_6_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_230-71_0_6_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_230-71_0_6_node_100 | 0.4 | n |  | TRUE
94 | bus_LV_230-71_0_6_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_230-71_0_6_node_98 | 0.4 | n |  | TRUE
96 | bus_LV_230-71_0_6_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_230-71_0_6_node_96 | 0.4 | n |  | TRUE
98 | bus_MV_371_0_node_85 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-71_0_6_load_0 | 0 | 0.00093839 | 0.00023518 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-71_0_6_load_3 | 3 | 0.0013325 | 0.00033397 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-71_0_6_load_14 | 5 | 0.00073027 | 0.00018302 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-71_0_6_load_84 | 6 | 0.00058394 | 0.00014635 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-71_0_6_load_83 | 7 | 0.010141 | 0.0025415 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-71_0_6_load_85 | 9 | 0.0030974 | 0.00077628 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-71_0_6_load_86 | 13 | 0.0044688 | 0.00112 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-71_0_6_load_89 | 16 | 0.0051029 | 0.0012789 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-71_0_6_load_94 | 19 | 0.0036005 | 0.00090237 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-71_0_6_load_99 | 20 | 0.021567 | 0.0054052 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-71_0_6_load_92 | 22 | 0.0051049 | 0.0012794 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-71_0_6_load_88 | 23 | 0.0051051 | 0.0012795 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-71_0_6_load_93 | 24 | 0.0082948 | 0.0020789 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-71_0_6_load_15 | 25 | 0.006246 | 0.0015654 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-71_0_6_load_16 | 26 | 7.0929e-05 | 1.7776e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-71_0_6_load_17 | 27 | 0.00059596 | 0.00014936 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-71_0_6_load_31 | 28 | 5.3649e-05 | 1.3446e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-71_0_6_load_18 | 30 | 0.00034327 | 8.6032e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-71_0_6_load_21 | 32 | 0.00063415 | 0.00015893 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-71_0_6_load_44 | 33 | 0.00014572 | 3.6521e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-71_0_6_load_53 | 36 | 0.0003219 | 8.0677e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-71_0_6_load_45 | 37 | 0.00042017 | 0.0001053 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-71_0_6_load_70 | 38 | 0.00012469 | 3.1251e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-71_0_6_load_49 | 39 | 0.00027169 | 6.8092e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-71_0_6_load_23 | 40 | 5.4362e-05 | 1.3624e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-71_0_6_load_27 | 43 | 0.00047881 | 0.00012 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-71_0_6_load_26 | 44 | 0.00028984 | 7.2642e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-71_0_6_load_29 | 45 | 9.6987e-05 | 2.4307e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-71_0_6_load_30 | 46 | 0.0002568 | 6.4359e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-71_0_6_load_32 | 47 | 0.0010779 | 0.00027015 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-71_0_6_load_39 | 48 | 7.3208e-05 | 1.8348e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-71_0_6_load_33 | 49 | 0.0029325 | 0.00073496 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-71_0_6_load_40 | 50 | 0.0037724 | 0.00094545 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-71_0_6_load_34 | 51 | 0.0049219 | 0.0012335 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-71_0_6_load_35 | 52 | 0.023464 | 0.0058806 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-71_0_6_load_38 | 55 | 0.04762 | 0.011935 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-71_0_6_load_95 | 56 | 0.003997 | 0.0010017 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-71_0_6_load_57 | 59 | 0.0072451 | 0.0018158 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-71_0_6_load_41 | 60 | 0.00031806 | 7.9713e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-71_0_6_load_43 | 62 | 0.0015816 | 0.00039639 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-71_0_6_load_68 | 63 | 0.0019494 | 0.00048857 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-71_0_6_load_46 | 68 | 0.00029123 | 7.299e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-71_0_6_load_47 | 69 | 0.0001145 | 2.8697e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-71_0_6_load_51 | 70 | 0.00014127 | 3.5406e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-71_0_6_load_76 | 71 | 0.00020566 | 5.1542e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-71_0_6_load_73 | 72 | 0.0012043 | 0.00030182 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-71_0_6_load_78 | 73 | 0.0019753 | 0.00049504 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-71_0_6_load_74 | 74 | 0.00053408 | 0.00013385 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-71_0_6_load_71 | 75 | 0.0011679 | 0.0002927 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-71_0_6_load_61 | 76 | 0.0058688 | 0.0014709 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-71_0_6_load_58 | 77 | 0.03015 | 0.0075562 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-71_0_6_load_91 | 78 | 0.0088301 | 0.002213 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-71_0_6_load_59 | 79 | 0.0010081 | 0.00025264 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-71_0_6_load_60 | 80 | 0.044479 | 0.011147 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-71_0_6_load_62 | 81 | 0.00094808 | 0.00023761 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-71_0_6_load_63 | 82 | 0.0048764 | 0.0012221 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-71_0_6_load_65 | 83 | 0.0010991 | 0.00027547 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-71_0_6_load_64 | 84 | 0.0030791 | 0.00077169 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-71_0_6_load_66 | 85 | 0.00068212 | 0.00017095 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-71_0_6_load_67 | 86 | 0.0022136 | 0.00055478 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-71_0_6_load_90 | 87 | 0.00063915 | 0.00016019 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-71_0_6_load_75 | 89 | 0.00038587 | 9.6709e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-71_0_6_load_100 | 93 | 0.034298 | 0.0085958 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-71_0_6_load_98 | 95 | 0.025282 | 0.0063363 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-71_0_6_load_97 | 96 | 0.0022292 | 0.00055869 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-71_0_6_load_96 | 97 | 0.0036922 | 0.00092536 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-71_0_6_line_0 |  | 0 | 1 | 0.046952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-71_0_6_line_1 |  | 0 | 2 | 0.0066416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-71_0_6_line_2 |  | 1 | 3 | 0.07028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-71_0_6_line_3 |  | 1 | 4 | 0.04261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-71_0_6_line_4 |  | 2 | 5 | 0.013883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-71_0_6_line_5 |  | 4 | 6 | 0.041111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-71_0_6_line_6 |  | 4 | 7 | 0.025412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-71_0_6_line_7 |  | 5 | 8 | 0.014263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-71_0_6_line_8 |  | 6 | 10 | 0.0058621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-71_0_6_line_9 |  | 8 | 9 | 0.018631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-71_0_6_line_10 |  | 9 | 12 | 0.032084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-71_0_6_line_11 |  | 10 | 11 | 0.034286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-71_0_6_line_12 |  | 11 | 23 | 0.02676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-71_0_6_line_13 |  | 12 | 13 | 0.00534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-71_0_6_line_14 |  | 14 | 15 | 0.057986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_230-71_0_6_line_15 |  | 14 | 16 | 0.018062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_230-71_0_6_line_16 |  | 15 | 22 | 0.017871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_230-71_0_6_line_17 |  | 15 | 21 | 0.11555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-71_0_6_line_18 |  | 16 | 23 | 0.00050651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-71_0_6_line_19 |  | 17 | 18 | 0.068813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-71_0_6_line_20 |  | 17 | 19 | 0.011578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-71_0_6_line_21 |  | 18 | 20 | 0.006809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-71_0_6_line_22 |  | 19 | 21 | 0.0038543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-71_0_6_line_23 |  | 22 | 24 | 0.00065133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_230-71_0_6_line_24 |  | 24 | 64 | 0.030822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_230-71_0_6_line_25 |  | 25 | 26 | 0.04881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-71_0_6_line_26 |  | 26 | 27 | 0.0028288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-71_0_6_line_27 |  | 27 | 28 | 0.040423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-71_0_6_line_28 |  | 28 | 29 | 0.036248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-71_0_6_line_29 |  | 29 | 45 | 0.025401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_230-71_0_6_line_30 |  | 29 | 46 | 0.050355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_230-71_0_6_line_31 |  | 29 | 44 | 0.030643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-71_0_6_line_32 |  | 30 | 31 | 0.020181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-71_0_6_line_33 |  | 31 | 32 | 0.079354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-71_0_6_line_34 |  | 32 | 33 | 0.098638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-71_0_6_line_35 |  | 33 | 37 | 0.0075796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-71_0_6_line_36 |  | 34 | 35 | 0.090696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-71_0_6_line_37 |  | 34 | 36 | 0.090731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-71_0_6_line_38 |  | 35 | 38 | 0.10687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-71_0_6_line_39 |  | 36 | 39 | 0.0094776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-71_0_6_line_40 |  | 37 | 65 | 0.025206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-71_0_6_line_41 |  | 38 | 75 | 0.035736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-71_0_6_line_42 |  | 39 | 69 | 0.0085144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-71_0_6_line_43 |  | 40 | 41 | 0.084259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-71_0_6_line_44 |  | 41 | 42 | 0.051765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-71_0_6_line_45 |  | 42 | 43 | 0.023611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-71_0_6_line_46 |  | 43 | 44 | 0.014531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-71_0_6_line_47 |  | 45 | 47 | 0.044692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_230-71_0_6_line_48 |  | 46 | 48 | 0.00040403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_230-71_0_6_line_49 |  | 47 | 49 | 0.013529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_230-71_0_6_line_50 |  | 48 | 50 | 0.00024673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_230-71_0_6_line_51 |  | 49 | 51 | 0.061028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_230-71_0_6_line_52 |  | 50 | 60 | 0.013359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_230-71_0_6_line_53 |  | 51 | 52 | 0.023678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_230-71_0_6_line_54 |  | 52 | 53 | 0.067763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_230-71_0_6_line_55 |  | 53 | 54 | 0.016422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-71_0_6_line_56 |  | 53 | 55 | 0.010815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_230-71_0_6_line_57 |  | 54 | 56 | 0.015605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-71_0_6_line_58 |  | 55 | 57 | 0.031267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_230-71_0_6_line_59 |  | 57 | 58 | 0.052995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_230-71_0_6_line_60 |  | 57 | 59 | 0.034005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-71_0_6_line_61 |  | 58 | 76 | 0.037254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-71_0_6_line_62 |  | 58 | 77 | 0.0048711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_230-71_0_6_line_63 |  | 60 | 61 | 0.052419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_230-71_0_6_line_64 |  | 61 | 62 | 0.28989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_230-71_0_6_line_65 |  | 62 | 63 | 0.0037461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_230-71_0_6_line_66 |  | 63 | 64 | 0.049473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_230-71_0_6_line_67 |  | 65 | 66 | 0.018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-71_0_6_line_68 |  | 65 | 67 | 0.022876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-71_0_6_line_69 |  | 66 | 71 | 0.0012541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-71_0_6_line_70 |  | 66 | 72 | 0.017376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-71_0_6_line_71 |  | 67 | 70 | 0.025803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-71_0_6_line_72 |  | 67 | 68 | 0.029021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-71_0_6_line_73 |  | 68 | 69 | 0.019381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-71_0_6_line_74 |  | 71 | 73 | 0.037091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-71_0_6_line_75 |  | 72 | 74 | 0.016872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-71_0_6_line_76 |  | 74 | 89 | 0.028486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-71_0_6_line_77 |  | 76 | 78 | 0.0040048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-71_0_6_line_78 |  | 77 | 79 | 0.02178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_230-71_0_6_line_79 |  | 79 | 80 | 0.034658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_230-71_0_6_line_80 |  | 80 | 81 | 0.020239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_230-71_0_6_line_81 |  | 81 | 82 | 0.023204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-71_0_6_line_82 |  | 82 | 83 | 0.033527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_230-71_0_6_line_83 |  | 83 | 84 | 7.4056e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-71_0_6_line_84 |  | 84 | 85 | 0.013944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-71_0_6_line_85 |  | 85 | 86 | 0.0017411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-71_0_6_line_86 |  | 86 | 87 | 0.0018716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-71_0_6_line_87 |  | 87 | 88 | 0.013611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-71_0_6_line_88 |  | 88 | 94 | 0.047111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-71_0_6_line_89 |  | 89 | 90 | 0.036615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-71_0_6_line_90 |  | 90 | 91 | 0.15693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-71_0_6_line_91 |  | 90 | 92 | 0.2132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-71_0_6_line_92 |  | 91 | 93 | 0.022227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-71_0_6_line_93 |  | 92 | 95 | 0.049019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-71_0_6_line_94 |  | 92 | 96 | 0.025896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-71_0_6_line_95 |  | 94 | 97 | 0.018744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-71_0_6_line_96 |  | 96 | 97 | 0.008429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-71_0_6_trafo_59 | 0.63 MVA 20/0.4 kV | 98 | 79 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2693527.0767 | 1262551.9523 | 2693564.1549 | 1262523.1474
1 | 2693569.3998 | 1262519.0729 | 2693564.1549 | 1262523.1474
2 | 2693527.0767 | 1262551.9523 | 2693496.8119 | 1262559.9136 | 2693465.223 | 1262582.762
3 | 2693496.988 | 1262580.2217 | 2693507.5451 | 1262574.4394 | 2693508.6361 | 1262569.297 | 2693527.0767 | 1262551.9523
4 | 2693569.3998 | 1262519.0729 | 2693578.2013 | 1262529.809
5 | 2693496.988 | 1262580.2217 | 2693464.7599 | 1262605.746
6 | 2693496.988 | 1262580.2217 | 2693498.8642 | 1262582.5977 | 2693500.5061 | 1262581.6896 | 2693502.7769 | 1262581.5031 | 2693504.7747 | 1262582.3909 | 2693506.217 | 1262583.6147 | 2693515.33 | 1262594.4416
7 | 2693587.244 | 1262540.8394 | 2693578.2013 | 1262529.809
8 | 2693460.1645 | 1262609.3855 | 2693464.7599 | 1262605.746
9 | 2693587.244 | 1262540.8394 | 2693572.7236 | 1262552.5137
10 | 2693547.7187 | 1262572.6176 | 2693572.7236 | 1262552.5137
11 | 2693433.3116 | 1262630.8008 | 2693460.1645 | 1262609.3855
12 | 2693433.3116 | 1262630.8008 | 2693450.468 | 1262651.3377
13 | 2693547.7187 | 1262572.6176 | 2693546.5651 | 1262571.2427 | 2693543.7948 | 1262573.4673
14 | 2693462.3725 | 1262665.5879 | 2693417.9377 | 1262702.994
15 | 2693462.3725 | 1262665.5879 | 2693450.7927 | 1262651.7264
16 | 2693417.9377 | 1262702.994 | 2693406.3699 | 1262689.3717
17 | 2693417.9377 | 1262702.994 | 2693403.3376 | 1262715.2733 | 2693404.7787 | 1262717.5312 | 2693394.9548 | 1262725.5715 | 2693396.8515 | 1262727.6031 | 2693404.7883 | 1262722.1685 | 2693406.444 | 1262724.1962 | 2693409.127 | 1262727.4857 | 2693427.1727 | 1262712.1917 | 2693440.2283 | 1262726.5984 | 2693450.1142 | 1262737.519 | 2693452.8098 | 1262740.4862
18 | 2693450.7927 | 1262651.7264 | 2693450.468 | 1262651.3377
19 | 2693464.3785 | 1262730.2718 | 2693471.9432 | 1262723.5971 | 2693481.1585 | 1262715.4584 | 2693482.786 | 1262714.0274 | 2693493.7818 | 1262704.3156 | 2693499.0563 | 1262697.1487 | 2693503.6394 | 1262693.2069 | 2693514.7531 | 1262683.6637
20 | 2693464.3785 | 1262730.2718 | 2693455.6991 | 1262737.9352
21 | 2693514.7531 | 1262683.6637 | 2693510.276 | 1262678.5221
22 | 2693452.8098 | 1262740.4862 | 2693455.6991 | 1262737.9352
23 | 2693406.3699 | 1262689.3717 | 2693405.9483 | 1262688.8752
24 | 2693385.998 | 1262665.3815 | 2693405.9483 | 1262688.8752
25 | 2692933.8689 | 1262855.8969 | 2692970.7933 | 1262823.9752
26 | 2692972.9333 | 1262822.1251 | 2692970.7933 | 1262823.9752
27 | 2692972.9333 | 1262822.1251 | 2693003.5133 | 1262795.6883
28 | 2693031.8136 | 1262773.0983 | 2693019.2097 | 1262782.1185 | 2693003.5133 | 1262795.6883
29 | 2693031.8136 | 1262773.0983 | 2693039.7015 | 1262754.9522 | 2693043.5389 | 1262750.8535
30 | 2693031.8136 | 1262773.0983 | 2693040.5117 | 1262782.4538 | 2693065.047 | 1262810.9197
31 | 2693031.8136 | 1262773.0983 | 2693025.8914 | 1262761.6182 | 2693014.2156 | 1262748.2815
32 | 2693171.7791 | 1262220.1448 | 2693164.897 | 1262239.1157
33 | 2693171.7791 | 1262220.1448 | 2693177.1331 | 1262221.319 | 2693239.317 | 1262234.9097 | 2693248.7341 | 1262238.8828
34 | 2693248.7341 | 1262238.8828 | 2693298.4056 | 1262259.8392 | 2693310.4493 | 1262264.9221 | 2693340.1098 | 1262253.8662
35 | 2693347.212 | 1262251.2188 | 2693340.1098 | 1262253.8662
36 | 2693231.2583 | 1262132.9117 | 2693291.6014 | 1262065.0529
37 | 2693231.2583 | 1262132.9117 | 2693288.2375 | 1262172.6753 | 2693305.4955 | 1262185.0725
38 | 2693291.6014 | 1262065.0529 | 2693395.6431 | 1262040.6088
39 | 2693305.4955 | 1262185.0725 | 2693313.193 | 1262190.602
40 | 2693370.9159 | 1262242.6472 | 2693347.7414 | 1262251.0215 | 2693347.212 | 1262251.2188
41 | 2693395.6431 | 1262040.6088 | 2693417.5419 | 1262068.8493
42 | 2693320.1082 | 1262195.5695 | 2693313.193 | 1262190.602
43 | 2692954.8084 | 1262680.8689 | 2692948.0492 | 1262656.4764 | 2692945.8921 | 1262634.1023 | 2692949.4233 | 1262597.8041
44 | 2692954.8084 | 1262680.8689 | 2692962.4175 | 1262690.9744 | 2692989.0916 | 1262719.5834
45 | 2692989.0916 | 1262719.5834 | 2693004.6442 | 1262737.3484
46 | 2693014.2156 | 1262748.2815 | 2693004.6442 | 1262737.3484
47 | 2693074.0845 | 1262718.2286 | 2693043.5389 | 1262750.8535
48 | 2693065.047 | 1262810.9197 | 2693065.3107 | 1262811.2257
49 | 2693074.0845 | 1262718.2286 | 2693083.331 | 1262708.3526
50 | 2693065.3107 | 1262811.2257 | 2693065.4718 | 1262811.4126
51 | 2693125.0416 | 1262663.8026 | 2693083.331 | 1262708.3526
52 | 2693074.1937 | 1262821.5317 | 2693065.4718 | 1262811.4126
53 | 2693125.0416 | 1262663.8026 | 2693141.2245 | 1262646.5181
54 | 2693187.5377 | 1262597.0521 | 2693141.2245 | 1262646.5181
55 | 2693187.5377 | 1262597.0521 | 2693182.2564 | 1262591.7647 | 2693175.7536 | 1262585.5795
56 | 2693187.5377 | 1262597.0521 | 2693195.3581 | 1262589.5825
57 | 2693175.7536 | 1262585.5795 | 2693164.4437 | 1262574.8273
58 | 2693217.9689 | 1262567.986 | 2693195.3581 | 1262589.5825
59 | 2693217.9689 | 1262567.986 | 2693259.8269 | 1262535.3305
60 | 2693217.9689 | 1262567.986 | 2693210.0405 | 1262561.9006 | 2693200.1866 | 1262554.6394 | 2693190.5888 | 1262547.8266
61 | 2693259.8269 | 1262535.3305 | 2693236.5856 | 1262506.2147
62 | 2693259.8269 | 1262535.3305 | 2693263.6244 | 1262532.2798
63 | 2693108.1922 | 1262861.4269 | 2693104.5458 | 1262857.1104 | 2693099.0243 | 1262850.3403 | 2693074.1937 | 1262821.5317
64 | 2693108.1922 | 1262861.4269 | 2693179.096 | 1262805.1313 | 2693190.0511 | 1262800.3445 | 2693199.771 | 1262796.4834 | 2693321.5604 | 1262692.2306 | 2693329.4166 | 1262688.0846 | 2693336.6061 | 1262685.1998
65 | 2693336.6061 | 1262685.1998 | 2693340.0828 | 1262683.8048
66 | 2693385.998 | 1262665.3815 | 2693340.0828 | 1262683.8048
67 | 2693370.9159 | 1262242.6472 | 2693384.0562 | 1262255.1091
68 | 2693370.9159 | 1262242.6472 | 2693365.4669 | 1262234.1321 | 2693360.1347 | 1262222.5164
69 | 2693384.0562 | 1262255.1091 | 2693385.1923 | 1262255.6399
70 | 2693384.0562 | 1262255.1091 | 2693399.23 | 1262246.6418
71 | 2693360.1347 | 1262222.5164 | 2693358.0575 | 1262212.342 | 2693356.5175 | 1262197.25 | 2693356.4945 | 1262197.0024
72 | 2693360.1347 | 1262222.5164 | 2693354.2876 | 1262220.1222 | 2693335.8492 | 1262206.877
73 | 2693335.8492 | 1262206.877 | 2693320.1082 | 1262195.5695
74 | 2693418.7962 | 1262271.3412 | 2693385.1923 | 1262255.6399
75 | 2693399.23 | 1262246.6418 | 2693399.23 | 1262246.6418 | 2693407.4411 | 1262244.87 | 2693415.8295 | 1262246.0535
76 | 2693415.8295 | 1262246.0535 | 2693422.0868 | 1262246.9363 | 2693429.7229 | 1262255.7974 | 2693437.3065 | 1262263.0152
77 | 2693236.5856 | 1262506.2147 | 2693234.0872 | 1262503.0848
78 | 2693263.6244 | 1262532.2798 | 2693280.6038 | 1262518.6391
79 | 2693307.6228 | 1262496.9331 | 2693280.6038 | 1262518.6391
80 | 2693307.6228 | 1262496.9331 | 2693323.4009 | 1262484.2576
81 | 2693341.4902 | 1262469.7253 | 2693323.4009 | 1262484.2576
82 | 2693367.6271 | 1262448.7279 | 2693341.4902 | 1262469.7253
83 | 2693367.6328 | 1262448.7233 | 2693367.6271 | 1262448.7279
84 | 2693367.6328 | 1262448.7233 | 2693378.5038 | 1262439.99
85 | 2693379.8611 | 1262438.8995 | 2693378.5038 | 1262439.99
86 | 2693379.8611 | 1262438.8995 | 2693381.3202 | 1262437.7273
87 | 2693391.9077 | 1262429.1733 | 2693389.1976 | 1262431.3989 | 2693381.3202 | 1262437.7273
88 | 2693422.185 | 1262465.2582 | 2693397.9427 | 1262435.8739 | 2693391.9077 | 1262429.1733
89 | 2693458.1042 | 1262292.7088 | 2693452.5635 | 1262281.4232 | 2693445.0374 | 1262270.3732 | 2693437.3065 | 1262263.0152
90 | 2693458.1042 | 1262292.7088 | 2693476.1581 | 1262305.571 | 2693512.3815 | 1262331.1308 | 2693516.5221 | 1262341.8382 | 2693520.2211 | 1262342.8308 | 2693523.6523 | 1262344.5643 | 2693542.6894 | 1262358.1318 | 2693546.714 | 1262360.4528 | 2693528.7621 | 1262374.9696 | 2693533.8538 | 1262381.2774 | 2693536.3811 | 1262384.4199 | 2693538.9381 | 1262387.5851 | 2693541.4209 | 1262390.6713
91 | 2693458.1042 | 1262292.7088 | 2693476.1581 | 1262305.571 | 2693512.3815 | 1262331.1308 | 2693494.9171 | 1262346.7451 | 2693434.7262 | 1262394.0322 | 2693431.8483 | 1262396.3887 | 2693437.6559 | 1262403.6529 | 2693459.1112 | 1262429.6461
92 | 2693523.9919 | 1262404.5291 | 2693532.4241 | 1262397.8237 | 2693541.4209 | 1262390.6713
93 | 2693459.1112 | 1262429.6461 | 2693490.314 | 1262467.4518
94 | 2693459.1112 | 1262429.6461 | 2693459.0343 | 1262431.6465 | 2693459.017 | 1262435.1268 | 2693443.2154 | 1262448.0506
95 | 2693422.185 | 1262465.2582 | 2693425.1241 | 1262462.8471 | 2693436.6908 | 1262453.387
96 | 2693436.6908 | 1262453.387 | 2693443.2154 | 1262448.0506

## bus_geodata
| x | y | coords
0 | 2693564.1549 | 1262523.1474
1 | 2693527.0767 | 1262551.9523
2 | 2693569.3998 | 1262519.0729
3 | 2693465.223 | 1262582.762
4 | 2693496.988 | 1262580.2217
5 | 2693578.2013 | 1262529.809
6 | 2693464.7599 | 1262605.746
7 | 2693515.33 | 1262594.4416
8 | 2693587.244 | 1262540.8394
9 | 2693572.7236 | 1262552.5137
10 | 2693460.1645 | 1262609.3855
11 | 2693433.3116 | 1262630.8008
12 | 2693547.7187 | 1262572.6176
13 | 2693543.7948 | 1262573.4673
14 | 2693462.3725 | 1262665.5879
15 | 2693417.9377 | 1262702.994
16 | 2693450.7927 | 1262651.7264
17 | 2693464.3785 | 1262730.2718
18 | 2693514.7531 | 1262683.6637
19 | 2693455.6991 | 1262737.9352
20 | 2693510.276 | 1262678.5221
21 | 2693452.8098 | 1262740.4862
22 | 2693406.3699 | 1262689.3717
23 | 2693450.468 | 1262651.3377
24 | 2693405.9483 | 1262688.8752
25 | 2692933.8689 | 1262855.8969
26 | 2692970.7933 | 1262823.9752
27 | 2692972.9333 | 1262822.1251
28 | 2693003.5133 | 1262795.6883
29 | 2693031.8136 | 1262773.0983
30 | 2693164.897 | 1262239.1157
31 | 2693171.7791 | 1262220.1448
32 | 2693248.7341 | 1262238.8828
33 | 2693340.1098 | 1262253.8662
34 | 2693231.2583 | 1262132.9117
35 | 2693291.6014 | 1262065.0529
36 | 2693305.4955 | 1262185.0725
37 | 2693347.212 | 1262251.2188
38 | 2693395.6431 | 1262040.6088
39 | 2693313.193 | 1262190.602
40 | 2692949.4233 | 1262597.8041
41 | 2692954.8084 | 1262680.8689
42 | 2692989.0916 | 1262719.5834
43 | 2693004.6442 | 1262737.3484
44 | 2693014.2156 | 1262748.2815
45 | 2693043.5389 | 1262750.8535
46 | 2693065.047 | 1262810.9197
47 | 2693074.0845 | 1262718.2286
48 | 2693065.3107 | 1262811.2257
49 | 2693083.331 | 1262708.3526
50 | 2693065.4718 | 1262811.4126
51 | 2693125.0416 | 1262663.8026
52 | 2693141.2245 | 1262646.5181
53 | 2693187.5377 | 1262597.0521
54 | 2693175.7536 | 1262585.5795
55 | 2693195.3581 | 1262589.5825
56 | 2693164.4437 | 1262574.8273
57 | 2693217.9689 | 1262567.986
58 | 2693259.8269 | 1262535.3305
59 | 2693190.5888 | 1262547.8266
60 | 2693074.1937 | 1262821.5317
61 | 2693108.1922 | 1262861.4269
62 | 2693336.6061 | 1262685.1998
63 | 2693340.0828 | 1262683.8048
64 | 2693385.998 | 1262665.3815
65 | 2693370.9159 | 1262242.6472
66 | 2693384.0562 | 1262255.1091
67 | 2693360.1347 | 1262222.5164
68 | 2693335.8492 | 1262206.877
69 | 2693320.1082 | 1262195.5695
70 | 2693356.4945 | 1262197.0024
71 | 2693385.1923 | 1262255.6399
72 | 2693399.23 | 1262246.6418
73 | 2693418.7962 | 1262271.3412
74 | 2693415.8295 | 1262246.0535
75 | 2693417.5419 | 1262068.8493
76 | 2693236.5856 | 1262506.2147
77 | 2693263.6244 | 1262532.2798
78 | 2693234.0872 | 1262503.0848
79 | 2693280.6038 | 1262518.6391
80 | 2693307.6228 | 1262496.9331
81 | 2693323.4009 | 1262484.2576
82 | 2693341.4902 | 1262469.7253
83 | 2693367.6271 | 1262448.7279
84 | 2693367.6328 | 1262448.7233
85 | 2693378.5038 | 1262439.99
86 | 2693379.8611 | 1262438.8995
87 | 2693381.3202 | 1262437.7273
88 | 2693391.9077 | 1262429.1733
89 | 2693437.3065 | 1262263.0152
90 | 2693458.1042 | 1262292.7088
91 | 2693541.4209 | 1262390.6713
92 | 2693459.1112 | 1262429.6461
93 | 2693523.9919 | 1262404.5291
94 | 2693422.185 | 1262465.2582
95 | 2693490.314 | 1262467.4517
96 | 2693443.2154 | 1262448.0506
97 | 2693436.6908 | 1262453.387
98 | 2693259.8269 | 1262535.3305

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97055 | -0.56881 | 0.00093839 | 0.00023518
1 | 0.97096 | -0.56079 | 0 | 0
2 | 0.9705 | -0.56983 | 0 | 0
3 | 0.97087 | -0.56252 | 0.0013325 | 0.00033397
4 | 0.97138 | -0.55246 | 0 | 0
5 | 0.97039 | -0.57196 | 0.00073027 | 0.00018302
6 | 0.97217 | -0.53674 | 0.00058394 | 0.00014635
7 | 0.97114 | -0.55722 | 0.010141 | 0.0025415
8 | 0.97029 | -0.57396 | 0 | 0
9 | 0.97016 | -0.57657 | 0.0030974 | 0.00077628
10 | 0.97229 | -0.53444 | 0 | 0
11 | 0.97297 | -0.52098 | 0 | 0
12 | 0.97003 | -0.57923 | 0 | 0
13 | 0.97001 | -0.57967 | 0.0044688 | 0.00112
14 | 0.97378 | -0.50501 | 0 | 0
15 | 0.97464 | -0.48823 | 0 | 0
16 | 0.97352 | -0.51024 | 0.0051029 | 0.0012789
17 | 0.97159 | -0.54815 | 0 | 0
18 | 0.97021 | -0.57559 | 0 | 0
19 | 0.97183 | -0.54354 | 0.0036005 | 0.00090237
20 | 0.97007 | -0.57831 | 0.021567 | 0.0054052
21 | 0.97192 | -0.54175 | 0 | 0
22 | 0.97495 | -0.48204 | 0.0051049 | 0.0012794
23 | 0.9735 | -0.51049 | 0.0051051 | 0.0012795
24 | 0.97496 | -0.48179 | 0.0082948 | 0.0020789
25 | 0.98539 | -0.27911 | 0.006246 | 0.0015654
26 | 0.98568 | -0.27364 | 7.0929e-05 | 1.7776e-05
27 | 0.98569 | -0.27332 | 0.00059596 | 0.00014936
28 | 0.98595 | -0.2683 | 5.3649e-05 | 1.3446e-05
29 | 0.98618 | -0.26378 | 0 | 0
30 | 0.97507 | -0.47927 | 0.00034327 | 8.6032e-05
31 | 0.97508 | -0.47914 | 0 | 0
32 | 0.97511 | -0.47864 | 0.00063415 | 0.00015893
33 | 0.9752 | -0.47686 | 0.00014572 | 3.6521e-05
34 | 0.97495 | -0.4817 | 0 | 0
35 | 0.97484 | -0.48386 | 0 | 0
36 | 0.97506 | -0.47953 | 0.0003219 | 8.0677e-05
37 | 0.9752 | -0.4767 | 0.00042017 | 0.0001053
38 | 0.97471 | -0.4864 | 0.00012469 | 3.1251e-05
39 | 0.97507 | -0.47925 | 0.00027169 | 6.8092e-05
40 | 0.98614 | -0.26453 | 5.4362e-05 | 1.3624e-05
41 | 0.98615 | -0.26445 | 0 | 0
42 | 0.98615 | -0.2644 | 0 | 0
43 | 0.98615 | -0.26437 | 0.00047881 | 0.00012
44 | 0.98616 | -0.26423 | 0.00028984 | 7.2642e-05
45 | 0.98686 | -0.25075 | 9.6987e-05 | 2.4307e-05
46 | 0.98496 | -0.28729 | 0.0002568 | 6.4359e-05
47 | 0.98805 | -0.22785 | 0.0010779 | 0.00027015
48 | 0.98495 | -0.28748 | 7.3208e-05 | 1.8348e-05
49 | 0.98842 | -0.22084 | 0.0029325 | 0.00073496
50 | 0.98494 | -0.2876 | 0.0037724 | 0.00094545
51 | 0.99012 | -0.18823 | 0.0049219 | 0.0012335
52 | 0.99082 | -0.17492 | 0.023464 | 0.0058806
53 | 0.9933 | -0.12756 | 0 | 0
54 | 0.99324 | -0.12872 | 0 | 0
55 | 0.99371 | -0.11976 | 0.04762 | 0.011935
56 | 0.99318 | -0.12982 | 0.003997 | 0.0010017
57 | 0.99534 | -0.088536 | 0 | 0
58 | 0.99823 | -0.033601 | 0 | 0
59 | 0.99512 | -0.092872 | 0.0072451 | 0.0018158
60 | 0.98464 | -0.29352 | 0.00031806 | 7.9713e-05
61 | 0.98344 | -0.31669 | 0 | 0
62 | 0.9768 | -0.44581 | 0.0015816 | 0.00039639
63 | 0.97671 | -0.44745 | 0.0019494 | 0.00048857
64 | 0.97563 | -0.4686 | 0 | 0
65 | 0.97524 | -0.47599 | 0 | 0
66 | 0.97531 | -0.47466 | 0 | 0
67 | 0.97519 | -0.47701 | 0 | 0
68 | 0.97513 | -0.47824 | 0.00029123 | 7.299e-05
69 | 0.97509 | -0.47895 | 0.0001145 | 2.8697e-05
70 | 0.97518 | -0.47708 | 0.00014127 | 3.5406e-05
71 | 0.9753 | -0.47471 | 0.00020566 | 5.1542e-05
72 | 0.97541 | -0.4727 | 0.0012043 | 0.00030182
73 | 0.97524 | -0.47606 | 0.0019753 | 0.00049504
74 | 0.97552 | -0.47041 | 0.00053408 | 0.00013385
75 | 0.97468 | -0.48716 | 0.0011679 | 0.0002927
76 | 0.99773 | -0.043184 | 0.0058688 | 0.0014709
77 | 0.99852 | -0.02815 | 0.03015 | 0.0075562
78 | 0.9977 | -0.043803 | 0.0088301 | 0.002213
79 | 1 | 0 | -0.36001 | -0.091515
80 | 0.9986 | -0.026586 | 0.044479 | 0.011147
81 | 0.99778 | -0.042052 | 0.00094808 | 0.00023761
82 | 0.99592 | -0.077223 | 0.0048764 | 0.0012221
83 | 0.99338 | -0.12539 | 0.0010991 | 0.00027547
84 | 0.99338 | -0.1254 | 0.0030791 | 0.00077169
85 | 0.99238 | -0.14447 | 0.00068212 | 0.00017095
86 | 0.99226 | -0.14683 | 0.0022136 | 0.00055478
87 | 0.99213 | -0.1493 | 0.00063915 | 0.00016019
88 | 0.99119 | -0.16711 | 0 | 0
89 | 0.97573 | -0.46628 | 0.00038587 | 9.6709e-05
90 | 0.97601 | -0.46071 | 0 | 0
91 | 0.97098 | -0.55972 | 0 | 0
92 | 0.98449 | -0.29591 | 0 | 0
93 | 0.97027 | -0.57382 | 0.034298 | 0.0085958
94 | 0.98796 | -0.22901 | 0 | 0
95 | 0.98335 | -0.31823 | 0.025282 | 0.0063363
96 | 0.98613 | -0.26435 | 0.0022292 | 0.00055869
97 | 0.98668 | -0.25376 | 0.0036922 | 0.00092536
98 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0092385 | -0.0023156 | 0.009242 | 0.0023173 | 3.5323e-06 | 1.6802e-06 | 0.014164 | 0.014164 | 0.014164 | 0.97055 | -0.56881 | 0.97096 | -0.56079 | 3.8913
1 | 0.0083001 | 0.0020805 | -0.0082997 | -0.0020803 | 4.0332e-07 | 1.7605e-07 | 0.012725 | 0.012725 | 0.012725 | 0.97055 | -0.56881 | 0.9705 | -0.56983 | 3.496
2 | 0.0013326 | 0.00033317 | -0.0013325 | -0.00033397 | 1.0991e-07 | -7.9883e-07 | 0.002042 | 0.0020423 | 0.0020423 | 0.97096 | -0.56079 | 0.97087 | -0.56252 | 0.56108
3 | -0.010575 | -0.0026505 | 0.010579 | 0.0026526 | 4.1965e-06 | 2.1585e-06 | 0.016206 | 0.016206 | 0.016206 | 0.97096 | -0.56079 | 0.97138 | -0.55246 | 4.4522
4 | 0.0082997 | 0.0020803 | -0.0082988 | -0.0020799 | 8.4306e-07 | 3.6803e-07 | 0.012725 | 0.012726 | 0.012726 | 0.9705 | -0.56983 | 0.97039 | -0.57196 | 3.496
5 | -0.020722 | -0.0051953 | 0.020737 | 0.0052047 | 1.5535e-05 | 9.4328e-06 | 0.031743 | 0.031743 | 0.031743 | 0.97138 | -0.55246 | 0.97217 | -0.53674 | 8.7207
6 | 0.010143 | 0.0025426 | -0.010141 | -0.0025415 | 2.3006e-06 | 1.1579e-06 | 0.015538 | 0.015538 | 0.015538 | 0.97138 | -0.55246 | 0.97114 | -0.55722 | 4.2686
7 | 0.0075686 | 0.0018969 | -0.0075678 | -0.0018966 | 7.2044e-07 | 2.8489e-07 | 0.011606 | 0.011606 | 0.011606 | 0.97039 | -0.57196 | 0.97029 | -0.57396 | 3.1884
8 | -0.021321 | -0.0053511 | 0.021324 | 0.0053525 | 2.3416e-06 | 1.4259e-06 | 0.032637 | 0.032637 | 0.032637 | 0.97217 | -0.53674 | 0.97229 | -0.53444 | 8.9662
9 | 0.0075678 | 0.0018966 | -0.0075669 | -0.0018962 | 9.4109e-07 | 3.7221e-07 | 0.011606 | 0.011606 | 0.011606 | 0.97029 | -0.57396 | 0.97016 | -0.57657 | 3.1884
10 | 0.0044695 | 0.00112 | -0.0044689 | -0.00112 | 5.6542e-07 | -3.426e-08 | 0.0068551 | 0.0068553 | 0.0068553 | 0.97016 | -0.57657 | 0.97003 | -0.57923 | 1.8833
11 | -0.021324 | -0.0053525 | 0.021337 | 0.0053608 | 1.3695e-05 | 8.3394e-06 | 0.032637 | 0.032637 | 0.032637 | 0.97229 | -0.53444 | 0.97297 | -0.52098 | 8.9662
12 | -0.021337 | -0.0053608 | 0.021348 | 0.0053673 | 1.0689e-05 | 6.5084e-06 | 0.032637 | 0.032637 | 0.032637 | 0.97297 | -0.52098 | 0.9735 | -0.51049 | 8.9662
13 | 0.0044689 | 0.00112 | -0.0044688 | -0.00112 | 9.4108e-08 | -5.69e-09 | 0.0068553 | 0.0068553 | 0.0068553 | 0.97003 | -0.57923 | 0.97001 | -0.57967 | 1.8833
14 | -0.031564 | -0.0079305 | 0.031589 | 0.0079452 | 2.53e-05 | 1.4748e-05 | 0.04824 | 0.048239 | 0.04824 | 0.97378 | -0.50501 | 0.97464 | -0.48823 | 6.6263
15 | 0.031564 | 0.0079305 | -0.031556 | -0.0079259 | 7.8809e-06 | 4.5945e-06 | 0.04824 | 0.04824 | 0.04824 | 0.97378 | -0.50501 | 0.97352 | -0.51024 | 6.6263
16 | -0.056859 | -0.014316 | 0.056876 | 0.014326 | 1.6844e-05 | 1.0112e-05 | 0.086833 | 0.086833 | 0.086833 | 0.97464 | -0.48823 | 0.97495 | -0.48204 | 7.9518
17 | 0.02527 | 0.0063706 | -0.025205 | -0.0063307 | 6.4542e-05 | 3.9871e-05 | 0.038594 | 0.038595 | 0.038595 | 0.97464 | -0.48823 | 0.97192 | -0.54175 | 10.6029
18 | 0.026453 | 0.006647 | -0.026453 | -0.0066468 | 3.1063e-07 | 1.9251e-07 | 0.04044 | 0.04044 | 0.04044 | 0.97352 | -0.51024 | 0.9735 | -0.51049 | 11.1099
19 | 0.021598 | 0.0054241 | -0.02157 | -0.0054069 | 2.8241e-05 | 1.7223e-05 | 0.033082 | 0.033082 | 0.033082 | 0.97159 | -0.54815 | 0.97021 | -0.57559 | 9.0885
20 | -0.021598 | -0.0054241 | 0.021603 | 0.005427 | 4.7518e-06 | 2.8977e-06 | 0.033082 | 0.033082 | 0.033082 | 0.97159 | -0.54815 | 0.97183 | -0.54354 | 9.0884
21 | 0.02157 | 0.0054069 | -0.021567 | -0.0054052 | 2.7945e-06 | 1.7044e-06 | 0.033082 | 0.033082 | 0.033082 | 0.97021 | -0.57559 | 0.97007 | -0.57831 | 9.0885
22 | -0.025203 | -0.0063294 | 0.025205 | 0.0063307 | 2.1529e-06 | 1.3301e-06 | 0.038595 | 0.038595 | 0.038595 | 0.97183 | -0.54354 | 0.97192 | -0.54175 | 10.6029
23 | -0.061981 | -0.015605 | 0.061982 | 0.015606 | 7.2898e-07 | 4.4218e-07 | 0.094624 | 0.094624 | 0.094624 | 0.97495 | -0.48204 | 0.97496 | -0.48179 | 8.6652
24 | -0.070277 | -0.017685 | 0.070321 | 0.017712 | 4.4344e-05 | 2.7226e-05 | 0.10728 | 0.10728 | 0.10728 | 0.97496 | -0.48179 | 0.97563 | -0.4686 | 9.8245
25 | -0.006246 | -0.0015654 | 0.0062476 | 0.0015658 | 1.6283e-06 | 4.2014e-07 | 0.0094319 | 0.0094317 | 0.0094319 | 0.98539 | -0.27911 | 0.98568 | -0.27364 | 2.5912
26 | -0.0063186 | -0.0015836 | 0.0063187 | 0.0015836 | 9.6521e-08 | 2.5716e-08 | 0.0095388 | 0.0095388 | 0.0095388 | 0.98568 | -0.27364 | 0.98569 | -0.27332 | 2.6205
27 | -0.0069146 | -0.001733 | 0.0069163 | 0.0017335 | 1.6517e-06 | 5.4168e-07 | 0.010438 | 0.010438 | 0.010438 | 0.98569 | -0.27332 | 0.98595 | -0.2683 | 2.8677
28 | -0.0069699 | -0.001747 | 0.0069714 | 0.0017475 | 1.5041e-06 | 5.0023e-07 | 0.010519 | 0.010519 | 0.010519 | 0.98595 | -0.2683 | 0.98618 | -0.26378 | 2.8899
29 | -0.086799 | -0.022107 | 0.086854 | 0.022141 | 5.4567e-05 | 3.395e-05 | 0.13109 | 0.13109 | 0.13109 | 0.98618 | -0.26378 | 0.98686 | -0.25075 | 12.005
30 | 0.079005 | 0.020156 | -0.078915 | -0.0201 | 8.9637e-05 | 5.5443e-05 | 0.11933 | 0.11934 | 0.11934 | 0.98618 | -0.26378 | 0.98496 | -0.28729 | 10.9282
31 | 0.00082304 | 0.00020367 | -0.00082302 | -0.00020405 | 1.7697e-08 | -3.7965e-07 | 0.0012409 | 0.0012411 | 0.0012411 | 0.98618 | -0.26378 | 0.98616 | -0.26423 | 0.34095
32 | -0.00034327 | -8.6032e-05 | 0.00034327 | 8.5781e-05 | 2.0764e-09 | -2.5039e-07 | 0.00052385 | 0.00052376 | 0.00052385 | 0.97507 | -0.47927 | 0.97508 | -0.47914 | 0.14391
33 | -0.00034327 | -8.5781e-05 | 0.00034328 | 8.4797e-05 | 8.1577e-09 | -9.8463e-07 | 0.00052376 | 0.00052341 | 0.00052376 | 0.97508 | -0.47914 | 0.97511 | -0.47864 | 0.14389
34 | -0.00097744 | -0.00024373 | 0.00097752 | 0.00024255 | 8.222e-08 | -1.1779e-06 | 0.0014911 | 0.0014907 | 0.0014911 | 0.97511 | -0.47864 | 0.9752 | -0.47686 | 0.40965
35 | -0.0011232 | -0.00027907 | 0.0011232 | 0.00027898 | 8.3407e-09 | -8.923e-08 | 0.001713 | 0.001713 | 0.001713 | 0.9752 | -0.47686 | 0.9752 | -0.4767 | 0.47061
36 | 0.0012929 | 0.00032126 | -0.0012928 | -0.0003223 | 1.3233e-07 | -1.0462e-06 | 0.0019723 | 0.0019727 | 0.0019727 | 0.97495 | -0.4817 | 0.97484 | -0.48386 | 0.54196
37 | -0.0012929 | -0.00032126 | 0.0012931 | 0.00032021 | 1.3233e-07 | -1.0469e-06 | 0.0019723 | 0.0019719 | 0.0019723 | 0.97495 | -0.4817 | 0.97506 | -0.47953 | 0.54185
38 | 0.0012928 | 0.0003223 | -0.0012926 | -0.00032354 | 1.5601e-07 | -1.2324e-06 | 0.0019727 | 0.0019732 | 0.0019732 | 0.97484 | -0.48386 | 0.97471 | -0.4864 | 0.54209
39 | -0.001615 | -0.00040089 | 0.001615 | 0.00040078 | 2.1563e-08 | -1.0442e-07 | 0.0024632 | 0.0024631 | 0.0024632 | 0.97506 | -0.47953 | 0.97507 | -0.47925 | 0.67669
40 | -0.0015434 | -0.00038429 | 0.0015435 | 0.00038401 | 5.2381e-08 | -2.8098e-07 | 0.0023541 | 0.002354 | 0.0023541 | 0.9752 | -0.4767 | 0.97524 | -0.47599 | 0.64674
41 | 0.0011679 | 0.00029228 | -0.0011679 | -0.0002927 | 4.26e-08 | -4.1814e-07 | 0.0017828 | 0.001783 | 0.001783 | 0.97471 | -0.4864 | 0.97468 | -0.48716 | 0.48984
42 | -0.0018867 | -0.00046887 | 0.0018867 | 0.00046879 | 2.6441e-08 | -8.9283e-08 | 0.0028777 | 0.0028777 | 0.0028777 | 0.97507 | -0.47925 | 0.97509 | -0.47895 | 0.79059
43 | -5.4362e-05 | -1.3624e-05 | 5.4362e-05 | 1.255e-05 | 2.1163e-10 | -1.0749e-06 | 8.2028e-05 | 8.166e-05 | 8.2028e-05 | 0.98614 | -0.26453 | 0.98615 | -0.26445 | 0.022535
44 | -5.4362e-05 | -1.255e-05 | 5.4362e-05 | 1.1889e-05 | 1.291e-10 | -6.6035e-07 | 8.166e-05 | 8.1448e-05 | 8.166e-05 | 0.98615 | -0.26445 | 0.98615 | -0.2644 | 0.022434
45 | -5.4362e-05 | -1.1889e-05 | 5.4362e-05 | 1.1588e-05 | 5.8666e-11 | -3.012e-07 | 8.1448e-05 | 8.1355e-05 | 8.1448e-05 | 0.98615 | -0.2644 | 0.98615 | -0.26437 | 0.022376
46 | -0.00053317 | -0.00013159 | 0.00053318 | 0.00013141 | 3.5202e-09 | -1.8314e-07 | 0.00080379 | 0.00080373 | 0.00080379 | 0.98615 | -0.26437 | 0.98616 | -0.26423 | 0.22082
47 | -0.086951 | -0.022165 | 0.087047 | 0.022225 | 9.6223e-05 | 5.9868e-05 | 0.13124 | 0.13124 | 0.13124 | 0.98686 | -0.25075 | 0.98805 | -0.22785 | 12.0184
48 | 0.078658 | 0.020036 | -0.078657 | -0.020036 | 7.1456e-07 | 4.4189e-07 | 0.11895 | 0.11895 | 0.11895 | 0.98496 | -0.28729 | 0.98495 | -0.28748 | 10.8926
49 | -0.088125 | -0.022495 | 0.088155 | 0.022514 | 2.9853e-05 | 1.8586e-05 | 0.13286 | 0.13286 | 0.13286 | 0.98805 | -0.22785 | 0.98842 | -0.22084 | 12.167
50 | 0.078584 | 0.020017 | -0.078584 | -0.020017 | 4.3554e-07 | 2.6932e-07 | 0.11884 | 0.11884 | 0.11884 | 0.98495 | -0.28748 | 0.98494 | -0.2876 | 10.8825
51 | -0.091087 | -0.023249 | 0.091231 | 0.023338 | 0.00014376 | 8.9656e-05 | 0.13728 | 0.13728 | 0.13728 | 0.98842 | -0.22084 | 0.99012 | -0.18823 | 12.5712
52 | 0.074811 | 0.019072 | -0.07479 | -0.019058 | 2.1375e-05 | 1.317e-05 | 0.11314 | 0.11314 | 0.11314 | 0.98494 | -0.2876 | 0.98464 | -0.29352 | 10.3606
53 | -0.096153 | -0.024572 | 0.096215 | 0.024611 | 6.1949e-05 | 3.8733e-05 | 0.14467 | 0.14467 | 0.14467 | 0.99012 | -0.18823 | 0.99082 | -0.17492 | 13.2485
54 | -0.11968 | -0.030491 | 0.11995 | 0.030664 | 0.00027417 | 0.00017284 | 0.17991 | 0.17991 | 0.17991 | 0.99082 | -0.17492 | 0.9933 | -0.12756 | 16.4754
55 | 0.0039974 | 0.0010016 | -0.0039972 | -0.0010017 | 2.2084e-07 | -7.1219e-08 | 0.0059883 | 0.0059884 | 0.0059884 | 0.9933 | -0.12756 | 0.99324 | -0.12872 | 1.6452
56 | -0.12395 | -0.031666 | 0.124 | 0.031695 | 4.6717e-05 | 2.9479e-05 | 0.1859 | 0.1859 | 0.1859 | 0.9933 | -0.12756 | 0.99371 | -0.11976 | 17.0237
57 | 0.0039972 | 0.0010017 | -0.003997 | -0.0010017 | 2.0986e-07 | -6.765e-08 | 0.0059884 | 0.0059884 | 0.0059884 | 0.99324 | -0.12872 | 0.99318 | -0.12982 | 1.6452
58 | -0.17162 | -0.04363 | 0.17188 | 0.043794 | 0.00025856 | 0.00016426 | 0.25721 | 0.25721 | 0.25721 | 0.99371 | -0.11976 | 0.99534 | -0.088536 | 23.5536
59 | -0.17912 | -0.04561 | 0.1796 | 0.045913 | 0.00047592 | 0.00030252 | 0.26804 | 0.26804 | 0.26804 | 0.99534 | -0.088536 | 0.99823 | -0.033601 | 24.5457
60 | 0.0072466 | 0.0018163 | -0.0072451 | -0.0018158 | 1.4966e-06 | 5.1598e-07 | 0.010834 | 0.010834 | 0.010834 | 0.99534 | -0.088536 | 0.99512 | -0.092872 | 2.9763
61 | 0.014706 | 0.0036878 | -0.014699 | -0.003684 | 6.7139e-06 | 3.8101e-06 | 0.021922 | 0.021922 | 0.021922 | 0.99823 | -0.033601 | 0.99773 | -0.043184 | 6.0226
62 | -0.1943 | -0.049601 | 0.19435 | 0.049633 | 5.1193e-05 | 3.2572e-05 | 0.28996 | 0.28996 | 0.28996 | 0.99823 | -0.033601 | 0.99852 | -0.02815 | 26.5531
63 | 0.074472 | 0.018979 | -0.074389 | -0.018927 | 8.3162e-05 | 5.1226e-05 | 0.11266 | 0.11266 | 0.11266 | 0.98464 | -0.29352 | 0.98344 | -0.31669 | 10.3167
64 | 0.074389 | 0.018927 | -0.073929 | -0.018644 | 0.00045993 | 0.00028339 | 0.11266 | 0.11266 | 0.11266 | 0.98344 | -0.31669 | 0.9768 | -0.44581 | 10.317
65 | 0.072347 | 0.018248 | -0.072341 | -0.018244 | 5.6921e-06 | 3.5023e-06 | 0.11025 | 0.11025 | 0.11025 | 0.9768 | -0.44581 | 0.97671 | -0.44745 | 10.0964
66 | 0.070392 | 0.017756 | -0.070321 | -0.017712 | 7.1178e-05 | 4.3698e-05 | 0.10728 | 0.10728 | 0.10728 | 0.97671 | -0.44745 | 0.97563 | -0.4686 | 9.8245
67 | -0.0039775 | -0.00098888 | 0.0039777 | 0.00098881 | 2.4949e-07 | -6.5951e-08 | 0.006066 | 0.0060659 | 0.006066 | 0.97524 | -0.47599 | 0.97531 | -0.47466 | 1.6665
68 | 0.002434 | 0.00060487 | -0.0024339 | -0.00060508 | 1.182e-07 | -2.0977e-07 | 0.003712 | 0.0037121 | 0.0037121 | 0.97524 | -0.47599 | 0.97519 | -0.47701 | 1.0198
69 | 0.002181 | 0.00054619 | -0.002181 | -0.0005462 | 5.2069e-09 | -1.2318e-08 | 0.0033274 | 0.0033274 | 0.0033274 | 0.97531 | -0.47466 | 0.9753 | -0.47471 | 0.91413
70 | -0.0061588 | -0.001535 | 0.0061594 | 0.0015352 | 5.7495e-07 | 1.511e-07 | 0.0093933 | 0.0093933 | 0.0093933 | 0.97531 | -0.47466 | 0.97541 | -0.4727 | 2.5806
71 | 0.00014127 | 3.5084e-05 | -0.00014127 | -3.5406e-05 | 4.4939e-10 | -3.2164e-07 | 0.00021545 | 0.00021556 | 0.00021556 | 0.97519 | -0.47701 | 0.97518 | -0.47708 | 0.059221
72 | 0.0022926 | 0.00057 | -0.0022925 | -0.00057027 | 1.3306e-07 | -2.7689e-07 | 0.0034966 | 0.0034968 | 0.0034968 | 0.97519 | -0.47701 | 0.97513 | -0.47824 | 0.96065
73 | 0.0020013 | 0.00049728 | -0.0020012 | -0.00049748 | 6.7717e-08 | -1.9843e-07 | 0.0030523 | 0.0030524 | 0.0030524 | 0.97513 | -0.47824 | 0.97509 | -0.47895 | 0.83858
74 | 0.0019754 | 0.00049466 | -0.0019753 | -0.00049504 | 1.2633e-07 | -3.8198e-07 | 0.0030137 | 0.0030138 | 0.0030138 | 0.9753 | -0.47471 | 0.97524 | -0.47606 | 0.82798
75 | -0.0073636 | -0.001837 | 0.0073644 | 0.0018373 | 7.9795e-07 | 3.0007e-07 | 0.01123 | 0.01123 | 0.01123 | 0.97541 | -0.4727 | 0.97552 | -0.47041 | 3.0853
76 | -0.0078985 | -0.0019711 | 0.0079 | 0.0019718 | 1.5498e-06 | 6.3614e-07 | 0.012045 | 0.012045 | 0.012045 | 0.97552 | -0.47041 | 0.97573 | -0.46628 | 3.3091
77 | 0.0088303 | 0.0022131 | -0.0088301 | -0.002213 | 2.6047e-07 | 1.144e-07 | 0.01317 | 0.01317 | 0.01317 | 0.99773 | -0.043184 | 0.9977 | -0.043803 | 3.618
78 | -0.2245 | -0.05719 | 0.22481 | 0.057384 | 0.00030533 | 0.00019456 | 0.33489 | 0.33489 | 0.33489 | 0.99852 | -0.02815 | 1 | 0 | 30.6675
79 | 0.13355 | 0.034131 | -0.13338 | -0.034022 | 0.00017148 | 0.00010839 | 0.19895 | 0.19896 | 0.19896 | 1 | 0 | 0.9986 | -0.026586 | 18.2193
80 | 0.088897 | 0.022875 | -0.08883 | -0.022833 | 6.6801e-05 | 4.2224e-05 | 0.13268 | 0.13268 | 0.13268 | 0.9986 | -0.026586 | 0.99778 | -0.042052 | 18.225
81 | 0.087882 | 0.022595 | -0.087732 | -0.022499 | 0.00014993 | 9.5651e-05 | 0.13126 | 0.13126 | 0.13126 | 0.99778 | -0.042052 | 0.99592 | -0.077223 | 36.0616
82 | 0.082856 | 0.021277 | -0.082663 | -0.021154 | 0.00019325 | 0.00012324 | 0.12398 | 0.12398 | 0.12398 | 0.99592 | -0.077223 | 0.99338 | -0.12539 | 34.06
83 | 0.081563 | 0.020878 | -0.081563 | -0.020878 | 4.1559e-08 | 2.6526e-08 | 0.12233 | 0.12233 | 0.12233 | 0.99338 | -0.12539 | 0.99338 | -0.1254 | 33.6077
84 | 0.078484 | 0.020107 | -0.078412 | -0.020061 | 7.2466e-05 | 4.6198e-05 | 0.11772 | 0.11772 | 0.11772 | 0.99338 | -0.1254 | 0.99238 | -0.14447 | 32.3407
85 | 0.07773 | 0.01989 | -0.077721 | -0.019884 | 8.8915e-06 | 5.6681e-06 | 0.1167 | 0.1167 | 0.1167 | 0.99238 | -0.14447 | 0.99226 | -0.14683 | 32.0597
86 | 0.075507 | 0.019329 | -0.075498 | -0.019323 | 9.0222e-06 | 5.75e-06 | 0.11338 | 0.11338 | 0.11338 | 0.99226 | -0.14683 | 0.99213 | -0.1493 | 31.1477
87 | 0.074859 | 0.019163 | -0.074795 | -0.019122 | 6.4508e-05 | 4.111e-05 | 0.11242 | 0.11242 | 0.11242 | 0.99213 | -0.1493 | 0.99119 | -0.16711 | 30.8844
88 | 0.074795 | 0.019122 | -0.074571 | -0.01898 | 0.00022327 | 0.00014229 | 0.11242 | 0.11242 | 0.11242 | 0.99119 | -0.16711 | 0.98796 | -0.22901 | 30.8845
89 | -0.0082859 | -0.0020685 | 0.0082881 | 0.0020694 | 2.1914e-06 | 9.4502e-07 | 0.012633 | 0.012633 | 0.012633 | 0.97573 | -0.46628 | 0.97601 | -0.46071 | 3.4707
90 | 0.034484 | 0.0087126 | -0.034321 | -0.0086103 | 0.00016282 | 0.00010225 | 0.052599 | 0.052599 | 0.052599 | 0.97601 | -0.46071 | 0.97098 | -0.55972 | 14.4504
91 | -0.042772 | -0.010782 | 0.043112 | 0.010997 | 0.00034019 | 0.00021503 | 0.065232 | 0.065231 | 0.065232 | 0.97601 | -0.46071 | 0.98449 | -0.29591 | 17.9208
92 | 0.034321 | 0.0086103 | -0.034298 | -0.0085958 | 2.3061e-05 | 1.4484e-05 | 0.052599 | 0.052599 | 0.052599 | 0.97098 | -0.55972 | 0.97027 | -0.57382 | 14.4504
93 | 0.025309 | 0.0063529 | -0.025282 | -0.0063363 | 2.6904e-05 | 1.6596e-05 | 0.038257 | 0.038257 | 0.038257 | 0.98449 | -0.29591 | 0.98335 | -0.31823 | 10.5102
94 | -0.068421 | -0.01735 | 0.068525 | 0.017416 | 0.000104 | 6.6231e-05 | 0.10349 | 0.10349 | 0.10349 | 0.98449 | -0.29591 | 0.98613 | -0.26435 | 28.4307
95 | 0.074571 | 0.01898 | -0.074483 | -0.018923 | 8.8834e-05 | 5.6614e-05 | 0.11242 | 0.11242 | 0.11242 | 0.98796 | -0.22901 | 0.98668 | -0.25376 | 30.8845
96 | -0.070754 | -0.017975 | 0.07079 | 0.017998 | 3.6088e-05 | 2.2989e-05 | 0.10685 | 0.10685 | 0.10685 | 0.98613 | -0.26435 | 0.98668 | -0.25376 | 29.3547

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36101 | 0.091767

## res_load
| p_mw | q_mvar
0 | 0.00093839 | 0.00023518
1 | 0.0013325 | 0.00033397
2 | 0.00073027 | 0.00018302
3 | 0.00058394 | 0.00014635
4 | 0.010141 | 0.0025415
5 | 0.0030974 | 0.00077628
6 | 0.0044688 | 0.00112
7 | 0.0051029 | 0.0012789
8 | 0.0036005 | 0.00090237
9 | 0.021567 | 0.0054052
10 | 0.0051049 | 0.0012794
11 | 0.0051051 | 0.0012795
12 | 0.0082948 | 0.0020789
13 | 0.006246 | 0.0015654
14 | 7.0929e-05 | 1.7776e-05
15 | 0.00059596 | 0.00014936
16 | 5.3649e-05 | 1.3446e-05
17 | 0.00034327 | 8.6032e-05
18 | 0.00063415 | 0.00015893
19 | 0.00014572 | 3.6521e-05
20 | 0.0003219 | 8.0677e-05
21 | 0.00042017 | 0.0001053
22 | 0.00012469 | 3.1251e-05
23 | 0.00027169 | 6.8092e-05
24 | 5.4362e-05 | 1.3624e-05
25 | 0.00047881 | 0.00012
26 | 0.00028984 | 7.2642e-05
27 | 9.6987e-05 | 2.4307e-05
28 | 0.0002568 | 6.4359e-05
29 | 0.0010779 | 0.00027015
30 | 7.3208e-05 | 1.8348e-05
31 | 0.0029325 | 0.00073496
32 | 0.0037724 | 0.00094545
33 | 0.0049219 | 0.0012335
34 | 0.023464 | 0.0058806
35 | 0.04762 | 0.011935
36 | 0.003997 | 0.0010017
37 | 0.0072451 | 0.0018158
38 | 0.00031806 | 7.9713e-05
39 | 0.0015816 | 0.00039639
40 | 0.0019494 | 0.00048857
41 | 0.00029123 | 7.299e-05
42 | 0.0001145 | 2.8697e-05
43 | 0.00014127 | 3.5406e-05
44 | 0.00020566 | 5.1542e-05
45 | 0.0012043 | 0.00030182
46 | 0.0019753 | 0.00049504
47 | 0.00053408 | 0.00013385
48 | 0.0011679 | 0.0002927
49 | 0.0058688 | 0.0014709
50 | 0.03015 | 0.0075562
51 | 0.0088301 | 0.002213
52 | 0.0010081 | 0.00025264
53 | 0.044479 | 0.011147
54 | 0.00094808 | 0.00023761
55 | 0.0048764 | 0.0012221
56 | 0.0010991 | 0.00027547
57 | 0.0030791 | 0.00077169
58 | 0.00068212 | 0.00017095
59 | 0.0022136 | 0.00055478
60 | 0.00063915 | 0.00016019
61 | 0.00038587 | 9.6709e-05
62 | 0.034298 | 0.0085958
63 | 0.025282 | 0.0063363
64 | 0.0022292 | 0.00055869
65 | 0.0036922 | 0.00092536

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1