## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-72_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-72_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-72_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_230-72_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_230-72_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-72_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_230-72_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_230-72_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_230-72_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_230-72_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_230-72_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_230-72_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_230-72_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_230-72_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_230-72_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_230-72_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_230-72_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_230-72_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_230-72_0_4_node_53 | 0.4 | n |  | TRUE
19 | bus_LV_230-72_0_4_node_49 | 0.4 | n |  | TRUE
20 | bus_LV_230-72_0_4_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_230-72_0_4_node_47 | 0.4 | n |  | TRUE
22 | bus_LV_230-72_0_4_node_48 | 0.4 | n |  | TRUE
23 | bus_LV_230-72_0_4_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_230-72_0_4_node_125 | 0.4 | n |  | TRUE
25 | bus_LV_230-72_0_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_230-72_0_4_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_230-72_0_4_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_230-72_0_4_node_122 | 0.4 | n |  | TRUE
29 | bus_LV_230-72_0_4_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_230-72_0_4_node_68 | 0.4 | n |  | TRUE
31 | bus_LV_230-72_0_4_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_230-72_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_230-72_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_230-72_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_230-72_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_230-72_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_230-72_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_230-72_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_230-72_0_4_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_230-72_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_230-72_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_230-72_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_230-72_0_4_node_111 | 0.4 | n |  | TRUE
44 | bus_LV_230-72_0_4_node_112 | 0.4 | n |  | TRUE
45 | bus_LV_230-72_0_4_node_115 | 0.4 | n |  | TRUE
46 | bus_LV_230-72_0_4_node_114 | 0.4 | n |  | TRUE
47 | bus_LV_230-72_0_4_node_110 | 0.4 | n |  | TRUE
48 | bus_LV_230-72_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_230-72_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_230-72_0_4_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_230-72_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_230-72_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_230-72_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_230-72_0_4_node_132 | 0.4 | n |  | TRUE
55 | bus_LV_230-72_0_4_node_134 | 0.4 | n |  | TRUE
56 | bus_LV_230-72_0_4_node_123 | 0.4 | n |  | TRUE
57 | bus_LV_230-72_0_4_node_124 | 0.4 | n |  | TRUE
58 | bus_LV_230-72_0_4_node_127 | 0.4 | n |  | TRUE
59 | bus_LV_230-72_0_4_node_133 | 0.4 | n |  | TRUE
60 | bus_LV_230-72_0_4_node_135 | 0.4 | n |  | TRUE
61 | bus_LV_230-72_0_4_node_121 | 0.4 | n |  | TRUE
62 | bus_LV_230-72_0_4_node_131 | 0.4 | n |  | TRUE
63 | bus_LV_230-72_0_4_node_126 | 0.4 | n |  | TRUE
64 | bus_LV_230-72_0_4_node_89 | 0.4 | n |  | TRUE
65 | bus_LV_230-72_0_4_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_230-72_0_4_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_230-72_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_230-72_0_4_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_230-72_0_4_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_230-72_0_4_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_230-72_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_230-72_0_4_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_230-72_0_4_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_230-72_0_4_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_230-72_0_4_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_230-72_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_230-72_0_4_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_230-72_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_230-72_0_4_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_230-72_0_4_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_230-72_0_4_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_230-72_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_230-72_0_4_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_230-72_0_4_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_230-72_0_4_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_230-72_0_4_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_230-72_0_4_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_230-72_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_230-72_0_4_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_230-72_0_4_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_230-72_0_4_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_230-72_0_4_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_230-72_0_4_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_230-72_0_4_node_136 | 0.4 | n |  | TRUE
95 | bus_LV_230-72_0_4_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_230-72_0_4_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_230-72_0_4_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_230-72_0_4_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_230-72_0_4_node_85 | 0.4 | n |  | TRUE
100 | bus_LV_230-72_0_4_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_230-72_0_4_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_230-72_0_4_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_230-72_0_4_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_230-72_0_4_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_230-72_0_4_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_230-72_0_4_node_96 | 0.4 | n |  | TRUE
107 | bus_LV_230-72_0_4_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_230-72_0_4_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_230-72_0_4_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_230-72_0_4_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_230-72_0_4_node_94 | 0.4 | n |  | TRUE
112 | bus_LV_230-72_0_4_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_230-72_0_4_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_230-72_0_4_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_230-72_0_4_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_230-72_0_4_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_230-72_0_4_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_230-72_0_4_node_101 | 0.4 | n |  | TRUE
119 | bus_LV_230-72_0_4_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_230-72_0_4_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_230-72_0_4_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_230-72_0_4_node_129 | 0.4 | n |  | TRUE
123 | bus_LV_230-72_0_4_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_230-72_0_4_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_230-72_0_4_node_106 | 0.4 | n |  | TRUE
126 | bus_LV_230-72_0_4_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_230-72_0_4_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_230-72_0_4_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_230-72_0_4_node_130 | 0.4 | n |  | TRUE
130 | bus_LV_230-72_0_4_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_230-72_0_4_node_120 | 0.4 | n |  | TRUE
132 | bus_MV_370_0_node_116 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-72_0_4_load_0 | 0 | 0.0019194 | 0.00048104 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-72_0_4_load_1 | 1 | 0.00014839 | 3.719e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-72_0_4_load_2 | 2 | 0.00016192 | 4.0582e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-72_0_4_load_3 | 3 | 0.00040382 | 0.00010121 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-72_0_4_load_6 | 7 | 0.00045659 | 0.00011443 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-72_0_4_load_11 | 8 | 0.0016317 | 0.00040893 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-72_0_4_load_7 | 9 | 0.00068571 | 0.00017185 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-72_0_4_load_8 | 10 | 0.00073447 | 0.00018408 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-72_0_4_load_10 | 12 | 0.000693 | 0.00017368 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-72_0_4_load_18 | 13 | 0.00041944 | 0.00010512 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-72_0_4_load_19 | 14 | 0.00018745 | 4.6979e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-72_0_4_load_16 | 16 | 0.0014225 | 0.00035651 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-72_0_4_load_53 | 18 | 0.0010233 | 0.00025647 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-72_0_4_load_49 | 19 | 0.00098187 | 0.00024608 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-72_0_4_load_41 | 20 | 0.0099334 | 0.0024896 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-72_0_4_load_48 | 22 | 0.0021939 | 0.00054985 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-72_0_4_load_125 | 24 | 0.010312 | 0.0025843 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-72_0_4_load_43 | 27 | 0.0025629 | 0.00064232 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-72_0_4_load_122 | 28 | 0.014894 | 0.0037327 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-72_0_4_load_42 | 29 | 0.0026818 | 0.00067211 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-72_0_4_load_68 | 30 | 0.0045493 | 0.0011402 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-72_0_4_load_67 | 31 | 0.0041892 | 0.0010499 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-72_0_4_load_27 | 33 | 0.00043343 | 0.00010863 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-72_0_4_load_24 | 34 | 0.0006019 | 0.00015085 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-72_0_4_load_23 | 35 | 0.00019308 | 4.8391e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-72_0_4_load_25 | 36 | 0.00035312 | 8.85e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-72_0_4_load_22 | 37 | 0.0012938 | 0.00032427 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-72_0_4_load_21 | 38 | 0.00032901 | 8.2457e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-72_0_4_load_26 | 39 | 0.00068765 | 0.00017234 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-72_0_4_load_30 | 42 | 0.00033851 | 8.4839e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-72_0_4_load_111 | 43 | 0.0019867 | 0.00049793 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-72_0_4_load_115 | 45 | 0.0097016 | 0.0024315 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-72_0_4_load_114 | 46 | 0.0097009 | 0.0024313 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-72_0_4_load_110 | 47 | 0.0012524 | 0.00031388 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-72_0_4_load_33 | 48 | 0.018692 | 0.0046848 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-72_0_4_load_40 | 53 | 0.010312 | 0.0025844 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-72_0_4_load_134 | 55 | 0.018617 | 0.0046659 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-72_0_4_load_123 | 56 | 0.015228 | 0.0038164 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-72_0_4_load_124 | 57 | 0.015544 | 0.0038957 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-72_0_4_load_127 | 58 | 0.010312 | 0.0025843 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-72_0_4_load_135 | 60 | 0.011059 | 0.0027715 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-72_0_4_load_131 | 62 | 0.0086017 | 0.0021558 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-72_0_4_load_126 | 63 | 0.0015371 | 0.00038522 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-72_0_4_load_89 | 64 | 0.01589 | 0.0039825 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-72_0_4_load_44 | 68 | 0.0086915 | 0.0021783 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-72_0_4_load_46 | 69 | 0.0086915 | 0.0021783 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-72_0_4_load_54 | 72 | 0.008686 | 0.0021769 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-72_0_4_load_58 | 73 | 0.0026494 | 0.000664 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-72_0_4_load_50 | 74 | 0.0012227 | 0.00030643 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-72_0_4_load_51 | 75 | 0.0015797 | 0.00039591 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-72_0_4_load_56 | 76 | 0.008692 | 0.0021784 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-72_0_4_load_57 | 77 | 0.0086921 | 0.0021784 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-72_0_4_load_62 | 78 | 0.0039817 | 0.00099791 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-72_0_4_load_69 | 79 | 0.0019903 | 0.00049881 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-72_0_4_load_73 | 80 | 0.0022618 | 0.00056685 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-72_0_4_load_63 | 81 | 0.0039836 | 0.00099838 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-72_0_4_load_66 | 83 | 0.0039833 | 0.00099831 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-72_0_4_load_74 | 85 | 0.0018534 | 0.0004645 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-72_0_4_load_70 | 86 | 0.0039819 | 0.00099797 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-72_0_4_load_77 | 87 | 0.0018534 | 0.0004645 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-72_0_4_load_71 | 88 | 0.0039792 | 0.00099728 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-72_0_4_load_79 | 92 | 0.0038675 | 0.00096929 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-72_0_4_load_78 | 93 | 0.0018541 | 0.00046467 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-72_0_4_load_136 | 94 | 0.015338 | 0.0038442 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-72_0_4_load_82 | 96 | 0.0034093 | 0.00085445 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-72_0_4_load_81 | 97 | 0.0062844 | 0.001575 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-72_0_4_load_83 | 98 | 0.0062873 | 0.0015758 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-72_0_4_load_85 | 99 | 0.0031327 | 0.00078514 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-72_0_4_load_84 | 100 | 0.0062844 | 0.001575 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-72_0_4_load_86 | 101 | 0.0025869 | 0.00064833 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-72_0_4_load_96 | 106 | 0.0062859 | 0.0015754 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-72_0_4_load_91 | 108 | 0.0012987 | 0.00032548 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-72_0_4_load_97 | 109 | 0.0053009 | 0.0013285 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-72_0_4_load_92 | 110 | 0.00129 | 0.0003233 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-72_0_4_load_94 | 111 | 0.0012842 | 0.00032185 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-72_0_4_load_100 | 112 | 0.0012782 | 0.00032034 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-72_0_4_load_113 | 116 | 0.0057679 | 0.0014456 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-72_0_4_load_116 | 120 | 0.0053534 | 0.0013417 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-72_0_4_load_107 | 121 | 0.011797 | 0.0029565 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-72_0_4_load_104 | 123 | 0.0052996 | 0.0013282 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-72_0_4_load_108 | 124 | 0.0012647 | 0.00031697 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-72_0_4_load_106 | 125 | 0.0061826 | 0.0015495 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-72_0_4_load_117 | 126 | 0.0053507 | 0.001341 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-72_0_4_load_118 | 127 | 0.0063656 | 0.0015954 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-72_0_4_load_119 | 128 | 0.007621 | 0.00191 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-72_0_4_load_128 | 130 | 0.019256 | 0.004826 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-72_0_4_line_0 |  | 0 | 1 | 0.027444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-72_0_4_line_1 |  | 0 | 2 | 0.028526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-72_0_4_line_2 |  | 1 | 3 | 0.0035651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-72_0_4_line_3 |  | 2 | 4 | 0.15077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_230-72_0_4_line_4 |  | 3 | 5 | 0.044515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-72_0_4_line_5 |  | 4 | 6 | 0.024514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_230-72_0_4_line_6 |  | 5 | 7 | 0.0097137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-72_0_4_line_7 |  | 6 | 8 | 0.011266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_230-72_0_4_line_8 |  | 7 | 9 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-72_0_4_line_9 |  | 8 | 15 | 0.049307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_230-72_0_4_line_10 |  | 9 | 10 | 0.017586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-72_0_4_line_11 |  | 10 | 11 | 0.054329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-72_0_4_line_12 |  | 11 | 12 | 0.13973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-72_0_4_line_13 |  | 12 | 13 | 0.0033583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-72_0_4_line_14 |  | 13 | 14 | 0.0115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-72_0_4_line_15 |  | 14 | 32 | 0.015139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-72_0_4_line_16 |  | 15 | 16 | 0.01381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_230-72_0_4_line_17 |  | 16 | 20 | 0.026992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_230-72_0_4_line_18 |  | 17 | 18 | 0.021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-72_0_4_line_19 |  | 17 | 19 | 0.0143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-72_0_4_line_20 |  | 18 | 21 | 0.0057656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-72_0_4_line_21 |  | 19 | 22 | 0.018586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-72_0_4_line_22 |  | 20 | 29 | 0.015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_230-72_0_4_line_23 |  | 21 | 71 | 0.015767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-72_0_4_line_24 |  | 21 | 26 | 0.027789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-72_0_4_line_25 |  | 22 | 74 | 0.00035384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-72_0_4_line_26 |  | 23 | 24 | 0.033278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-72_0_4_line_27 |  | 23 | 25 | 0.026145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-72_0_4_line_28 |  | 24 | 63 | 0.010398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-72_0_4_line_29 |  | 25 | 56 | 0.023876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-72_0_4_line_30 |  | 25 | 28 | 0.019305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-72_0_4_line_31 |  | 26 | 27 | 0.0097632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-72_0_4_line_32 |  | 27 | 68 | 0.015966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-72_0_4_line_33 |  | 29 | 65 | 0.016991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_230-72_0_4_line_34 |  | 30 | 31 | 0.01067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-72_0_4_line_35 |  | 31 | 66 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-72_0_4_line_36 |  | 32 | 33 | 0.014203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-72_0_4_line_37 |  | 32 | 34 | 0.037151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-72_0_4_line_38 |  | 32 | 35 | 0.11819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-72_0_4_line_39 |  | 34 | 36 | 0.018402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-72_0_4_line_40 |  | 35 | 37 | 0.0062401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-72_0_4_line_41 |  | 36 | 39 | 0.0036135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-72_0_4_line_42 |  | 37 | 38 | 0.016524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-72_0_4_line_43 |  | 40 | 41 | 0.10442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-72_0_4_line_44 |  | 40 | 42 | 0.06738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-72_0_4_line_45 |  | 41 | 43 | 0.010051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-72_0_4_line_46 |  | 43 | 47 | 0.0092599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-72_0_4_line_47 |  | 44 | 45 | 0.032802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-72_0_4_line_48 |  | 44 | 46 | 0.018169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-72_0_4_line_49 |  | 46 | 117 | 0.0071532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-72_0_4_line_50 |  | 47 | 124 | 0.0058254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-72_0_4_line_51 |  | 48 | 49 | 0.033169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-72_0_4_line_52 |  | 48 | 50 | 0.028467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-72_0_4_line_53 |  | 49 | 51 | 0.046819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_230-72_0_4_line_54 |  | 49 | 52 | 0.012954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_230-72_0_4_line_55 |  | 50 | 53 | 0.015239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-72_0_4_line_56 |  | 51 | 54 | 0.031243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_230-72_0_4_line_57 |  | 51 | 55 | 0.032556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-72_0_4_line_58 |  | 52 | 57 | 0.012394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_230-72_0_4_line_59 |  | 53 | 58 | 0.015877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-72_0_4_line_60 |  | 54 | 61 | 0.018441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_230-72_0_4_line_61 |  | 54 | 62 | 0.025384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-72_0_4_line_62 |  | 55 | 59 | 0.0060718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-72_0_4_line_63 |  | 57 | 64 | 0.023442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_230-72_0_4_line_64 |  | 58 | 63 | 0.0054746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-72_0_4_line_65 |  | 59 | 60 | 0.015291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-72_0_4_line_66 |  | 61 | 131 | 0.039215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_230-72_0_4_line_67 |  | 62 | 129 | 0.0076208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-72_0_4_line_68 |  | 65 | 66 | 0.032025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-72_0_4_line_69 |  | 65 | 67 | 0.029369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_230-72_0_4_line_70 |  | 67 | 78 | 0.009805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_230-72_0_4_line_71 |  | 67 | 77 | 0.012437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_230-72_0_4_line_72 |  | 68 | 69 | 0.015964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-72_0_4_line_73 |  | 69 | 70 | 0.031066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-72_0_4_line_74 |  | 70 | 72 | 0.023728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-72_0_4_line_75 |  | 71 | 73 | 0.0059351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-72_0_4_line_76 |  | 72 | 76 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_230-72_0_4_line_77 |  | 74 | 75 | 0.0045488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-72_0_4_line_78 |  | 76 | 77 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_230-72_0_4_line_79 |  | 78 | 81 | 0.01596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_230-72_0_4_line_80 |  | 79 | 80 | 0.0079782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-72_0_4_line_81 |  | 80 | 84 | 0.0057074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-72_0_4_line_82 |  | 81 | 82 | 0.009152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_230-72_0_4_line_83 |  | 82 | 83 | 0.026052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_230-72_0_4_line_84 |  | 83 | 86 | 0.030408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_230-72_0_4_line_85 |  | 84 | 85 | 0.0081963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-72_0_4_line_86 |  | 85 | 87 | 0.0057231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-72_0_4_line_87 |  | 86 | 88 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_230-72_0_4_line_88 |  | 87 | 93 | 0.0057255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-72_0_4_line_89 |  | 88 | 89 | 0.008775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_230-72_0_4_line_90 |  | 89 | 90 | 0.01892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_230-72_0_4_line_91 |  | 89 | 91 | 0.03696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-72_0_4_line_92 |  | 90 | 92 | 0.0051334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_230-72_0_4_line_93 |  | 90 | 93 | 0.0152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-72_0_4_line_94 |  | 91 | 94 | 0.007316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-72_0_4_line_95 |  | 92 | 95 | 0.015508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_230-72_0_4_line_96 |  | 95 | 96 | 0.0032249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_230-72_0_4_line_97 |  | 96 | 99 | 0.023004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_230-72_0_4_line_98 |  | 97 | 98 | 0.015968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-72_0_4_line_99 |  | 98 | 100 | 0.014138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-72_0_4_line_100 |  | 99 | 101 | 0.022355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_230-72_0_4_line_101 |  | 100 | 102 | 0.0048928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_230-72_0_4_line_102 |  | 101 | 104 | 0.014277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_230-72_0_4_line_103 |  | 102 | 103 | 0.018036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-72_0_4_line_104 |  | 103 | 106 | 0.012512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-72_0_4_line_105 |  | 104 | 105 | 0.003761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_230-72_0_4_line_106 |  | 105 | 107 | 0.029557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_230-72_0_4_line_107 |  | 105 | 108 | 0.021183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-72_0_4_line_108 |  | 106 | 109 | 0.016288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-72_0_4_line_109 |  | 107 | 113 | 0.015871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_230-72_0_4_line_110 |  | 108 | 110 | 0.0058099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-72_0_4_line_111 |  | 109 | 115 | 0.021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_230-72_0_4_line_112 |  | 110 | 111 | 0.0058194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_230-72_0_4_line_113 |  | 111 | 112 | 0.0058152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-72_0_4_line_114 |  | 112 | 114 | 0.0017631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-72_0_4_line_115 |  | 113 | 115 | 0.005571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_230-72_0_4_line_116 |  | 114 | 124 | 0.0040615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-72_0_4_line_117 |  | 114 | 117 | 0.027703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-72_0_4_line_118 |  | 115 | 118 | 0.00271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_230-72_0_4_line_119 |  | 116 | 117 | 0.019225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-72_0_4_line_120 |  | 118 | 119 | 0.026472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_230-72_0_4_line_121 |  | 118 | 120 | 0.053675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-72_0_4_line_122 |  | 119 | 125 | 0.0056823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_230-72_0_4_line_123 |  | 119 | 123 | 0.02485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-72_0_4_line_124 |  | 120 | 126 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-72_0_4_line_125 |  | 121 | 122 | 0.0019241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_230-72_0_4_line_126 |  | 122 | 129 | 0.012099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-72_0_4_line_127 |  | 122 | 130 | 0.022951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-72_0_4_line_128 |  | 125 | 127 | 0.014493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_230-72_0_4_line_129 |  | 127 | 128 | 0.011275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_230-72_0_4_line_130 |  | 128 | 131 | 0.023599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-72_0_4_trafo_89 | 0.63 MVA 20/0.4 kV | 132 | 64 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2698598.5081 | 1260326.3401 | 2698591.8421 | 1260309.7472 | 2698588.2793 | 1260300.8733
1 | 2698598.5081 | 1260326.3401 | 2698601.7862 | 1260334.4997 | 2698603.2177 | 1260339.0606 | 2698607.0398 | 1260351.2342 | 2698607.4165 | 1260353.3948
2 | 2698586.9509 | 1260297.5648 | 2698588.2793 | 1260300.8733
3 | 2698609.1123 | 1260503.5594 | 2698609.1269 | 1260486.8683 | 2698613.9907 | 1260419.4055 | 2698613.5859 | 1260402.5517 | 2698612.2099 | 1260385.6261 | 2698610.6722 | 1260372.0673 | 2698607.4165 | 1260353.3948
4 | 2698574.8515 | 1260255.0641 | 2698577.4544 | 1260273.9117 | 2698586.9509 | 1260297.5648
5 | 2698607.9897 | 1260527.9383 | 2698608.6849 | 1260522.8569 | 2698608.1624 | 1260509.4484 | 2698609.1123 | 1260503.5594
6 | 2698574.8515 | 1260255.0641 | 2698580.3278 | 1260247.0413
7 | 2698607.9897 | 1260527.9383 | 2698616.5072 | 1260520.5645
8 | 2698580.3278 | 1260247.0413 | 2698588.4658 | 1260235.1192 | 2698590.1998 | 1260231.7772
9 | 2698653.7858 | 1260488.2916 | 2698616.5072 | 1260520.5645
10 | 2698598.2992 | 1260216.1673 | 2698590.1998 | 1260231.7772
11 | 2698637.7169 | 1260179.1722 | 2698628.8106 | 1260186.185 | 2698605.5703 | 1260206.581 | 2698599.3459 | 1260214.1501 | 2698598.2992 | 1260216.1673
12 | 2698637.7169 | 1260179.1722 | 2698658.2623 | 1260169.8627 | 2698754.3209 | 1260134.97 | 2698768.3891 | 1260129.8524
13 | 2698768.3891 | 1260129.8524 | 2698771.545 | 1260128.7044
14 | 2698782.3539 | 1260124.7786 | 2698780.304 | 1260125.5182 | 2698771.545 | 1260128.7044
15 | 2698796.5939 | 1260119.6409 | 2698782.3539 | 1260124.7786
16 | 2698653.7858 | 1260488.2916 | 2698663.205 | 1260498.3902
17 | 2698663.205 | 1260498.3902 | 2698690.1785 | 1260497.3813
18 | 2698660.3251 | 1260561.6604 | 2698673.5013 | 1260558.4553 | 2698680.6253 | 1260555.7307
19 | 2698660.3251 | 1260561.6604 | 2698657.4984 | 1260547.6422
20 | 2698686.0104 | 1260553.6711 | 2698680.6253 | 1260555.7307
21 | 2698653.8246 | 1260529.4227 | 2698657.4984 | 1260547.6422
22 | 2698700.455 | 1260502.9374 | 2698700.2073 | 1260497.0062 | 2698690.1785 | 1260497.3813
23 | 2698686.0104 | 1260553.6711 | 2698699.438 | 1260545.3438
24 | 2698687.9469 | 1260581.2592 | 2698687.392 | 1260558.5092 | 2698686.0104 | 1260553.6711
25 | 2698653.8246 | 1260529.4227 | 2698653.7547 | 1260529.0758
26 | 2698789.2669 | 1260596.9405 | 2698800.4565 | 1260610.227 | 2698816.3619 | 1260609.9501
27 | 2698789.2669 | 1260596.9405 | 2698806.91 | 1260583.9801 | 2698804.1909 | 1260580.7098
28 | 2698816.3619 | 1260609.9501 | 2698826.7585 | 1260609.7691
29 | 2698800.2909 | 1260557.8927 | 2698801.324 | 1260577.2591 | 2698804.1909 | 1260580.7098
30 | 2698804.1909 | 1260580.7098 | 2698788.5391 | 1260592.0103
31 | 2698687.9469 | 1260581.2592 | 2698697.7089 | 1260581.1084
32 | 2698697.7089 | 1260581.1084 | 2698713.6731 | 1260580.8619
33 | 2698717.4427 | 1260502.5983 | 2698711.9012 | 1260502.6837 | 2698702.7472 | 1260502.8867 | 2698700.455 | 1260502.9374 | 2698700.455 | 1260502.9374
34 | 2698719.9223 | 1260463.3565 | 2698719.3688 | 1260452.7009
35 | 2698728.406 | 1260473.0349 | 2698720.31 | 1260470.8202 | 2698719.9223 | 1260463.3565
36 | 2698796.5939 | 1260119.6409 | 2698809.9526 | 1260114.8175
37 | 2698796.5939 | 1260119.6409 | 2698807.8636 | 1260155.0415
38 | 2698796.5939 | 1260119.6409 | 2698755.5236 | 1260008.8128
39 | 2698807.8636 | 1260155.0415 | 2698813.4458 | 1260172.5765
40 | 2698760.8531 | 1260005.6071 | 2698759.5938 | 1260006.1198 | 2698755.5236 | 1260008.8128
41 | 2698814.542 | 1260176.0198 | 2698813.4458 | 1260172.5765
42 | 2698776.1568 | 1259999.3761 | 2698760.8531 | 1260005.6071
43 | 2698878.4672 | 1260320.0604 | 2698868.634 | 1260306.3182 | 2698865.7879 | 1260303.4239 | 2698859.4472 | 1260295.8451 | 2698856.7594 | 1260293.3982 | 2698863.6031 | 1260287.5745 | 2698886.9426 | 1260266.703 | 2698911.338 | 1260249.8526
44 | 2698911.338 | 1260249.8526 | 2698929.3436 | 1260233.7738 | 2698961.9274 | 1260205.3487
45 | 2698878.4672 | 1260320.0604 | 2698876.0283 | 1260327.0698 | 2698876.0872 | 1260329.6981
46 | 2698876.2946 | 1260338.9557 | 2698876.0872 | 1260329.6981
47 | 2698929.6128 | 1260347.8824 | 2698931.7456 | 1260366.8223 | 2698932.0398 | 1260380.5619
48 | 2698929.6128 | 1260347.8824 | 2698911.4438 | 1260348.0013
49 | 2698904.2907 | 1260348.0481 | 2698911.4438 | 1260348.0013
50 | 2698876.425 | 1260344.7796 | 2698876.2946 | 1260338.9557
51 | 2698855.9546 | 1260549.3599 | 2698859.3454 | 1260554.8321 | 2698859.994 | 1260581.556
52 | 2698863.3443 | 1260609.1321 | 2698860.5682 | 1260605.2159 | 2698859.994 | 1260581.556
53 | 2698893.4722 | 1260521.2083 | 2698855.9546 | 1260549.3599
54 | 2698855.9546 | 1260549.3599 | 2698848.762 | 1260553.9769 | 2698846.237 | 1260550.3651
55 | 2698863.3443 | 1260609.1321 | 2698848.1073 | 1260609.3974
56 | 2698918.1979 | 1260502.1283 | 2698912.4315 | 1260506.1908 | 2698898.9382 | 1260517.0741 | 2698893.4722 | 1260521.2083
57 | 2698893.4722 | 1260521.2083 | 2698894.1564 | 1260553.7574
58 | 2698846.237 | 1260550.3651 | 2698844.8016 | 1260548.3061 | 2698844.4947 | 1260538.4272
59 | 2698832.2323 | 1260609.6738 | 2698848.1073 | 1260609.3974
60 | 2698918.1979 | 1260502.1283 | 2698933.6315 | 1260491.9669
61 | 2698918.1979 | 1260502.1283 | 2698915.2844 | 1260497.865 | 2698914.0316 | 1260477.6832
62 | 2698900.2182 | 1260554.1035 | 2698894.1564 | 1260553.7574
63 | 2698844.4947 | 1260538.4272 | 2698843.7667 | 1260514.9968
64 | 2698832.2323 | 1260609.6738 | 2698826.7585 | 1260609.7691
65 | 2698900.2182 | 1260554.1035 | 2698915.5043 | 1260553.7153
66 | 2698933.6315 | 1260491.9669 | 2698938.2577 | 1260489.3755 | 2698950.7327 | 1260483.9464 | 2698970.722 | 1260480.3666
67 | 2698906.4367 | 1260477.0557 | 2698914.0316 | 1260477.6832
68 | 2698728.406 | 1260473.0349 | 2698723.0721 | 1260481.4527 | 2698719.2616 | 1260490.7189 | 2698717.8431 | 1260497.5786 | 2698717.4427 | 1260502.5983
69 | 2698742.143 | 1260496.2941 | 2698717.8431 | 1260497.5786 | 2698717.4427 | 1260502.5983
70 | 2698742.143 | 1260496.2941 | 2698742.1556 | 1260491.4793 | 2698747.1392 | 1260491.2252
71 | 2698742.143 | 1260496.2941 | 2698742.5024 | 1260508.7259
72 | 2698713.6731 | 1260580.8619 | 2698729.6354 | 1260580.6153
73 | 2698740.1488 | 1260560.6355 | 2698740.8808 | 1260580.4416 | 2698729.6354 | 1260580.6153
74 | 2698740.1488 | 1260560.6355 | 2698739.6135 | 1260554.7773 | 2698743.8151 | 1260554.1358 | 2698743.4222 | 1260540.5463
75 | 2698699.438 | 1260545.3438 | 2698703.2812 | 1260540.8211
76 | 2698743.4222 | 1260540.5463 | 2698742.9623 | 1260524.6361
77 | 2698652.8555 | 1260524.6168 | 2698653.7547 | 1260529.0758
78 | 2698742.9623 | 1260524.6361 | 2698742.5024 | 1260508.7259
79 | 2698747.1392 | 1260491.2252 | 2698763.0782 | 1260490.4125
80 | 2698759.9185 | 1260445.6664 | 2698765.9421 | 1260440.4349
81 | 2698770.2512 | 1260436.6925 | 2698765.9421 | 1260440.4349
82 | 2698772.2183 | 1260489.9465 | 2698763.0782 | 1260490.4125
83 | 2698772.2183 | 1260489.9465 | 2698789.7776 | 1260489.239 | 2698795.2302 | 1260482.747
84 | 2698795.2302 | 1260482.747 | 2698801.2503 | 1260482.4362 | 2698800.5678 | 1260458.0664
85 | 2698770.2512 | 1260436.6925 | 2698776.6628 | 1260431.5864
86 | 2698776.6628 | 1260431.5864 | 2698781.1396 | 1260428.0211
87 | 2698800.5678 | 1260458.0664 | 2698800.1223 | 1260442.1559
88 | 2698781.1396 | 1260428.0211 | 2698785.6183 | 1260424.4543
89 | 2698799.8766 | 1260433.3844 | 2698800.1223 | 1260442.1559
90 | 2698797.5082 | 1260414.9854 | 2698799.5555 | 1260418.7671 | 2698799.8766 | 1260433.3844
91 | 2698799.8766 | 1260433.3844 | 2698803.7149 | 1260433.7377 | 2698804.5125 | 1260463.5864 | 2698806.0248 | 1260466.4584
92 | 2698797.5082 | 1260414.9854 | 2698801.4822 | 1260411.736
93 | 2698797.5082 | 1260414.9854 | 2698785.6183 | 1260424.4543
94 | 2698813.3613 | 1260466.3142 | 2698806.0248 | 1260466.4584
95 | 2698813.4878 | 1260401.9194 | 2698801.4822 | 1260411.736
96 | 2698813.4878 | 1260401.9194 | 2698816.3722 | 1260400.4772
97 | 2698816.3722 | 1260400.4772 | 2698831.3506 | 1260392.9882 | 2698837.4636 | 1260391.651
98 | 2698829.362 | 1260425.1615 | 2698845.3282 | 1260424.8962
99 | 2698845.3282 | 1260424.8962 | 2698859.4642 | 1260424.6614
100 | 2698837.4636 | 1260391.651 | 2698853.5473 | 1260388.1328 | 2698859.4379 | 1260388.2313
101 | 2698859.7217 | 1260429.5475 | 2698859.4642 | 1260424.6614
102 | 2698873.7126 | 1260388.47 | 2698859.4379 | 1260388.2313
103 | 2698859.7217 | 1260429.5475 | 2698870.5445 | 1260429.1724 | 2698874.5644 | 1260429.0284 | 2698877.7468 | 1260428.937
104 | 2698877.7468 | 1260428.937 | 2698881.4295 | 1260427.3306 | 2698889.9195 | 1260427.0531
105 | 2698877.4085 | 1260389.2212 | 2698873.7126 | 1260388.47
106 | 2698877.4085 | 1260389.2212 | 2698889.9093 | 1260393.5337 | 2698904.8641 | 1260400.2891
107 | 2698877.4085 | 1260389.2212 | 2698876.9404 | 1260368.0431
108 | 2698889.9195 | 1260427.0531 | 2698905.5103 | 1260426.5435 | 2698906.1994 | 1260426.5458
109 | 2698917.6172 | 1260409.7878 | 2698904.8641 | 1260400.2891
110 | 2698876.9404 | 1260368.0431 | 2698876.8121 | 1260362.2346
111 | 2698921.8684 | 1260413.3951 | 2698910.5 | 1260426.5603 | 2698906.1994 | 1260426.5458
112 | 2698876.8121 | 1260362.2346 | 2698876.6835 | 1260356.4166
113 | 2698876.6835 | 1260356.4166 | 2698876.555 | 1260350.6028
114 | 2698876.516 | 1260348.8401 | 2698876.555 | 1260350.6028
115 | 2698917.6172 | 1260409.7878 | 2698919.069 | 1260410.8685 | 2698921.8684 | 1260413.3951
116 | 2698876.516 | 1260348.8401 | 2698876.425 | 1260344.7796
117 | 2698904.2907 | 1260348.0481 | 2698876.516 | 1260348.8401
118 | 2698921.8684 | 1260413.3951 | 2698923.8883 | 1260415.2082
119 | 2698904.2907 | 1260348.0481 | 2698904.5017 | 1260367.2724
120 | 2698923.8883 | 1260415.2082 | 2698931.6186 | 1260422.1653 | 2698943.159 | 1260433.4119
121 | 2698923.8883 | 1260415.2082 | 2698943.6983 | 1260379.11 | 2698956.1868 | 1260378.6105
122 | 2698943.159 | 1260433.4119 | 2698946.5211 | 1260437.9927
123 | 2698943.159 | 1260433.4119 | 2698931.4878 | 1260443.9475 | 2698922.3639 | 1260444.1809
124 | 2698973.6883 | 1260377.9105 | 2698956.1868 | 1260378.6105
125 | 2698894.3145 | 1260477.6091 | 2698894.2234 | 1260475.6871
126 | 2698906.4367 | 1260477.0557 | 2698894.3145 | 1260477.6091
127 | 2698894.3145 | 1260477.6091 | 2698894.9651 | 1260500.5511
128 | 2698946.5211 | 1260437.9927 | 2698955.0964 | 1260449.6761
129 | 2698955.0964 | 1260449.6761 | 2698958.1487 | 1260453.8347 | 2698961.2715 | 1260459.0936
130 | 2698970.722 | 1260480.3666 | 2698969.2404 | 1260472.5132 | 2698961.2715 | 1260459.0936

## bus_geodata
| x | y | coords
0 | 2698598.5081 | 1260326.3401
1 | 2698588.2793 | 1260300.8733
2 | 2698607.4165 | 1260353.3948
3 | 2698586.9509 | 1260297.5648
4 | 2698609.1123 | 1260503.5594
5 | 2698574.8515 | 1260255.0641
6 | 2698607.9897 | 1260527.9383
7 | 2698580.3278 | 1260247.0413
8 | 2698616.5072 | 1260520.5645
9 | 2698590.1998 | 1260231.7772
10 | 2698598.2992 | 1260216.1673
11 | 2698637.7169 | 1260179.1722
12 | 2698768.3891 | 1260129.8524
13 | 2698771.545 | 1260128.7044
14 | 2698782.3539 | 1260124.7786
15 | 2698653.7858 | 1260488.2916
16 | 2698663.205 | 1260498.3902
17 | 2698660.3251 | 1260561.6604
18 | 2698680.6253 | 1260555.7307
19 | 2698657.4984 | 1260547.6422
20 | 2698690.1785 | 1260497.3813
21 | 2698686.0104 | 1260553.6711
22 | 2698653.8246 | 1260529.4227
23 | 2698789.2669 | 1260596.9405
24 | 2698816.3619 | 1260609.9501
25 | 2698804.1909 | 1260580.7098
26 | 2698687.9469 | 1260581.2592
27 | 2698697.7089 | 1260581.1084
28 | 2698788.5391 | 1260592.0103
29 | 2698700.455 | 1260502.9374
30 | 2698719.3688 | 1260452.7009
31 | 2698719.9223 | 1260463.3565
32 | 2698796.5939 | 1260119.6409
33 | 2698809.9526 | 1260114.8175
34 | 2698807.8636 | 1260155.0415
35 | 2698755.5236 | 1260008.8128
36 | 2698813.4458 | 1260172.5765
37 | 2698760.8531 | 1260005.6071
38 | 2698776.1568 | 1259999.3761
39 | 2698814.542 | 1260176.0198
40 | 2698911.338 | 1260249.8526
41 | 2698878.4672 | 1260320.0604
42 | 2698961.9274 | 1260205.3487
43 | 2698876.0872 | 1260329.6981
44 | 2698929.6128 | 1260347.8824
45 | 2698932.0398 | 1260380.5619
46 | 2698911.4438 | 1260348.0013
47 | 2698876.2946 | 1260338.9557
48 | 2698859.994 | 1260581.556
49 | 2698855.9546 | 1260549.3599
50 | 2698863.3443 | 1260609.1321
51 | 2698893.4722 | 1260521.2083
52 | 2698846.237 | 1260550.3651
53 | 2698848.1073 | 1260609.3974
54 | 2698918.1979 | 1260502.1283
55 | 2698894.1564 | 1260553.7574
56 | 2698800.2909 | 1260557.8927
57 | 2698844.4947 | 1260538.4272
58 | 2698832.2323 | 1260609.6738
59 | 2698900.2182 | 1260554.1035
60 | 2698915.5043 | 1260553.7153
61 | 2698933.6315 | 1260491.9669
62 | 2698914.0316 | 1260477.6832
63 | 2698826.7585 | 1260609.7691
64 | 2698843.7667 | 1260514.9968
65 | 2698717.4427 | 1260502.5983
66 | 2698728.406 | 1260473.0349
67 | 2698742.143 | 1260496.2941
68 | 2698713.6731 | 1260580.8619
69 | 2698729.6354 | 1260580.6153
70 | 2698740.1489 | 1260560.6355
71 | 2698699.438 | 1260545.3438
72 | 2698743.4222 | 1260540.5463
73 | 2698703.2812 | 1260540.8211
74 | 2698653.7547 | 1260529.0758
75 | 2698652.8555 | 1260524.6168
76 | 2698742.9623 | 1260524.6362
77 | 2698742.5024 | 1260508.7259
78 | 2698747.1392 | 1260491.2252
79 | 2698759.9185 | 1260445.6664
80 | 2698765.9421 | 1260440.4349
81 | 2698763.0782 | 1260490.4125
82 | 2698772.2183 | 1260489.9465
83 | 2698795.2302 | 1260482.747
84 | 2698770.2512 | 1260436.6925
85 | 2698776.6628 | 1260431.5864
86 | 2698800.5678 | 1260458.0664
87 | 2698781.1396 | 1260428.0211
88 | 2698800.1222 | 1260442.1559
89 | 2698799.8766 | 1260433.3844
90 | 2698797.5082 | 1260414.9854
91 | 2698806.0248 | 1260466.4584
92 | 2698801.4822 | 1260411.736
93 | 2698785.6183 | 1260424.4543
94 | 2698813.3613 | 1260466.3142
95 | 2698813.4878 | 1260401.9194
96 | 2698816.3722 | 1260400.4772
97 | 2698829.362 | 1260425.1615
98 | 2698845.3282 | 1260424.8962
99 | 2698837.4636 | 1260391.651
100 | 2698859.4642 | 1260424.6614
101 | 2698859.4379 | 1260388.2313
102 | 2698859.7217 | 1260429.5475
103 | 2698877.7468 | 1260428.937
104 | 2698873.7126 | 1260388.47
105 | 2698877.4085 | 1260389.2212
106 | 2698889.9195 | 1260427.0531
107 | 2698904.8641 | 1260400.2891
108 | 2698876.9404 | 1260368.0431
109 | 2698906.1994 | 1260426.5458
110 | 2698876.8121 | 1260362.2346
111 | 2698876.6835 | 1260356.4166
112 | 2698876.555 | 1260350.6028
113 | 2698917.6172 | 1260409.7878
114 | 2698876.516 | 1260348.8401
115 | 2698921.8684 | 1260413.3951
116 | 2698904.5017 | 1260367.2724
117 | 2698904.2907 | 1260348.0481
118 | 2698923.8883 | 1260415.2082
119 | 2698943.159 | 1260433.4119
120 | 2698956.1868 | 1260378.6105
121 | 2698894.2234 | 1260475.6871
122 | 2698894.3145 | 1260477.6091
123 | 2698922.3639 | 1260444.1809
124 | 2698876.425 | 1260344.7796
125 | 2698946.5211 | 1260437.9927
126 | 2698973.6883 | 1260377.9105
127 | 2698955.0964 | 1260449.6761
128 | 2698961.2715 | 1260459.0936
129 | 2698906.4367 | 1260477.0557
130 | 2698894.9651 | 1260500.5511
131 | 2698970.722 | 1260480.3666
132 | 2698846.237 | 1260550.3651

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97211 | -0.53854 | 0.0019194 | 0.00048104
1 | 0.97191 | -0.54241 | 0.00014839 | 3.719e-05
2 | 0.97236 | -0.53351 | 0.00016192 | 4.0582e-05
3 | 0.97189 | -0.5429 | 0.00040382 | 0.00010121
4 | 0.97281 | -0.5245 | 0 | 0
5 | 0.97159 | -0.54872 | 0 | 0
6 | 0.97287 | -0.52341 | 0 | 0
7 | 0.97153 | -0.54999 | 0.00045659 | 0.00011443
8 | 0.9729 | -0.5229 | 0.0016317 | 0.00040893
9 | 0.97142 | -0.55222 | 0.00068571 | 0.00017185
10 | 0.97132 | -0.55415 | 0.00073447 | 0.00018408
11 | 0.97105 | -0.55938 | 0 | 0
12 | 0.97038 | -0.57282 | 0.000693 | 0.00017368
13 | 0.97036 | -0.5731 | 0.00041944 | 0.00010512
14 | 0.97032 | -0.57397 | 0.00018745 | 4.6979e-05
15 | 0.97303 | -0.52032 | 0 | 0
16 | 0.97306 | -0.5196 | 0.0014225 | 0.00035651
17 | 0.97026 | -0.57491 | 0 | 0
18 | 0.97038 | -0.57256 | 0.0010233 | 0.00025647
19 | 0.97018 | -0.57649 | 0.00098187 | 0.00024608
20 | 0.97314 | -0.51801 | 0.0099334 | 0.0024896
21 | 0.97042 | -0.57182 | 0 | 0
22 | 0.9701 | -0.57821 | 0.0021939 | 0.00054985
23 | 0.98814 | -0.22737 | 0 | 0
24 | 0.98906 | -0.20949 | 0.010312 | 0.0025843
25 | 0.98742 | -0.24144 | 0 | 0
26 | 0.97067 | -0.56685 | 0 | 0
27 | 0.97076 | -0.56511 | 0.0025629 | 0.00064232
28 | 0.98715 | -0.24658 | 0.014894 | 0.0037327
29 | 0.97323 | -0.51633 | 0.0026818 | 0.00067211
30 | 0.97289 | -0.52295 | 0.0045493 | 0.0011402
31 | 0.97294 | -0.52205 | 0.0041892 | 0.0010499
32 | 0.97026 | -0.57506 | 0 | 0
33 | 0.97026 | -0.57518 | 0.00043343 | 0.00010863
34 | 0.97021 | -0.57619 | 0.0006019 | 0.00015085
35 | 0.97006 | -0.57904 | 0.00019308 | 4.8391e-05
36 | 0.97019 | -0.57655 | 0.00035312 | 8.85e-05
37 | 0.97005 | -0.57923 | 0.0012938 | 0.00032427
38 | 0.97005 | -0.57933 | 0.00032901 | 8.2457e-05
39 | 0.97019 | -0.57659 | 0.00068765 | 0.00017234
40 | 0.97835 | -0.41576 | 0 | 0
41 | 0.97838 | -0.41511 | 0 | 0
42 | 0.97833 | -0.41618 | 0.00033851 | 8.4839e-05
43 | 0.97839 | -0.41505 | 0.0019867 | 0.00049793
44 | 0.97751 | -0.43236 | 0 | 0
45 | 0.97721 | -0.43817 | 0.0097016 | 0.0024315
46 | 0.97767 | -0.42915 | 0.0097009 | 0.0024313
47 | 0.97841 | -0.41465 | 0.0012524 | 0.00031388
48 | 0.99293 | -0.13466 | 0.018692 | 0.0046848
49 | 0.9954 | -0.087109 | 0 | 0
50 | 0.99129 | -0.16621 | 0 | 0
51 | 0.99194 | -0.15304 | 0 | 0
52 | 0.9966 | -0.064327 | 0 | 0
53 | 0.99042 | -0.18315 | 0.010312 | 0.0025844
54 | 0.98984 | -0.19317 | 0 | 0
55 | 0.99105 | -0.17017 | 0.018617 | 0.0046659
56 | 0.98708 | -0.24794 | 0.015228 | 0.0038164
57 | 0.99775 | -0.042582 | 0.015544 | 0.0038957
58 | 0.98966 | -0.19791 | 0.010312 | 0.0025843
59 | 0.99099 | -0.17136 | 0 | 0
60 | 0.99084 | -0.17436 | 0.011059 | 0.0027715
61 | 0.98877 | -0.21367 | 0 | 0
62 | 0.98892 | -0.21109 | 0.0086017 | 0.0021558
63 | 0.98945 | -0.202 | 0.0015371 | 0.00038522
64 | 1 | 0 | -0.42443 | -0.10862
65 | 0.97333 | -0.51435 | 0 | 0
66 | 0.97307 | -0.5195 | 0 | 0
67 | 0.97356 | -0.50973 | 0 | 0
68 | 0.97094 | -0.5615 | 0.0086915 | 0.0021783
69 | 0.97125 | -0.55533 | 0.0086915 | 0.0021783
70 | 0.97211 | -0.53836 | 0 | 0
71 | 0.97038 | -0.57259 | 0 | 0
72 | 0.97277 | -0.52541 | 0.008686 | 0.0021769
73 | 0.97037 | -0.57288 | 0.0026494 | 0.000664
74 | 0.9701 | -0.57823 | 0.0012227 | 0.00030643
75 | 0.97009 | -0.57836 | 0.0015797 | 0.00039591
76 | 0.97305 | -0.5198 | 0.008692 | 0.0021784
77 | 0.9734 | -0.51292 | 0.0086921 | 0.0021784
78 | 0.97377 | -0.50568 | 0.0039817 | 0.00099791
79 | 0.97652 | -0.45147 | 0.0019903 | 0.00049881
80 | 0.97654 | -0.45118 | 0.0022618 | 0.00056685
81 | 0.97412 | -0.49881 | 0.0039836 | 0.00099838
82 | 0.97432 | -0.4947 | 0 | 0
83 | 0.97492 | -0.48301 | 0.0039833 | 0.00099831
84 | 0.97656 | -0.45073 | 0 | 0
85 | 0.97659 | -0.4501 | 0.0018534 | 0.0004645
86 | 0.97564 | -0.46882 | 0.0039819 | 0.00099797
87 | 0.97663 | -0.44946 | 0.0018534 | 0.0004645
88 | 0.97603 | -0.46112 | 0.0039792 | 0.00099728
89 | 0.97626 | -0.45672 | 0 | 0
90 | 0.97681 | -0.4459 | 0 | 0
91 | 0.97573 | -0.46709 | 0 | 0
92 | 0.97697 | -0.44274 | 0.0038675 | 0.00096929
93 | 0.97667 | -0.44862 | 0.0018541 | 0.00046467
94 | 0.97562 | -0.46914 | 0.015338 | 0.0038442
95 | 0.97747 | -0.43292 | 0 | 0
96 | 0.97757 | -0.43087 | 0.0034093 | 0.00085445
97 | 0.98002 | -0.38329 | 0.0062844 | 0.001575
98 | 0.98011 | -0.38147 | 0.0062873 | 0.0015758
99 | 0.97833 | -0.41597 | 0.0031327 | 0.00078514
100 | 0.98028 | -0.37825 | 0.0062844 | 0.001575
101 | 0.97909 | -0.40119 | 0.0025869 | 0.00064833
102 | 0.98036 | -0.37657 | 0 | 0
103 | 0.98068 | -0.37041 | 0 | 0
104 | 0.97958 | -0.39159 | 0 | 0
105 | 0.97971 | -0.38907 | 0 | 0
106 | 0.98089 | -0.36613 | 0.0062859 | 0.0015754
107 | 0.98097 | -0.36453 | 0 | 0
108 | 0.97902 | -0.40261 | 0.0012987 | 0.00032548
109 | 0.98127 | -0.35872 | 0.0053009 | 0.0013285
110 | 0.97884 | -0.40619 | 0.00129 | 0.0003233
111 | 0.97866 | -0.40964 | 0.0012842 | 0.00032185
112 | 0.97849 | -0.41295 | 0.0012782 | 0.00032034
113 | 0.98165 | -0.35138 | 0 | 0
114 | 0.97844 | -0.41391 | 0 | 0
115 | 0.98188 | -0.34677 | 0 | 0
116 | 0.9777 | -0.42864 | 0.0057679 | 0.0014456
117 | 0.9778 | -0.42662 | 0 | 0
118 | 0.98202 | -0.34415 | 0 | 0
119 | 0.9834 | -0.31736 | 0 | 0
120 | 0.98149 | -0.35454 | 0.0053534 | 0.0013417
121 | 0.98834 | -0.22242 | 0.011797 | 0.0029565
122 | 0.98836 | -0.22201 | 0 | 0
123 | 0.98328 | -0.31974 | 0.0052996 | 0.0013282
124 | 0.97843 | -0.41427 | 0.0012647 | 0.00031697
125 | 0.9837 | -0.31149 | 0.0061826 | 0.0015495
126 | 0.9814 | -0.35624 | 0.0053507 | 0.001341
127 | 0.98449 | -0.29612 | 0.0063656 | 0.0015954
128 | 0.98513 | -0.28385 | 0.007621 | 0.00191
129 | 0.9887 | -0.21531 | 0 | 0
130 | 0.98795 | -0.2299 | 0.019256 | 0.004826
131 | 0.9865 | -0.25742 | 0 | 0
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0076316 | 0.0019099 | -0.0076302 | -0.0019094 | 1.4042e-06 | 5.5853e-07 | 0.011681 | 0.011681 | 0.011681 | 0.97211 | -0.53854 | 0.97191 | -0.54241 | 3.2091
1 | -0.009551 | -0.002391 | 0.0095533 | 0.0023921 | 2.2861e-06 | 1.1094e-06 | 0.014619 | 0.014619 | 0.014619 | 0.97211 | -0.53854 | 0.97236 | -0.53351 | 4.0162
2 | 0.0074818 | 0.0018722 | -0.0074817 | -0.0018721 | 1.7539e-07 | 6.807e-08 | 0.011454 | 0.011454 | 0.011454 | 0.97191 | -0.54241 | 0.97189 | -0.5429 | 3.1467
3 | -0.0097152 | -0.0024327 | 0.0097194 | 0.0024297 | 4.1647e-06 | -2.9477e-06 | 0.014867 | 0.014865 | 0.014867 | 0.97236 | -0.53351 | 0.97281 | -0.5245 | 1.3614
4 | 0.0070778 | 0.0017709 | -0.0070759 | -0.0017702 | 1.9599e-06 | 7.0291e-07 | 0.010836 | 0.010836 | 0.010836 | 0.97189 | -0.5429 | 0.97159 | -0.54872 | 2.9768
5 | -0.0097194 | -0.0024297 | 0.0097199 | 0.0024288 | 5.0778e-07 | -8.9252e-07 | 0.014865 | 0.014864 | 0.014865 | 0.97281 | -0.5245 | 0.97287 | -0.52341 | 1.0209
6 | 0.0070759 | 0.0017702 | -0.0070755 | -0.00177 | 4.2769e-07 | 1.5343e-07 | 0.010836 | 0.010836 | 0.010836 | 0.97159 | -0.54872 | 0.97153 | -0.54999 | 2.9769
7 | -0.0097199 | -0.0024288 | 0.0097201 | 0.0024284 | 2.3335e-07 | -4.1023e-07 | 0.014864 | 0.014864 | 0.014864 | 0.97287 | -0.52341 | 0.9729 | -0.5229 | 1.0209
8 | 0.0066189 | 0.0016556 | -0.0066182 | -0.0016554 | 7.0126e-07 | 2.2346e-07 | 0.010136 | 0.010137 | 0.010137 | 0.97153 | -0.54999 | 0.97142 | -0.55222 | 2.7848
9 | -0.011352 | -0.0028373 | 0.011353 | 0.0028358 | 1.3929e-06 | -1.558e-06 | 0.017359 | 0.017359 | 0.017359 | 0.9729 | -0.5229 | 0.97303 | -0.52032 | 1.1923
10 | 0.0059325 | 0.0014835 | -0.0059319 | -0.0014834 | 5.4446e-07 | 1.3076e-07 | 0.0090862 | 0.0090862 | 0.0090862 | 0.97142 | -0.55222 | 0.97132 | -0.55415 | 2.4962
11 | 0.0051974 | 0.0012993 | -0.0051961 | -0.0012992 | 1.2913e-06 | 1.5414e-07 | 0.0079611 | 0.0079613 | 0.0079613 | 0.97132 | -0.55415 | 0.97105 | -0.55938 | 2.1872
12 | 0.0051961 | 0.0012992 | -0.0051928 | -0.0012988 | 3.3213e-06 | 3.9833e-07 | 0.0079613 | 0.0079619 | 0.0079619 | 0.97105 | -0.55938 | 0.97038 | -0.57282 | 2.1873
13 | 0.0044998 | 0.0011251 | -0.0044998 | -0.0011251 | 5.9945e-08 | -3.1212e-09 | 0.0068993 | 0.0068993 | 0.0068993 | 0.97038 | -0.57282 | 0.97036 | -0.5731 | 1.8954
14 | 0.0040803 | 0.00102 | -0.0040802 | -0.00102 | 1.6878e-07 | -3.4031e-08 | 0.0062561 | 0.0062561 | 0.0062561 | 0.97036 | -0.5731 | 0.97032 | -0.57397 | 1.7187
15 | 0.0038927 | 0.00097303 | -0.0038925 | -0.00097309 | 2.0224e-07 | -5.7545e-08 | 0.0059687 | 0.0059687 | 0.0059687 | 0.97032 | -0.57397 | 0.97026 | -0.57506 | 1.6398
16 | -0.011353 | -0.0028358 | 0.011354 | 0.0028353 | 3.901e-07 | -4.3648e-07 | 0.017359 | 0.017358 | 0.017359 | 0.97303 | -0.52032 | 0.97306 | -0.5196 | 1.1922
17 | -0.012776 | -0.0031919 | 0.012777 | 0.0031911 | 9.6553e-07 | -7.2337e-07 | 0.019534 | 0.019533 | 0.019534 | 0.97306 | -0.5196 | 0.97314 | -0.51801 | 1.3416
18 | -0.005979 | -0.0014984 | 0.0059797 | 0.0014985 | 6.6804e-07 | 1.6583e-07 | 0.0091695 | 0.0091694 | 0.0091695 | 0.97026 | -0.57491 | 0.97038 | -0.57256 | 2.5191
19 | 0.005979 | 0.0014984 | -0.0059786 | -0.0014982 | 4.5089e-07 | 1.1197e-07 | 0.0091695 | 0.0091696 | 0.0091696 | 0.97026 | -0.57491 | 0.97018 | -0.57649 | 2.5191
20 | -0.007003 | -0.001755 | 0.0070033 | 0.0017551 | 2.4933e-07 | 8.834e-08 | 0.010739 | 0.010739 | 0.010739 | 0.97038 | -0.57256 | 0.97042 | -0.57182 | 2.9502
21 | 0.0049967 | 0.0012522 | -0.0049963 | -0.0012521 | 4.0935e-07 | 3.2493e-08 | 0.0076636 | 0.0076637 | 0.0076637 | 0.97018 | -0.57649 | 0.9701 | -0.57821 | 2.1054
22 | -0.02271 | -0.0056807 | 0.022712 | 0.005681 | 1.8053e-06 | 3.6155e-07 | 0.034722 | 0.034722 | 0.034722 | 0.97314 | -0.51801 | 0.97323 | -0.51633 | 2.3848
23 | 0.0026495 | 0.00066382 | -0.0026494 | -0.00066395 | 9.7589e-08 | -1.3233e-07 | 0.0040626 | 0.0040627 | 0.0040627 | 0.97042 | -0.57182 | 0.97038 | -0.57259 | 1.1161
24 | -0.0096528 | -0.0024189 | 0.0096551 | 0.00242 | 2.2829e-06 | 1.1177e-06 | 0.014801 | 0.014801 | 0.014801 | 0.97042 | -0.57182 | 0.97067 | -0.56685 | 4.0663
25 | 0.0028024 | 0.00070229 | -0.0028024 | -0.00070229 | 2.4518e-09 | -2.7993e-09 | 0.0042985 | 0.0042985 | 0.0042985 | 0.9701 | -0.57821 | 0.9701 | -0.57823 | 1.1809
26 | -0.03015 | -0.0075665 | 0.030175 | 0.0075825 | 2.5728e-05 | 1.6039e-05 | 0.045405 | 0.045405 | 0.045405 | 0.98814 | -0.22737 | 0.98906 | -0.20949 | 12.474
27 | 0.03015 | 0.0075665 | -0.030129 | -0.0075539 | 2.0213e-05 | 1.2602e-05 | 0.045405 | 0.045405 | 0.045405 | 0.98814 | -0.22737 | 0.98742 | -0.24144 | 12.474
28 | -0.040487 | -0.010167 | 0.040502 | 0.010176 | 1.4471e-05 | 9.1278e-06 | 0.060919 | 0.060919 | 0.060919 | 0.98906 | -0.20949 | 0.98945 | -0.202 | 16.7359
29 | 0.015232 | 0.0038191 | -0.015228 | -0.0038164 | 4.718e-06 | 2.7142e-06 | 0.022955 | 0.022955 | 0.022955 | 0.98742 | -0.24144 | 0.98708 | -0.24794 | 6.3064
30 | 0.014897 | 0.0037348 | -0.014894 | -0.0037327 | 3.6487e-06 | 2.0883e-06 | 0.02245 | 0.02245 | 0.02245 | 0.98742 | -0.24144 | 0.98715 | -0.24658 | 6.1677
31 | -0.0096551 | -0.00242 | 0.0096559 | 0.0024204 | 8.0206e-07 | 3.9263e-07 | 0.014801 | 0.014801 | 0.014801 | 0.97067 | -0.56685 | 0.97076 | -0.56511 | 4.0662
32 | -0.012219 | -0.0030627 | 0.012221 | 0.0030639 | 2.1003e-06 | 1.1468e-06 | 0.01873 | 0.018729 | 0.01873 | 0.97076 | -0.56511 | 0.97094 | -0.5615 | 5.1455
33 | -0.025394 | -0.0063532 | 0.025396 | 0.0063539 | 2.4008e-06 | 6.9186e-07 | 0.038822 | 0.038822 | 0.038822 | 0.97323 | -0.51633 | 0.97333 | -0.51435 | 2.6664
34 | -0.0045493 | -0.0011402 | 0.0045495 | 0.0011401 | 1.9371e-07 | -8.5255e-09 | 0.006958 | 0.006958 | 0.006958 | 0.97289 | -0.52295 | 0.97294 | -0.52205 | 1.9115
35 | -0.0087386 | -0.00219 | 0.0087397 | 0.0021905 | 1.0628e-06 | 4.8313e-07 | 0.013365 | 0.013365 | 0.013365 | 0.97294 | -0.52205 | 0.97307 | -0.5195 | 3.6717
36 | 0.00043344 | 0.00010846 | -0.00043343 | -0.00010863 | 2.3532e-09 | -1.7391e-07 | 0.00066466 | 0.00066473 | 0.00066473 | 0.97026 | -0.57506 | 0.97026 | -0.57518 | 0.18262
37 | 0.0016428 | 0.00041103 | -0.0016427 | -0.00041143 | 8.8418e-08 | -4.0223e-07 | 0.0025192 | 0.0025193 | 0.0025193 | 0.97026 | -0.57506 | 0.97021 | -0.57619 | 0.69212
38 | 0.0018163 | 0.0004536 | -0.0018159 | -0.00045484 | 3.4382e-07 | -1.2394e-06 | 0.0027849 | 0.0027854 | 0.0027854 | 0.97026 | -0.57506 | 0.97006 | -0.57904 | 0.76523
39 | 0.0010408 | 0.00026058 | -0.0010408 | -0.0002608 | 1.7583e-08 | -2.1599e-07 | 0.0015962 | 0.0015963 | 0.0015963 | 0.97021 | -0.57619 | 0.97019 | -0.57655 | 0.43853
40 | 0.0016229 | 0.00040645 | -0.0016228 | -0.00040652 | 1.45e-08 | -6.7756e-08 | 0.0024893 | 0.0024893 | 0.0024893 | 0.97006 | -0.57904 | 0.97005 | -0.57923 | 0.68387
41 | 0.00068765 | 0.0001723 | -0.00068765 | -0.00017234 | 1.5073e-09 | -4.3658e-08 | 0.0010547 | 0.0010547 | 0.0010547 | 0.97019 | -0.57655 | 0.97019 | -0.57659 | 0.28975
42 | 0.00032901 | 8.2254e-05 | -0.00032901 | -8.2457e-05 | 1.578e-09 | -2.0298e-07 | 0.00050461 | 0.00050468 | 0.00050468 | 0.97005 | -0.57923 | 0.97005 | -0.57933 | 0.13865
43 | -0.00033852 | -8.3997e-05 | 0.00033853 | 8.2693e-05 | 1.0359e-08 | -1.3046e-06 | 0.00051457 | 0.0005141 | 0.00051457 | 0.97835 | -0.41576 | 0.97838 | -0.41511 | 0.14136
44 | 0.00033852 | 8.3997e-05 | -0.00033851 | -8.4839e-05 | 6.6942e-09 | -8.4181e-07 | 0.00051457 | 0.00051487 | 0.00051487 | 0.97835 | -0.41576 | 0.97833 | -0.41618 | 0.14145
45 | -0.00033853 | -8.2693e-05 | 0.00033853 | 8.2567e-05 | 9.9607e-10 | -1.2558e-07 | 0.0005141 | 0.00051406 | 0.0005141 | 0.97838 | -0.41511 | 0.97839 | -0.41505 | 0.14124
46 | -0.0023253 | -0.00058049 | 0.0023253 | 0.0005804 | 4.3408e-08 | -8.8509e-08 | 0.0035357 | 0.0035356 | 0.0035357 | 0.97839 | -0.41505 | 0.97841 | -0.41465 | 0.97134
47 | 0.0097043 | 0.0024328 | -0.0097016 | -0.0024315 | 2.6845e-06 | 1.307e-06 | 0.014773 | 0.014773 | 0.014773 | 0.97751 | -0.43236 | 0.97721 | -0.43817 | 4.0585
48 | -0.0097043 | -0.0024328 | 0.0097058 | 0.0024335 | 1.4869e-06 | 7.2383e-07 | 0.014773 | 0.014773 | 0.014773 | 0.97751 | -0.43236 | 0.97767 | -0.42915 | 4.0584
49 | -0.019407 | -0.0048648 | 0.019409 | 0.0048662 | 2.3403e-06 | 1.4081e-06 | 0.029537 | 0.029537 | 0.029537 | 0.97767 | -0.42915 | 0.9778 | -0.42662 | 8.1147
50 | -0.0035777 | -0.00089428 | 0.0035778 | 0.00089425 | 6.4655e-08 | -3.1782e-08 | 0.0054403 | 0.0054403 | 0.0054403 | 0.97841 | -0.41465 | 0.97843 | -0.41427 | 1.4946
51 | -0.081545 | -0.020536 | 0.081731 | 0.020654 | 0.00018586 | 0.00011852 | 0.12224 | 0.12224 | 0.12224 | 0.99293 | -0.13466 | 0.9954 | -0.087109 | 33.5823
52 | 0.062853 | 0.015851 | -0.062758 | -0.015791 | 9.4782e-05 | 6.0293e-05 | 0.094227 | 0.094227 | 0.094227 | 0.99293 | -0.13466 | 0.99129 | -0.16621 | 25.8865
53 | 0.32376 | 0.082954 | -0.32273 | -0.082296 | 0.0010309 | 0.00065734 | 0.48463 | 0.48463 | 0.48463 | 0.9954 | -0.087109 | 0.99194 | -0.15304 | 33.285
54 | -0.40549 | -0.10361 | 0.40594 | 0.10389 | 0.00044725 | 0.00028557 | 0.60687 | 0.60687 | 0.60687 | 0.9954 | -0.087109 | 0.9966 | -0.064327 | 41.6804
55 | 0.062758 | 0.015791 | -0.062707 | -0.015758 | 5.074e-05 | 3.2277e-05 | 0.094227 | 0.094227 | 0.094227 | 0.99129 | -0.16621 | 0.99042 | -0.18315 | 25.8865
56 | 0.29302 | 0.074843 | -0.29246 | -0.074481 | 0.00056723 | 0.00036142 | 0.44007 | 0.44007 | 0.44007 | 0.99194 | -0.15304 | 0.98984 | -0.19317 | 30.2246
57 | 0.029702 | 0.0074536 | -0.029678 | -0.0074385 | 2.4241e-05 | 1.5094e-05 | 0.04456 | 0.04456 | 0.04456 | 0.99194 | -0.15304 | 0.99105 | -0.17017 | 12.2417
58 | -0.40594 | -0.10389 | 0.40636 | 0.10417 | 0.00042791 | 0.00027322 | 0.60687 | 0.60687 | 0.60687 | 0.9966 | -0.064327 | 0.99775 | -0.042582 | 41.6804
59 | 0.052395 | 0.013174 | -0.052358 | -0.013151 | 3.691e-05 | 2.3418e-05 | 0.078735 | 0.078735 | 0.078735 | 0.99042 | -0.18315 | 0.98966 | -0.19791 | 21.6304
60 | 0.25274 | 0.064507 | -0.25249 | -0.064348 | 0.00025012 | 0.00015913 | 0.38036 | 0.38036 | 0.38036 | 0.98984 | -0.19317 | 0.98877 | -0.21367 | 26.1239
61 | 0.039712 | 0.0099743 | -0.039678 | -0.0099529 | 3.3935e-05 | 2.1392e-05 | 0.059706 | 0.059707 | 0.059707 | 0.98984 | -0.19317 | 0.98892 | -0.21109 | 16.4029
62 | 0.011061 | 0.0027727 | -0.01106 | -0.0027723 | 6.2798e-07 | 3.2367e-07 | 0.016607 | 0.016607 | 0.016607 | 0.99105 | -0.17017 | 0.99099 | -0.17136 | 4.5625
63 | -0.42191 | -0.10806 | 0.42278 | 0.10862 | 0.00087238 | 0.0005571 | 0.63005 | 0.63005 | 0.63005 | 0.99775 | -0.042582 | 1 | 0 | 43.2725
64 | 0.042047 | 0.010566 | -0.042039 | -0.010561 | 8.2079e-06 | 5.1827e-06 | 0.06323 | 0.06323 | 0.06323 | 0.98966 | -0.19791 | 0.98945 | -0.202 | 17.371
65 | 0.01106 | 0.0027723 | -0.011059 | -0.0027715 | 1.5815e-06 | 8.1518e-07 | 0.016607 | 0.016607 | 0.016607 | 0.99099 | -0.17136 | 0.99084 | -0.17436 | 4.5625
66 | 0.25249 | 0.064348 | -0.25196 | -0.064009 | 0.00053189 | 0.0003384 | 0.38036 | 0.38037 | 0.38037 | 0.98877 | -0.21367 | 0.9865 | -0.25742 | 26.124
67 | 0.031076 | 0.0077971 | -0.03107 | -0.0077932 | 6.2495e-06 | 3.9019e-06 | 0.046764 | 0.046764 | 0.046764 | 0.98892 | -0.21109 | 0.9887 | -0.21531 | 12.8471
68 | 0.0087418 | 0.0021915 | -0.0087397 | -0.0021905 | 2.1451e-06 | 9.7492e-07 | 0.013365 | 0.013365 | 0.013365 | 0.97333 | -0.51435 | 0.97307 | -0.5195 | 3.6716
69 | -0.034138 | -0.0085454 | 0.034146 | 0.0085487 | 7.4986e-06 | 3.3386e-06 | 0.052187 | 0.052186 | 0.052187 | 0.97333 | -0.51435 | 0.97356 | -0.50973 | 3.5842
70 | -0.089902 | -0.022554 | 0.08992 | 0.022564 | 1.7358e-05 | 1.0621e-05 | 0.13742 | 0.13742 | 0.13742 | 0.97356 | -0.50973 | 0.97377 | -0.50568 | 9.438
71 | 0.055757 | 0.014005 | -0.055748 | -0.014 | 8.47e-06 | 4.8023e-06 | 0.085231 | 0.085231 | 0.085231 | 0.97356 | -0.50973 | 0.9734 | -0.51292 | 5.8538
72 | -0.020912 | -0.0052422 | 0.020919 | 0.0052459 | 6.1493e-06 | 3.738e-06 | 0.03205 | 0.03205 | 0.03205 | 0.97094 | -0.5615 | 0.97125 | -0.55533 | 8.8049
73 | -0.02961 | -0.0074242 | 0.029634 | 0.0074392 | 2.3976e-05 | 1.496e-05 | 0.045366 | 0.045365 | 0.045366 | 0.97125 | -0.55533 | 0.97211 | -0.53836 | 12.4631
74 | -0.029634 | -0.0074392 | 0.029652 | 0.0074506 | 1.8312e-05 | 1.1425e-05 | 0.045365 | 0.045365 | 0.045365 | 0.97211 | -0.53836 | 0.97277 | -0.52541 | 12.463
75 | 0.0026494 | 0.00066395 | -0.0026494 | -0.000664 | 3.6736e-08 | -4.9808e-08 | 0.0040627 | 0.0040627 | 0.0040627 | 0.97038 | -0.57259 | 0.97037 | -0.57288 | 1.1161
76 | -0.038338 | -0.0096275 | 0.038349 | 0.0096337 | 1.0266e-05 | 6.1752e-06 | 0.058652 | 0.058652 | 0.058652 | 0.97277 | -0.52541 | 0.97305 | -0.5198 | 8.0566
77 | 0.0015797 | 0.00039586 | -0.0015797 | -0.00039591 | 1.0015e-08 | -4.9751e-08 | 0.0024231 | 0.0024231 | 0.0024231 | 0.9701 | -0.57823 | 0.97009 | -0.57836 | 0.66569
78 | -0.047041 | -0.011812 | 0.047056 | 0.011822 | 1.5447e-05 | 9.4906e-06 | 0.071944 | 0.071944 | 0.071944 | 0.97305 | -0.5198 | 0.9734 | -0.51292 | 9.8824
79 | -0.093901 | -0.023562 | 0.093932 | 0.023581 | 3.0811e-05 | 1.8925e-05 | 0.1435 | 0.1435 | 0.1435 | 0.97377 | -0.50568 | 0.97412 | -0.49881 | 9.8559
80 | -0.0019903 | -0.00049881 | 0.0019903 | 0.00049872 | 2.7517e-08 | -8.2202e-08 | 0.0030327 | 0.0030327 | 0.0030327 | 0.97652 | -0.45147 | 0.97654 | -0.45118 | 0.83317
81 | -0.0042521 | -0.0010656 | 0.0042522 | 0.0010656 | 8.9846e-08 | -1.3905e-08 | 0.0064791 | 0.0064791 | 0.0064791 | 0.97654 | -0.45118 | 0.97656 | -0.45073 | 1.78
82 | -0.097916 | -0.024579 | 0.097935 | 0.024591 | 1.9199e-05 | 1.1831e-05 | 0.14959 | 0.14959 | 0.14959 | 0.97412 | -0.49881 | 0.97432 | -0.4947 | 10.2738
83 | -0.097935 | -0.024591 | 0.09799 | 0.024625 | 5.4649e-05 | 3.3677e-05 | 0.14959 | 0.14959 | 0.14959 | 0.97432 | -0.4947 | 0.97492 | -0.48301 | 10.2738
84 | -0.10197 | -0.025623 | 0.10204 | 0.025666 | 6.9077e-05 | 4.2692e-05 | 0.15567 | 0.15566 | 0.15567 | 0.97492 | -0.48301 | 0.97564 | -0.46882 | 10.6913
85 | -0.0042522 | -0.0010656 | 0.0042523 | 0.0010655 | 1.2903e-07 | -1.9975e-08 | 0.0064791 | 0.0064791 | 0.0064791 | 0.97656 | -0.45073 | 0.97659 | -0.4501 | 1.78
86 | -0.0061057 | -0.00153 | 0.0061059 | 0.0015301 | 1.8574e-07 | 4.7263e-08 | 0.009303 | 0.009303 | 0.009303 | 0.97659 | -0.4501 | 0.97663 | -0.44946 | 2.5558
87 | -0.10602 | -0.026664 | 0.10606 | 0.026688 | 3.9034e-05 | 2.4187e-05 | 0.16174 | 0.16174 | 0.16174 | 0.97564 | -0.46882 | 0.97603 | -0.46112 | 11.1084
88 | -0.0079593 | -0.0019946 | 0.0079596 | 0.0019947 | 3.1575e-07 | 1.3043e-07 | 0.012127 | 0.012127 | 0.012127 | 0.97663 | -0.44946 | 0.97667 | -0.44862 | 3.3316
89 | -0.11004 | -0.027685 | 0.11007 | 0.0277 | 2.3164e-05 | 1.4386e-05 | 0.1678 | 0.1678 | 0.1678 | 0.97603 | -0.46112 | 0.97626 | -0.45672 | 11.525
90 | -0.12541 | -0.031549 | 0.12548 | 0.03159 | 6.4842e-05 | 4.0552e-05 | 0.1912 | 0.1912 | 0.1912 | 0.97626 | -0.45672 | 0.97681 | -0.4459 | 13.1317
91 | 0.015348 | 0.0038494 | -0.01534 | -0.003845 | 7.5852e-06 | 4.3926e-06 | 0.023394 | 0.023394 | 0.023394 | 0.97626 | -0.45672 | 0.97573 | -0.46709 | 6.4269
92 | -0.13529 | -0.03405 | 0.13531 | 0.034063 | 2.0452e-05 | 1.2832e-05 | 0.20615 | 0.20615 | 0.20615 | 0.97681 | -0.4459 | 0.97697 | -0.44274 | 14.1586
93 | 0.0098149 | 0.00246 | -0.0098136 | -0.0024594 | 1.2742e-06 | 6.2525e-07 | 0.014952 | 0.014952 | 0.014952 | 0.97681 | -0.4459 | 0.97667 | -0.44862 | 4.1076
94 | 0.01534 | 0.003845 | -0.015338 | -0.0038442 | 1.5015e-06 | 8.6957e-07 | 0.023394 | 0.023394 | 0.023394 | 0.97573 | -0.46709 | 0.97562 | -0.46914 | 6.4269
95 | -0.13918 | -0.035032 | 0.13925 | 0.035073 | 6.5367e-05 | 4.1058e-05 | 0.21204 | 0.21204 | 0.21204 | 0.97697 | -0.44274 | 0.97747 | -0.43292 | 14.5631
96 | -0.13925 | -0.035073 | 0.13926 | 0.035081 | 1.3593e-05 | 8.5379e-06 | 0.21204 | 0.21204 | 0.21204 | 0.97747 | -0.43292 | 0.97757 | -0.43087 | 14.5631
97 | -0.14267 | -0.035936 | 0.14277 | 0.036 | 0.00010177 | 6.3976e-05 | 0.21723 | 0.21723 | 0.21723 | 0.97757 | -0.43087 | 0.97833 | -0.41597 | 14.9195
98 | -0.0062844 | -0.001575 | 0.0062849 | 0.0015752 | 5.4521e-07 | 1.4771e-07 | 0.0095419 | 0.0095418 | 0.0095419 | 0.98002 | -0.38329 | 0.98011 | -0.38147 | 2.6214
99 | -0.012572 | -0.0031509 | 0.012574 | 0.003152 | 1.9316e-06 | 1.058e-06 | 0.019087 | 0.019087 | 0.019087 | 0.98011 | -0.38147 | 0.98028 | -0.37825 | 5.2438
100 | -0.1459 | -0.036785 | 0.14601 | 0.03685 | 0.00010328 | 6.4978e-05 | 0.22199 | 0.22199 | 0.22199 | 0.97833 | -0.41597 | 0.97909 | -0.40119 | 15.2468
101 | -0.018859 | -0.004727 | 0.01886 | 0.0047279 | 1.5036e-06 | 9.0062e-07 | 0.028627 | 0.028627 | 0.028627 | 0.98028 | -0.37825 | 0.98036 | -0.37657 | 7.8645
102 | -0.14859 | -0.037498 | 0.14866 | 0.037541 | 6.8316e-05 | 4.3004e-05 | 0.22592 | 0.22592 | 0.22592 | 0.97909 | -0.40119 | 0.97958 | -0.39159 | 15.5168
103 | -0.01886 | -0.0047279 | 0.018866 | 0.0047312 | 5.5425e-06 | 3.3197e-06 | 0.028627 | 0.028627 | 0.028627 | 0.98036 | -0.37657 | 0.98068 | -0.37041 | 7.8645
104 | -0.018866 | -0.0047312 | 0.018869 | 0.0047335 | 3.8451e-06 | 2.303e-06 | 0.028627 | 0.028627 | 0.028627 | 0.98068 | -0.37041 | 0.98089 | -0.36613 | 7.8645
105 | -0.14866 | -0.037541 | 0.14868 | 0.037553 | 1.7997e-05 | 1.1329e-05 | 0.22592 | 0.22592 | 0.22592 | 0.97958 | -0.39159 | 0.97971 | -0.38907 | 15.5167
106 | -0.18391 | -0.046401 | 0.18412 | 0.046538 | 0.00021637 | 0.00013698 | 0.27943 | 0.27943 | 0.27943 | 0.97971 | -0.38907 | 0.98097 | -0.36453 | 19.1919
107 | 0.035226 | 0.0088487 | -0.035204 | -0.0088344 | 2.2746e-05 | 1.4291e-05 | 0.05351 | 0.05351 | 0.05351 | 0.97971 | -0.38907 | 0.97902 | -0.40261 | 14.7006
108 | -0.025155 | -0.0063089 | 0.025164 | 0.0063144 | 8.8956e-06 | 5.4875e-06 | 0.038162 | 0.038162 | 0.038162 | 0.98089 | -0.36613 | 0.98127 | -0.35872 | 10.4841
109 | -0.18412 | -0.046538 | 0.18424 | 0.046612 | 0.00011618 | 7.3553e-05 | 0.27943 | 0.27943 | 0.27943 | 0.98097 | -0.36453 | 0.98165 | -0.35138 | 19.1919
110 | 0.033905 | 0.0085089 | -0.033899 | -0.0085053 | 5.7867e-06 | 3.6305e-06 | 0.051537 | 0.051537 | 0.051537 | 0.97902 | -0.40261 | 0.97884 | -0.40619 | 14.1584
111 | -0.030465 | -0.0076429 | 0.030483 | 0.0076538 | 1.7365e-05 | 1.084e-05 | 0.046201 | 0.0462 | 0.046201 | 0.98127 | -0.35872 | 0.98188 | -0.34677 | 12.6925
112 | 0.032609 | 0.008182 | -0.032604 | -0.0081786 | 5.3635e-06 | 3.3595e-06 | 0.049576 | 0.049576 | 0.049576 | 0.97884 | -0.40619 | 0.97866 | -0.40964 | 13.6197
113 | 0.03132 | 0.0078568 | -0.031315 | -0.0078537 | 4.9457e-06 | 3.0922e-06 | 0.047623 | 0.047623 | 0.047623 | 0.97866 | -0.40964 | 0.97849 | -0.41295 | 13.0833
114 | 0.030037 | 0.0075333 | -0.030035 | -0.0075325 | 1.3796e-06 | 8.608e-07 | 0.045679 | 0.045679 | 0.045679 | 0.97849 | -0.41295 | 0.97844 | -0.41391 | 12.5493
115 | -0.18424 | -0.046612 | 0.18428 | 0.046638 | 4.0781e-05 | 2.5818e-05 | 0.27943 | 0.27943 | 0.27943 | 0.98165 | -0.35138 | 0.98188 | -0.34677 | 19.1918
116 | 0.0048426 | 0.0012112 | -0.0048425 | -0.0012112 | 8.2587e-08 | 1.8447e-09 | 0.0073637 | 0.0073637 | 0.0073637 | 0.97844 | -0.41391 | 0.97843 | -0.41427 | 2.023
117 | 0.025193 | 0.0063213 | -0.025177 | -0.0063118 | 1.5251e-05 | 9.4132e-06 | 0.038316 | 0.038316 | 0.038316 | 0.97844 | -0.41391 | 0.9778 | -0.42662 | 10.5263
118 | -0.21476 | -0.054291 | 0.21479 | 0.054309 | 2.694e-05 | 1.7104e-05 | 0.32563 | 0.32563 | 0.32563 | 0.98188 | -0.34677 | 0.98202 | -0.34415 | 22.3649
119 | -0.0057679 | -0.0014456 | 0.0057684 | 0.0014457 | 5.5558e-07 | 1.1445e-07 | 0.0087785 | 0.0087784 | 0.0087785 | 0.9777 | -0.42864 | 0.9778 | -0.42662 | 2.4117
120 | -0.2255 | -0.056994 | 0.22579 | 0.057178 | 0.00029004 | 0.00018428 | 0.34186 | 0.34186 | 0.34186 | 0.98202 | -0.34415 | 0.9834 | -0.31736 | 23.4795
121 | 0.01071 | 0.0026855 | -0.010705 | -0.0026828 | 5.3013e-06 | 2.7141e-06 | 0.016229 | 0.016229 | 0.016229 | 0.98202 | -0.34415 | 0.98149 | -0.35454 | 4.4585
122 | -0.23109 | -0.058507 | 0.23115 | 0.058548 | 6.5213e-05 | 4.1448e-05 | 0.34988 | 0.34988 | 0.34988 | 0.9834 | -0.31736 | 0.9837 | -0.31149 | 24.0303
123 | 0.0053002 | 0.0013283 | -0.0052996 | -0.0013282 | 5.9937e-07 | 6.8358e-08 | 0.0080199 | 0.00802 | 0.00802 | 0.9834 | -0.31736 | 0.98328 | -0.31974 | 2.2033
124 | 0.0053511 | 0.0013411 | -0.0053507 | -0.001341 | 4.3231e-07 | 5.5336e-08 | 0.0081128 | 0.0081128 | 0.0081128 | 0.98149 | -0.35454 | 0.9814 | -0.35624 | 2.2288
125 | -0.011797 | -0.0029565 | 0.011797 | 0.0029567 | 2.2761e-07 | 1.2101e-07 | 0.017761 | 0.017761 | 0.017761 | 0.98834 | -0.22242 | 0.98836 | -0.22201 | 4.8794
126 | -0.03106 | -0.007787 | 0.03107 | 0.0077932 | 9.922e-06 | 6.1949e-06 | 0.046764 | 0.046764 | 0.046764 | 0.98836 | -0.22201 | 0.9887 | -0.21531 | 12.8472
127 | 0.019263 | 0.0048304 | -0.019256 | -0.004826 | 7.2396e-06 | 4.3394e-06 | 0.029003 | 0.029003 | 0.029003 | 0.98836 | -0.22201 | 0.98795 | -0.2299 | 7.9678
128 | -0.23734 | -0.060098 | 0.23751 | 0.060209 | 0.00017534 | 0.00011148 | 0.35923 | 0.35923 | 0.35923 | 0.9837 | -0.31149 | 0.98449 | -0.29612 | 24.6726
129 | -0.24388 | -0.061804 | 0.24402 | 0.061896 | 0.00014381 | 9.1464e-05 | 0.36885 | 0.36885 | 0.36885 | 0.98449 | -0.29612 | 0.98513 | -0.28385 | 25.3334
130 | -0.25164 | -0.063806 | 0.25196 | 0.064009 | 0.00032009 | 0.00020365 | 0.38037 | 0.38037 | 0.38037 | 0.98513 | -0.28385 | 0.9865 | -0.25742 | 26.124

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44032 | 0.1126

## res_load
| p_mw | q_mvar
0 | 0.0019194 | 0.00048104
1 | 0.00014839 | 3.719e-05
2 | 0.00016192 | 4.0582e-05
3 | 0.00040382 | 0.00010121
4 | 0.00045659 | 0.00011443
5 | 0.0016317 | 0.00040893
6 | 0.00068571 | 0.00017185
7 | 0.00073447 | 0.00018408
8 | 0.000693 | 0.00017368
9 | 0.00041944 | 0.00010512
10 | 0.00018745 | 4.6979e-05
11 | 0.0014225 | 0.00035651
12 | 0.0010233 | 0.00025647
13 | 0.00098187 | 0.00024608
14 | 0.0099334 | 0.0024896
15 | 0.0021939 | 0.00054985
16 | 0.010312 | 0.0025843
17 | 0.0025629 | 0.00064232
18 | 0.014894 | 0.0037327
19 | 0.0026818 | 0.00067211
20 | 0.0045493 | 0.0011402
21 | 0.0041892 | 0.0010499
22 | 0.00043343 | 0.00010863
23 | 0.0006019 | 0.00015085
24 | 0.00019308 | 4.8391e-05
25 | 0.00035312 | 8.85e-05
26 | 0.0012938 | 0.00032427
27 | 0.00032901 | 8.2457e-05
28 | 0.00068765 | 0.00017234
29 | 0.00033851 | 8.4839e-05
30 | 0.0019867 | 0.00049793
31 | 0.0097016 | 0.0024315
32 | 0.0097009 | 0.0024313
33 | 0.0012524 | 0.00031388
34 | 0.018692 | 0.0046848
35 | 0.010312 | 0.0025844
36 | 0.018617 | 0.0046659
37 | 0.015228 | 0.0038164
38 | 0.015544 | 0.0038957
39 | 0.010312 | 0.0025843
40 | 0.011059 | 0.0027715
41 | 0.0086017 | 0.0021558
42 | 0.0015371 | 0.00038522
43 | 0.01589 | 0.0039825
44 | 0.0086915 | 0.0021783
45 | 0.0086915 | 0.0021783
46 | 0.008686 | 0.0021769
47 | 0.0026494 | 0.000664
48 | 0.0012227 | 0.00030643
49 | 0.0015797 | 0.00039591
50 | 0.008692 | 0.0021784
51 | 0.0086921 | 0.0021784
52 | 0.0039817 | 0.00099791
53 | 0.0019903 | 0.00049881
54 | 0.0022618 | 0.00056685
55 | 0.0039836 | 0.00099838
56 | 0.0039833 | 0.00099831
57 | 0.0018534 | 0.0004645
58 | 0.0039819 | 0.00099797
59 | 0.0018534 | 0.0004645
60 | 0.0039792 | 0.00099728
61 | 0.0038675 | 0.00096929
62 | 0.0018541 | 0.00046467
63 | 0.015338 | 0.0038442
64 | 0.0034093 | 0.00085445
65 | 0.0062844 | 0.001575
66 | 0.0062873 | 0.0015758
67 | 0.0031327 | 0.00078514
68 | 0.0062844 | 0.001575
69 | 0.0025869 | 0.00064833
70 | 0.0062859 | 0.0015754
71 | 0.0012987 | 0.00032548
72 | 0.0053009 | 0.0013285
73 | 0.00129 | 0.0003233
74 | 0.0012842 | 0.00032185
75 | 0.0012782 | 0.00032034
76 | 0.0057679 | 0.0014456
77 | 0.0053534 | 0.0013417
78 | 0.011797 | 0.0029565
79 | 0.0052996 | 0.0013282
80 | 0.0012647 | 0.00031697
81 | 0.0061826 | 0.0015495
82 | 0.0053507 | 0.001341
83 | 0.0063656 | 0.0015954
84 | 0.007621 | 0.00191
85 | 0.019256 | 0.004826

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1