## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-78_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-78_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_230-78_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_230-78_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_230-78_0_4_node_159 | 0.4 | n |  | TRUE
5 | bus_LV_230-78_0_4_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_230-78_0_4_node_273 | 0.4 | n |  | TRUE
7 | bus_LV_230-78_0_4_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_230-78_0_4_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_230-78_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_230-78_0_4_node_160 | 0.4 | n |  | TRUE
11 | bus_LV_230-78_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_230-78_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_230-78_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_230-78_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_230-78_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_230-78_0_4_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_230-78_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_230-78_0_4_node_41 | 0.4 | n |  | TRUE
19 | bus_LV_230-78_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_230-78_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_230-78_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_230-78_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_230-78_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_230-78_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_230-78_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_230-78_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_230-78_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_230-78_0_4_node_162 | 0.4 | n |  | TRUE
29 | bus_LV_230-78_0_4_node_165 | 0.4 | n |  | TRUE
30 | bus_LV_230-78_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_230-78_0_4_node_163 | 0.4 | n |  | TRUE
32 | bus_LV_230-78_0_4_node_78 | 0.4 | n |  | TRUE
33 | bus_LV_230-78_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_230-78_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_230-78_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_230-78_0_4_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_230-78_0_4_node_144 | 0.4 | n |  | TRUE
38 | bus_LV_230-78_0_4_node_192 | 0.4 | n |  | TRUE
39 | bus_LV_230-78_0_4_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_230-78_0_4_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_230-78_0_4_node_76 | 0.4 | n |  | TRUE
42 | bus_LV_230-78_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_230-78_0_4_node_74 | 0.4 | n |  | TRUE
44 | bus_LV_230-78_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_230-78_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_230-78_0_4_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_230-78_0_4_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_230-78_0_4_node_164 | 0.4 | n |  | TRUE
49 | bus_LV_230-78_0_4_node_274 | 0.4 | n |  | TRUE
50 | bus_LV_230-78_0_4_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_230-78_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_230-78_0_4_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_230-78_0_4_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_230-78_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_230-78_0_4_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_230-78_0_4_node_156 | 0.4 | n |  | TRUE
57 | bus_LV_230-78_0_4_node_155 | 0.4 | n |  | TRUE
58 | bus_LV_230-78_0_4_node_157 | 0.4 | n |  | TRUE
59 | bus_LV_230-78_0_4_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_230-78_0_4_node_154 | 0.4 | n |  | TRUE
61 | bus_LV_230-78_0_4_node_158 | 0.4 | n |  | TRUE
62 | bus_LV_230-78_0_4_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_230-78_0_4_node_276 | 0.4 | n |  | TRUE
64 | bus_LV_230-78_0_4_node_279 | 0.4 | n |  | TRUE
65 | bus_LV_230-78_0_4_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_230-78_0_4_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_230-78_0_4_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_230-78_0_4_node_140 | 0.4 | n |  | TRUE
69 | bus_LV_230-78_0_4_node_188 | 0.4 | n |  | TRUE
70 | bus_LV_230-78_0_4_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_230-78_0_4_node_143 | 0.4 | n |  | TRUE
72 | bus_LV_230-78_0_4_node_177 | 0.4 | n |  | TRUE
73 | bus_LV_230-78_0_4_node_178 | 0.4 | n |  | TRUE
74 | bus_LV_230-78_0_4_node_173 | 0.4 | n |  | TRUE
75 | bus_LV_230-78_0_4_node_141 | 0.4 | n |  | TRUE
76 | bus_LV_230-78_0_4_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_230-78_0_4_node_281 | 0.4 | n |  | TRUE
78 | bus_LV_230-78_0_4_node_282 | 0.4 | n |  | TRUE
79 | bus_LV_230-78_0_4_node_286 | 0.4 | n |  | TRUE
80 | bus_LV_230-78_0_4_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_230-78_0_4_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_230-78_0_4_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_230-78_0_4_node_55 | 0.4 | n |  | TRUE
84 | bus_LV_230-78_0_4_node_198 | 0.4 | n |  | TRUE
85 | bus_LV_230-78_0_4_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_230-78_0_4_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_230-78_0_4_node_197 | 0.4 | n |  | TRUE
88 | bus_LV_230-78_0_4_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_230-78_0_4_node_153 | 0.4 | n |  | TRUE
90 | bus_LV_230-78_0_4_node_179 | 0.4 | n |  | TRUE
91 | bus_LV_230-78_0_4_node_60 | 0.4 | n |  | TRUE
92 | bus_LV_230-78_0_4_node_62 | 0.4 | n |  | TRUE
93 | bus_LV_230-78_0_4_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_230-78_0_4_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_230-78_0_4_node_171 | 0.4 | n |  | TRUE
96 | bus_LV_230-78_0_4_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_230-78_0_4_node_172 | 0.4 | n |  | TRUE
98 | bus_LV_230-78_0_4_node_112 | 0.4 | n |  | TRUE
99 | bus_LV_230-78_0_4_node_111 | 0.4 | n |  | TRUE
100 | bus_LV_230-78_0_4_node_66 | 0.4 | n |  | TRUE
101 | bus_LV_230-78_0_4_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_230-78_0_4_node_113 | 0.4 | n |  | TRUE
103 | bus_LV_230-78_0_4_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_230-78_0_4_node_70 | 0.4 | n |  | TRUE
105 | bus_LV_230-78_0_4_node_67 | 0.4 | n |  | TRUE
106 | bus_LV_230-78_0_4_node_68 | 0.4 | n |  | TRUE
107 | bus_LV_230-78_0_4_node_69 | 0.4 | n |  | TRUE
108 | bus_LV_230-78_0_4_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_230-78_0_4_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_230-78_0_4_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_230-78_0_4_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_230-78_0_4_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_230-78_0_4_node_75 | 0.4 | n |  | TRUE
114 | bus_LV_230-78_0_4_node_77 | 0.4 | n |  | TRUE
115 | bus_LV_230-78_0_4_node_81 | 0.4 | n |  | TRUE
116 | bus_LV_230-78_0_4_node_79 | 0.4 | n |  | TRUE
117 | bus_LV_230-78_0_4_node_80 | 0.4 | n |  | TRUE
118 | bus_LV_230-78_0_4_node_82 | 0.4 | n |  | TRUE
119 | bus_LV_230-78_0_4_node_83 | 0.4 | n |  | TRUE
120 | bus_LV_230-78_0_4_node_84 | 0.4 | n |  | TRUE
121 | bus_LV_230-78_0_4_node_85 | 0.4 | n |  | TRUE
122 | bus_LV_230-78_0_4_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_230-78_0_4_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_230-78_0_4_node_94 | 0.4 | n |  | TRUE
125 | bus_LV_230-78_0_4_node_101 | 0.4 | n |  | TRUE
126 | bus_LV_230-78_0_4_node_92 | 0.4 | n |  | TRUE
127 | bus_LV_230-78_0_4_node_86 | 0.4 | n |  | TRUE
128 | bus_LV_230-78_0_4_node_87 | 0.4 | n |  | TRUE
129 | bus_LV_230-78_0_4_node_88 | 0.4 | n |  | TRUE
130 | bus_LV_230-78_0_4_node_89 | 0.4 | n |  | TRUE
131 | bus_LV_230-78_0_4_node_90 | 0.4 | n |  | TRUE
132 | bus_LV_230-78_0_4_node_114 | 0.4 | n |  | TRUE
133 | bus_LV_230-78_0_4_node_161 | 0.4 | n |  | TRUE
134 | bus_LV_230-78_0_4_node_187 | 0.4 | n |  | TRUE
135 | bus_LV_230-78_0_4_node_115 | 0.4 | n |  | TRUE
136 | bus_LV_230-78_0_4_node_109 | 0.4 | n |  | TRUE
137 | bus_LV_230-78_0_4_node_91 | 0.4 | n |  | TRUE
138 | bus_LV_230-78_0_4_node_93 | 0.4 | n |  | TRUE
139 | bus_LV_230-78_0_4_node_95 | 0.4 | n |  | TRUE
140 | bus_LV_230-78_0_4_node_96 | 0.4 | n |  | TRUE
141 | bus_LV_230-78_0_4_node_97 | 0.4 | n |  | TRUE
142 | bus_LV_230-78_0_4_node_287 | 0.4 | n |  | TRUE
143 | bus_LV_230-78_0_4_node_103 | 0.4 | n |  | TRUE
144 | bus_LV_230-78_0_4_node_99 | 0.4 | n |  | TRUE
145 | bus_LV_230-78_0_4_node_98 | 0.4 | n |  | TRUE
146 | bus_LV_230-78_0_4_node_288 | 0.4 | n |  | TRUE
147 | bus_LV_230-78_0_4_node_100 | 0.4 | n |  | TRUE
148 | bus_LV_230-78_0_4_node_107 | 0.4 | n |  | TRUE
149 | bus_LV_230-78_0_4_node_125 | 0.4 | n |  | TRUE
150 | bus_LV_230-78_0_4_node_126 | 0.4 | n |  | TRUE
151 | bus_LV_230-78_0_4_node_128 | 0.4 | n |  | TRUE
152 | bus_LV_230-78_0_4_node_124 | 0.4 | n |  | TRUE
153 | bus_LV_230-78_0_4_node_123 | 0.4 | n |  | TRUE
154 | bus_LV_230-78_0_4_node_116 | 0.4 | n |  | TRUE
155 | bus_LV_230-78_0_4_node_117 | 0.4 | n |  | TRUE
156 | bus_LV_230-78_0_4_node_118 | 0.4 | n |  | TRUE
157 | bus_LV_230-78_0_4_node_119 | 0.4 | n |  | TRUE
158 | bus_LV_230-78_0_4_node_120 | 0.4 | n |  | TRUE
159 | bus_LV_230-78_0_4_node_121 | 0.4 | n |  | TRUE
160 | bus_LV_230-78_0_4_node_130 | 0.4 | n |  | TRUE
161 | bus_LV_230-78_0_4_node_134 | 0.4 | n |  | TRUE
162 | bus_LV_230-78_0_4_node_135 | 0.4 | n |  | TRUE
163 | bus_LV_230-78_0_4_node_132 | 0.4 | n |  | TRUE
164 | bus_LV_230-78_0_4_node_122 | 0.4 | n |  | TRUE
165 | bus_LV_230-78_0_4_node_129 | 0.4 | n |  | TRUE
166 | bus_LV_230-78_0_4_node_194 | 0.4 | n |  | TRUE
167 | bus_LV_230-78_0_4_node_136 | 0.4 | n |  | TRUE
168 | bus_LV_230-78_0_4_node_133 | 0.4 | n |  | TRUE
169 | bus_LV_230-78_0_4_node_127 | 0.4 | n |  | TRUE
170 | bus_LV_230-78_0_4_node_131 | 0.4 | n |  | TRUE
171 | bus_LV_230-78_0_4_node_249 | 0.4 | n |  | TRUE
172 | bus_LV_230-78_0_4_node_247 | 0.4 | n |  | TRUE
173 | bus_LV_230-78_0_4_node_137 | 0.4 | n |  | TRUE
174 | bus_LV_230-78_0_4_node_138 | 0.4 | n |  | TRUE
175 | bus_LV_230-78_0_4_node_139 | 0.4 | n |  | TRUE
176 | bus_LV_230-78_0_4_node_195 | 0.4 | n |  | TRUE
177 | bus_LV_230-78_0_4_node_199 | 0.4 | n |  | TRUE
178 | bus_LV_230-78_0_4_node_191 | 0.4 | n |  | TRUE
179 | bus_LV_230-78_0_4_node_193 | 0.4 | n |  | TRUE
180 | bus_LV_230-78_0_4_node_190 | 0.4 | n |  | TRUE
181 | bus_LV_230-78_0_4_node_142 | 0.4 | n |  | TRUE
182 | bus_LV_230-78_0_4_node_148 | 0.4 | n |  | TRUE
183 | bus_LV_230-78_0_4_node_277 | 0.4 | n |  | TRUE
184 | bus_LV_230-78_0_4_node_146 | 0.4 | n |  | TRUE
185 | bus_LV_230-78_0_4_node_278 | 0.4 | n |  | TRUE
186 | bus_LV_230-78_0_4_node_174 | 0.4 | n |  | TRUE
187 | bus_LV_230-78_0_4_node_186 | 0.4 | n |  | TRUE
188 | bus_LV_230-78_0_4_node_145 | 0.4 | n |  | TRUE
189 | bus_LV_230-78_0_4_node_149 | 0.4 | n |  | TRUE
190 | bus_LV_230-78_0_4_node_204 | 0.4 | n |  | TRUE
191 | bus_LV_230-78_0_4_node_229 | 0.4 | n |  | TRUE
192 | bus_LV_230-78_0_4_node_272 | 0.4 | n |  | TRUE
193 | bus_LV_230-78_0_4_node_270 | 0.4 | n |  | TRUE
194 | bus_LV_230-78_0_4_node_285 | 0.4 | n |  | TRUE
195 | bus_LV_230-78_0_4_node_284 | 0.4 | n |  | TRUE
196 | bus_LV_230-78_0_4_node_203 | 0.4 | n |  | TRUE
197 | bus_LV_230-78_0_4_node_183 | 0.4 | n |  | TRUE
198 | bus_LV_230-78_0_4_node_185 | 0.4 | n |  | TRUE
199 | bus_LV_230-78_0_4_node_181 | 0.4 | n |  | TRUE
200 | bus_LV_230-78_0_4_node_289 | 0.4 | n |  | TRUE
201 | bus_LV_230-78_0_4_node_275 | 0.4 | n |  | TRUE
202 | bus_LV_230-78_0_4_node_166 | 0.4 | n |  | TRUE
203 | bus_LV_230-78_0_4_node_167 | 0.4 | n |  | TRUE
204 | bus_LV_230-78_0_4_node_168 | 0.4 | n |  | TRUE
205 | bus_LV_230-78_0_4_node_169 | 0.4 | n |  | TRUE
206 | bus_LV_230-78_0_4_node_170 | 0.4 | n |  | TRUE
207 | bus_LV_230-78_0_4_node_218 | 0.4 | n |  | TRUE
208 | bus_LV_230-78_0_4_node_219 | 0.4 | n |  | TRUE
209 | bus_LV_230-78_0_4_node_255 | 0.4 | n |  | TRUE
210 | bus_LV_230-78_0_4_node_240 | 0.4 | n |  | TRUE
211 | bus_LV_230-78_0_4_node_246 | 0.4 | n |  | TRUE
212 | bus_LV_230-78_0_4_node_239 | 0.4 | n |  | TRUE
213 | bus_LV_230-78_0_4_node_228 | 0.4 | n |  | TRUE
214 | bus_LV_230-78_0_4_node_176 | 0.4 | n |  | TRUE
215 | bus_LV_230-78_0_4_node_175 | 0.4 | n |  | TRUE
216 | bus_LV_230-78_0_4_node_254 | 0.4 | n |  | TRUE
217 | bus_LV_230-78_0_4_node_262 | 0.4 | n |  | TRUE
218 | bus_LV_230-78_0_4_node_200 | 0.4 | n |  | TRUE
219 | bus_LV_230-78_0_4_node_253 | 0.4 | n |  | TRUE
220 | bus_LV_230-78_0_4_node_223 | 0.4 | n |  | TRUE
221 | bus_LV_230-78_0_4_node_201 | 0.4 | n |  | TRUE
222 | bus_LV_230-78_0_4_node_196 | 0.4 | n |  | TRUE
223 | bus_LV_230-78_0_4_node_182 | 0.4 | n |  | TRUE
224 | bus_LV_230-78_0_4_node_184 | 0.4 | n |  | TRUE
225 | bus_LV_230-78_0_4_node_205 | 0.4 | n |  | TRUE
226 | bus_LV_230-78_0_4_node_206 | 0.4 | n |  | TRUE
227 | bus_LV_230-78_0_4_node_207 | 0.4 | n |  | TRUE
228 | bus_LV_230-78_0_4_node_189 | 0.4 | n |  | TRUE
229 | bus_LV_230-78_0_4_node_242 | 0.4 | n |  | TRUE
230 | bus_LV_230-78_0_4_node_251 | 0.4 | n |  | TRUE
231 | bus_LV_230-78_0_4_node_202 | 0.4 | n |  | TRUE
232 | bus_LV_230-78_0_4_node_256 | 0.4 | n |  | TRUE
233 | bus_LV_230-78_0_4_node_237 | 0.4 | n |  | TRUE
234 | bus_LV_230-78_0_4_node_232 | 0.4 | n |  | TRUE
235 | bus_LV_230-78_0_4_node_259 | 0.4 | n |  | TRUE
236 | bus_LV_230-78_0_4_node_230 | 0.4 | n |  | TRUE
237 | bus_LV_230-78_0_4_node_241 | 0.4 | n |  | TRUE
238 | bus_LV_230-78_0_4_node_227 | 0.4 | n |  | TRUE
239 | bus_LV_230-78_0_4_node_250 | 0.4 | n |  | TRUE
240 | bus_LV_230-78_0_4_node_208 | 0.4 | n |  | TRUE
241 | bus_LV_230-78_0_4_node_209 | 0.4 | n |  | TRUE
242 | bus_LV_230-78_0_4_node_210 | 0.4 | n |  | TRUE
243 | bus_LV_230-78_0_4_node_211 | 0.4 | n |  | TRUE
244 | bus_LV_230-78_0_4_node_212 | 0.4 | n |  | TRUE
245 | bus_LV_230-78_0_4_node_217 | 0.4 | n |  | TRUE
246 | bus_LV_230-78_0_4_node_220 | 0.4 | n |  | TRUE
247 | bus_LV_230-78_0_4_node_263 | 0.4 | n |  | TRUE
248 | bus_LV_230-78_0_4_node_215 | 0.4 | n |  | TRUE
249 | bus_LV_230-78_0_4_node_221 | 0.4 | n |  | TRUE
250 | bus_LV_230-78_0_4_node_213 | 0.4 | n |  | TRUE
251 | bus_LV_230-78_0_4_node_214 | 0.4 | n |  | TRUE
252 | bus_LV_230-78_0_4_node_216 | 0.4 | n |  | TRUE
253 | bus_LV_230-78_0_4_node_260 | 0.4 | n |  | TRUE
254 | bus_LV_230-78_0_4_node_245 | 0.4 | n |  | TRUE
255 | bus_LV_230-78_0_4_node_222 | 0.4 | n |  | TRUE
256 | bus_LV_230-78_0_4_node_264 | 0.4 | n |  | TRUE
257 | bus_LV_230-78_0_4_node_224 | 0.4 | n |  | TRUE
258 | bus_LV_230-78_0_4_node_225 | 0.4 | n |  | TRUE
259 | bus_LV_230-78_0_4_node_226 | 0.4 | n |  | TRUE
260 | bus_LV_230-78_0_4_node_231 | 0.4 | n |  | TRUE
261 | bus_LV_230-78_0_4_node_244 | 0.4 | n |  | TRUE
262 | bus_LV_230-78_0_4_node_243 | 0.4 | n |  | TRUE
263 | bus_LV_230-78_0_4_node_261 | 0.4 | n |  | TRUE
264 | bus_LV_230-78_0_4_node_257 | 0.4 | n |  | TRUE
265 | bus_LV_230-78_0_4_node_233 | 0.4 | n |  | TRUE
266 | bus_LV_230-78_0_4_node_234 | 0.4 | n |  | TRUE
267 | bus_LV_230-78_0_4_node_235 | 0.4 | n |  | TRUE
268 | bus_LV_230-78_0_4_node_236 | 0.4 | n |  | TRUE
269 | bus_LV_230-78_0_4_node_238 | 0.4 | n |  | TRUE
270 | bus_LV_230-78_0_4_node_248 | 0.4 | n |  | TRUE
271 | bus_LV_230-78_0_4_node_252 | 0.4 | n |  | TRUE
272 | bus_LV_230-78_0_4_node_258 | 0.4 | n |  | TRUE
273 | bus_LV_230-78_0_4_node_265 | 0.4 | n |  | TRUE
274 | bus_LV_230-78_0_4_node_266 | 0.4 | n |  | TRUE
275 | bus_LV_230-78_0_4_node_267 | 0.4 | n |  | TRUE
276 | bus_LV_230-78_0_4_node_268 | 0.4 | n |  | TRUE
277 | bus_LV_230-78_0_4_node_269 | 0.4 | n |  | TRUE
278 | bus_LV_230-78_0_4_node_271 | 0.4 | n |  | TRUE
279 | bus_LV_230-78_0_4_node_280 | 0.4 | n |  | TRUE
280 | bus_LV_230-78_0_4_node_283 | 0.4 | n |  | TRUE
281 | bus_MV_369_1_node_140 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-78_0_4_load_0 | 0 | 0.0040201 | 0.0010075 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-78_0_4_load_4 | 2 | 0.0011489 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-78_0_4_load_5 | 3 | 0.0011489 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-78_0_4_load_159 | 4 | 0.0011489 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-78_0_4_load_273 | 6 | 0.0015604 | 0.00039108 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-78_0_4_load_32 | 7 | 0.0029421 | 0.00073735 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-78_0_4_load_33 | 8 | 0.0015377 | 0.00038538 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-78_0_4_load_30 | 9 | 0.0015116 | 0.00037884 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-78_0_4_load_160 | 10 | 0.0011489 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-78_0_4_load_6 | 11 | 0.002293 | 0.00057468 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-78_0_4_load_9 | 13 | 0.0020148 | 0.00050497 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-78_0_4_load_10 | 14 | 0.0014112 | 0.00035368 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-78_0_4_load_11 | 15 | 0.0015429 | 0.00038668 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-78_0_4_load_40 | 16 | 0.0030082 | 0.00075392 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-78_0_4_load_12 | 17 | 0.002774 | 0.00069523 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-78_0_4_load_41 | 18 | 0.0013773 | 0.00034518 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-78_0_4_load_21 | 19 | 0.0016065 | 0.00040263 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-78_0_4_load_20 | 20 | 0.0054635 | 0.0013693 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-78_0_4_load_13 | 21 | 0.0053988 | 0.0013531 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-78_0_4_load_14 | 22 | 0.0056287 | 0.0014107 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-78_0_4_load_17 | 24 | 0.0013557 | 0.00033977 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-78_0_4_load_18 | 25 | 0.0013565 | 0.00033997 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-78_0_4_load_16 | 26 | 0.0041798 | 0.0010475 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-78_0_4_load_19 | 27 | 0.0041995 | 0.0010525 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-78_0_4_load_165 | 29 | 0.0011489 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-78_0_4_load_163 | 31 | 0.0012337 | 0.00030919 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-78_0_4_load_78 | 32 | 0.0018358 | 0.00046009 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-78_0_4_load_25 | 33 | 0.0020848 | 0.0005225 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-78_0_4_load_22 | 34 | 0.0019293 | 0.00048352 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-78_0_4_load_192 | 38 | 0.0023374 | 0.0005858 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-78_0_4_load_43 | 39 | 0.0032655 | 0.0008184 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-78_0_4_load_26 | 42 | 0.0018687 | 0.00046833 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-78_0_4_load_74 | 43 | 0.0018887 | 0.00047334 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-78_0_4_load_27 | 44 | 0.001317 | 0.00033008 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-78_0_4_load_28 | 45 | 0.0012744 | 0.00031939 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-78_0_4_load_164 | 48 | 0.0033598 | 0.00084205 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-78_0_4_load_274 | 49 | 0.0034478 | 0.0008641 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-78_0_4_load_34 | 50 | 0.0011598 | 0.00029067 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-78_0_4_load_35 | 51 | 0.0014392 | 0.00036071 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-78_0_4_load_37 | 53 | 0.0023589 | 0.00059119 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-78_0_4_load_39 | 55 | 0.0012985 | 0.00032544 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-78_0_4_load_156 | 56 | 0.0013538 | 0.00033931 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-78_0_4_load_155 | 57 | 0.00098223 | 0.00024617 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-78_0_4_load_157 | 58 | 0.001885 | 0.00047243 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-78_0_4_load_154 | 60 | 0.0015627 | 0.00039165 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-78_0_4_load_42 | 62 | 0.00095466 | 0.00023926 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-78_0_4_load_276 | 63 | 0.00094883 | 0.0002378 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-78_0_4_load_279 | 64 | 0.00090721 | 0.00022737 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-78_0_4_load_46 | 65 | 0.0013554 | 0.00033969 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-78_0_4_load_48 | 67 | 0.0012404 | 0.00031086 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-78_0_4_load_140 | 68 | 0.003375 | 0.00084586 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-78_0_4_load_188 | 69 | 0.0053052 | 0.0013296 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-78_0_4_load_49 | 70 | 0.0012997 | 0.00032574 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-78_0_4_load_177 | 72 | 0.0024912 | 0.00062435 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-78_0_4_load_173 | 74 | 0.0035575 | 0.00089159 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-78_0_4_load_141 | 75 | 0.0010943 | 0.00027426 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-78_0_4_load_50 | 76 | 0.00096286 | 0.00024131 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-78_0_4_load_281 | 77 | 0.0015561 | 0.00038998 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-78_0_4_load_282 | 78 | 0.00096285 | 0.00024131 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-78_0_4_load_286 | 79 | 0.0015597 | 0.0003909 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-78_0_4_load_52 | 80 | 0.00046056 | 0.00011543 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-78_0_4_load_53 | 81 | 0.00079201 | 0.0001985 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-78_0_4_load_54 | 82 | 0.0021222 | 0.00053187 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-78_0_4_load_56 | 85 | 0.00089422 | 0.00022411 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-78_0_4_load_57 | 86 | 0.00035314 | 8.8505e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-78_0_4_load_59 | 88 | 0.0021748 | 0.00054507 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-78_0_4_load_153 | 89 | 0.0015627 | 0.00039165 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-78_0_4_load_179 | 90 | 0.00053424 | 0.00013389 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-78_0_4_load_60 | 91 | 0.0033326 | 0.00083522 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-78_0_4_load_62 | 92 | 0.0021686 | 0.0005435 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-78_0_4_load_63 | 94 | 0.0017834 | 0.00044696 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-78_0_4_load_171 | 95 | 0.0026651 | 0.00066793 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-78_0_4_load_172 | 97 | 0.0029166 | 0.00073098 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-78_0_4_load_112 | 98 | 0.0083149 | 0.0020839 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-78_0_4_load_111 | 99 | 0.0014219 | 0.00035635 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-78_0_4_load_113 | 102 | 0.01083 | 0.0027143 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-78_0_4_load_73 | 103 | 0.0018089 | 0.00045335 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-78_0_4_load_70 | 104 | 0.0040067 | 0.0010042 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-78_0_4_load_67 | 105 | 0.0029458 | 0.00073828 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-78_0_4_load_68 | 106 | 0.0035752 | 0.00089603 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-78_0_4_load_105 | 109 | 0.0087427 | 0.0021911 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-78_0_4_load_104 | 111 | 0.005337 | 0.0013376 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-78_0_4_load_102 | 112 | 0.0024773 | 0.00062087 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-78_0_4_load_75 | 113 | 0.0020295 | 0.00050865 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-78_0_4_load_77 | 114 | 0.0015856 | 0.0003974 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-78_0_4_load_81 | 115 | 0.0018229 | 0.00045686 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-78_0_4_load_79 | 116 | 0.0015856 | 0.0003974 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-78_0_4_load_80 | 117 | 0.0018209 | 0.00045636 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-78_0_4_load_82 | 118 | 0.0016745 | 0.00041967 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-78_0_4_load_83 | 119 | 0.0027421 | 0.00068724 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_230-78_0_4_load_84 | 120 | 0.0043536 | 0.0010911 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_230-78_0_4_load_85 | 121 | 0.0044027 | 0.0011034 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_230-78_0_4_load_110 | 122 | 0.0045183 | 0.0011324 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_230-78_0_4_load_92 | 126 | 0.0055434 | 0.0013893 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_230-78_0_4_load_86 | 127 | 0.0078288 | 0.0019621 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_230-78_0_4_load_87 | 128 | 0.0039689 | 0.0009947 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_230-78_0_4_load_88 | 129 | 0.011915 | 0.0029861 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_230-78_0_4_load_90 | 131 | 0.0050841 | 0.0012742 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_230-78_0_4_load_161 | 133 | 0.0050792 | 0.001273 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_230-78_0_4_load_187 | 134 | 0.0081386 | 0.0020397 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_230-78_0_4_load_109 | 136 | 0.0044398 | 0.0011127 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_230-78_0_4_load_91 | 137 | 0.0024318 | 0.00060947 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_230-78_0_4_load_95 | 139 | 0.0052985 | 0.0013279 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_230-78_0_4_load_96 | 140 | 0.0034222 | 0.00085768 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_230-78_0_4_load_97 | 141 | 0.0015831 | 0.00039677 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_230-78_0_4_load_287 | 142 | 0.0027129 | 0.00067991 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_230-78_0_4_load_103 | 143 | 0.0040966 | 0.0010267 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_230-78_0_4_load_99 | 144 | 0.0034956 | 0.00087608 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_230-78_0_4_load_98 | 145 | 0.0024051 | 0.00060277 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_230-78_0_4_load_100 | 147 | 0.0052775 | 0.0013227 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_230-78_0_4_load_107 | 148 | 0.016845 | 0.0042218 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_230-78_0_4_load_125 | 149 | 0.0024723 | 0.00061961 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_230-78_0_4_load_126 | 150 | 0.0049179 | 0.0012325 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_230-78_0_4_load_128 | 151 | 0.0034458 | 0.0008636 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_230-78_0_4_load_124 | 152 | 0.0012272 | 0.00030756 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_230-78_0_4_load_123 | 153 | 0.0012578 | 0.00031523 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_230-78_0_4_load_116 | 154 | 0.0020961 | 0.00052532 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_230-78_0_4_load_117 | 155 | 0.0018537 | 0.00046458 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_230-78_0_4_load_119 | 157 | 0.0009864 | 0.00024721 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_230-78_0_4_load_121 | 159 | 0.0010317 | 0.00025856 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_230-78_0_4_load_130 | 160 | 0.00098508 | 0.00024689 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_230-78_0_4_load_135 | 162 | 0.0019637 | 0.00049216 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_230-78_0_4_load_132 | 163 | 0.0024136 | 0.0006049 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_230-78_0_4_load_122 | 164 | 0.0014376 | 0.00036029 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_230-78_0_4_load_194 | 166 | 0.0016963 | 0.00042513 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_230-78_0_4_load_136 | 167 | 0.0018505 | 0.00046377 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_230-78_0_4_load_133 | 168 | 0.0013699 | 0.00034333 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_230-78_0_4_load_127 | 169 | 0.0021438 | 0.00053729 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_230-78_0_4_load_131 | 170 | 0.002326 | 0.00058296 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_230-78_0_4_load_249 | 171 | 0.0018529 | 0.00046437 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_230-78_0_4_load_137 | 173 | 0.003303 | 0.00082782 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_230-78_0_4_load_138 | 174 | 0.0022471 | 0.00056317 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_230-78_0_4_load_195 | 176 | 0.0015863 | 0.00039757 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_230-78_0_4_load_190 | 180 | 0.0013763 | 0.00034494 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_230-78_0_4_load_277 | 183 | 0.0010312 | 0.00025845 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_230-78_0_4_load_146 | 184 | 0.0010312 | 0.00025845 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_230-78_0_4_load_278 | 185 | 0.0010312 | 0.00025845 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_230-78_0_4_load_186 | 187 | 0.0053046 | 0.0013295 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_230-78_0_4_load_145 | 188 | 0.0031628 | 0.00079268 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_230-78_0_4_load_149 | 189 | 0.0019435 | 0.00048709 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_230-78_0_4_load_229 | 191 | 0.0011747 | 0.00029441 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_230-78_0_4_load_272 | 192 | 0.001521 | 0.00038121 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_230-78_0_4_load_270 | 193 | 0.0010091 | 0.00025291 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_230-78_0_4_load_285 | 194 | 0.00096142 | 0.00024096 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_230-78_0_4_load_284 | 195 | 0.00096214 | 0.00024113 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_230-78_0_4_load_203 | 196 | 0.0013102 | 0.00032836 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_230-78_0_4_load_185 | 198 | 0.0011065 | 0.00027732 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_230-78_0_4_load_181 | 199 | 0.0011837 | 0.00029666 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_230-78_0_4_load_289 | 200 | 0.005578 | 0.001398 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_230-78_0_4_load_275 | 201 | 0.0052684 | 0.0013204 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_230-78_0_4_load_166 | 202 | 0.0014013 | 0.00035121 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_230-78_0_4_load_167 | 203 | 0.0013699 | 0.00034333 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_230-78_0_4_load_168 | 204 | 0.0013887 | 0.00034805 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_230-78_0_4_load_170 | 206 | 0.0014221 | 0.00035642 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_230-78_0_4_load_218 | 207 | 0.0012542 | 0.00031432 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_230-78_0_4_load_219 | 208 | 0.0013677 | 0.00034278 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_230-78_0_4_load_240 | 210 | 0.0012939 | 0.00032428 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_230-78_0_4_load_246 | 211 | 0.0012545 | 0.00031441 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_230-78_0_4_load_239 | 212 | 0.0011976 | 0.00030014 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_230-78_0_4_load_228 | 213 | 0.0014199 | 0.00035586 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_230-78_0_4_load_176 | 214 | 0.0017595 | 0.00044096 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_230-78_0_4_load_254 | 216 | 0.0016972 | 0.00042535 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_230-78_0_4_load_262 | 217 | 0.0011859 | 0.00029721 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_230-78_0_4_load_200 | 218 | 0.0014293 | 0.00035822 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_230-78_0_4_load_253 | 219 | 0.0015767 | 0.00039515 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_230-78_0_4_load_223 | 220 | 0.0011877 | 0.00029767 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_230-78_0_4_load_201 | 221 | 0.0010952 | 0.00027449 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_230-78_0_4_load_196 | 222 | 0.00088267 | 0.00022122 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_230-78_0_4_load_182 | 223 | 0.0011847 | 0.0002969 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_230-78_0_4_load_205 | 225 | 0.0044024 | 0.0011033 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_230-78_0_4_load_206 | 226 | 0.001186 | 0.00029724 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_230-78_0_4_load_207 | 227 | 0.0011747 | 0.00029441 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_230-78_0_4_load_189 | 228 | 0.0010776 | 0.00027008 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_230-78_0_4_load_242 | 229 | 0.0011742 | 0.00029428 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_230-78_0_4_load_202 | 231 | 0.0010952 | 0.00027449 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_230-78_0_4_load_256 | 232 | 0.0013709 | 0.00034358 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_230-78_0_4_load_237 | 233 | 0.0013523 | 0.00033892 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_230-78_0_4_load_232 | 234 | 0.0019435 | 0.00048709 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_230-78_0_4_load_230 | 236 | 0.0011854 | 0.0002971 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_230-78_0_4_load_241 | 237 | 0.0011847 | 0.0002969 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_230-78_0_4_load_227 | 238 | 0.0012813 | 0.00032113 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_230-78_0_4_load_250 | 239 | 0.0010929 | 0.00027391 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_230-78_0_4_load_208 | 240 | 0.0011849 | 0.00029695 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_230-78_0_4_load_209 | 241 | 0.001237 | 0.00031001 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_230-78_0_4_load_210 | 242 | 0.0011852 | 0.00029705 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_230-78_0_4_load_211 | 243 | 0.0011867 | 0.00029742 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_230-78_0_4_load_220 | 246 | 0.0012945 | 0.00032442 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_230-78_0_4_load_263 | 247 | 0.001942 | 0.00048672 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_230-78_0_4_load_215 | 248 | 0.001236 | 0.00030978 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_230-78_0_4_load_221 | 249 | 0.0012948 | 0.00032451 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_230-78_0_4_load_213 | 250 | 0.0012347 | 0.00030945 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_230-78_0_4_load_214 | 251 | 0.0012359 | 0.00030974 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_230-78_0_4_load_216 | 252 | 0.0011977 | 0.00030018 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_230-78_0_4_load_260 | 253 | 0.001942 | 0.00048672 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_230-78_0_4_load_245 | 254 | 0.0013699 | 0.00034333 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_230-78_0_4_load_222 | 255 | 0.0012945 | 0.00032442 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_230-78_0_4_load_264 | 256 | 0.0012952 | 0.00032462 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_230-78_0_4_load_224 | 257 | 0.0012793 | 0.00032063 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_230-78_0_4_load_225 | 258 | 0.0010941 | 0.00027421 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_230-78_0_4_load_226 | 259 | 0.0014221 | 0.00035641 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_230-78_0_4_load_231 | 260 | 0.0011755 | 0.0002946 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_230-78_0_4_load_244 | 261 | 0.0011853 | 0.00029708 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_230-78_0_4_load_243 | 262 | 0.0011747 | 0.00029441 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_230-78_0_4_load_261 | 263 | 0.0019085 | 0.00047832 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_230-78_0_4_load_257 | 264 | 0.0019406 | 0.00048637 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_230-78_0_4_load_233 | 265 | 0.0013575 | 0.00034023 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_230-78_0_4_load_234 | 266 | 0.001352 | 0.00033885 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_230-78_0_4_load_236 | 268 | 0.0027603 | 0.00069179 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_230-78_0_4_load_238 | 269 | 0.0010932 | 0.00027397 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_230-78_0_4_load_248 | 270 | 0.0027769 | 0.00069595 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_230-78_0_4_load_252 | 271 | 0.0010949 | 0.00027441 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_230-78_0_4_load_258 | 272 | 0.0019402 | 0.00048626 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_230-78_0_4_load_265 | 273 | 0.0019074 | 0.00047803 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_230-78_0_4_load_266 | 274 | 0.0010947 | 0.00027436 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_230-78_0_4_load_267 | 275 | 0.000907 | 0.00022731 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_230-78_0_4_load_268 | 276 | 0.0012359 | 0.00030974 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_230-78_0_4_load_269 | 277 | 0.001477 | 0.00037016 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_230-78_0_4_load_271 | 278 | 0.00096195 | 0.00024109 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_230-78_0_4_load_280 | 279 | 0.00098529 | 0.00024694 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_230-78_0_4_load_283 | 280 | 0.00096143 | 0.00024096 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-78_0_4_line_0 |  | 0 | 1 | 0.007012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-78_0_4_line_1 |  | 1 | 2 | 0.01357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-78_0_4_line_2 |  | 1 | 3 | 0.011274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-78_0_4_line_3 |  | 2 | 4 | 0.0076513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-78_0_4_line_4 |  | 4 | 10 | 0.0076541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-78_0_4_line_5 |  | 5 | 6 | 0.018578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-78_0_4_line_6 |  | 5 | 7 | 0.01392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-78_0_4_line_7 |  | 6 | 79 | 0.0081933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-78_0_4_line_8 |  | 7 | 46 | 0.010501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-78_0_4_line_9 |  | 8 | 9 | 0.0092179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_230-78_0_4_line_10 |  | 9 | 45 | 0.026189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_230-78_0_4_line_11 |  | 10 | 29 | 0.0076513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_230-78_0_4_line_12 |  | 11 | 12 | 0.019725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_230-78_0_4_line_13 |  | 12 | 13 | 0.00063584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-78_0_4_line_14 |  | 12 | 14 | 0.016329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-78_0_4_line_15 |  | 13 | 15 | 0.017098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-78_0_4_line_16 |  | 14 | 16 | 0.0055402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-78_0_4_line_17 |  | 15 | 17 | 0.0014852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-78_0_4_line_18 |  | 16 | 18 | 0.011265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-78_0_4_line_19 |  | 17 | 19 | 0.018009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-78_0_4_line_20 |  | 18 | 62 | 0.0094126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-78_0_4_line_21 |  | 19 | 20 | 1.8741e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-78_0_4_line_22 |  | 20 | 34 | 0.017082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-78_0_4_line_23 |  | 21 | 22 | 0.0025893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-78_0_4_line_24 |  | 21 | 23 | 0.017486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-78_0_4_line_25 |  | 23 | 24 | 0.0072545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-78_0_4_line_26 |  | 23 | 25 | 0.00039163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-78_0_4_line_27 |  | 24 | 28 | 0.018271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-78_0_4_line_28 |  | 25 | 29 | 0.0076541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-78_0_4_line_29 |  | 26 | 27 | 0.0025763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-78_0_4_line_30 |  | 27 | 30 | 0.014664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-78_0_4_line_31 |  | 28 | 31 | 0.010945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-78_0_4_line_32 |  | 28 | 32 | 0.0033741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-78_0_4_line_33 |  | 30 | 33 | 0.011101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-78_0_4_line_34 |  | 31 | 47 | 0.012285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-78_0_4_line_35 |  | 32 | 41 | 0.010332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-78_0_4_line_36 |  | 33 | 41 | 0.017252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-78_0_4_line_37 |  | 34 | 35 | 0.014814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-78_0_4_line_38 |  | 35 | 36 | 0.014256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-78_0_4_line_39 |  | 36 | 37 | 0.016904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-78_0_4_line_40 |  | 36 | 38 | 0.0070072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-78_0_4_line_41 |  | 37 | 69 | 0.013977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-78_0_4_line_42 |  | 37 | 66 | 0.010181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-78_0_4_line_43 |  | 38 | 42 | 0.0031891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-78_0_4_line_44 |  | 39 | 40 | 0.016693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-78_0_4_line_45 |  | 40 | 65 | 0.020567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_230-78_0_4_line_46 |  | 40 | 66 | 0.003474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-78_0_4_line_47 |  | 41 | 43 | 0.019406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_230-78_0_4_line_48 |  | 43 | 113 | 0.0060442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_230-78_0_4_line_49 |  | 44 | 45 | 0.0082736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_230-78_0_4_line_50 |  | 44 | 46 | 0.015719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-78_0_4_line_51 |  | 46 | 47 | 0.022648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_230-78_0_4_line_52 |  | 47 | 48 | 0.013081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_230-78_0_4_line_53 |  | 48 | 49 | 0.015516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-78_0_4_line_54 |  | 49 | 201 | 0.007796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_230-78_0_4_line_55 |  | 50 | 51 | 0.0087213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_230-78_0_4_line_56 |  | 50 | 52 | 0.018092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-78_0_4_line_57 |  | 51 | 53 | 0.0027209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-78_0_4_line_58 |  | 52 | 54 | 0.009934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-78_0_4_line_59 |  | 52 | 55 | 0.020227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-78_0_4_line_60 |  | 54 | 56 | 0.03427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-78_0_4_line_61 |  | 54 | 57 | 0.032217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-78_0_4_line_62 |  | 55 | 58 | 0.026542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_230-78_0_4_line_63 |  | 56 | 59 | 0.037709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-78_0_4_line_64 |  | 57 | 60 | 0.019246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-78_0_4_line_65 |  | 58 | 61 | 0.020894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-78_0_4_line_66 |  | 59 | 90 | 0.026108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-78_0_4_line_67 |  | 60 | 89 | 0.019608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-78_0_4_line_68 |  | 61 | 177 | 0.035274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_230-78_0_4_line_69 |  | 61 | 166 | 0.024888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_230-78_0_4_line_70 |  | 62 | 63 | 0.0049587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-78_0_4_line_71 |  | 63 | 64 | 0.0077648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-78_0_4_line_72 |  | 64 | 279 | 0.0032301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-78_0_4_line_73 |  | 65 | 67 | 0.020697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-78_0_4_line_74 |  | 66 | 68 | 0.018992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-78_0_4_line_75 |  | 67 | 70 | 0.0038767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-78_0_4_line_76 |  | 68 | 75 | 0.015529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-78_0_4_line_77 |  | 69 | 187 | 0.010559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-78_0_4_line_78 |  | 70 | 76 | 0.022251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-78_0_4_line_79 |  | 71 | 72 | 0.015044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-78_0_4_line_80 |  | 71 | 73 | 0.007393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-78_0_4_line_81 |  | 71 | 74 | 0.010357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-78_0_4_line_82 |  | 72 | 149 | 0.0065087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_230-78_0_4_line_83 |  | 73 | 134 | 0.010861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-78_0_4_line_84 |  | 74 | 186 | 0.014318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-78_0_4_line_85 |  | 76 | 77 | 0.006709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-78_0_4_line_86 |  | 77 | 78 | 0.0083072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_230-78_0_4_line_87 |  | 78 | 280 | 0.0062287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-78_0_4_line_88 |  | 79 | 145 | 0.0015835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-78_0_4_line_89 |  | 80 | 81 | 0.021518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-78_0_4_line_90 |  | 80 | 82 | 0.0097932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-78_0_4_line_91 |  | 81 | 83 | 0.080597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-78_0_4_line_92 |  | 81 | 84 | 0.11713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-78_0_4_line_93 |  | 83 | 85 | 0.02263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-78_0_4_line_94 |  | 83 | 86 | 0.0058641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-78_0_4_line_95 |  | 84 | 87 | 0.074324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-78_0_4_line_96 |  | 85 | 88 | 0.02195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_230-78_0_4_line_97 |  | 86 | 89 | 0.019247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_230-78_0_4_line_98 |  | 87 | 222 | 0.083163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-78_0_4_line_99 |  | 88 | 91 | 0.0032634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-78_0_4_line_100 |  | 92 | 93 | 0.0074398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_230-78_0_4_line_101 |  | 93 | 96 | 0.018244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_230-78_0_4_line_102 |  | 94 | 95 | 0.018729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-78_0_4_line_103 |  | 95 | 97 | 0.016543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-78_0_4_line_104 |  | 96 | 98 | 0.025524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-78_0_4_line_105 |  | 96 | 99 | 0.0085015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-78_0_4_line_106 |  | 97 | 161 | 0.0033307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_230-78_0_4_line_107 |  | 98 | 102 | 0.017344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-78_0_4_line_108 |  | 99 | 100 | 0.013584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-78_0_4_line_109 |  | 100 | 101 | 0.024746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-78_0_4_line_110 |  | 101 | 103 | 0.013494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-78_0_4_line_111 |  | 101 | 104 | 0.0077555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_230-78_0_4_line_112 |  | 102 | 132 | 0.020624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_230-78_0_4_line_113 |  | 103 | 111 | 0.014838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-78_0_4_line_114 |  | 105 | 106 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-78_0_4_line_115 |  | 105 | 107 | 0.03113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-78_0_4_line_116 |  | 107 | 108 | 0.028444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-78_0_4_line_117 |  | 108 | 109 | 0.02518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-78_0_4_line_118 |  | 109 | 110 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_230-78_0_4_line_119 |  | 110 | 148 | 0.024853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_230-78_0_4_line_120 |  | 111 | 112 | 0.012743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-78_0_4_line_121 |  | 112 | 147 | 0.0098199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-78_0_4_line_122 |  | 113 | 114 | 0.0093927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-78_0_4_line_123 |  | 114 | 115 | 0.0093805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-78_0_4_line_124 |  | 115 | 116 | 2.1434e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-78_0_4_line_125 |  | 116 | 117 | 0.0089486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_230-78_0_4_line_126 |  | 117 | 118 | 0.0074217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_230-78_0_4_line_127 |  | 118 | 119 | 0.0082713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_230-78_0_4_line_128 |  | 119 | 120 | 0.0043261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_230-78_0_4_line_129 |  | 120 | 121 | 0.0094765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_230-78_0_4_line_130 |  | 121 | 122 | 0.016258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
131 | LV_230-78_0_4_line_131 |  | 122 | 123 | 0.021835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_230-78_0_4_line_132 |  | 123 | 136 | 0.018057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
133 | LV_230-78_0_4_line_133 |  | 123 | 143 | 0.0083431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_230-78_0_4_line_134 |  | 124 | 125 | 0.009847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-78_0_4_line_135 |  | 124 | 126 | 0.0030566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-78_0_4_line_136 |  | 125 | 143 | 0.017677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_230-78_0_4_line_137 |  | 125 | 144 | 0.0084021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_230-78_0_4_line_138 |  | 127 | 128 | 0.0028063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_230-78_0_4_line_139 |  | 127 | 129 | 0.022604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_230-78_0_4_line_140 |  | 128 | 130 | 0.01512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
141 | LV_230-78_0_4_line_141 |  | 129 | 131 | 0.022951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_230-78_0_4_line_142 |  | 130 | 132 | 0.01079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
143 | LV_230-78_0_4_line_143 |  | 131 | 133 | 0.00018486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
144 | LV_230-78_0_4_line_144 |  | 132 | 135 | 0.004034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
145 | LV_230-78_0_4_line_145 |  | 133 | 136 | 0.00015826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
146 | LV_230-78_0_4_line_146 |  | 134 | 187 | 0.020773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_230-78_0_4_line_147 |  | 135 | 149 | 0.012034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
148 | LV_230-78_0_4_line_148 |  | 135 | 150 | 0.016707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
149 | LV_230-78_0_4_line_149 |  | 137 | 138 | 0.037417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_230-78_0_4_line_150 |  | 138 | 139 | 0.029856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_230-78_0_4_line_151 |  | 138 | 140 | 0.032611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_230-78_0_4_line_152 |  | 139 | 141 | 0.006937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_230-78_0_4_line_153 |  | 140 | 142 | 0.0099617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_230-78_0_4_line_154 |  | 141 | 145 | 0.017263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_230-78_0_4_line_155 |  | 142 | 146 | 0.033137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_230-78_0_4_line_156 |  | 146 | 148 | 0.043452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_230-78_0_4_line_157 |  | 150 | 151 | 0.0080108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
158 | LV_230-78_0_4_line_158 |  | 151 | 169 | 0.0027887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
159 | LV_230-78_0_4_line_159 |  | 152 | 153 | 0.019685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_230-78_0_4_line_160 |  | 153 | 164 | 0.041467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_230-78_0_4_line_161 |  | 154 | 155 | 0.016455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_230-78_0_4_line_162 |  | 154 | 156 | 0.017212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_230-78_0_4_line_163 |  | 155 | 157 | 0.011062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_230-78_0_4_line_164 |  | 156 | 158 | 0.014788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_230-78_0_4_line_165 |  | 156 | 159 | 0.038217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_230-78_0_4_line_166 |  | 157 | 160 | 0.0061882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_230-78_0_4_line_167 |  | 158 | 161 | 0.003105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_230-78_0_4_line_168 |  | 158 | 162 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_230-78_0_4_line_169 |  | 158 | 163 | 0.012875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_230-78_0_4_line_170 |  | 159 | 164 | 0.018671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_230-78_0_4_line_171 |  | 160 | 165 | 0.017797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_230-78_0_4_line_172 |  | 161 | 166 | 0.016963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_230-78_0_4_line_173 |  | 162 | 167 | 0.019029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_230-78_0_4_line_174 |  | 163 | 168 | 0.0068886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_230-78_0_4_line_175 |  | 165 | 170 | 0.028973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_230-78_0_4_line_176 |  | 165 | 169 | 0.0073585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
177 | LV_230-78_0_4_line_177 |  | 167 | 173 | 0.019356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_230-78_0_4_line_178 |  | 170 | 171 | 0.0034301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_230-78_0_4_line_179 |  | 171 | 172 | 0.010048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_230-78_0_4_line_180 |  | 172 | 254 | 0.01805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_230-78_0_4_line_181 |  | 173 | 174 | 0.018526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_230-78_0_4_line_182 |  | 174 | 175 | 0.017531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_230-78_0_4_line_183 |  | 175 | 176 | 0.00855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_230-78_0_4_line_184 |  | 177 | 200 | 0.006813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_230-78_0_4_line_185 |  | 178 | 179 | 0.034729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_230-78_0_4_line_186 |  | 178 | 180 | 0.014467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_230-78_0_4_line_187 |  | 179 | 196 | 0.010655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_230-78_0_4_line_188 |  | 180 | 228 | 0.0079251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_230-78_0_4_line_189 |  | 181 | 182 | 0.026117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_230-78_0_4_line_190 |  | 181 | 183 | 0.015996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_230-78_0_4_line_191 |  | 182 | 184 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_230-78_0_4_line_192 |  | 183 | 185 | 0.0001682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_230-78_0_4_line_193 |  | 184 | 188 | 0.020562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_230-78_0_4_line_194 |  | 185 | 269 | 0.0012006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_230-78_0_4_line_195 |  | 186 | 214 | 0.014927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_230-78_0_4_line_196 |  | 189 | 190 | 0.018211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_230-78_0_4_line_197 |  | 190 | 191 | 0.01468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_230-78_0_4_line_198 |  | 191 | 236 | 0.0033412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_230-78_0_4_line_199 |  | 192 | 193 | 0.014856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_230-78_0_4_line_200 |  | 193 | 276 | 0.0095039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_230-78_0_4_line_201 |  | 194 | 195 | 0.005979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_230-78_0_4_line_202 |  | 195 | 280 | 0.018957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_230-78_0_4_line_203 |  | 197 | 198 | 0.016052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_230-78_0_4_line_204 |  | 197 | 199 | 0.0091948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_230-78_0_4_line_205 |  | 198 | 228 | 0.0071157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_230-78_0_4_line_206 |  | 199 | 223 | 0.0040143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_230-78_0_4_line_207 |  | 202 | 203 | 0.0069807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_230-78_0_4_line_208 |  | 202 | 204 | 0.0097189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_230-78_0_4_line_209 |  | 203 | 205 | 0.00041033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_230-78_0_4_line_210 |  | 204 | 206 | 0.0039839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_230-78_0_4_line_211 |  | 205 | 207 | 0.015757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_230-78_0_4_line_212 |  | 205 | 208 | 0.0061939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_230-78_0_4_line_213 |  | 206 | 209 | 0.0066999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_230-78_0_4_line_214 |  | 207 | 210 | 0.0053269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_230-78_0_4_line_215 |  | 208 | 211 | 0.0032238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_230-78_0_4_line_216 |  | 209 | 212 | 0.015252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_230-78_0_4_line_217 |  | 209 | 213 | 0.00042963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_230-78_0_4_line_218 |  | 211 | 254 | 0.003672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_230-78_0_4_line_219 |  | 212 | 252 | 0.0069651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_230-78_0_4_line_220 |  | 213 | 259 | 0.0070446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_230-78_0_4_line_221 |  | 214 | 218 | 0.0068867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_230-78_0_4_line_222 |  | 215 | 216 | 0.014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_230-78_0_4_line_223 |  | 215 | 217 | 0.020146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_230-78_0_4_line_224 |  | 216 | 219 | 0.0088164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_230-78_0_4_line_225 |  | 217 | 220 | 0.0069638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_230-78_0_4_line_226 |  | 218 | 221 | 0.0081124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_230-78_0_4_line_227 |  | 219 | 270 | 0.019046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_230-78_0_4_line_228 |  | 220 | 244 | 0.0011648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_230-78_0_4_line_229 |  | 221 | 231 | 0.0057732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_230-78_0_4_line_230 |  | 223 | 224 | 0.010733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_230-78_0_4_line_231 |  | 224 | 225 | 0.01865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_230-78_0_4_line_232 |  | 224 | 226 | 0.013319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_230-78_0_4_line_233 |  | 224 | 227 | 0.012994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_230-78_0_4_line_234 |  | 226 | 229 | 0.0041137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_230-78_0_4_line_235 |  | 227 | 230 | 0.017081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_230-78_0_4_line_236 |  | 229 | 237 | 0.0028799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_230-78_0_4_line_237 |  | 230 | 238 | 0.008359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_230-78_0_4_line_238 |  | 230 | 239 | 0.015509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_230-78_0_4_line_239 |  | 231 | 232 | 0.004466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_230-78_0_4_line_240 |  | 232 | 233 | 0.0066907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_230-78_0_4_line_241 |  | 233 | 267 | 0.0030187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_230-78_0_4_line_242 |  | 234 | 235 | 0.0041906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_230-78_0_4_line_243 |  | 235 | 263 | 0.014875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_230-78_0_4_line_244 |  | 235 | 264 | 0.0028349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_230-78_0_4_line_245 |  | 236 | 260 | 0.0033948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_230-78_0_4_line_246 |  | 237 | 262 | 0.0038573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_230-78_0_4_line_247 |  | 238 | 258 | 0.0020962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_230-78_0_4_line_248 |  | 239 | 271 | 0.0048013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_230-78_0_4_line_249 |  | 240 | 241 | 0.0043235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_230-78_0_4_line_250 |  | 240 | 242 | 0.0069589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_230-78_0_4_line_251 |  | 241 | 243 | 0.0026407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_230-78_0_4_line_252 |  | 242 | 244 | 0.0059463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_230-78_0_4_line_253 |  | 243 | 245 | 0.0091112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_230-78_0_4_line_254 |  | 244 | 246 | 0.010943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_230-78_0_4_line_255 |  | 245 | 247 | 0.0058907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_230-78_0_4_line_256 |  | 245 | 248 | 0.017996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_230-78_0_4_line_257 |  | 246 | 249 | 0.0070346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_230-78_0_4_line_258 |  | 247 | 253 | 0.0069396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_230-78_0_4_line_259 |  | 248 | 250 | 0.0069665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_230-78_0_4_line_260 |  | 249 | 255 | 0.0070346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_230-78_0_4_line_261 |  | 250 | 251 | 0.0069667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_230-78_0_4_line_262 |  | 251 | 252 | 0.0069653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_230-78_0_4_line_263 |  | 253 | 272 | 0.0069376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_230-78_0_4_line_264 |  | 255 | 256 | 0.0045997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_230-78_0_4_line_265 |  | 257 | 258 | 0.0049484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_230-78_0_4_line_266 |  | 257 | 259 | 0.0070446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_230-78_0_4_line_267 |  | 260 | 261 | 0.0035986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
268 | LV_230-78_0_4_line_268 |  | 261 | 262 | 0.0031378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_230-78_0_4_line_269 |  | 263 | 273 | 0.0068083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
270 | LV_230-78_0_4_line_270 |  | 264 | 272 | 0.0069347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_230-78_0_4_line_271 |  | 265 | 266 | 0.0066871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
272 | LV_230-78_0_4_line_272 |  | 265 | 267 | 0.0033556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
273 | LV_230-78_0_4_line_273 |  | 266 | 268 | 0.0037115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
274 | LV_230-78_0_4_line_274 |  | 267 | 269 | 0.01302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
275 | LV_230-78_0_4_line_275 |  | 273 | 274 | 0.0042676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
276 | LV_230-78_0_4_line_276 |  | 275 | 276 | 0.0021293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
277 | LV_230-78_0_4_line_277 |  | 275 | 277 | 0.0097852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
278 | LV_230-78_0_4_line_278 |  | 277 | 278 | 0.0030778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
279 | LV_230-78_0_4_line_279 |  | 278 | 279 | 0.0078033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-78_0_4_trafo_177 | 0.63 MVA 20/0.4 kV | 281 | 72 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2696532.1571 | 1263133.415 | 2696538.5168 | 1263136.3685
1 | 2696532.1571 | 1263133.415 | 2696519.8433 | 1263127.7124
2 | 2696532.1571 | 1263133.415 | 2696536.6923 | 1263123.0938
3 | 2696519.8433 | 1263127.7124 | 2696512.9003 | 1263124.4971
4 | 2696505.9548 | 1263121.2806 | 2696512.9003 | 1263124.4971
5 | 2696490.6144 | 1263037.4144 | 2696486.2732 | 1263036.1203 | 2696472.4946 | 1263033.3828
6 | 2696490.6144 | 1263037.4144 | 2696487.3145 | 1263050.9374
7 | 2696472.4946 | 1263033.3828 | 2696464.4583 | 1263031.7861
8 | 2696484.8251 | 1263061.1393 | 2696487.3145 | 1263050.9374
9 | 2696538.8539 | 1263085.819 | 2696530.4694 | 1263081.989
10 | 2696506.6482 | 1263071.1078 | 2696530.4694 | 1263081.989
11 | 2696499.0119 | 1263118.0653 | 2696505.9548 | 1263121.2806
12 | 2696498.7008 | 1263206.6178 | 2696516.098 | 1263215.9137
13 | 2696498.1675 | 1263206.2715 | 2696498.7008 | 1263206.6178
14 | 2696498.7008 | 1263206.6178 | 2696492.7588 | 1263221.8275
15 | 2696483.8281 | 1263196.9598 | 2696498.1675 | 1263206.2715
16 | 2696490.7427 | 1263226.988 | 2696492.7588 | 1263221.8275
17 | 2696483.8281 | 1263196.9598 | 2696482.5825 | 1263196.1509
18 | 2696490.7427 | 1263226.988 | 2696486.6435 | 1263237.4808
19 | 2696467.3665 | 1263186.5322 | 2696469.6115 | 1263187.7278 | 2696482.5825 | 1263196.1509
20 | 2696486.6435 | 1263237.4808 | 2696483.2184 | 1263246.2481
21 | 2696467.35 | 1263186.5234 | 2696467.3665 | 1263186.5322
22 | 2696452.2728 | 1263178.4935 | 2696467.35 | 1263186.5234
23 | 2696482.9542 | 1263129.8191 | 2696481.6575 | 1263132.0603
24 | 2696491.711 | 1263114.6842 | 2696482.9542 | 1263129.8191
25 | 2696491.711 | 1263114.6842 | 2696485.1272 | 1263111.6376
26 | 2696492.0664 | 1263114.8488 | 2696491.711 | 1263114.6842
27 | 2696468.5453 | 1263103.9643 | 2696485.1272 | 1263111.6376
28 | 2696492.0664 | 1263114.8488 | 2696499.0119 | 1263118.0653
29 | 2696461.6692 | 1263147.4759 | 2696459.3751 | 1263146.3035
30 | 2696446.3177 | 1263139.6309 | 2696459.3751 | 1263146.3035
31 | 2696468.5453 | 1263103.9643 | 2696472.9756 | 1263093.9558
32 | 2696468.5453 | 1263103.9643 | 2696466.9261 | 1263106.9244
33 | 2696446.3177 | 1263139.6309 | 2696452.445 | 1263130.3745
34 | 2696477.9481 | 1263082.7225 | 2696472.9756 | 1263093.9558
35 | 2696461.9676 | 1263115.989 | 2696466.9261 | 1263106.9244
36 | 2696461.9676 | 1263115.989 | 2696452.445 | 1263130.3745
37 | 2696439.1973 | 1263171.5297 | 2696452.2728 | 1263178.4935
38 | 2696426.0192 | 1263166.0548 | 2696435.8959 | 1263169.7744 | 2696439.1973 | 1263171.5297
39 | 2696426.0192 | 1263166.0548 | 2696410.7339 | 1263173.3672
40 | 2696426.0192 | 1263166.0548 | 2696428.372 | 1263159.4545
41 | 2696410.7339 | 1263173.3672 | 2696400.2553 | 1263174.6752 | 2696396.9194 | 1263175.4156
42 | 2696409.0933 | 1263183.4153 | 2696410.7339 | 1263173.3672
43 | 2696428.372 | 1263159.4545 | 2696430.547 | 1263157.1221
44 | 2696412.5434 | 1263183.9053 | 2696413.788 | 1263180.1225 | 2696415.2652 | 1263177.778 | 2696418.1859 | 1263175.6238 | 2696422.177 | 1263174.3545 | 2696424.2849 | 1263174.1093
45 | 2696412.5434 | 1263183.9053 | 2696408.9905 | 1263203.1075 | 2696408.8313 | 1263204.1343
46 | 2696409.0933 | 1263183.4153 | 2696412.5434 | 1263183.9053
47 | 2696461.9676 | 1263115.989 | 2696443.7137 | 1263109.4009
48 | 2696443.7137 | 1263109.4009 | 2696438.0284 | 1263107.349
49 | 2696506.6482 | 1263071.1078 | 2696499.1226 | 1263067.6702
50 | 2696484.8251 | 1263061.1393 | 2696499.1226 | 1263067.6702
51 | 2696477.9481 | 1263082.7225 | 2696484.8251 | 1263061.1393
52 | 2696477.9481 | 1263082.7225 | 2696465.4342 | 1263078.913
53 | 2696465.4342 | 1263078.913 | 2696450.5906 | 1263074.3943
54 | 2696443.1325 | 1263072.1238 | 2696450.5906 | 1263074.3943
55 | 2696152.7453 | 1263299.8052 | 2696149.4046 | 1263307.8613
56 | 2696150.5947 | 1263281.9878 | 2696153.1535 | 1263298.8209 | 2696152.7453 | 1263299.8052
57 | 2696148.3623 | 1263310.3746 | 2696149.4046 | 1263307.8613
58 | 2696150.5947 | 1263281.9878 | 2696149.5651 | 1263272.1074
59 | 2696150.5947 | 1263281.9878 | 2696155.3353 | 1263275.3928 | 2696167.3998 | 1263274.4
60 | 2696149.5651 | 1263272.1074 | 2696145.3081 | 1263271.6601 | 2696115.4983 | 1263268.3822
61 | 2696149.5651 | 1263272.1074 | 2696158.0931 | 1263241.0394
62 | 2696193.8524 | 1263272.2231 | 2696167.3998 | 1263274.4
63 | 2696078.0152 | 1263264.2605 | 2696115.4983 | 1263268.3822
64 | 2696158.0931 | 1263241.0394 | 2696163.1875 | 1263222.4803
65 | 2696214.6764 | 1263270.5094 | 2696193.8524 | 1263272.2231
66 | 2696078.0152 | 1263264.2605 | 2696067.1049 | 1263264.7948 | 2696053.0216 | 1263270.4721
67 | 2696168.3777 | 1263203.5721 | 2696163.1875 | 1263222.4803
68 | 2696214.6764 | 1263270.5094 | 2696206.8313 | 1263278.0546 | 2696203.4671 | 1263282.4702 | 2696198.6869 | 1263288.2527 | 2696188.6617 | 1263293.6607
69 | 2696214.6764 | 1263270.5094 | 2696218.2674 | 1263245.8815
70 | 2696481.4139 | 1263250.8669 | 2696483.2184 | 1263246.2481
71 | 2696481.4139 | 1263250.8669 | 2696478.5884 | 1263258.0993
72 | 2696478.5884 | 1263258.0993 | 2696477.413 | 1263261.108
73 | 2696408.8313 | 1263204.1343 | 2696407.1466 | 1263214.9982 | 2696406.3406 | 1263223.303 | 2696406.2749 | 1263224.6612
74 | 2696409.0933 | 1263183.4153 | 2696406.6473 | 1263202.249
75 | 2696406.2749 | 1263224.6612 | 2696406.0877 | 1263228.5334
76 | 2696404.6473 | 1263217.6486 | 2696404.6473 | 1263217.6486 | 2696406.6473 | 1263202.249
77 | 2696396.9194 | 1263175.4156 | 2696387.5597 | 1263177.4928 | 2696386.5975 | 1263177.6258
78 | 2696406.0877 | 1263228.5334 | 2696405.7948 | 1263234.5922 | 2696405.6943 | 1263243.9871 | 2696406.057 | 1263250.7674
79 | 2696353.9085 | 1263186.9967 | 2696350.1191 | 1263186.5235 | 2696347.7937 | 1263183.1273 | 2696340.7665 | 1263182.0498
80 | 2696355.0898 | 1263179.6989 | 2696353.9085 | 1263186.9967
81 | 2696353.9085 | 1263186.9967 | 2696352.2461 | 1263197.2195
82 | 2696334.3858 | 1263180.7986 | 2696337.325 | 1263181.5221 | 2696340.7665 | 1263182.0498
83 | 2696355.0898 | 1263179.6989 | 2696361.048 | 1263179.7738 | 2696365.9475 | 1263179.6158
84 | 2696349.9478 | 1263211.3521 | 2696352.2461 | 1263197.2195
85 | 2696406.057 | 1263250.7674 | 2696406.2081 | 1263253.5922 | 2696406.5957 | 1263257.4529
86 | 2696406.5957 | 1263257.4529 | 2696407.2256 | 1263263.7282 | 2696407.5338 | 1263265.7047
87 | 2696407.5338 | 1263265.7047 | 2696408.4936 | 1263271.859
88 | 2696464.4583 | 1263031.7861 | 2696462.9051 | 1263031.4775
89 | 2696148.4388 | 1263090.1732 | 2696146.5217 | 1263100.2844 | 2696145.6195 | 1263111.4742
90 | 2696150.2632 | 1263080.5514 | 2696148.4388 | 1263090.1732
91 | 2696175.0247 | 1263179.3568 | 2696147.0982 | 1263152.3696 | 2696143.1237 | 1263142.4302 | 2696145.6195 | 1263111.4742
92 | 2696145.6195 | 1263111.4742 | 2696028.516 | 1263114.1231
93 | 2696175.0247 | 1263179.3568 | 2696194.8582 | 1263168.459
94 | 2696175.0247 | 1263179.3568 | 2696173.4725 | 1263185.0117
95 | 2696028.516 | 1263114.1231 | 2696016.1324 | 1263145.9702 | 2695994.3361 | 1263143.6701 | 2695985.9721 | 1263142.8115 | 2695976.0322 | 1263143.4284
96 | 2696194.8582 | 1263168.459 | 2696214.0951 | 1263157.889
97 | 2696168.3777 | 1263203.5721 | 2696173.4725 | 1263185.0117
98 | 2695976.0322 | 1263143.4284 | 2695972.9519 | 1263143.8232 | 2695971.004 | 1263144.0807 | 2695948.8269 | 1263143.8874 | 2695924.3561 | 1263143.4346 | 2695922.7571 | 1263132.8667 | 2695914.0208 | 1263123.3839 | 2695909.6489 | 1263116.8547
99 | 2696216.9553 | 1263156.3175 | 2696214.0951 | 1263157.889
100 | 2696255.7987 | 1263133.4556 | 2696249.7431 | 1263137.7776
101 | 2696255.7987 | 1263133.4556 | 2696273.948 | 1263135.7862
102 | 2696229.1287 | 1263191.4863 | 2696228.1829 | 1263194.278 | 2696224.2802 | 1263209.5695
103 | 2696221.1947 | 1263225.8001 | 2696222.598 | 1263216.1606 | 2696224.2802 | 1263209.5695
104 | 2696273.948 | 1263135.7862 | 2696282.439 | 1263144.5649 | 2696292.7482 | 1263152.9849
105 | 2696273.948 | 1263135.7862 | 2696271.1525 | 1263127.7574
106 | 2696220.7148 | 1263229.0961 | 2696221.1947 | 1263225.8001
107 | 2696292.7482 | 1263152.9849 | 2696293.1084 | 1263153.279 | 2696301.6211 | 1263159.8007 | 2696306.717 | 1263163.2533
108 | 2696266.6859 | 1263114.9287 | 2696271.1525 | 1263127.7574
109 | 2696263.1973 | 1263090.4298 | 2696266.6859 | 1263114.9287
110 | 2696263.1973 | 1263090.4298 | 2696275.1547 | 1263084.1754
111 | 2696263.1973 | 1263090.4298 | 2696258.4989 | 1263084.2594
112 | 2696324.5272 | 1263173.5071 | 2696319.5795 | 1263171.5249 | 2696310.2651 | 1263165.6574 | 2696306.717 | 1263163.2533
113 | 2696288.3026 | 1263077.2983 | 2696275.1547 | 1263084.1754
114 | 2696195.2344 | 1263047.9853 | 2696205.5698 | 1263054.2626
115 | 2696231.4527 | 1263045.2875 | 2696213.6899 | 1263043.7306 | 2696205.5698 | 1263054.2626
116 | 2696227.7411 | 1263017.3599 | 2696227.1408 | 1263026.9246 | 2696231.4527 | 1263045.2875
117 | 2696227.7411 | 1263017.3599 | 2696252.3731 | 1263012.1357
118 | 2696273.7441 | 1263006.7776 | 2696259.6835 | 1263010.5852 | 2696252.3731 | 1263012.1357
119 | 2696273.7441 | 1263006.7776 | 2696297.7337 | 1263000.2825
120 | 2696288.3026 | 1263077.2983 | 2696295.485 | 1263073.5416 | 2696299.9998 | 1263072.4806
121 | 2696309.5593 | 1263070.2342 | 2696299.9998 | 1263072.4806
122 | 2696438.0284 | 1263107.349 | 2696436.0223 | 1263106.6249 | 2696428.9169 | 1263105.1348
123 | 2696419.7362 | 1263103.2093 | 2696428.9169 | 1263105.1348
124 | 2696419.7362 | 1263103.2093 | 2696419.7152 | 1263103.2049
125 | 2696419.7152 | 1263103.2049 | 2696410.9571 | 1263101.3681
126 | 2696410.9571 | 1263101.3681 | 2696403.6935 | 1263099.8447
127 | 2696395.5246 | 1263098.6988 | 2696399.2835 | 1263098.9198 | 2696403.6935 | 1263099.8447
128 | 2696395.5246 | 1263098.6988 | 2696391.206 | 1263098.4449
129 | 2696381.7458 | 1263097.8887 | 2696391.206 | 1263098.4449
130 | 2696381.7458 | 1263097.8887 | 2696365.5165 | 1263096.9216
131 | 2696343.7204 | 1263095.6229 | 2696365.5165 | 1263096.9216
132 | 2696343.7204 | 1263095.6229 | 2696343.3238 | 1263113.6759
133 | 2696343.7204 | 1263095.6229 | 2696343.738 | 1263087.2798
134 | 2696343.7754 | 1263069.6025 | 2696353.6265 | 1263068.8958
135 | 2696353.6265 | 1263068.8958 | 2696355.5562 | 1263066.5253
136 | 2696343.7754 | 1263069.6025 | 2696343.738 | 1263087.2798
137 | 2696343.7754 | 1263069.6025 | 2696335.3741 | 1263069.7144
138 | 2696338.5565 | 1263159.1734 | 2696337.975 | 1263161.9188
139 | 2696342.4366 | 1263136.9475 | 2696342.0409 | 1263142.7228 | 2696338.5565 | 1263159.1734
140 | 2696334.8418 | 1263176.7111 | 2696337.975 | 1263161.9188
141 | 2696343.3163 | 1263114.0189 | 2696342.99 | 1263128.8714 | 2696342.4366 | 1263136.9475
142 | 2696334.8418 | 1263176.7111 | 2696328.0826 | 1263174.9329 | 2696324.5272 | 1263173.5071
143 | 2696343.3163 | 1263114.0189 | 2696343.3203 | 1263113.8341
144 | 2696322.9149 | 1263177.2061 | 2696324.5272 | 1263173.5071
145 | 2696343.3203 | 1263113.8341 | 2696343.3238 | 1263113.6759
146 | 2696365.9475 | 1263179.6158 | 2696374.1037 | 1263179.3529 | 2696386.5975 | 1263177.6258
147 | 2696322.9149 | 1263177.2061 | 2696329.9711 | 1263179.712 | 2696334.3858 | 1263180.7986
148 | 2696322.9149 | 1263177.2061 | 2696307.6244 | 1263183.9374
149 | 2696410.9703 | 1263016.632 | 2696390.8394 | 1263048.1722
150 | 2696410.9703 | 1263016.632 | 2696439.5221 | 1263025.3595
151 | 2696410.9703 | 1263016.632 | 2696391.1243 | 1263007.4455 | 2696381.3772 | 1263002.9312
152 | 2696446.1561 | 1263027.3874 | 2696439.5221 | 1263025.3595
153 | 2696381.3772 | 1263002.9312 | 2696372.3379 | 1262998.7446
154 | 2696462.9051 | 1263031.4775 | 2696453.2824 | 1263029.5657 | 2696446.1561 | 1263027.3874
155 | 2696340.2298 | 1262991.7702 | 2696364.4959 | 1262995.1126 | 2696372.3379 | 1262998.7446
156 | 2696340.2298 | 1262991.7702 | 2696320.1943 | 1262994.2014 | 2696297.7337 | 1263000.2825
157 | 2696300.2926 | 1263187.1651 | 2696307.6244 | 1263183.9374
158 | 2696300.2926 | 1263187.1651 | 2696297.7402 | 1263188.2887
159 | 2696271.6126 | 1263141.2923 | 2696274.0412 | 1263143.0158 | 2696284.6815 | 1263151.6627 | 2696286.9853 | 1263153.5782
160 | 2696243.6036 | 1263160.7873 | 2696247.2287 | 1263149.8739 | 2696249.5298 | 1263145.5189 | 2696253.2327 | 1263141.5871 | 2696259.1927 | 1263138.7818 | 2696265.201 | 1263138.5572 | 2696269.8554 | 1263140.0453 | 2696271.6126 | 1263141.2923
161 | 2696259.1235 | 1263205.8083 | 2696246.8595 | 1263211.407 | 2696243.9382 | 1263211.9623
162 | 2696227.0289 | 1263215.1763 | 2696243.9382 | 1263211.9623
163 | 2696259.1235 | 1263205.8083 | 2696269.1861 | 1263201.2145
164 | 2696227.0289 | 1263215.1763 | 2696224.4582 | 1263225.921 | 2696223.788 | 1263229.602
165 | 2696227.0289 | 1263215.1763 | 2696228.9583 | 1263207.2679 | 2696232.6356 | 1263193.8056 | 2696237.7178 | 1263178.506
166 | 2696274.8155 | 1263198.6446 | 2696269.1861 | 1263201.2145
167 | 2696220.7148 | 1263229.0961 | 2696223.788 | 1263229.602
168 | 2696223.788 | 1263229.602 | 2696223.4075 | 1263231.6864 | 2696222.0718 | 1263239.2264 | 2696221.7446 | 1263241.4847
169 | 2696223.788 | 1263229.602 | 2696236.4953 | 1263231.6707
170 | 2696237.7178 | 1263178.506 | 2696243.6036 | 1263160.7873
171 | 2696291.0055 | 1263191.2536 | 2696274.8155 | 1263198.6446
172 | 2696220.7148 | 1263229.0961 | 2696218.2674 | 1263245.8815
173 | 2696221.7446 | 1263241.4847 | 2696220.6543 | 1263249.0113 | 2696219.8815 | 1263256.2157 | 2696219.5366 | 1263260.3793
174 | 2696243.2944 | 1263232.7776 | 2696236.4953 | 1263231.6707
175 | 2696291.0055 | 1263191.2536 | 2696284.9801 | 1263219.5936
176 | 2696291.0055 | 1263191.2536 | 2696297.7402 | 1263188.2887
177 | 2696219.5366 | 1263260.3793 | 2696219.347 | 1263262.6679 | 2696218.7805 | 1263271.0877 | 2696218.4576 | 1263279.7027
178 | 2696284.2668 | 1263222.9487 | 2696284.9801 | 1263219.5936
179 | 2696282.1772 | 1263232.7771 | 2696284.2668 | 1263222.9487
180 | 2696282.1772 | 1263232.7771 | 2696278.7137 | 1263250.4915
181 | 2696218.1683 | 1263298.2254 | 2696218.3277 | 1263283.168 | 2696218.4576 | 1263279.7027
182 | 2696214.2983 | 1263315.0174 | 2696218.0897 | 1263305.6492 | 2696218.1683 | 1263298.2254
183 | 2696214.2983 | 1263315.0174 | 2696217.859 | 1263322.7907
184 | 2696185.1761 | 1263299.5199 | 2696188.6617 | 1263293.6607
185 | 2696211.0768 | 1263366.6627 | 2696219.6166 | 1263371.9726 | 2696219.4695 | 1263386.0928 | 2696217.6275 | 1263396.5047
186 | 2696211.0768 | 1263366.6627 | 2696225.3916 | 1263368.7567
187 | 2696217.6275 | 1263396.5047 | 2696227.498 | 1263395.9649 | 2696228.2274 | 1263396.212
188 | 2696225.3916 | 1263368.7567 | 2696233.2333 | 1263369.9038
189 | 2696403.32 | 1263244.5155 | 2696405.0195 | 1263270.5756
190 | 2696403.32 | 1263244.5155 | 2696398.7052 | 1263243.8398 | 2696391.4751 | 1263242.7655 | 2696387.4962 | 1263242.1733
191 | 2696405.0195 | 1263270.5756 | 2696390.0108 | 1263275.7241
192 | 2696387.4962 | 1263242.1733 | 2696387.3298 | 1263242.1486
193 | 2696390.0108 | 1263275.7241 | 2696381.8494 | 1263294.597
194 | 2696386.1423 | 1263241.9719 | 2696387.3298 | 1263242.1486
195 | 2696349.9478 | 1263211.3521 | 2696364.6437 | 1263213.9671
196 | 2696312.317 | 1263355.0343 | 2696330.4779 | 1263356.385
197 | 2696312.317 | 1263355.0343 | 2696297.7147 | 1263353.5297
198 | 2696297.7147 | 1263353.5297 | 2696294.3911 | 1263353.1872
199 | 2696465.6596 | 1263291.1931 | 2696460.2538 | 1263305.0303
200 | 2696469.118 | 1263282.3408 | 2696465.6596 | 1263291.1931
201 | 2696412.5519 | 1263290.3564 | 2696413.1956 | 1263292.6269 | 2696414.2572 | 1263296.0867
202 | 2696408.4936 | 1263271.859 | 2696408.8148 | 1263273.918 | 2696410.7094 | 1263283.857 | 2696412.5519 | 1263290.3564
203 | 2696256.157 | 1263373.2571 | 2696240.2741 | 1263370.9337
204 | 2696256.157 | 1263373.2571 | 2696257.7368 | 1263364.199
205 | 2696240.2741 | 1263370.9337 | 2696233.2333 | 1263369.9038
206 | 2696258.4265 | 1263360.2444 | 2696257.7368 | 1263364.199
207 | 2696276.1293 | 1263263.7419 | 2696274.8915 | 1263270.612
208 | 2696273.1682 | 1263280.1768 | 2696274.8915 | 1263270.612
209 | 2696276.1293 | 1263263.7419 | 2696276.2021 | 1263263.3381
210 | 2696273.1682 | 1263280.1768 | 2696272.4618 | 1263284.0976
211 | 2696276.2021 | 1263263.3381 | 2696291.7077 | 1263266.1421
212 | 2696276.2021 | 1263263.3381 | 2696277.3906 | 1263257.2592
213 | 2696271.2738 | 1263290.6913 | 2696272.4618 | 1263284.0976
214 | 2696296.9496 | 1263267.09 | 2696291.7077 | 1263266.1421
215 | 2696278.0092 | 1263254.0953 | 2696277.3906 | 1263257.2592
216 | 2696271.2738 | 1263290.6913 | 2696286.2418 | 1263293.6189
217 | 2696271.2738 | 1263290.6913 | 2696271.1958 | 1263291.1138
218 | 2696278.7137 | 1263250.4915 | 2696278.0092 | 1263254.0953
219 | 2696293.0773 | 1263294.9559 | 2696286.2418 | 1263293.6189
220 | 2696271.1958 | 1263291.1138 | 2696269.9158 | 1263298.0411
221 | 2696371.4239 | 1263215.1736 | 2696364.6437 | 1263213.9671
222 | 2696343.5735 | 1263246.5103 | 2696329.3283 | 1263243.3239
223 | 2696343.5735 | 1263246.5103 | 2696339.1252 | 1263266.1587
224 | 2696320.7245 | 1263241.3994 | 2696329.3283 | 1263243.3239
225 | 2696339.1252 | 1263266.1587 | 2696337.5875 | 1263272.9506
226 | 2696371.4239 | 1263215.1736 | 2696373.8891 | 1263215.6123 | 2696376.7791 | 1263220.4189 | 2696376.7791 | 1263220.4189
227 | 2696320.7245 | 1263241.3994 | 2696302.1374 | 1263237.2418
228 | 2696337.3303 | 1263274.0867 | 2696337.5875 | 1263272.9506
229 | 2696376.7791 | 1263220.4189 | 2696375.762 | 1263226.1017
230 | 2696260.2704 | 1263349.6715 | 2696258.4265 | 1263360.2444
231 | 2696260.2704 | 1263349.6715 | 2696241.9592 | 1263346.1347
232 | 2696260.2704 | 1263349.6715 | 2696273.5196 | 1263351.0366
233 | 2696260.2704 | 1263349.6715 | 2696262.6756 | 1263336.9019
234 | 2696277.6116 | 1263351.4583 | 2696273.5196 | 1263351.0366
235 | 2696265.8372 | 1263320.1157 | 2696262.6756 | 1263336.9019
236 | 2696280.4763 | 1263351.7535 | 2696277.6116 | 1263351.4583
237 | 2696265.8372 | 1263320.1157 | 2696267.356 | 1263311.8958
238 | 2696265.8372 | 1263320.1157 | 2696281.0566 | 1263323.0979
239 | 2696374.9752 | 1263230.4979 | 2696375.762 | 1263226.1017
240 | 2696373.7964 | 1263237.0839 | 2696374.9752 | 1263230.4979
241 | 2696373.2645 | 1263240.0554 | 2696373.7964 | 1263237.0839
242 | 2696322.6585 | 1263330.6828 | 2696321.4682 | 1263334.7008
243 | 2696322.6585 | 1263330.6828 | 2696308.0142 | 1263328.073
244 | 2696322.6585 | 1263330.6828 | 2696323.4829 | 1263327.9704
245 | 2696294.3911 | 1263353.1872 | 2696291.0142 | 1263352.8393
246 | 2696280.4763 | 1263351.7535 | 2696284.3133 | 1263352.1488
247 | 2696267.356 | 1263311.8958 | 2696267.7368 | 1263309.8345
248 | 2696285.7684 | 1263324.0211 | 2696281.0566 | 1263323.0979
249 | 2696334.6219 | 1263286.7045 | 2696333.7145 | 1263290.9317
250 | 2696334.6219 | 1263286.7045 | 2696336.0824 | 1263279.9005
251 | 2696333.7145 | 1263290.9317 | 2696333.1603 | 1263293.5136
252 | 2696337.3303 | 1263274.0867 | 2696336.0824 | 1263279.9005
253 | 2696331.2482 | 1263302.4218 | 2696333.1603 | 1263293.5136
254 | 2696337.3303 | 1263274.0867 | 2696326.5255 | 1263272.3531
255 | 2696331.2482 | 1263302.4218 | 2696329.5351 | 1263308.058
256 | 2696331.2482 | 1263302.4218 | 2696313.5872 | 1263298.9675
257 | 2696326.5255 | 1263272.3531 | 2696319.5797 | 1263271.2386
258 | 2696327.517 | 1263314.6977 | 2696329.5351 | 1263308.058
259 | 2696306.7502 | 1263297.6302 | 2696313.5872 | 1263298.9675
260 | 2696319.5797 | 1263271.2386 | 2696312.6339 | 1263270.1242
261 | 2696306.7502 | 1263297.6302 | 2696299.9131 | 1263296.2929
262 | 2696299.9131 | 1263296.2929 | 2696293.0773 | 1263294.9559
263 | 2696327.517 | 1263314.6977 | 2696325.4995 | 1263321.3355
264 | 2696308.0924 | 1263269.3956 | 2696312.6339 | 1263270.1242
265 | 2696268.6359 | 1263304.9685 | 2696267.7368 | 1263309.8345
266 | 2696268.6359 | 1263304.9685 | 2696269.9158 | 1263298.0411
267 | 2696291.0142 | 1263352.8393 | 2696287.4345 | 1263352.4704
268 | 2696284.3133 | 1263352.1488 | 2696287.4345 | 1263352.4704
269 | 2696308.0142 | 1263328.073 | 2696301.3115 | 1263326.8785
270 | 2696323.4829 | 1263327.9704 | 2696325.4995 | 1263321.3355
271 | 2696372.6721 | 1263243.3583 | 2696371.4915 | 1263249.9403
272 | 2696373.2645 | 1263240.0554 | 2696372.6721 | 1263243.3583
273 | 2696370.8363 | 1263253.5936 | 2696371.4915 | 1263249.9403
274 | 2696373.2645 | 1263240.0554 | 2696386.1423 | 1263241.9719
275 | 2696297.1101 | 1263326.1297 | 2696301.3115 | 1263326.8785
276 | 2696469.8928 | 1263280.3575 | 2696469.118 | 1263282.3408
277 | 2696469.8928 | 1263280.3575 | 2696473.4535 | 1263271.2431
278 | 2696473.4535 | 1263271.2431 | 2696474.5735 | 1263268.3763
279 | 2696477.413 | 1263261.108 | 2696474.5735 | 1263268.3763

## bus_geodata
| x | y | coords
0 | 2696538.5168 | 1263136.3685
1 | 2696532.1571 | 1263133.415
2 | 2696519.8433 | 1263127.7124
3 | 2696536.6923 | 1263123.0938
4 | 2696512.9003 | 1263124.4971
5 | 2696490.6144 | 1263037.4144
6 | 2696472.4946 | 1263033.3828
7 | 2696487.3145 | 1263050.9374
8 | 2696538.8539 | 1263085.819
9 | 2696530.4694 | 1263081.989
10 | 2696505.9548 | 1263121.2806
11 | 2696516.098 | 1263215.9137
12 | 2696498.7008 | 1263206.6178
13 | 2696498.1675 | 1263206.2715
14 | 2696492.7588 | 1263221.8275
15 | 2696483.8281 | 1263196.9598
16 | 2696490.7427 | 1263226.988
17 | 2696482.5825 | 1263196.1509
18 | 2696486.6435 | 1263237.4808
19 | 2696467.3665 | 1263186.5322
20 | 2696467.35 | 1263186.5234
21 | 2696482.9542 | 1263129.8191
22 | 2696481.6575 | 1263132.0603
23 | 2696491.711 | 1263114.6842
24 | 2696485.1272 | 1263111.6376
25 | 2696492.0664 | 1263114.8488
26 | 2696461.6692 | 1263147.4759
27 | 2696459.3751 | 1263146.3035
28 | 2696468.5453 | 1263103.9643
29 | 2696499.0119 | 1263118.0653
30 | 2696446.3177 | 1263139.6309
31 | 2696472.9756 | 1263093.9558
32 | 2696466.9261 | 1263106.9244
33 | 2696452.445 | 1263130.3745
34 | 2696452.2728 | 1263178.4935
35 | 2696439.1973 | 1263171.5297
36 | 2696426.0192 | 1263166.0548
37 | 2696410.7339 | 1263173.3672
38 | 2696428.372 | 1263159.4545
39 | 2696424.2849 | 1263174.1093
40 | 2696412.5434 | 1263183.9053
41 | 2696461.9676 | 1263115.989
42 | 2696430.547 | 1263157.1221
43 | 2696443.7137 | 1263109.4009
44 | 2696499.1226 | 1263067.6702
45 | 2696506.6482 | 1263071.1078
46 | 2696484.8251 | 1263061.1393
47 | 2696477.9481 | 1263082.7225
48 | 2696465.4342 | 1263078.913
49 | 2696450.5906 | 1263074.3943
50 | 2696152.7453 | 1263299.8052
51 | 2696149.4046 | 1263307.8613
52 | 2696150.5947 | 1263281.9878
53 | 2696148.3623 | 1263310.3746
54 | 2696149.5651 | 1263272.1074
55 | 2696167.3998 | 1263274.4
56 | 2696115.4983 | 1263268.3822
57 | 2696158.0931 | 1263241.0394
58 | 2696193.8524 | 1263272.2231
59 | 2696078.0152 | 1263264.2605
60 | 2696163.1875 | 1263222.4803
61 | 2696214.6764 | 1263270.5094
62 | 2696483.2184 | 1263246.2481
63 | 2696481.4139 | 1263250.8669
64 | 2696478.5884 | 1263258.0993
65 | 2696408.8313 | 1263204.1343
66 | 2696409.0933 | 1263183.4153
67 | 2696406.2749 | 1263224.6612
68 | 2696406.6473 | 1263202.249
69 | 2696396.9194 | 1263175.4156
70 | 2696406.0877 | 1263228.5334
71 | 2696353.9085 | 1263186.9967
72 | 2696340.7666 | 1263182.0498
73 | 2696355.0898 | 1263179.6989
74 | 2696352.2461 | 1263197.2195
75 | 2696404.6473 | 1263217.6486
76 | 2696406.057 | 1263250.7674
77 | 2696406.5957 | 1263257.4529
78 | 2696407.5338 | 1263265.7047
79 | 2696464.4583 | 1263031.7861
80 | 2696148.4388 | 1263090.1732
81 | 2696145.6195 | 1263111.4742
82 | 2696150.2632 | 1263080.5514
83 | 2696175.0247 | 1263179.3568
84 | 2696028.516 | 1263114.1231
85 | 2696194.8582 | 1263168.459
86 | 2696173.4725 | 1263185.0117
87 | 2695976.0322 | 1263143.4284
88 | 2696214.0951 | 1263157.889
89 | 2696168.3777 | 1263203.5721
90 | 2696053.0216 | 1263270.4721
91 | 2696216.9553 | 1263156.3175
92 | 2696249.7431 | 1263137.7776
93 | 2696255.7987 | 1263133.4556
94 | 2696229.1287 | 1263191.4863
95 | 2696224.2802 | 1263209.5695
96 | 2696273.948 | 1263135.7862
97 | 2696221.1947 | 1263225.8001
98 | 2696292.7482 | 1263152.9849
99 | 2696271.1525 | 1263127.7574
100 | 2696266.6859 | 1263114.9287
101 | 2696263.1973 | 1263090.4298
102 | 2696306.717 | 1263163.2534
103 | 2696275.1547 | 1263084.1754
104 | 2696258.4989 | 1263084.2594
105 | 2696205.5698 | 1263054.2626
106 | 2696195.2344 | 1263047.9853
107 | 2696231.4527 | 1263045.2875
108 | 2696227.7411 | 1263017.3599
109 | 2696252.3731 | 1263012.1357
110 | 2696273.7441 | 1263006.7776
111 | 2696288.3026 | 1263077.2983
112 | 2696299.9998 | 1263072.4806
113 | 2696438.0284 | 1263107.349
114 | 2696428.9169 | 1263105.1348
115 | 2696419.7362 | 1263103.2093
116 | 2696419.7152 | 1263103.2049
117 | 2696410.9571 | 1263101.3681
118 | 2696403.6935 | 1263099.8447
119 | 2696395.5246 | 1263098.6988
120 | 2696391.206 | 1263098.4449
121 | 2696381.7458 | 1263097.8887
122 | 2696365.5165 | 1263096.9216
123 | 2696343.7204 | 1263095.6229
124 | 2696353.6265 | 1263068.8958
125 | 2696343.7754 | 1263069.6025
126 | 2696355.5562 | 1263066.5253
127 | 2696338.5565 | 1263159.1734
128 | 2696337.975 | 1263161.9188
129 | 2696342.4366 | 1263136.9475
130 | 2696334.8418 | 1263176.7111
131 | 2696343.3163 | 1263114.0189
132 | 2696324.5272 | 1263173.5071
133 | 2696343.3203 | 1263113.8341
134 | 2696365.9475 | 1263179.6158
135 | 2696322.9149 | 1263177.2061
136 | 2696343.3238 | 1263113.6759
137 | 2696390.8394 | 1263048.1722
138 | 2696410.9703 | 1263016.632
139 | 2696439.5221 | 1263025.3595
140 | 2696381.3772 | 1263002.9312
141 | 2696446.1561 | 1263027.3874
142 | 2696372.3379 | 1262998.7446
143 | 2696343.738 | 1263087.2798
144 | 2696335.3741 | 1263069.7144
145 | 2696462.9051 | 1263031.4775
146 | 2696340.2298 | 1262991.7702
147 | 2696309.5593 | 1263070.2342
148 | 2696297.7337 | 1263000.2825
149 | 2696334.3858 | 1263180.7986
150 | 2696307.6244 | 1263183.9374
151 | 2696300.2926 | 1263187.1651
152 | 2696286.9853 | 1263153.5782
153 | 2696271.6126 | 1263141.2923
154 | 2696243.9382 | 1263211.9623
155 | 2696259.1235 | 1263205.8083
156 | 2696227.0289 | 1263215.1763
157 | 2696269.1861 | 1263201.2145
158 | 2696223.788 | 1263229.602
159 | 2696237.7178 | 1263178.506
160 | 2696274.8155 | 1263198.6446
161 | 2696220.7148 | 1263229.0961
162 | 2696221.7446 | 1263241.4847
163 | 2696236.4953 | 1263231.6707
164 | 2696243.6036 | 1263160.7873
165 | 2696291.0055 | 1263191.2536
166 | 2696218.2674 | 1263245.8815
167 | 2696219.5366 | 1263260.3793
168 | 2696243.2944 | 1263232.7776
169 | 2696297.7402 | 1263188.2887
170 | 2696284.9801 | 1263219.5936
171 | 2696284.2668 | 1263222.9487
172 | 2696282.1772 | 1263232.7771
173 | 2696218.4576 | 1263279.7027
174 | 2696218.1683 | 1263298.2254
175 | 2696214.2983 | 1263315.0174
176 | 2696217.859 | 1263322.7907
177 | 2696188.6617 | 1263293.6607
178 | 2696211.0768 | 1263366.6627
179 | 2696217.6275 | 1263396.5047
180 | 2696225.3916 | 1263368.7567
181 | 2696403.32 | 1263244.5155
182 | 2696405.0195 | 1263270.5756
183 | 2696387.4962 | 1263242.1733
184 | 2696390.0108 | 1263275.7241
185 | 2696387.3298 | 1263242.1486
186 | 2696349.9478 | 1263211.3521
187 | 2696386.5975 | 1263177.6258
188 | 2696381.8494 | 1263294.597
189 | 2696330.4779 | 1263356.385
190 | 2696312.317 | 1263355.0343
191 | 2696297.7147 | 1263353.5297
192 | 2696460.2538 | 1263305.0303
193 | 2696465.6596 | 1263291.1931
194 | 2696414.2572 | 1263296.0867
195 | 2696412.5519 | 1263290.3564
196 | 2696228.2274 | 1263396.212
197 | 2696256.157 | 1263373.2571
198 | 2696240.2741 | 1263370.9337
199 | 2696257.7368 | 1263364.199
200 | 2696185.1761 | 1263299.5199
201 | 2696443.1325 | 1263072.1238
202 | 2696274.8915 | 1263270.612
203 | 2696276.1293 | 1263263.7419
204 | 2696273.1682 | 1263280.1768
205 | 2696276.2021 | 1263263.3381
206 | 2696272.4618 | 1263284.0976
207 | 2696291.7077 | 1263266.1421
208 | 2696277.3906 | 1263257.2592
209 | 2696271.2738 | 1263290.6913
210 | 2696296.9496 | 1263267.09
211 | 2696278.0092 | 1263254.0953
212 | 2696286.2418 | 1263293.6189
213 | 2696271.1958 | 1263291.1138
214 | 2696364.6437 | 1263213.9671
215 | 2696343.5735 | 1263246.5103
216 | 2696329.3283 | 1263243.3239
217 | 2696339.1252 | 1263266.1587
218 | 2696371.4239 | 1263215.1736
219 | 2696320.7245 | 1263241.3994
220 | 2696337.5875 | 1263272.9506
221 | 2696376.7791 | 1263220.4189
222 | 2695909.6489 | 1263116.8547
223 | 2696258.4265 | 1263360.2444
224 | 2696260.2704 | 1263349.6715
225 | 2696241.9592 | 1263346.1347
226 | 2696273.5196 | 1263351.0366
227 | 2696262.6756 | 1263336.9019
228 | 2696233.2333 | 1263369.9038
229 | 2696277.6116 | 1263351.4583
230 | 2696265.8372 | 1263320.1157
231 | 2696375.762 | 1263226.1017
232 | 2696374.9752 | 1263230.4979
233 | 2696373.7964 | 1263237.0839
234 | 2696321.4682 | 1263334.7008
235 | 2696322.6585 | 1263330.6828
236 | 2696294.3911 | 1263353.1872
237 | 2696280.4763 | 1263351.7535
238 | 2696267.356 | 1263311.8958
239 | 2696281.0566 | 1263323.0979
240 | 2696334.6219 | 1263286.7045
241 | 2696333.7145 | 1263290.9317
242 | 2696336.0824 | 1263279.9005
243 | 2696333.1603 | 1263293.5136
244 | 2696337.3303 | 1263274.0867
245 | 2696331.2482 | 1263302.4218
246 | 2696326.5255 | 1263272.3531
247 | 2696329.5351 | 1263308.058
248 | 2696313.5872 | 1263298.9675
249 | 2696319.5797 | 1263271.2386
250 | 2696306.7502 | 1263297.6302
251 | 2696299.9131 | 1263296.2929
252 | 2696293.0773 | 1263294.9559
253 | 2696327.517 | 1263314.6977
254 | 2696278.7137 | 1263250.4915
255 | 2696312.6339 | 1263270.1242
256 | 2696308.0924 | 1263269.3955
257 | 2696268.6359 | 1263304.9685
258 | 2696267.7368 | 1263309.8345
259 | 2696269.9158 | 1263298.0411
260 | 2696291.0142 | 1263352.8393
261 | 2696287.4346 | 1263352.4704
262 | 2696284.3133 | 1263352.1488
263 | 2696308.0142 | 1263328.073
264 | 2696323.4829 | 1263327.9704
265 | 2696372.6721 | 1263243.3583
266 | 2696371.4915 | 1263249.9403
267 | 2696373.2645 | 1263240.0554
268 | 2696370.8363 | 1263253.5936
269 | 2696386.1423 | 1263241.9719
270 | 2696302.1374 | 1263237.2418
271 | 2696285.7684 | 1263324.0211
272 | 2696325.4995 | 1263321.3355
273 | 2696301.3115 | 1263326.8785
274 | 2696297.1101 | 1263326.1297
275 | 2696469.8928 | 1263280.3575
276 | 2696469.118 | 1263282.3408
277 | 2696473.4535 | 1263271.2431
278 | 2696474.5735 | 1263268.3763
279 | 2696477.413 | 1263261.108
280 | 2696408.4936 | 1263271.859
281 | 2696353.9085 | 1263186.9967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98245 | -0.33662 | 0.0040201 | 0.0010075
1 | 0.98248 | -0.33611 | 0 | 0
2 | 0.98254 | -0.33485 | 0.0011489 | 0.00028793
3 | 0.98247 | -0.33635 | 0.0011489 | 0.00028793
4 | 0.98259 | -0.33398 | 0.0011489 | 0.00028793
5 | 0.97918 | -0.40026 | 0 | 0
6 | 0.97826 | -0.41821 | 0.0015604 | 0.00039108
7 | 0.97987 | -0.38683 | 0.0029421 | 0.00073735
8 | 0.98021 | -0.38012 | 0.0015377 | 0.00038538
9 | 0.98023 | -0.37986 | 0.0015116 | 0.00037884
10 | 0.98264 | -0.33294 | 0.0011489 | 0.00028793
11 | 0.99194 | -0.15505 | 0.002293 | 0.00057468
12 | 0.99199 | -0.15425 | 0 | 0
13 | 0.992 | -0.15403 | 0.0020148 | 0.00050497
14 | 0.99174 | -0.15908 | 0.0014112 | 0.00035368
15 | 0.99232 | -0.14767 | 0.0015429 | 0.00038668
16 | 0.99166 | -0.16058 | 0.0030082 | 0.00075392
17 | 0.99236 | -0.14708 | 0.002774 | 0.00069523
18 | 0.99153 | -0.16304 | 0.0013773 | 0.00034518
19 | 0.99277 | -0.13901 | 0.0016065 | 0.00040263
20 | 0.99277 | -0.139 | 0.0054635 | 0.0013693
21 | 0.9826 | -0.33381 | 0.0053988 | 0.0013531
22 | 0.98258 | -0.33407 | 0.0056287 | 0.0014107
23 | 0.98278 | -0.33033 | 0 | 0
24 | 0.98292 | -0.32743 | 0.0013557 | 0.00033977
25 | 0.98277 | -0.3304 | 0.0013565 | 0.00033997
26 | 0.98422 | -0.30236 | 0.0041798 | 0.0010475
27 | 0.98423 | -0.30217 | 0.0041995 | 0.0010525
28 | 0.98332 | -0.31968 | 0 | 0
29 | 0.9827 | -0.33175 | 0.0011489 | 0.00028793
30 | 0.98434 | -0.29995 | 0 | 0
31 | 0.98256 | -0.33449 | 0.0012337 | 0.00030919
32 | 0.98363 | -0.31369 | 0.0018358 | 0.00046009
33 | 0.98442 | -0.29828 | 0.0020848 | 0.0005225
34 | 0.99328 | -0.12921 | 0.0019293 | 0.00048352
35 | 0.99374 | -0.12023 | 0 | 0
36 | 0.99419 | -0.1116 | 0 | 0
37 | 0.99479 | -0.10011 | 0 | 0
38 | 0.99416 | -0.11212 | 0.0023374 | 0.0005858
39 | 0.99453 | -0.10513 | 0.0032655 | 0.0008184
40 | 0.99458 | -0.10417 | 0 | 0
41 | 0.98459 | -0.29503 | 0 | 0
42 | 0.99416 | -0.11222 | 0.0018687 | 0.00046833
43 | 0.98659 | -0.25645 | 0.0018887 | 0.00047334
44 | 0.98033 | -0.37777 | 0.001317 | 0.00033008
45 | 0.9803 | -0.37841 | 0.0012744 | 0.00031939
46 | 0.98041 | -0.37616 | 0 | 0
47 | 0.98171 | -0.35086 | 0 | 0
48 | 0.98157 | -0.35372 | 0.0033598 | 0.00084205
49 | 0.98144 | -0.35616 | 0.0034478 | 0.0008641
50 | 0.98832 | -0.22461 | 0.0011598 | 0.00029067
51 | 0.98829 | -0.2252 | 0.0014392 | 0.00036071
52 | 0.9884 | -0.22301 | 0 | 0
53 | 0.98828 | -0.22532 | 0.0023589 | 0.00059119
54 | 0.98825 | -0.22603 | 0 | 0
55 | 0.98881 | -0.21508 | 0.0012985 | 0.00032544
56 | 0.98819 | -0.22718 | 0.0013538 | 0.00033931
57 | 0.9878 | -0.23473 | 0.00098223 | 0.00024617
58 | 0.98938 | -0.20407 | 0.001885 | 0.00047243
59 | 0.98817 | -0.22754 | 0 | 0
60 | 0.98755 | -0.2396 | 0.0015627 | 0.00039165
61 | 0.98986 | -0.19471 | 0 | 0
62 | 0.99144 | -0.16486 | 0.00095466 | 0.00023926
63 | 0.99139 | -0.16573 | 0.00094883 | 0.0002378
64 | 0.99133 | -0.16697 | 0.00090721 | 0.00022737
65 | 0.99438 | -0.10789 | 0.0013554 | 0.00033969
66 | 0.99462 | -0.10334 | 0 | 0
67 | 0.99422 | -0.11114 | 0.0012404 | 0.00031086
68 | 0.99454 | -0.10484 | 0.003375 | 0.00084586
69 | 0.99551 | -0.086204 | 0.0053052 | 0.0013296
70 | 0.99419 | -0.11167 | 0.0012997 | 0.00032574
71 | 0.99863 | -0.0262 | 0 | 0
72 | 1 | 0 | -0.50558 | -0.12827
73 | 0.99812 | -0.035934 | 0 | 0
74 | 0.9984 | -0.030633 | 0.0035575 | 0.00089159
75 | 0.99453 | -0.10514 | 0.0010943 | 0.00027426
76 | 0.99406 | -0.11417 | 0.00096286 | 0.00024131
77 | 0.99403 | -0.11481 | 0.0015561 | 0.00038998
78 | 0.994 | -0.11537 | 0.00096285 | 0.00024131
79 | 0.97786 | -0.4259 | 0.0015597 | 0.0003909
80 | 0.98671 | -0.25608 | 0.00046056 | 0.00011543
81 | 0.98676 | -0.25509 | 0.00079201 | 0.0001985
82 | 0.98669 | -0.25645 | 0.0021222 | 0.00053187
83 | 0.98707 | -0.24893 | 0 | 0
84 | 0.98666 | -0.25695 | 0 | 0
85 | 0.98694 | -0.25152 | 0.00089422 | 0.00022411
86 | 0.98713 | -0.24781 | 0.00035314 | 8.8505e-05
87 | 0.9866 | -0.25813 | 0 | 0
88 | 0.98683 | -0.25369 | 0.0021748 | 0.00054507
89 | 0.98732 | -0.24401 | 0.0015627 | 0.00039165
90 | 0.98816 | -0.22779 | 0.00053424 | 0.00013389
91 | 0.98682 | -0.25388 | 0.0033326 | 0.00083522
92 | 0.99561 | -0.083906 | 0.0021686 | 0.0005435
93 | 0.99563 | -0.083622 | 0 | 0
94 | 0.99095 | -0.17366 | 0.0017834 | 0.00044696
95 | 0.99098 | -0.17307 | 0.0026651 | 0.00066793
96 | 0.99566 | -0.082927 | 0 | 0
97 | 0.99104 | -0.17176 | 0.0029166 | 0.00073098
98 | 0.99618 | -0.072834 | 0.0083149 | 0.0020839
99 | 0.9955 | -0.085966 | 0.0014219 | 0.00035635
100 | 0.99527 | -0.090485 | 0 | 0
101 | 0.99484 | -0.098722 | 0 | 0
102 | 0.99667 | -0.063451 | 0.01083 | 0.0027143
103 | 0.99466 | -0.10226 | 0.0018089 | 0.00045335
104 | 0.99482 | -0.099269 | 0.0040067 | 0.0010042
105 | 0.97063 | -0.56834 | 0.0029458 | 0.00073828
106 | 0.97059 | -0.56914 | 0.0035752 | 0.00089603
107 | 0.97082 | -0.56458 | 0 | 0
108 | 0.97099 | -0.56115 | 0 | 0
109 | 0.97114 | -0.55812 | 0.0087427 | 0.0021911
110 | 0.97146 | -0.5519 | 0 | 0
111 | 0.99448 | -0.10569 | 0.005337 | 0.0013376
112 | 0.99439 | -0.10743 | 0.0024773 | 0.00062087
113 | 0.98722 | -0.24426 | 0.0020295 | 0.00050865
114 | 0.98822 | -0.22501 | 0.0015856 | 0.0003974
115 | 0.98923 | -0.20556 | 0.0018229 | 0.00045686
116 | 0.98923 | -0.20552 | 0.0015856 | 0.0003974
117 | 0.98973 | -0.19598 | 0.0018209 | 0.00045636
118 | 0.99001 | -0.19063 | 0.0016745 | 0.00041967
119 | 0.99032 | -0.18459 | 0.0027421 | 0.00068724
120 | 0.99049 | -0.18136 | 0.0043536 | 0.0010911
121 | 0.99087 | -0.17405 | 0.0044027 | 0.0011034
122 | 0.99155 | -0.1611 | 0.0045183 | 0.0011324
123 | 0.99248 | -0.14316 | 0 | 0
124 | 0.99219 | -0.14889 | 0 | 0
125 | 0.99224 | -0.14792 | 0 | 0
126 | 0.99217 | -0.14919 | 0.0055434 | 0.0013893
127 | 0.99577 | -0.080358 | 0.0078288 | 0.0019621
128 | 0.99593 | -0.077288 | 0.0039689 | 0.0009947
129 | 0.99453 | -0.10408 | 0.011915 | 0.0029861
130 | 0.99682 | -0.060414 | 0 | 0
131 | 0.99335 | -0.12662 | 0.0050841 | 0.0012742
132 | 0.99745 | -0.048391 | 0 | 0
133 | 0.99334 | -0.12679 | 0.0050792 | 0.001273
134 | 0.99738 | -0.050251 | 0.0081386 | 0.0020397
135 | 0.99774 | -0.042919 | 0 | 0
136 | 0.99333 | -0.12694 | 0.0044398 | 0.0011127
137 | 0.97551 | -0.47204 | 0.0024318 | 0.00060947
138 | 0.97559 | -0.47037 | 0 | 0
139 | 0.97673 | -0.44815 | 0.0052985 | 0.0013279
140 | 0.97443 | -0.49324 | 0.0034222 | 0.00085768
141 | 0.97703 | -0.44232 | 0.0015831 | 0.00039677
142 | 0.97411 | -0.49961 | 0.0027129 | 0.00067991
143 | 0.99238 | -0.14509 | 0.0040966 | 0.0010267
144 | 0.99221 | -0.14844 | 0.0034956 | 0.00087608
145 | 0.97779 | -0.42734 | 0.0024051 | 0.00060277
146 | 0.97311 | -0.51918 | 0 | 0
147 | 0.99435 | -0.10834 | 0.0052775 | 0.0013227
148 | 0.97181 | -0.5449 | 0.016845 | 0.0042218
149 | 0.9992 | -0.015103 | 0.0024723 | 0.00061961
150 | 0.9969 | -0.058949 | 0.0049179 | 0.0012325
151 | 0.99651 | -0.066415 | 0.0034458 | 0.0008636
152 | 0.99156 | -0.16174 | 0.0012272 | 0.00030756
153 | 0.99158 | -0.16131 | 0.0012578 | 0.00031523
154 | 0.99286 | -0.1367 | 0.0020961 | 0.00052532
155 | 0.99379 | -0.11879 | 0.0018537 | 0.00046458
156 | 0.99192 | -0.15483 | 0 | 0
157 | 0.99443 | -0.10641 | 0.0009864 | 0.00024721
158 | 0.99118 | -0.16913 | 0 | 0
159 | 0.99175 | -0.15819 | 0.0010317 | 0.00025856
160 | 0.99479 | -0.099386 | 0.00098508 | 0.00024689
161 | 0.99107 | -0.17133 | 0 | 0
162 | 0.99106 | -0.17148 | 0.0019637 | 0.00049216
163 | 0.99114 | -0.17 | 0.0024136 | 0.0006049
164 | 0.99168 | -0.15949 | 0.0014376 | 0.00036029
165 | 0.99586 | -0.078896 | 0 | 0
166 | 0.99056 | -0.1811 | 0.0016963 | 0.00042513
167 | 0.9909 | -0.17451 | 0.0018505 | 0.00046377
168 | 0.99113 | -0.17017 | 0.0013699 | 0.00034333
169 | 0.99638 | -0.068959 | 0.0021438 | 0.00053729
170 | 0.99351 | -0.12398 | 0.002326 | 0.00058296
171 | 0.99324 | -0.12919 | 0.0018529 | 0.00046437
172 | 0.99246 | -0.14414 | 0 | 0
173 | 0.99078 | -0.17697 | 0.003303 | 0.00082782
174 | 0.99071 | -0.17823 | 0.0022471 | 0.00056317
175 | 0.99069 | -0.17872 | 0 | 0
176 | 0.99067 | -0.17896 | 0.0015863 | 0.00039757
177 | 0.98968 | -0.19821 | 0 | 0
178 | 0.98647 | -0.26025 | 0 | 0
179 | 0.98643 | -0.26106 | 0 | 0
180 | 0.98649 | -0.25991 | 0.0013763 | 0.00034494
181 | 0.99717 | -0.054411 | 0 | 0
182 | 0.99707 | -0.056332 | 0 | 0
183 | 0.99723 | -0.053234 | 0.0010312 | 0.00025845
184 | 0.99701 | -0.057499 | 0.0010312 | 0.00025845
185 | 0.99723 | -0.053219 | 0.0010312 | 0.00025845
186 | 0.99813 | -0.035874 | 0 | 0
187 | 0.9961 | -0.074725 | 0.0053046 | 0.0013295
188 | 0.99695 | -0.05864 | 0.0031628 | 0.00079268
189 | 0.98639 | -0.26181 | 0.0019435 | 0.00048709
190 | 0.98642 | -0.26118 | 0 | 0
191 | 0.98645 | -0.26066 | 0.0011747 | 0.00029441
192 | 0.99115 | -0.17054 | 0.001521 | 0.00038121
193 | 0.99117 | -0.17014 | 0.0010091 | 0.00025291
194 | 0.99394 | -0.11643 | 0.00096142 | 0.00024096
195 | 0.99395 | -0.11633 | 0.00096214 | 0.00024113
196 | 0.98641 | -0.26131 | 0.0013102 | 0.00032836
197 | 0.9866 | -0.25764 | 0 | 0
198 | 0.98653 | -0.25904 | 0.0011065 | 0.00027732
199 | 0.98664 | -0.25684 | 0.0011837 | 0.00029666
200 | 0.98965 | -0.19888 | 0.005578 | 0.001398
201 | 0.98141 | -0.35691 | 0.0052684 | 0.0013204
202 | 0.98957 | -0.19997 | 0.0014013 | 0.00035121
203 | 0.99006 | -0.1905 | 0.0013699 | 0.00034333
204 | 0.9889 | -0.21292 | 0.0013887 | 0.00034805
205 | 0.99009 | -0.18994 | 0 | 0
206 | 0.98863 | -0.21814 | 0.0014221 | 0.00035642
207 | 0.99005 | -0.19065 | 0.0012542 | 0.00031432
208 | 0.99054 | -0.18111 | 0.0013677 | 0.00034278
209 | 0.98819 | -0.22675 | 0 | 0
210 | 0.99005 | -0.19077 | 0.0012939 | 0.00032428
211 | 0.99079 | -0.17645 | 0.0012545 | 0.00031441
212 | 0.98764 | -0.2374 | 0.0011976 | 0.00030014
213 | 0.98818 | -0.227 | 0.0014199 | 0.00035586
214 | 0.99784 | -0.04134 | 0.0017595 | 0.00044096
215 | 0.98557 | -0.27766 | 0 | 0
216 | 0.98549 | -0.27925 | 0.0016972 | 0.00042535
217 | 0.98569 | -0.27548 | 0.0011859 | 0.00029721
218 | 0.99772 | -0.043651 | 0.0014293 | 0.00035822
219 | 0.98546 | -0.27994 | 0.0015767 | 0.00039515
220 | 0.98573 | -0.27457 | 0.0011877 | 0.00029767
221 | 0.99759 | -0.046171 | 0.0010952 | 0.00027449
222 | 0.98653 | -0.25945 | 0.00088267 | 0.00022122
223 | 0.98667 | -0.25641 | 0.0011847 | 0.0002969
224 | 0.98674 | -0.25501 | 0 | 0
225 | 0.98666 | -0.25648 | 0.0044024 | 0.0011033
226 | 0.9866 | -0.25773 | 0.001186 | 0.00029724
227 | 0.98701 | -0.24966 | 0.0011747 | 0.00029441
228 | 0.98651 | -0.25952 | 0.0010776 | 0.00027008
229 | 0.98656 | -0.25848 | 0.0011742 | 0.00029428
230 | 0.98739 | -0.24226 | 0 | 0
231 | 0.99751 | -0.047853 | 0.0010952 | 0.00027449
232 | 0.99744 | -0.04907 | 0.0013709 | 0.00034358
233 | 0.99736 | -0.050731 | 0.0013523 | 0.00033892
234 | 0.98586 | -0.27208 | 0.0019435 | 0.00048709
235 | 0.98587 | -0.27194 | 0 | 0
236 | 0.98646 | -0.26048 | 0.0011854 | 0.0002971
237 | 0.98653 | -0.25895 | 0.0011847 | 0.0002969
238 | 0.98759 | -0.23832 | 0.0012813 | 0.00032113
239 | 0.98736 | -0.24287 | 0.0010929 | 0.00027391
240 | 0.98591 | -0.2711 | 0.0011849 | 0.00029695
241 | 0.98597 | -0.26986 | 0.001237 | 0.00031001
242 | 0.98582 | -0.27294 | 0.0011852 | 0.00029705
243 | 0.98602 | -0.26905 | 0.0011867 | 0.00029742
244 | 0.98574 | -0.2744 | 0 | 0
245 | 0.98617 | -0.26604 | 0 | 0
246 | 0.98569 | -0.27541 | 0.0012945 | 0.00032442
247 | 0.98609 | -0.26758 | 0.001942 | 0.00048672
248 | 0.98672 | -0.2554 | 0.001236 | 0.00030978
249 | 0.98566 | -0.2759 | 0.0012948 | 0.00032451
250 | 0.98694 | -0.25112 | 0.0012347 | 0.00030945
251 | 0.98716 | -0.2467 | 0.0012359 | 0.00030974
252 | 0.9874 | -0.24213 | 0.0011977 | 0.00030018
253 | 0.98601 | -0.26916 | 0.001942 | 0.00048672
254 | 0.99107 | -0.17105 | 0.0013699 | 0.00034333
255 | 0.98565 | -0.27623 | 0.0012945 | 0.00032442
256 | 0.98564 | -0.27634 | 0.0012952 | 0.00032462
257 | 0.98778 | -0.23474 | 0.0012793 | 0.00032063
258 | 0.98765 | -0.23728 | 0.0010941 | 0.00027421
259 | 0.98797 | -0.23096 | 0.0014221 | 0.00035641
260 | 0.98647 | -0.26022 | 0.0011755 | 0.0002946
261 | 0.98649 | -0.25986 | 0.0011853 | 0.00029708
262 | 0.98651 | -0.25949 | 0.0011747 | 0.00029441
263 | 0.9858 | -0.27325 | 0.0019085 | 0.00047832
264 | 0.98588 | -0.27159 | 0.0019406 | 0.00048637
265 | 0.99731 | -0.051731 | 0.0013575 | 0.00034023
266 | 0.99728 | -0.052213 | 0.001352 | 0.00033885
267 | 0.99732 | -0.05141 | 0 | 0
268 | 0.99727 | -0.052393 | 0.0027603 | 0.00069179
269 | 0.99724 | -0.053087 | 0.0010932 | 0.00027397
270 | 0.98541 | -0.28089 | 0.0027769 | 0.00069595
271 | 0.98736 | -0.24296 | 0.0010949 | 0.00027441
272 | 0.98594 | -0.2705 | 0.0019402 | 0.00048626
273 | 0.98578 | -0.27362 | 0.0019074 | 0.00047803
274 | 0.98578 | -0.2737 | 0.0010947 | 0.00027436
275 | 0.9912 | -0.16957 | 0.000907 | 0.00022731
276 | 0.99119 | -0.16971 | 0.0012359 | 0.00030974
277 | 0.99124 | -0.16876 | 0.001477 | 0.00037016
278 | 0.99125 | -0.16842 | 0.00096195 | 0.00024109
279 | 0.9913 | -0.16744 | 0.00098529 | 0.00024694
280 | 0.99398 | -0.11569 | 0.00096143 | 0.00024096
281 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0040201 | -0.0010075 | 0.0040202 | 0.0010075 | 9.7485e-08 | -2.6405e-08 | 0.0060888 | 0.0060888 | 0.0060888 | 0.98245 | -0.33662 | 0.98248 | -0.33611 | 1.6727
1 | -0.0051691 | -0.0012953 | 0.0051694 | 0.0012953 | 3.1189e-07 | 2.775e-08 | 0.0078288 | 0.0078287 | 0.0078288 | 0.98248 | -0.33611 | 0.98254 | -0.33485 | 2.1508
2 | 0.0011489 | 0.0002878 | -0.0011489 | -0.00028793 | 1.28e-08 | -1.3457e-07 | 0.00174 | 0.00174 | 0.00174 | 0.98248 | -0.33611 | 0.98247 | -0.33635 | 0.47803
3 | -0.0063183 | -0.0015833 | 0.0063185 | 0.0015833 | 2.627e-07 | 7.1219e-08 | 0.0095686 | 0.0095686 | 0.0095686 | 0.98254 | -0.33485 | 0.98259 | -0.33398 | 2.6287
4 | -0.0074674 | -0.0018713 | 0.0074678 | 0.0018714 | 3.6705e-07 | 1.3796e-07 | 0.011308 | 0.011308 | 0.011308 | 0.98259 | -0.33398 | 0.98264 | -0.33294 | 3.1067
5 | 0.053377 | 0.013487 | -0.053331 | -0.013458 | 4.5883e-05 | 2.9131e-05 | 0.081154 | 0.081154 | 0.081154 | 0.97918 | -0.40026 | 0.97826 | -0.41821 | 22.295
6 | -0.053377 | -0.013487 | 0.053411 | 0.013509 | 3.4378e-05 | 2.1827e-05 | 0.081154 | 0.081154 | 0.081154 | 0.97918 | -0.40026 | 0.97987 | -0.38683 | 22.295
7 | 0.05177 | 0.013067 | -0.051751 | -0.013055 | 1.9069e-05 | 1.2101e-05 | 0.07878 | 0.07878 | 0.07878 | 0.97826 | -0.41821 | 0.97786 | -0.4259 | 21.643
8 | -0.056353 | -0.014246 | 0.056382 | 0.014265 | 2.8869e-05 | 1.8344e-05 | 0.085622 | 0.085622 | 0.085622 | 0.97987 | -0.38683 | 0.98041 | -0.37616 | 23.5224
9 | -0.0015377 | -0.00038538 | 0.0015377 | 0.00038527 | 1.8835e-08 | -1.0414e-07 | 0.0023343 | 0.0023342 | 0.0023343 | 0.98021 | -0.38012 | 0.98023 | -0.37986 | 0.64129
10 | -0.0030493 | -0.00076412 | 0.0030495 | 0.00076392 | 2.1042e-07 | -1.9548e-07 | 0.0046289 | 0.0046288 | 0.0046289 | 0.98023 | -0.37986 | 0.9803 | -0.37841 | 1.2717
11 | -0.0086166 | -0.0021593 | 0.0086171 | 0.0021596 | 4.885e-07 | 2.1571e-07 | 0.013048 | 0.013048 | 0.013048 | 0.98264 | -0.33294 | 0.9827 | -0.33175 | 3.5846
12 | -0.002293 | -0.00057468 | 0.0022931 | 0.00057448 | 8.7515e-08 | -1.9863e-07 | 0.0034397 | 0.0034396 | 0.0034397 | 0.99194 | -0.15505 | 0.99199 | -0.15425 | 0.94498
13 | -0.019007 | -0.0047656 | 0.019007 | 0.0047657 | 1.9383e-07 | 1.1584e-07 | 0.028512 | 0.028512 | 0.028512 | 0.99199 | -0.15425 | 0.992 | -0.15403 | 7.8329
14 | 0.016714 | 0.0041911 | -0.01671 | -0.0041888 | 3.8493e-06 | 2.2528e-06 | 0.025072 | 0.025072 | 0.025072 | 0.99199 | -0.15425 | 0.99174 | -0.15908 | 6.888
15 | -0.021022 | -0.0052706 | 0.021028 | 0.0052745 | 6.3757e-06 | 3.8596e-06 | 0.031534 | 0.031534 | 0.031534 | 0.992 | -0.15403 | 0.99232 | -0.14767 | 8.6632
16 | 0.015299 | 0.0038351 | -0.015298 | -0.0038345 | 1.0947e-06 | 6.2914e-07 | 0.022955 | 0.022955 | 0.022955 | 0.99174 | -0.15908 | 0.99166 | -0.16058 | 6.3063
17 | -0.022571 | -0.0056612 | 0.022572 | 0.0056616 | 6.3807e-07 | 3.8917e-07 | 0.033848 | 0.033848 | 0.033848 | 0.99232 | -0.14767 | 0.99236 | -0.14708 | 9.2988
18 | 0.012289 | 0.0030806 | -0.012288 | -0.0030798 | 1.4366e-06 | 7.7411e-07 | 0.018441 | 0.018441 | 0.018441 | 0.99166 | -0.16058 | 0.99153 | -0.16304 | 5.0662
19 | -0.025346 | -0.0063568 | 0.025356 | 0.0063628 | 9.7557e-06 | 6.0109e-06 | 0.038007 | 0.038007 | 0.038007 | 0.99236 | -0.14708 | 0.99277 | -0.13901 | 10.4415
20 | 0.010911 | 0.0027346 | -0.01091 | -0.0027342 | 9.4636e-07 | 4.8428e-07 | 0.016374 | 0.016374 | 0.016374 | 0.99153 | -0.16304 | 0.99144 | -0.16486 | 4.4984
21 | -0.026962 | -0.0067654 | 0.026962 | 0.0067655 | 1.1479e-08 | 7.1047e-09 | 0.040415 | 0.040415 | 0.040415 | 0.99277 | -0.13901 | 0.99277 | -0.139 | 11.103
22 | -0.032426 | -0.0081347 | 0.032441 | 0.0081442 | 1.5133e-05 | 9.4639e-06 | 0.048604 | 0.048604 | 0.048604 | 0.99277 | -0.139 | 0.99328 | -0.12921 | 13.3527
23 | 0.0056288 | 0.0014107 | -0.0056287 | -0.0014107 | 7.0552e-08 | 1.2356e-08 | 0.0085241 | 0.0085241 | 0.0085241 | 0.9826 | -0.33381 | 0.98258 | -0.33407 | 2.3418
24 | -0.011028 | -0.0027638 | 0.011029 | 0.0027647 | 1.8287e-06 | 9.4883e-07 | 0.0167 | 0.0167 | 0.0167 | 0.9826 | -0.33381 | 0.98278 | -0.33033 | 4.5879
25 | -0.022153 | -0.0055525 | 0.022156 | 0.0055544 | 3.0606e-06 | 1.8668e-06 | 0.033541 | 0.033541 | 0.033541 | 0.98278 | -0.33033 | 0.98292 | -0.32743 | 9.2147
26 | 0.011123 | 0.0027878 | -0.011123 | -0.0027878 | 4.1655e-08 | 2.1697e-08 | 0.016842 | 0.016842 | 0.016842 | 0.98278 | -0.33033 | 0.98277 | -0.3304 | 4.6268
27 | -0.023511 | -0.0058941 | 0.02352 | 0.0058995 | 8.6805e-06 | 5.3238e-06 | 0.035594 | 0.035594 | 0.035594 | 0.98292 | -0.32743 | 0.98332 | -0.31968 | 9.7785
28 | 0.0097666 | 0.0024478 | -0.009766 | -0.0024475 | 6.2766e-07 | 3.0472e-07 | 0.014788 | 0.014788 | 0.014788 | 0.98277 | -0.3304 | 0.9827 | -0.33175 | 4.0626
29 | -0.0041798 | -0.0010475 | 0.0041798 | 0.0010475 | 3.858e-08 | -8.0494e-09 | 0.0063193 | 0.0063193 | 0.0063193 | 0.98422 | -0.30236 | 0.98423 | -0.30217 | 1.7361
30 | -0.0083793 | -0.0021 | 0.0083801 | 0.0021004 | 8.8248e-07 | 3.7841e-07 | 0.012668 | 0.012668 | 0.012668 | 0.98423 | -0.30217 | 0.98434 | -0.29995 | 3.4803
31 | 0.075523 | 0.019135 | -0.07547 | -0.0191 | 5.3679e-05 | 3.4216e-05 | 0.11436 | 0.11436 | 0.11436 | 0.98332 | -0.31968 | 0.98256 | -0.33449 | 31.4177
32 | -0.099043 | -0.025034 | 0.099072 | 0.025052 | 2.8451e-05 | 1.8166e-05 | 0.14995 | 0.14995 | 0.14995 | 0.98332 | -0.31968 | 0.98363 | -0.31369 | 41.1961
33 | -0.0083801 | -0.0021004 | 0.0083808 | 0.0021007 | 6.6805e-07 | 2.8643e-07 | 0.012668 | 0.012668 | 0.012668 | 0.98434 | -0.29995 | 0.98442 | -0.29828 | 3.4803
34 | 0.074236 | 0.018791 | -0.074178 | -0.018754 | 5.8296e-05 | 3.7154e-05 | 0.11249 | 0.11249 | 0.11249 | 0.98256 | -0.33449 | 0.98171 | -0.35086 | 30.9044
35 | -0.10091 | -0.025512 | 0.101 | 0.02557 | 9.038e-05 | 5.7712e-05 | 0.15273 | 0.15273 | 0.15273 | 0.98363 | -0.31369 | 0.98459 | -0.29503 | 41.959
36 | -0.010466 | -0.0026232 | 0.010467 | 0.002624 | 1.619e-06 | 8.1679e-07 | 0.01582 | 0.015819 | 0.01582 | 0.98442 | -0.29828 | 0.98459 | -0.29503 | 4.346
37 | -0.03437 | -0.0086277 | 0.034385 | 0.008637 | 1.4731e-05 | 9.2359e-06 | 0.051494 | 0.051494 | 0.051494 | 0.99328 | -0.12921 | 0.99374 | -0.12023 | 14.1467
38 | -0.034385 | -0.008637 | 0.034399 | 0.0086459 | 1.4176e-05 | 8.8876e-06 | 0.051494 | 0.051494 | 0.051494 | 0.99374 | -0.12023 | 0.99419 | -0.1116 | 14.1467
39 | -0.038605 | -0.0096999 | 0.038626 | 0.0097133 | 2.117e-05 | 1.3329e-05 | 0.057789 | 0.057789 | 0.057789 | 0.99419 | -0.1116 | 0.99479 | -0.10011 | 15.8762
40 | 0.0042062 | 0.0010541 | -0.0042061 | -0.0010541 | 1.0414e-07 | -2.4211e-08 | 0.0062954 | 0.0062954 | 0.0062954 | 0.99419 | -0.1116 | 0.99416 | -0.11212 | 1.7295
41 | -0.056632 | -0.014227 | 0.056669 | 0.014251 | 3.7622e-05 | 2.3896e-05 | 0.084722 | 0.084722 | 0.084722 | 0.99479 | -0.10011 | 0.99551 | -0.086204 | 23.2754
42 | 0.018005 | 0.0045135 | -0.018003 | -0.0045118 | 2.7694e-06 | 1.6403e-06 | 0.026933 | 0.026933 | 0.026933 | 0.99479 | -0.10011 | 0.99462 | -0.10334 | 7.3992
43 | 0.0018687 | 0.0004683 | -0.0018687 | -0.00046833 | 9.3554e-09 | -3.5364e-08 | 0.0027969 | 0.002797 | 0.002797 | 0.99416 | -0.11212 | 0.99416 | -0.11222 | 0.7684
44 | -0.0032655 | -0.0008184 | 0.0032656 | 0.00081828 | 1.4943e-07 | -1.2098e-07 | 0.0048858 | 0.0048857 | 0.0048858 | 0.99453 | -0.10513 | 0.99458 | -0.10417 | 1.3423
45 | 0.010267 | 0.0025734 | -0.010265 | -0.0025725 | 1.8198e-06 | 8.9781e-07 | 0.015361 | 0.015361 | 0.015361 | 0.99458 | -0.10417 | 0.99438 | -0.10789 | 4.2199
46 | -0.013532 | -0.0033917 | 0.013533 | 0.003392 | 5.3401e-07 | 2.9668e-07 | 0.020246 | 0.020246 | 0.020246 | 0.99458 | -0.10417 | 0.99462 | -0.10334 | 5.5622
47 | -0.11147 | -0.028194 | 0.11167 | 0.028326 | 0.00020675 | 0.00013207 | 0.16855 | 0.16855 | 0.16855 | 0.98459 | -0.29503 | 0.98659 | -0.25645 | 46.305
48 | -0.11356 | -0.028799 | 0.11363 | 0.028842 | 6.6586e-05 | 4.2538e-05 | 0.1714 | 0.1714 | 0.1714 | 0.98659 | -0.25645 | 0.98722 | -0.24426 | 47.0875
49 | 0.004324 | 0.0010833 | -0.0043239 | -0.0010833 | 1.3364e-07 | -1.878e-08 | 0.0065631 | 0.0065632 | 0.0065632 | 0.98033 | -0.37777 | 0.9803 | -0.37841 | 1.8031
50 | -0.005641 | -0.0014134 | 0.0056415 | 0.0014134 | 4.3213e-07 | 7.836e-08 | 0.0085622 | 0.0085621 | 0.0085622 | 0.98033 | -0.37777 | 0.98041 | -0.37616 | 2.3523
51 | -0.062023 | -0.015678 | 0.062099 | 0.015726 | 7.5338e-05 | 4.793e-05 | 0.094184 | 0.094184 | 0.094184 | 0.98041 | -0.37616 | 0.98171 | -0.35086 | 25.8746
52 | 0.012079 | 0.0030279 | -0.012077 | -0.003027 | 1.6443e-06 | 8.8698e-07 | 0.018309 | 0.018309 | 0.018309 | 0.98171 | -0.35086 | 0.98157 | -0.35372 | 5.0298
53 | 0.0087174 | 0.002185 | -0.0087164 | -0.0021845 | 1.0162e-06 | 4.5425e-07 | 0.013215 | 0.013215 | 0.013215 | 0.98157 | -0.35372 | 0.98144 | -0.35616 | 3.6306
54 | 0.0052686 | 0.0013204 | -0.0052684 | -0.0013204 | 1.8654e-07 | 2.0872e-08 | 0.0079879 | 0.007988 | 0.007988 | 0.98144 | -0.35616 | 0.98141 | -0.35691 | 2.1945
55 | 0.0037983 | 0.00095183 | -0.0037981 | -0.00095188 | 1.0695e-07 | -4.3306e-08 | 0.0057186 | 0.0057187 | 0.0057187 | 0.98832 | -0.22461 | 0.98829 | -0.2252 | 1.5711
56 | -0.004958 | -0.0012425 | 0.0049584 | 0.0012425 | 3.7805e-07 | 1.0089e-08 | 0.0074648 | 0.0074647 | 0.0074648 | 0.98832 | -0.22461 | 0.9884 | -0.22301 | 2.0508
57 | 0.0023589 | 0.00059117 | -0.0023589 | -0.00059119 | 1.2871e-08 | -2.6627e-08 | 0.0035517 | 0.0035517 | 0.0035517 | 0.98829 | -0.2252 | 0.98828 | -0.22532 | 0.97574
58 | 0.017028 | 0.0042674 | -0.017026 | -0.004266 | 2.4481e-06 | 1.4395e-06 | 0.025635 | 0.025635 | 0.025635 | 0.9884 | -0.22301 | 0.98825 | -0.22603 | 7.0427
59 | -0.021987 | -0.0055099 | 0.021995 | 0.005515 | 8.3105e-06 | 5.0594e-06 | 0.0331 | 0.0331 | 0.0331 | 0.9884 | -0.22301 | 0.98881 | -0.21508 | 9.0934
60 | 0.0018882 | 0.00047202 | -0.0018881 | -0.00047239 | 1.0385e-07 | -3.726e-07 | 0.0028427 | 0.0028428 | 0.0028428 | 0.98825 | -0.22603 | 0.98819 | -0.22718 | 0.781
61 | 0.015138 | 0.0037939 | -0.015131 | -0.0037903 | 6.2765e-06 | 3.6043e-06 | 0.022793 | 0.022793 | 0.022793 | 0.98825 | -0.22603 | 0.9878 | -0.23473 | 6.2618
62 | -0.023293 | -0.0058404 | 0.023306 | 0.0058479 | 1.223e-05 | 7.4868e-06 | 0.035054 | 0.035054 | 0.035054 | 0.98881 | -0.21508 | 0.98938 | -0.20407 | 9.6302
63 | 0.00053426 | 0.00013309 | -0.00053425 | -0.00013356 | 9.1474e-09 | -4.7724e-07 | 0.0008042 | 0.00080437 | 0.00080437 | 0.98819 | -0.22718 | 0.98817 | -0.22754 | 0.22098
64 | 0.014149 | 0.0035442 | -0.014146 | -0.0035423 | 3.2784e-06 | 1.8519e-06 | 0.021313 | 0.021313 | 0.021313 | 0.9878 | -0.23473 | 0.98755 | -0.2396 | 5.8553
65 | -0.025191 | -0.0063203 | 0.025202 | 0.0063273 | 1.1248e-05 | 6.9305e-06 | 0.037889 | 0.037889 | 0.037889 | 0.98938 | -0.20407 | 0.98986 | -0.19471 | 10.4091
66 | 0.00053425 | 0.00013356 | -0.00053424 | -0.00013389 | 6.3355e-09 | -3.304e-07 | 0.00080437 | 0.00080449 | 0.00080449 | 0.98817 | -0.22754 | 0.98816 | -0.22779 | 0.22101
67 | 0.012583 | 0.0031507 | -0.01258 | -0.0031492 | 2.6429e-06 | 1.4406e-06 | 0.018959 | 0.018959 | 0.018959 | 0.98755 | -0.2396 | 0.98732 | -0.24401 | 5.2085
68 | 0.0055791 | 0.0013981 | -0.0055782 | -0.001398 | 9.3043e-07 | 1.4213e-07 | 0.0083868 | 0.0083869 | 0.0083869 | 0.98986 | -0.19471 | 0.98968 | -0.19821 | 2.3041
69 | -0.030781 | -0.0077254 | 0.030801 | 0.0077379 | 1.9986e-05 | 1.2471e-05 | 0.046276 | 0.046276 | 0.046276 | 0.98986 | -0.19471 | 0.99056 | -0.1811 | 12.7131
70 | 0.0099551 | 0.0024949 | -0.0099547 | -0.0024947 | 4.1512e-07 | 2.0174e-07 | 0.014941 | 0.014941 | 0.014941 | 0.99144 | -0.16486 | 0.99139 | -0.16573 | 4.1048
71 | 0.0090059 | 0.0022569 | -0.0090053 | -0.0022567 | 5.3203e-07 | 2.4038e-07 | 0.013517 | 0.013517 | 0.013517 | 0.99139 | -0.16573 | 0.99133 | -0.16697 | 3.7135
72 | 0.0080981 | 0.0020293 | -0.008098 | -0.0020292 | 1.7897e-07 | 7.29e-08 | 0.012155 | 0.012155 | 0.012155 | 0.99133 | -0.16697 | 0.9913 | -0.16744 | 3.3394
73 | 0.0089095 | 0.0022328 | -0.0089082 | -0.0022322 | 1.3796e-06 | 6.1452e-07 | 0.013332 | 0.013332 | 0.013332 | 0.99438 | -0.10789 | 0.99422 | -0.11114 | 3.6628
74 | 0.0044697 | 0.0011199 | -0.0044693 | -0.0011199 | 3.1845e-07 | -4.2658e-08 | 0.0066868 | 0.0066869 | 0.0066869 | 0.99462 | -0.10334 | 0.99454 | -0.10484 | 1.8371
75 | 0.0076678 | 0.0019213 | -0.0076676 | -0.0019212 | 1.9146e-07 | 7.2263e-08 | 0.011476 | 0.011476 | 0.011476 | 0.99422 | -0.11114 | 0.99419 | -0.11167 | 3.1528
76 | 0.0010943 | 0.00027406 | -0.0010943 | -0.00027426 | 1.561e-08 | -1.9152e-07 | 0.0016372 | 0.0016373 | 0.0016373 | 0.99454 | -0.10484 | 0.99453 | -0.10514 | 0.4498
77 | -0.061974 | -0.01558 | 0.062008 | 0.015602 | 3.399e-05 | 2.1616e-05 | 0.092652 | 0.092652 | 0.092652 | 0.99551 | -0.086204 | 0.9961 | -0.074725 | 25.4539
78 | 0.0063679 | 0.0015955 | -0.0063671 | -0.0015953 | 7.5796e-07 | 1.9659e-07 | 0.0095307 | 0.0095309 | 0.0095309 | 0.99419 | -0.11167 | 0.99406 | -0.11417 | 2.6184
79 | -0.10012 | -0.025226 | 0.10025 | 0.025306 | 0.00012564 | 8.0215e-05 | 0.14923 | 0.14923 | 0.14923 | 0.99863 | -0.0262 | 1 | 0 | 40.9986
80 | 0.075617 | 0.019077 | -0.075582 | -0.019054 | 3.5224e-05 | 2.2447e-05 | 0.11272 | 0.11272 | 0.11272 | 0.99863 | -0.0262 | 0.99812 | -0.035934 | 30.9666
81 | 0.024505 | 0.0061492 | -0.0245 | -0.006146 | 5.1791e-06 | 3.1791e-06 | 0.036517 | 0.036517 | 0.036517 | 0.99863 | -0.0262 | 0.9984 | -0.030633 | 10.0321
82 | 0.40369 | 0.10296 | -0.40339 | -0.10277 | 0.00029419 | 0.00018802 | 0.60132 | 0.60132 | 0.60132 | 1 | 0 | 0.9992 | -0.015103 | 55.0663
83 | 0.075582 | 0.019054 | -0.07553 | -0.019021 | 5.1746e-05 | 3.2976e-05 | 0.11272 | 0.11272 | 0.11272 | 0.99812 | -0.035934 | 0.99738 | -0.050251 | 30.9666
84 | 0.020942 | 0.0052545 | -0.020937 | -0.0052513 | 5.2317e-06 | 3.1611e-06 | 0.031215 | 0.031215 | 0.031215 | 0.9984 | -0.030633 | 0.99813 | -0.035874 | 8.5755
85 | 0.0054043 | 0.001354 | -0.0054041 | -0.001354 | 1.6464e-07 | 1.8399e-08 | 0.0080895 | 0.0080896 | 0.0080896 | 0.99406 | -0.11417 | 0.99403 | -0.11481 | 2.2224
86 | 0.0038481 | 0.00096398 | -0.003848 | -0.00096402 | 1.0336e-07 | -4.153e-08 | 0.0057602 | 0.0057603 | 0.0057603 | 0.99403 | -0.11481 | 0.994 | -0.11537 | 1.5825
87 | 0.0028851 | 0.00072271 | -0.0028851 | -0.00072276 | 4.3568e-08 | -5.2853e-08 | 0.0043189 | 0.0043189 | 0.0043189 | 0.994 | -0.11537 | 0.99398 | -0.11569 | 1.1865
88 | 0.050192 | 0.012664 | -0.050188 | -0.012662 | 3.4668e-06 | 2.1989e-06 | 0.076407 | 0.076407 | 0.076407 | 0.97786 | -0.4259 | 0.97779 | -0.42734 | 20.9909
89 | -0.0025828 | -0.00064719 | 0.0025829 | 0.000647 | 1.2241e-07 | -1.9651e-07 | 0.003895 | 0.0038949 | 0.003895 | 0.98671 | -0.25608 | 0.98676 | -0.25509 | 1.07
90 | 0.0021222 | 0.00053177 | -0.0021222 | -0.00053187 | 3.7616e-08 | -1.0101e-07 | 0.0032004 | 0.0032004 | 0.0032004 | 0.98671 | -0.25608 | 0.98669 | -0.25645 | 0.87924
91 | -0.0042578 | -0.0010633 | 0.004259 | 0.0010631 | 1.2454e-06 | -2.3284e-07 | 0.0064193 | 0.0064189 | 0.0064193 | 0.98676 | -0.25509 | 0.98707 | -0.24893 | 1.7635
92 | 0.00088285 | 0.00021783 | -0.00088277 | -0.00021927 | 7.7743e-08 | -1.4464e-06 | 0.0013301 | 0.0013306 | 0.0013306 | 0.98676 | -0.25509 | 0.98666 | -0.25695 | 0.36556
93 | 0.006403 | 0.0016047 | -0.0064022 | -0.0016045 | 7.9069e-07 | 2.1682e-07 | 0.0096525 | 0.0096526 | 0.0096526 | 0.98707 | -0.24893 | 0.98694 | -0.25152 | 2.6518
94 | -0.010662 | -0.0026678 | 0.010663 | 0.002668 | 5.68e-07 | 2.8856e-07 | 0.016071 | 0.016071 | 0.016071 | 0.98707 | -0.24893 | 0.98713 | -0.24781 | 4.4152
95 | 0.00088277 | 0.00021927 | -0.00088272 | -0.00022019 | 4.9362e-08 | -9.1759e-07 | 0.0013306 | 0.001331 | 0.001331 | 0.98666 | -0.25695 | 0.9866 | -0.25813 | 0.36565
96 | 0.005508 | 0.0013803 | -0.0055074 | -0.0013803 | 5.6765e-07 | 8.2838e-08 | 0.0083044 | 0.0083045 | 0.0083045 | 0.98694 | -0.25152 | 0.98683 | -0.25369 | 2.2815
97 | -0.011016 | -0.0027566 | 0.011018 | 0.0027576 | 1.9898e-06 | 1.0274e-06 | 0.016604 | 0.016604 | 0.016604 | 0.98713 | -0.24781 | 0.98732 | -0.24401 | 4.5615
98 | 0.00088272 | 0.00022019 | -0.00088267 | -0.00022122 | 5.5261e-08 | -1.0266e-06 | 0.001331 | 0.0013313 | 0.0013313 | 0.9866 | -0.25813 | 0.98653 | -0.25945 | 0.36576
99 | 0.0033326 | 0.00083519 | -0.0033326 | -0.00083522 | 3.0903e-08 | -2.1915e-08 | 0.0050251 | 0.0050251 | 0.0050251 | 0.98683 | -0.25369 | 0.98682 | -0.25388 | 1.3805
100 | -0.0021686 | -0.0005435 | 0.0021686 | 0.00054343 | 2.9308e-08 | -7.7995e-08 | 0.0032411 | 0.0032411 | 0.0032411 | 0.99561 | -0.083906 | 0.99563 | -0.083622 | 0.89042
101 | -0.0021686 | -0.00054343 | 0.0021687 | 0.00054323 | 7.1867e-08 | -1.9127e-07 | 0.0032411 | 0.003241 | 0.0032411 | 0.99563 | -0.083622 | 0.99566 | -0.082927 | 0.89041
102 | -0.0017834 | -0.00044696 | 0.0017834 | 0.00044675 | 5.0367e-08 | -2.0906e-07 | 0.002678 | 0.0026779 | 0.002678 | 0.99095 | -0.17366 | 0.99098 | -0.17307 | 0.7357
103 | -0.0044485 | -0.0011147 | 0.0044488 | 0.0011146 | 2.768e-07 | -3.6003e-08 | 0.0066797 | 0.0066796 | 0.0066797 | 0.99098 | -0.17307 | 0.99104 | -0.17176 | 1.8351
104 | -0.022518 | -0.0056497 | 0.022529 | 0.0056563 | 1.0841e-05 | 6.6063e-06 | 0.033655 | 0.033655 | 0.033655 | 0.99566 | -0.082927 | 0.99618 | -0.072834 | 9.2459
105 | 0.020349 | 0.0051065 | -0.020346 | -0.0051047 | 2.949e-06 | 1.7768e-06 | 0.030414 | 0.030414 | 0.030414 | 0.99566 | -0.082927 | 0.9955 | -0.085966 | 8.3556
106 | -0.0073654 | -0.0018456 | 0.0073656 | 0.0018457 | 1.5275e-07 | 5.4843e-08 | 0.011059 | 0.011059 | 0.011059 | 0.99104 | -0.17176 | 0.99107 | -0.17133 | 3.0381
107 | -0.030844 | -0.0077402 | 0.030857 | 0.0077488 | 1.3808e-05 | 8.6109e-06 | 0.046075 | 0.046075 | 0.046075 | 0.99618 | -0.072834 | 0.99667 | -0.063451 | 12.658
108 | 0.018924 | 0.0047483 | -0.01892 | -0.0047459 | 4.0766e-06 | 2.4324e-06 | 0.028289 | 0.028289 | 0.028289 | 0.9955 | -0.085966 | 0.99527 | -0.090485 | 7.7717
109 | 0.01892 | 0.0047459 | -0.018913 | -0.0047415 | 7.4263e-06 | 4.4314e-06 | 0.028289 | 0.028289 | 0.028289 | 0.99527 | -0.090485 | 0.99484 | -0.098722 | 7.7717
110 | 0.014906 | 0.0037373 | -0.014904 | -0.0037359 | 2.5156e-06 | 1.4348e-06 | 0.022296 | 0.022296 | 0.022296 | 0.99484 | -0.098722 | 0.99466 | -0.10226 | 6.1253
111 | 0.0040068 | 0.0010041 | -0.0040067 | -0.0010042 | 1.0446e-07 | -3.3845e-08 | 0.005993 | 0.0059931 | 0.0059931 | 0.99484 | -0.098722 | 0.99482 | -0.099269 | 1.6464
112 | -0.041688 | -0.010463 | 0.041718 | 0.010482 | 2.9965e-05 | 1.8909e-05 | 0.062244 | 0.062244 | 0.062244 | 0.99667 | -0.063451 | 0.99745 | -0.048391 | 17.1001
113 | 0.013095 | 0.0032825 | -0.013093 | -0.0032814 | 2.1354e-06 | 1.1741e-06 | 0.01959 | 0.01959 | 0.01959 | 0.99466 | -0.10226 | 0.99448 | -0.10569 | 5.3819
114 | 0.0035753 | 0.00089596 | -0.0035752 | -0.00089603 | 1.3623e-07 | -6.2265e-08 | 0.0054811 | 0.0054812 | 0.0054812 | 0.97063 | -0.56834 | 0.97059 | -0.56914 | 1.5058
115 | -0.0065211 | -0.0016342 | 0.0065223 | 0.0016346 | 1.1667e-06 | 3.6184e-07 | 0.0099971 | 0.009997 | 0.0099971 | 0.97063 | -0.56834 | 0.97082 | -0.56458 | 2.7465
116 | -0.0065223 | -0.0016346 | 0.0065233 | 0.0016349 | 1.066e-06 | 3.3047e-07 | 0.009997 | 0.0099969 | 0.009997 | 0.97082 | -0.56458 | 0.97099 | -0.56115 | 2.7464
117 | -0.0065233 | -0.0016349 | 0.0065243 | 0.0016352 | 9.4364e-07 | 2.9243e-07 | 0.0099969 | 0.0099967 | 0.0099969 | 0.97099 | -0.56115 | 0.97114 | -0.55812 | 2.7464
118 | -0.015267 | -0.0038264 | 0.015272 | 0.003829 | 4.5227e-06 | 2.6218e-06 | 0.023393 | 0.023393 | 0.023393 | 0.97114 | -0.55812 | 0.97146 | -0.5519 | 6.4265
119 | -0.015272 | -0.003829 | 0.015277 | 0.0038319 | 5.1e-06 | 2.9562e-06 | 0.023393 | 0.023392 | 0.023393 | 0.97146 | -0.5519 | 0.97181 | -0.5449 | 6.4265
120 | 0.0077556 | 0.0019438 | -0.007755 | -0.0019435 | 6.4353e-07 | 2.4653e-07 | 0.011605 | 0.011605 | 0.011605 | 0.99448 | -0.10569 | 0.99439 | -0.10743 | 3.1881
121 | 0.0052777 | 0.0013227 | -0.0052775 | -0.0013227 | 2.2968e-07 | 1.9613e-08 | 0.0078975 | 0.0078976 | 0.0078976 | 0.99439 | -0.10743 | 0.99435 | -0.10834 | 2.1697
122 | -0.11566 | -0.029351 | 0.11576 | 0.029419 | 0.0001072 | 6.8489e-05 | 0.17446 | 0.17446 | 0.17446 | 0.98722 | -0.24426 | 0.98822 | -0.22501 | 47.9279
123 | -0.11735 | -0.029817 | 0.11746 | 0.029887 | 0.00011001 | 7.0288e-05 | 0.17685 | 0.17685 | 0.17685 | 0.98822 | -0.22501 | 0.98923 | -0.20556 | 48.5839
124 | -0.11928 | -0.030344 | 0.11928 | 0.030344 | 2.5923e-07 | 1.6563e-07 | 0.17959 | 0.17959 | 0.17959 | 0.98923 | -0.20556 | 0.98923 | -0.20552 | 49.3371
125 | -0.12087 | -0.030741 | 0.12092 | 0.030777 | 5.5561e-05 | 3.5329e-05 | 0.18197 | 0.18197 | 0.18197 | 0.98923 | -0.20552 | 0.98973 | -0.19598 | 24.9962
126 | -0.12274 | -0.031233 | 0.12278 | 0.031253 | 3.1651e-05 | 1.9971e-05 | 0.18471 | 0.18471 | 0.18471 | 0.98973 | -0.19598 | 0.99001 | -0.19063 | 16.9148
127 | -0.12445 | -0.031673 | 0.12449 | 0.031695 | 3.6242e-05 | 2.2876e-05 | 0.18723 | 0.18723 | 0.18723 | 0.99001 | -0.19063 | 0.99032 | -0.18459 | 17.1453
128 | -0.12723 | -0.032383 | 0.12725 | 0.032395 | 1.9799e-05 | 1.2504e-05 | 0.19135 | 0.19135 | 0.19135 | 0.99032 | -0.18459 | 0.99049 | -0.18136 | 17.5226
129 | -0.1316 | -0.033486 | 0.13165 | 0.033516 | 4.6387e-05 | 2.9321e-05 | 0.19789 | 0.19789 | 0.19789 | 0.99049 | -0.18136 | 0.99087 | -0.17405 | 18.1215
130 | -0.13605 | -0.034619 | 0.13614 | 0.034673 | 8.4989e-05 | 5.3764e-05 | 0.2045 | 0.2045 | 0.2045 | 0.99087 | -0.17405 | 0.99155 | -0.1611 | 18.727
131 | -0.14066 | -0.035805 | 0.14078 | 0.035882 | 0.00012183 | 7.7128e-05 | 0.21128 | 0.21128 | 0.21128 | 0.99155 | -0.1611 | 0.99248 | -0.14316 | 19.3479
132 | -0.15392 | -0.039176 | 0.15404 | 0.039252 | 0.00012042 | 7.6369e-05 | 0.23098 | 0.23098 | 0.23098 | 0.99248 | -0.14316 | 0.99333 | -0.12694 | 21.1517
133 | 0.013138 | 0.0032933 | -0.013137 | -0.0032926 | 1.214e-06 | 6.6916e-07 | 0.019698 | 0.019699 | 0.019699 | 0.99248 | -0.14316 | 0.99238 | -0.14509 | 5.4117
134 | -0.0055435 | -0.0013893 | 0.0055437 | 0.0013894 | 2.5523e-07 | 3.6163e-08 | 0.0083137 | 0.0083137 | 0.0083137 | 0.99219 | -0.14889 | 0.99224 | -0.14792 | 2.284
135 | 0.0055435 | 0.0013893 | -0.0055434 | -0.0013893 | 7.9226e-08 | 1.1228e-08 | 0.0083137 | 0.0083137 | 0.0083137 | 0.99219 | -0.14889 | 0.99217 | -0.14919 | 2.284
136 | -0.0090394 | -0.0022654 | 0.0090406 | 0.0022659 | 1.2182e-06 | 5.5127e-07 | 0.013556 | 0.013556 | 0.013556 | 0.99224 | -0.14792 | 0.99238 | -0.14509 | 3.7242
137 | 0.0034957 | 0.00087603 | -0.0034956 | -0.00087608 | 8.6589e-08 | -5.3104e-08 | 0.0052423 | 0.0052423 | 0.0052423 | 0.99224 | -0.14792 | 0.99221 | -0.14844 | 1.4402
138 | -0.18878 | -0.04811 | 0.1888 | 0.048128 | 2.797e-05 | 1.7792e-05 | 0.28238 | 0.28238 | 0.28238 | 0.99577 | -0.080358 | 0.99593 | -0.077288 | 25.8586
139 | 0.18095 | 0.046148 | -0.18074 | -0.046016 | 0.00020702 | 0.00013161 | 0.27068 | 0.27068 | 0.27068 | 0.99577 | -0.080358 | 0.99453 | -0.10408 | 24.7874
140 | -0.19277 | -0.049122 | 0.19293 | 0.049222 | 0.0001571 | 9.9955e-05 | 0.28831 | 0.28831 | 0.28831 | 0.99593 | -0.077288 | 0.99682 | -0.060414 | 26.4017
141 | 0.16882 | 0.04303 | -0.16864 | -0.042913 | 0.00018342 | 0.0001165 | 0.25285 | 0.25285 | 0.25285 | 0.99453 | -0.10408 | 0.99335 | -0.12662 | 23.1549
142 | -0.19293 | -0.049222 | 0.19304 | 0.049294 | 0.00011211 | 7.1327e-05 | 0.28831 | 0.28831 | 0.28831 | 0.99682 | -0.060414 | 0.99745 | -0.048391 | 26.4016
143 | 0.16356 | 0.041639 | -0.16356 | -0.041638 | 1.3897e-06 | 8.8224e-07 | 0.24524 | 0.24524 | 0.24524 | 0.99335 | -0.12662 | 0.99334 | -0.12679 | 22.4575
144 | -0.23476 | -0.059776 | 0.23482 | 0.059815 | 6.1965e-05 | 3.9499e-05 | 0.35055 | 0.35055 | 0.35055 | 0.99745 | -0.048391 | 0.99774 | -0.042919 | 32.1016
145 | 0.15848 | 0.040365 | -0.15848 | -0.040365 | 1.1171e-06 | 7.0879e-07 | 0.23763 | 0.23763 | 0.23763 | 0.99334 | -0.12679 | 0.99333 | -0.12694 | 21.7608
146 | 0.067392 | 0.016981 | -0.067313 | -0.016931 | 7.8799e-05 | 5.0161e-05 | 0.10058 | 0.10058 | 0.10058 | 0.99738 | -0.050251 | 0.9961 | -0.074725 | 27.6308
147 | -0.40038 | -0.10181 | 0.40092 | 0.10215 | 0.0005373 | 0.0003434 | 0.59764 | 0.59764 | 0.59764 | 0.99774 | -0.042919 | 0.9992 | -0.015103 | 54.7291
148 | 0.16556 | 0.041995 | -0.16543 | -0.041914 | 0.0001275 | 8.0947e-05 | 0.24709 | 0.24709 | 0.24709 | 0.99774 | -0.042919 | 0.9969 | -0.058949 | 22.6275
149 | -0.0024318 | -0.00060947 | 0.002432 | 0.00060912 | 1.9306e-07 | -3.4362e-07 | 0.0037094 | 0.0037092 | 0.0037094 | 0.97551 | -0.47204 | 0.97559 | -0.47037 | 1.0191
150 | -0.040811 | -0.010277 | 0.040854 | 0.010304 | 4.3404e-05 | 2.7406e-05 | 0.062264 | 0.062264 | 0.062264 | 0.97559 | -0.47037 | 0.97673 | -0.44815 | 17.1055
151 | 0.038379 | 0.0096679 | -0.038337 | -0.0096415 | 4.1929e-05 | 2.6428e-05 | 0.058555 | 0.058555 | 0.058555 | 0.97559 | -0.47037 | 0.97443 | -0.49324 | 16.0865
152 | -0.046153 | -0.011632 | 0.046166 | 0.011641 | 1.2869e-05 | 8.1496e-06 | 0.070336 | 0.070336 | 0.070336 | 0.97673 | -0.44815 | 0.97703 | -0.44232 | 19.3231
153 | 0.034915 | 0.0087838 | -0.034904 | -0.0087772 | 1.0624e-05 | 6.6754e-06 | 0.053329 | 0.053329 | 0.053329 | 0.97443 | -0.49324 | 0.97411 | -0.49961 | 14.6508
154 | -0.047749 | -0.012037 | 0.047783 | 0.012059 | 3.4259e-05 | 2.1709e-05 | 0.072747 | 0.072747 | 0.072747 | 0.97703 | -0.44232 | 0.97779 | -0.42734 | 19.9855
155 | 0.032191 | 0.0080973 | -0.032161 | -0.0080784 | 3.0062e-05 | 1.8827e-05 | 0.049185 | 0.049185 | 0.049185 | 0.97411 | -0.49961 | 0.97311 | -0.51918 | 13.5124
156 | 0.032161 | 0.0080784 | -0.032122 | -0.0080537 | 3.9419e-05 | 2.4689e-05 | 0.049185 | 0.049185 | 0.049185 | 0.97311 | -0.51918 | 0.97181 | -0.5449 | 13.5124
157 | 0.16052 | 0.040681 | -0.16046 | -0.040645 | 5.7559e-05 | 3.6524e-05 | 0.23975 | 0.23975 | 0.23975 | 0.9969 | -0.058949 | 0.99651 | -0.066415 | 21.9553
158 | 0.15701 | 0.039781 | -0.15699 | -0.039769 | 1.9187e-05 | 1.2171e-05 | 0.23461 | 0.23461 | 0.23461 | 0.99651 | -0.066415 | 0.99638 | -0.068959 | 21.4841
159 | -0.0012272 | -0.00030756 | 0.0012272 | 0.00030732 | 2.5034e-08 | -2.379e-07 | 0.0018416 | 0.0018415 | 0.0018416 | 0.99156 | -0.16174 | 0.99158 | -0.16131 | 0.50593
160 | -0.002485 | -0.00062255 | 0.0024852 | 0.00062216 | 2.1622e-07 | -3.9657e-07 | 0.003729 | 0.0037288 | 0.003729 | 0.99158 | -0.16131 | 0.99168 | -0.15949 | 1.0245
161 | -0.061761 | -0.015537 | 0.061813 | 0.015571 | 5.2892e-05 | 3.3638e-05 | 0.092583 | 0.092583 | 0.092583 | 0.99286 | -0.1367 | 0.99379 | -0.11879 | 25.4348
162 | 0.059665 | 0.015012 | -0.059613 | -0.014979 | 5.1634e-05 | 3.2824e-05 | 0.089441 | 0.089441 | 0.089441 | 0.99286 | -0.1367 | 0.99192 | -0.15483 | 24.5718
163 | -0.063667 | -0.016035 | 0.063705 | 0.016059 | 3.7719e-05 | 2.3997e-05 | 0.095358 | 0.095358 | 0.095358 | 0.99379 | -0.11879 | 0.99443 | -0.10641 | 26.1973
164 | 0.054657 | 0.013738 | -0.05462 | -0.013714 | 3.7295e-05 | 2.3678e-05 | 0.082008 | 0.082008 | 0.082008 | 0.99192 | -0.15483 | 0.99118 | -0.16913 | 22.5296
165 | 0.0049555 | 0.0012409 | -0.0049547 | -0.0012409 | 7.9195e-07 | 1.362e-08 | 0.0074336 | 0.0074337 | 0.0074337 | 0.99192 | -0.15483 | 0.99175 | -0.15819 | 2.0422
166 | -0.064691 | -0.016307 | 0.064713 | 0.016321 | 2.176e-05 | 1.3846e-05 | 0.096834 | 0.096834 | 0.096834 | 0.99443 | -0.10641 | 0.99479 | -0.099386 | 26.6028
167 | 0.039882 | 0.010021 | -0.039878 | -0.010018 | 4.1753e-06 | 2.6322e-06 | 0.059882 | 0.059882 | 0.059882 | 0.99118 | -0.16913 | 0.99107 | -0.17133 | 16.4512
168 | 0.010954 | 0.0027456 | -0.010953 | -0.002745 | 1.2229e-06 | 6.2726e-07 | 0.016445 | 0.016445 | 0.016445 | 0.99118 | -0.16913 | 0.99106 | -0.17148 | 4.5179
169 | 0.0037836 | 0.00094808 | -0.0037835 | -0.00094814 | 1.5577e-07 | -6.6239e-08 | 0.0056801 | 0.0056802 | 0.0056802 | 0.99118 | -0.16913 | 0.99114 | -0.17 | 1.5605
170 | 0.003923 | 0.00098236 | -0.0039228 | -0.00098245 | 2.4256e-07 | -8.5668e-08 | 0.0058858 | 0.0058859 | 0.0058859 | 0.99175 | -0.15819 | 0.99168 | -0.15949 | 1.617
171 | -0.065698 | -0.016567 | 0.065763 | 0.016608 | 6.45e-05 | 4.1049e-05 | 0.098308 | 0.098307 | 0.098308 | 0.99479 | -0.099386 | 0.99586 | -0.078896 | 27.0076
172 | 0.032512 | 0.0081725 | -0.032497 | -0.008163 | 1.5163e-05 | 9.486e-06 | 0.048824 | 0.048824 | 0.048824 | 0.99107 | -0.17133 | 0.99056 | -0.1811 | 13.4131
173 | 0.0089893 | 0.0022528 | -0.008988 | -0.0022522 | 1.2999e-06 | 5.8678e-07 | 0.013497 | 0.013497 | 0.013497 | 0.99106 | -0.17148 | 0.9909 | -0.17451 | 3.708
174 | 0.0013699 | 0.00034324 | -0.0013699 | -0.00034333 | 1.0927e-08 | -8.1784e-08 | 0.0020566 | 0.0020567 | 0.0020567 | 0.99114 | -0.17 | 0.99113 | -0.17017 | 0.56502
175 | 0.089013 | 0.022576 | -0.08882 | -0.022453 | 0.00019247 | 0.00012281 | 0.1331 | 0.1331 | 0.1331 | 0.99586 | -0.078896 | 0.99351 | -0.12398 | 36.5653
176 | -0.15478 | -0.039185 | 0.15485 | 0.039232 | 7.3881e-05 | 4.7093e-05 | 0.23141 | 0.23141 | 0.23141 | 0.99586 | -0.078896 | 0.99638 | -0.068959 | 31.7864
177 | 0.0071375 | 0.0017885 | -0.0071367 | -0.0017882 | 8.3387e-07 | 2.8437e-07 | 0.010718 | 0.010718 | 0.010718 | 0.9909 | -0.17451 | 0.99078 | -0.17697 | 2.9446
178 | 0.086494 | 0.02187 | -0.086473 | -0.021857 | 2.1609e-05 | 1.3786e-05 | 0.12961 | 0.12961 | 0.12961 | 0.99351 | -0.12398 | 0.99324 | -0.12919 | 35.6083
179 | 0.08462 | 0.021392 | -0.084559 | -0.021354 | 6.0619e-05 | 3.8667e-05 | 0.12684 | 0.12684 | 0.12684 | 0.99324 | -0.12919 | 0.99246 | -0.14414 | 34.8457
180 | 0.084559 | 0.021354 | -0.08445 | -0.021284 | 0.00010889 | 6.946e-05 | 0.12684 | 0.12684 | 0.12684 | 0.99246 | -0.14414 | 0.99107 | -0.17105 | 34.8457
181 | 0.0038337 | 0.00096035 | -0.0038335 | -0.00096044 | 2.303e-07 | -9.1177e-08 | 0.0057575 | 0.0057576 | 0.0057576 | 0.99078 | -0.17697 | 0.99071 | -0.17823 | 1.5818
182 | 0.0015864 | 0.00039727 | -0.0015863 | -0.00039747 | 3.7319e-08 | -2.0185e-07 | 0.0023826 | 0.0023826 | 0.0023826 | 0.99071 | -0.17823 | 0.99069 | -0.17872 | 0.65457
183 | 0.0015863 | 0.00039747 | -0.0015863 | -0.00039757 | 1.8202e-08 | -9.844e-08 | 0.0023826 | 0.0023827 | 0.0023827 | 0.99069 | -0.17872 | 0.99067 | -0.17896 | 0.65458
184 | 0.0055782 | 0.001398 | -0.005578 | -0.001398 | 1.7971e-07 | 2.7473e-08 | 0.0083869 | 0.008387 | 0.008387 | 0.98968 | -0.19821 | 0.98965 | -0.19888 | 2.3041
185 | 0.0013103 | 0.00032783 | -0.0013102 | -0.00032824 | 5.0866e-08 | -4.108e-07 | 0.0019762 | 0.0019764 | 0.0019764 | 0.98647 | -0.26025 | 0.98643 | -0.26106 | 0.54296
186 | -0.0013103 | -0.00032783 | 0.0013103 | 0.00032766 | 2.1187e-08 | -1.7114e-07 | 0.0019762 | 0.0019762 | 0.0019762 | 0.98647 | -0.26025 | 0.98649 | -0.25991 | 0.54292
187 | 0.0013102 | 0.00032824 | -0.0013102 | -0.00032836 | 1.5608e-08 | -1.2603e-07 | 0.0019764 | 0.0019764 | 0.0019764 | 0.98643 | -0.26106 | 0.98641 | -0.26131 | 0.54297
188 | -0.0026866 | -0.0006726 | 0.0026867 | 0.00067253 | 4.88e-08 | -6.9951e-08 | 0.0040522 | 0.0040522 | 0.0040522 | 0.98649 | -0.25991 | 0.98651 | -0.25952 | 1.1133
189 | 0.0041949 | 0.0010508 | -0.0041945 | -0.0010509 | 3.8376e-07 | -9.506e-08 | 0.0062596 | 0.0062597 | 0.0062597 | 0.99717 | -0.054411 | 0.99707 | -0.056332 | 1.7197
190 | -0.0041949 | -0.0010508 | 0.0041951 | 0.0010508 | 2.3504e-07 | -5.8261e-08 | 0.0062596 | 0.0062595 | 0.0062596 | 0.99717 | -0.054411 | 0.99723 | -0.053234 | 1.7197
191 | 0.0041945 | 0.0010509 | -0.0041942 | -0.001051 | 2.3315e-07 | -5.7715e-08 | 0.0062597 | 0.0062598 | 0.0062598 | 0.99707 | -0.056332 | 0.99701 | -0.057499 | 1.7197
192 | -0.0052263 | -0.0013092 | 0.0052263 | 0.0013092 | 3.8356e-09 | 2.6053e-10 | 0.0077983 | 0.0077983 | 0.0077983 | 0.99723 | -0.053234 | 0.99723 | -0.053219 | 2.1424
193 | 0.003163 | 0.00079253 | -0.0031628 | -0.00079268 | 1.7184e-07 | -1.5816e-07 | 0.0047207 | 0.0047208 | 0.0047208 | 0.99701 | -0.057499 | 0.99695 | -0.05864 | 1.2969
194 | -0.0062576 | -0.0015677 | 0.0062576 | 0.0015677 | 3.925e-08 | 9.4563e-09 | 0.009337 | 0.009337 | 0.009337 | 0.99723 | -0.053219 | 0.99724 | -0.053087 | 2.5651
195 | 0.020937 | 0.0052513 | -0.020932 | -0.005248 | 5.454e-06 | 3.2955e-06 | 0.031215 | 0.031215 | 0.031215 | 0.99813 | -0.035874 | 0.99784 | -0.04134 | 8.5755
196 | -0.0019435 | -0.00048709 | 0.0019436 | 0.0004869 | 5.8701e-08 | -1.9489e-07 | 0.0029319 | 0.0029318 | 0.0029319 | 0.98639 | -0.26181 | 0.98642 | -0.26118 | 0.80546
197 | -0.0019436 | -0.0004869 | 0.0019436 | 0.00048674 | 4.7316e-08 | -1.5711e-07 | 0.0029318 | 0.0029317 | 0.0029318 | 0.98642 | -0.26118 | 0.98645 | -0.26066 | 0.80544
198 | -0.0031183 | -0.00078115 | 0.0031184 | 0.00078112 | 2.7722e-08 | -2.4913e-08 | 0.0047037 | 0.0047037 | 0.0047037 | 0.98645 | -0.26066 | 0.98646 | -0.26048 | 1.2922
199 | -0.001521 | -0.00038121 | 0.0015211 | 0.00038104 | 2.9049e-08 | -1.7287e-07 | 0.0022836 | 0.0022835 | 0.0022836 | 0.99115 | -0.17054 | 0.99117 | -0.17014 | 0.62735
200 | -0.0025302 | -0.00063395 | 0.0025302 | 0.00063386 | 5.1421e-08 | -8.9584e-08 | 0.0037985 | 0.0037984 | 0.0037985 | 0.99117 | -0.17014 | 0.99119 | -0.16971 | 1.0435
201 | -0.00096142 | -0.00024096 | 0.00096143 | 0.00024088 | 4.6448e-09 | -7.452e-08 | 0.0014393 | 0.0014393 | 0.0014393 | 0.99394 | -0.11643 | 0.99395 | -0.11633 | 0.39542
202 | -0.0019236 | -0.00048202 | 0.0019236 | 0.00048181 | 5.8951e-08 | -2.0799e-07 | 0.0028797 | 0.0028796 | 0.0028797 | 0.99395 | -0.11633 | 0.99398 | -0.11569 | 0.79113
203 | 0.0048712 | 0.0012199 | -0.0048709 | -0.0012199 | 3.2488e-07 | 2.9555e-09 | 0.0073465 | 0.0073466 | 0.0073466 | 0.9866 | -0.25764 | 0.98653 | -0.25904 | 2.0183
204 | -0.0048712 | -0.0012199 | 0.0048714 | 0.0012199 | 1.861e-07 | 1.6777e-09 | 0.0073465 | 0.0073465 | 0.0073465 | 0.9866 | -0.25764 | 0.98664 | -0.25684 | 2.0183
205 | 0.0037644 | 0.00094257 | -0.0037643 | -0.0009426 | 8.6017e-08 | -3.5802e-08 | 0.0056776 | 0.0056776 | 0.0056776 | 0.98653 | -0.25904 | 0.98651 | -0.25952 | 1.5598
206 | -0.0060551 | -0.0015165 | 0.0060552 | 0.0015166 | 1.2553e-07 | 2.9069e-08 | 0.0091317 | 0.0091316 | 0.0091317 | 0.98664 | -0.25684 | 0.98667 | -0.25641 | 2.5087
207 | -0.07643 | -0.019232 | 0.076464 | 0.019254 | 3.4592e-05 | 2.2049e-05 | 0.11495 | 0.11495 | 0.11495 | 0.98957 | -0.19997 | 0.99006 | -0.1905 | 31.5809
208 | 0.075028 | 0.01888 | -0.074982 | -0.018851 | 4.6412e-05 | 2.9579e-05 | 0.11285 | 0.11285 | 0.11285 | 0.98957 | -0.19997 | 0.9889 | -0.21292 | 31.002
209 | -0.077834 | -0.019597 | 0.077836 | 0.019598 | 2.1069e-06 | 1.3431e-06 | 0.11701 | 0.11701 | 0.11701 | 0.99006 | -0.1905 | 0.99009 | -0.18994 | 32.1465
210 | 0.073593 | 0.018503 | -0.073575 | -0.018491 | 1.8327e-05 | 1.1678e-05 | 0.11076 | 0.11076 | 0.11076 | 0.9889 | -0.21292 | 0.98863 | -0.21814 | 30.4279
211 | 0.0025481 | 0.00063839 | -0.002548 | -0.00063854 | 8.6658e-08 | -1.4718e-07 | 0.0038295 | 0.0038296 | 0.0038296 | 0.99009 | -0.18994 | 0.99005 | -0.19065 | 1.0521
212 | -0.080384 | -0.020237 | 0.080418 | 0.020258 | 3.3919e-05 | 2.1628e-05 | 0.12084 | 0.12084 | 0.12084 | 0.99009 | -0.18994 | 0.99054 | -0.18111 | 33.1986
213 | 0.072153 | 0.018135 | -0.072123 | -0.018116 | 2.9641e-05 | 1.8885e-05 | 0.10862 | 0.10862 | 0.10862 | 0.98863 | -0.21814 | 0.98819 | -0.22675 | 29.8399
214 | 0.0012939 | 0.00032421 | -0.0012939 | -0.00032428 | 7.5544e-09 | -6.3667e-08 | 0.0019447 | 0.0019447 | 0.0019447 | 0.99005 | -0.19065 | 0.99005 | -0.19077 | 0.53425
215 | -0.081786 | -0.020601 | 0.081804 | 0.020613 | 1.826e-05 | 1.1645e-05 | 0.1229 | 0.1229 | 0.1229 | 0.99054 | -0.18111 | 0.99079 | -0.17645 | 33.763
216 | 0.039198 | 0.0098519 | -0.039178 | -0.0098394 | 1.9932e-05 | 1.2561e-05 | 0.059034 | 0.059034 | 0.059034 | 0.98819 | -0.22675 | 0.98764 | -0.2374 | 16.2182
217 | 0.032925 | 0.0082639 | -0.032925 | -0.0082636 | 3.9609e-07 | 2.4799e-07 | 0.049583 | 0.049583 | 0.049583 | 0.98819 | -0.22675 | 0.98818 | -0.227 | 13.6217
218 | -0.083059 | -0.020927 | 0.08308 | 0.020941 | 2.144e-05 | 1.3675e-05 | 0.12478 | 0.12478 | 0.12478 | 0.99079 | -0.17645 | 0.99107 | -0.17105 | 34.2806
219 | 0.037981 | 0.0095392 | -0.037972 | -0.0095338 | 8.5548e-06 | 5.3859e-06 | 0.05723 | 0.05723 | 0.05723 | 0.98764 | -0.2374 | 0.9874 | -0.24213 | 15.7226
220 | 0.031505 | 0.0079078 | -0.031499 | -0.0079041 | 5.9466e-06 | 3.7156e-06 | 0.047445 | 0.047445 | 0.047445 | 0.98818 | -0.227 | 0.98797 | -0.23096 | 13.0343
221 | 0.019172 | 0.004807 | -0.01917 | -0.0048058 | 2.1111e-06 | 1.2611e-06 | 0.028591 | 0.028591 | 0.028591 | 0.99784 | -0.04134 | 0.99772 | -0.043651 | 7.8547
222 | 0.0060514 | 0.0015164 | -0.006051 | -0.0015163 | 4.5693e-07 | 1.0643e-07 | 0.0091364 | 0.0091364 | 0.0091364 | 0.98557 | -0.27766 | 0.98549 | -0.27925 | 2.51
223 | -0.0060514 | -0.0015164 | 0.0060521 | 0.0015165 | 6.306e-07 | 1.4683e-07 | 0.0091364 | 0.0091363 | 0.0091364 | 0.98557 | -0.27766 | 0.98569 | -0.27548 | 2.51
224 | 0.0043538 | 0.0010909 | -0.0043537 | -0.0010909 | 1.4288e-07 | -2.0888e-08 | 0.0065738 | 0.0065739 | 0.0065739 | 0.98549 | -0.27925 | 0.98546 | -0.27994 | 1.806
225 | -0.0072379 | -0.0018137 | 0.0072383 | 0.0018138 | 3.1177e-07 | 1.1077e-07 | 0.010926 | 0.010926 | 0.010926 | 0.98569 | -0.27548 | 0.98573 | -0.27457 | 3.0018
226 | 0.017741 | 0.0044476 | -0.017739 | -0.0044463 | 2.1298e-06 | 1.2572e-06 | 0.026459 | 0.026459 | 0.026459 | 0.99772 | -0.043651 | 0.99759 | -0.046171 | 7.2691
227 | 0.002777 | 0.00069578 | -0.0027769 | -0.00069595 | 1.2558e-07 | -1.6228e-07 | 0.0041931 | 0.0041932 | 0.0041932 | 0.98546 | -0.27994 | 0.98541 | -0.28089 | 1.152
228 | -0.008426 | -0.0021115 | 0.008426 | 0.0021115 | 7.0669e-08 | 3.0379e-08 | 0.012719 | 0.012719 | 0.012719 | 0.98573 | -0.27457 | 0.98574 | -0.2744 | 3.4943
229 | 0.016644 | 0.0041718 | -0.016642 | -0.004171 | 1.3343e-06 | 7.7858e-07 | 0.024826 | 0.024826 | 0.024826 | 0.99759 | -0.046171 | 0.99751 | -0.047853 | 6.8203
230 | -0.0072398 | -0.0018135 | 0.0072403 | 0.0018136 | 4.7978e-07 | 1.6997e-07 | 0.010918 | 0.010918 | 0.010918 | 0.98667 | -0.25641 | 0.98674 | -0.25501 | 2.9995
231 | 0.0044027 | 0.0011033 | -0.0044024 | -0.0011033 | 3.0829e-07 | -4.0901e-08 | 0.0066393 | 0.0066394 | 0.0066394 | 0.98674 | -0.25501 | 0.98666 | -0.25648 | 1.824
232 | 0.011387 | 0.0028539 | -0.011385 | -0.0028531 | 1.4727e-06 | 7.7243e-07 | 0.017171 | 0.017171 | 0.017171 | 0.98674 | -0.25501 | 0.9866 | -0.25773 | 4.7174
233 | -0.02303 | -0.0057709 | 0.023036 | 0.0057744 | 5.877e-06 | 3.5953e-06 | 0.034729 | 0.034729 | 0.034729 | 0.98674 | -0.25501 | 0.98701 | -0.24966 | 9.5409
234 | 0.010199 | 0.0025559 | -0.010199 | -0.0025557 | 3.6502e-07 | 1.8109e-07 | 0.015383 | 0.015383 | 0.015383 | 0.9866 | -0.25773 | 0.98656 | -0.25848 | 4.226
235 | -0.02421 | -0.0060689 | 0.024219 | 0.0060741 | 8.5336e-06 | 5.2431e-06 | 0.0365 | 0.0365 | 0.0365 | 0.98701 | -0.24966 | 0.98739 | -0.24226 | 10.0274
236 | 0.0090246 | 0.0022614 | -0.0090244 | -0.0022613 | 2.0009e-07 | 9.1287e-08 | 0.013612 | 0.013612 | 0.013612 | 0.98656 | -0.25848 | 0.98653 | -0.25895 | 3.7395
237 | -0.026407 | -0.0066222 | 0.026412 | 0.0066253 | 4.9646e-06 | 3.0704e-06 | 0.039797 | 0.039797 | 0.039797 | 0.98739 | -0.24226 | 0.98759 | -0.23832 | 10.9332
238 | 0.0021879 | 0.00054811 | -0.0021878 | -0.00054826 | 6.3225e-08 | -1.579e-07 | 0.0032971 | 0.0032972 | 0.0032972 | 0.98739 | -0.24226 | 0.98736 | -0.24287 | 0.90582
239 | 0.015547 | 0.0038965 | -0.015546 | -0.003896 | 9.0081e-07 | 5.1822e-07 | 0.023192 | 0.023192 | 0.023192 | 0.99751 | -0.047853 | 0.99744 | -0.04907 | 6.3715
240 | 0.014175 | 0.0035525 | -0.014174 | -0.0035518 | 1.122e-06 | 6.3077e-07 | 0.021147 | 0.021147 | 0.021147 | 0.99744 | -0.04907 | 0.99736 | -0.050731 | 5.8096
241 | 0.012822 | 0.0032129 | -0.012821 | -0.0032127 | 4.1424e-07 | 2.2572e-07 | 0.019129 | 0.019129 | 0.019129 | 0.99736 | -0.050731 | 0.99732 | -0.05141 | 5.2553
242 | -0.0019435 | -0.00048709 | 0.0019435 | 0.00048705 | 1.3523e-08 | -4.478e-08 | 0.0029335 | 0.0029334 | 0.0029335 | 0.98586 | -0.27208 | 0.98587 | -0.27194 | 0.8059
243 | 0.004911 | 0.0012306 | -0.0049107 | -0.0012306 | 3.0648e-07 | 6.485e-09 | 0.0074123 | 0.0074123 | 0.0074123 | 0.98587 | -0.27194 | 0.9858 | -0.27325 | 2.0364
244 | -0.0068545 | -0.0017177 | 0.0068546 | 0.0017177 | 1.1379e-07 | 3.6674e-08 | 0.010346 | 0.010346 | 0.010346 | 0.98587 | -0.27194 | 0.98588 | -0.27159 | 2.8422
245 | -0.0043038 | -0.0010782 | 0.0043039 | 0.0010782 | 5.3652e-08 | -9.0022e-09 | 0.0064919 | 0.0064919 | 0.0064919 | 0.98646 | -0.26048 | 0.98647 | -0.26022 | 1.7835
246 | 0.0078398 | 0.0019644 | -0.0078396 | -0.0019643 | 2.0226e-07 | 8.0194e-08 | 0.011825 | 0.011825 | 0.011825 | 0.98653 | -0.25895 | 0.98651 | -0.25949 | 3.2486
247 | -0.027693 | -0.0069464 | 0.027694 | 0.0069473 | 1.3687e-06 | 8.4912e-07 | 0.041727 | 0.041727 | 0.041727 | 0.98759 | -0.23832 | 0.98765 | -0.23728 | 11.4636
248 | 0.0010949 | 0.00027435 | -0.0010949 | -0.00027441 | 4.9025e-09 | -5.827e-08 | 0.0016501 | 0.0016501 | 0.0016501 | 0.98736 | -0.24287 | 0.98736 | -0.24296 | 0.45333
249 | -0.015978 | -0.0040047 | 0.015979 | 0.0040052 | 9.4286e-07 | 5.4829e-07 | 0.024115 | 0.024115 | 0.024115 | 0.98591 | -0.2711 | 0.98597 | -0.26986 | 6.625
250 | 0.014793 | 0.0037077 | -0.014792 | -0.003707 | 1.3008e-06 | 7.438e-07 | 0.022327 | 0.022327 | 0.022327 | 0.98591 | -0.2711 | 0.98582 | -0.27294 | 6.1337
251 | -0.017216 | -0.0043152 | 0.017216 | 0.0043156 | 6.6848e-07 | 3.9415e-07 | 0.025982 | 0.025982 | 0.025982 | 0.98597 | -0.26986 | 0.98602 | -0.26905 | 7.1379
252 | 0.013606 | 0.0034099 | -0.013605 | -0.0034094 | 9.4056e-07 | 5.2615e-07 | 0.020538 | 0.020538 | 0.020538 | 0.98582 | -0.27294 | 0.98574 | -0.2744 | 5.6422
253 | -0.018403 | -0.004613 | 0.018406 | 0.0046146 | 2.6354e-06 | 1.5704e-06 | 0.027773 | 0.027773 | 0.027773 | 0.98602 | -0.26905 | 0.98617 | -0.26604 | 7.6299
254 | 0.0051794 | 0.0012978 | -0.0051791 | -0.0012978 | 2.5085e-07 | 2.1049e-08 | 0.0078184 | 0.0078184 | 0.0078184 | 0.98574 | -0.2744 | 0.98569 | -0.27541 | 2.1479
255 | 0.014623 | 0.0036654 | -0.014622 | -0.0036648 | 1.0754e-06 | 6.1311e-07 | 0.022064 | 0.022064 | 0.022064 | 0.98617 | -0.26604 | 0.98609 | -0.26758 | 6.0616
256 | -0.033028 | -0.0082801 | 0.033045 | 0.0082905 | 1.6761e-05 | 1.0497e-05 | 0.049837 | 0.049837 | 0.049837 | 0.98617 | -0.26604 | 0.98672 | -0.2554 | 13.6914
257 | 0.0038847 | 0.0009734 | -0.0038846 | -0.00097343 | 9.072e-08 | -3.1603e-08 | 0.0058643 | 0.0058643 | 0.0058643 | 0.98569 | -0.27541 | 0.98566 | -0.2759 | 1.6111
258 | 0.01268 | 0.0031781 | -0.012679 | -0.0031776 | 9.5272e-07 | 5.2122e-07 | 0.019134 | 0.019134 | 0.019134 | 0.98609 | -0.26758 | 0.98601 | -0.26916 | 5.2565
259 | -0.034281 | -0.0086003 | 0.034288 | 0.0086047 | 6.983e-06 | 4.3801e-06 | 0.051701 | 0.051701 | 0.051701 | 0.98672 | -0.2554 | 0.98694 | -0.25112 | 14.2035
260 | 0.0025897 | 0.00064892 | -0.0025897 | -0.00064899 | 4.0322e-08 | -6.3854e-08 | 0.0039096 | 0.0039096 | 0.0039096 | 0.98566 | -0.2759 | 0.98565 | -0.27623 | 1.0741
261 | -0.035523 | -0.0089142 | 0.03553 | 0.0089189 | 7.4951e-06 | 4.7078e-06 | 0.053562 | 0.053562 | 0.053562 | 0.98694 | -0.25112 | 0.98716 | -0.2467 | 14.7149
262 | -0.036766 | -0.0092286 | 0.036774 | 0.0092337 | 8.0238e-06 | 5.0462e-06 | 0.055425 | 0.055425 | 0.055425 | 0.98716 | -0.2467 | 0.9874 | -0.24213 | 15.2267
263 | 0.010737 | 0.0026909 | -0.010736 | -0.0026905 | 6.8301e-07 | 3.4865e-07 | 0.016203 | 0.016203 | 0.016203 | 0.98601 | -0.26916 | 0.98594 | -0.2705 | 4.4514
264 | 0.0012953 | 0.00032456 | -0.0012952 | -0.00032462 | 6.5953e-09 | -5.4403e-08 | 0.0019554 | 0.0019554 | 0.0019554 | 0.98565 | -0.27623 | 0.98564 | -0.27634 | 0.5372
265 | 0.028792 | 0.0072236 | -0.028789 | -0.0072215 | 3.4914e-06 | 2.1711e-06 | 0.043376 | 0.043376 | 0.043376 | 0.98778 | -0.23474 | 0.98765 | -0.23728 | 11.9164
266 | -0.030071 | -0.0075443 | 0.030077 | 0.0075477 | 5.4218e-06 | 3.3797e-06 | 0.045303 | 0.045303 | 0.045303 | 0.98778 | -0.23474 | 0.98797 | -0.23096 | 12.4459
267 | -0.0054793 | -0.0013728 | 0.0054794 | 0.0013728 | 9.2182e-08 | 1.3054e-08 | 0.008265 | 0.008265 | 0.008265 | 0.98647 | -0.26022 | 0.98649 | -0.25986 | 2.2706
268 | -0.0066648 | -0.0016699 | 0.0066649 | 0.0016699 | 1.1891e-07 | 3.6044e-08 | 0.010053 | 0.010053 | 0.010053 | 0.98649 | -0.25986 | 0.98651 | -0.25949 | 2.7618
269 | 0.0030021 | 0.00075229 | -0.0030021 | -0.00075234 | 5.2428e-08 | -5.3246e-08 | 0.0045315 | 0.0045316 | 0.0045316 | 0.9858 | -0.27325 | 0.98578 | -0.27362 | 1.2449
270 | -0.0087952 | -0.0022041 | 0.0087957 | 0.0022043 | 4.5826e-07 | 2.0485e-07 | 0.013275 | 0.013275 | 0.013275 | 0.98588 | -0.27159 | 0.98594 | -0.2705 | 3.6469
271 | 0.0041124 | 0.0010306 | -0.0041123 | -0.0010306 | 9.441e-08 | -2.6833e-08 | 0.0061359 | 0.0061359 | 0.0061359 | 0.99731 | -0.051731 | 0.99728 | -0.052213 | 1.6857
272 | -0.00547 | -0.0013708 | 0.0054701 | 0.0013708 | 8.3816e-08 | 9.8552e-09 | 0.0081614 | 0.0081613 | 0.0081614 | 0.99731 | -0.051731 | 0.99732 | -0.05141 | 2.2421
273 | 0.0027603 | 0.00069176 | -0.0027603 | -0.00069179 | 2.3609e-08 | -3.3318e-08 | 0.0041186 | 0.0041186 | 0.0041186 | 0.99728 | -0.052213 | 0.99727 | -0.052393 | 1.1315
274 | 0.0073514 | 0.0018419 | -0.0073508 | -0.0018416 | 5.8735e-07 | 2.0602e-07 | 0.010968 | 0.010968 | 0.010968 | 0.99732 | -0.05141 | 0.99724 | -0.053087 | 3.0132
275 | 0.0010947 | 0.00027431 | -0.0010947 | -0.00027436 | 4.3699e-09 | -5.161e-08 | 0.0016525 | 0.0016525 | 0.0016525 | 0.98578 | -0.27362 | 0.98578 | -0.2737 | 0.45398
276 | 0.0037662 | 0.00094359 | -0.0037661 | -0.0009436 | 2.5524e-08 | -1.111e-08 | 0.0056538 | 0.0056538 | 0.0056538 | 0.9912 | -0.16957 | 0.99119 | -0.16971 | 1.5532
277 | -0.0046732 | -0.0011709 | 0.0046733 | 0.0011709 | 1.8059e-07 | -1.055e-08 | 0.0070154 | 0.0070153 | 0.0070154 | 0.9912 | -0.16957 | 0.99124 | -0.16876 | 1.9273
278 | -0.0061503 | -0.0015411 | 0.0061504 | 0.0015411 | 9.8381e-08 | 2.3289e-08 | 0.0092325 | 0.0092325 | 0.0092325 | 0.99124 | -0.16876 | 0.99125 | -0.16842 | 2.5364
279 | -0.0071123 | -0.0017822 | 0.0071127 | 0.0017823 | 3.3356e-07 | 1.1288e-07 | 0.010677 | 0.010676 | 0.010677 | 0.99125 | -0.16842 | 0.9913 | -0.16744 | 2.9331

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50808 | 0.12889

## res_load
| p_mw | q_mvar
0 | 0.0040201 | 0.0010075
1 | 0.0011489 | 0.00028793
2 | 0.0011489 | 0.00028793
3 | 0.0011489 | 0.00028793
4 | 0.0015604 | 0.00039108
5 | 0.0029421 | 0.00073735
6 | 0.0015377 | 0.00038538
7 | 0.0015116 | 0.00037884
8 | 0.0011489 | 0.00028793
9 | 0.002293 | 0.00057468
10 | 0.0020148 | 0.00050497
11 | 0.0014112 | 0.00035368
12 | 0.0015429 | 0.00038668
13 | 0.0030082 | 0.00075392
14 | 0.002774 | 0.00069523
15 | 0.0013773 | 0.00034518
16 | 0.0016065 | 0.00040263
17 | 0.0054635 | 0.0013693
18 | 0.0053988 | 0.0013531
19 | 0.0056287 | 0.0014107
20 | 0.0013557 | 0.00033977
21 | 0.0013565 | 0.00033997
22 | 0.0041798 | 0.0010475
23 | 0.0041995 | 0.0010525
24 | 0.0011489 | 0.00028793
25 | 0.0012337 | 0.00030919
26 | 0.0018358 | 0.00046009
27 | 0.0020848 | 0.0005225
28 | 0.0019293 | 0.00048352
29 | 0.0023374 | 0.0005858
30 | 0.0032655 | 0.0008184
31 | 0.0018687 | 0.00046833
32 | 0.0018887 | 0.00047334
33 | 0.001317 | 0.00033008
34 | 0.0012744 | 0.00031939
35 | 0.0033598 | 0.00084205
36 | 0.0034478 | 0.0008641
37 | 0.0011598 | 0.00029067
38 | 0.0014392 | 0.00036071
39 | 0.0023589 | 0.00059119
40 | 0.0012985 | 0.00032544
41 | 0.0013538 | 0.00033931
42 | 0.00098223 | 0.00024617
43 | 0.001885 | 0.00047243
44 | 0.0015627 | 0.00039165
45 | 0.00095466 | 0.00023926
46 | 0.00094883 | 0.0002378
47 | 0.00090721 | 0.00022737
48 | 0.0013554 | 0.00033969
49 | 0.0012404 | 0.00031086
50 | 0.003375 | 0.00084586
51 | 0.0053052 | 0.0013296
52 | 0.0012997 | 0.00032574
53 | 0.0024912 | 0.00062435
54 | 0.0035575 | 0.00089159
55 | 0.0010943 | 0.00027426
56 | 0.00096286 | 0.00024131
57 | 0.0015561 | 0.00038998
58 | 0.00096285 | 0.00024131
59 | 0.0015597 | 0.0003909
60 | 0.00046056 | 0.00011543
61 | 0.00079201 | 0.0001985
62 | 0.0021222 | 0.00053187
63 | 0.00089422 | 0.00022411
64 | 0.00035314 | 8.8505e-05
65 | 0.0021748 | 0.00054507
66 | 0.0015627 | 0.00039165
67 | 0.00053424 | 0.00013389
68 | 0.0033326 | 0.00083522
69 | 0.0021686 | 0.0005435
70 | 0.0017834 | 0.00044696
71 | 0.0026651 | 0.00066793
72 | 0.0029166 | 0.00073098
73 | 0.0083149 | 0.0020839
74 | 0.0014219 | 0.00035635
75 | 0.01083 | 0.0027143
76 | 0.0018089 | 0.00045335
77 | 0.0040067 | 0.0010042
78 | 0.0029458 | 0.00073828
79 | 0.0035752 | 0.00089603
80 | 0.0087427 | 0.0021911
81 | 0.005337 | 0.0013376
82 | 0.0024773 | 0.00062087
83 | 0.0020295 | 0.00050865
84 | 0.0015856 | 0.0003974
85 | 0.0018229 | 0.00045686
86 | 0.0015856 | 0.0003974
87 | 0.0018209 | 0.00045636
88 | 0.0016745 | 0.00041967
89 | 0.0027421 | 0.00068724
90 | 0.0043536 | 0.0010911
91 | 0.0044027 | 0.0011034
92 | 0.0045183 | 0.0011324
93 | 0.0055434 | 0.0013893
94 | 0.0078288 | 0.0019621
95 | 0.0039689 | 0.0009947
96 | 0.011915 | 0.0029861
97 | 0.0050841 | 0.0012742
98 | 0.0050792 | 0.001273
99 | 0.0081386 | 0.0020397
100 | 0.0044398 | 0.0011127
101 | 0.0024318 | 0.00060947
102 | 0.0052985 | 0.0013279
103 | 0.0034222 | 0.00085768
104 | 0.0015831 | 0.00039677
105 | 0.0027129 | 0.00067991
106 | 0.0040966 | 0.0010267
107 | 0.0034956 | 0.00087608
108 | 0.0024051 | 0.00060277
109 | 0.0052775 | 0.0013227
110 | 0.016845 | 0.0042218
111 | 0.0024723 | 0.00061961
112 | 0.0049179 | 0.0012325
113 | 0.0034458 | 0.0008636
114 | 0.0012272 | 0.00030756
115 | 0.0012578 | 0.00031523
116 | 0.0020961 | 0.00052532
117 | 0.0018537 | 0.00046458
118 | 0.0009864 | 0.00024721
119 | 0.0010317 | 0.00025856
120 | 0.00098508 | 0.00024689
121 | 0.0019637 | 0.00049216
122 | 0.0024136 | 0.0006049
123 | 0.0014376 | 0.00036029
124 | 0.0016963 | 0.00042513
125 | 0.0018505 | 0.00046377
126 | 0.0013699 | 0.00034333
127 | 0.0021438 | 0.00053729
128 | 0.002326 | 0.00058296
129 | 0.0018529 | 0.00046437
130 | 0.003303 | 0.00082782
131 | 0.0022471 | 0.00056317
132 | 0.0015863 | 0.00039757
133 | 0.0013763 | 0.00034494
134 | 0.0010312 | 0.00025845
135 | 0.0010312 | 0.00025845
136 | 0.0010312 | 0.00025845
137 | 0.0053046 | 0.0013295
138 | 0.0031628 | 0.00079268
139 | 0.0019435 | 0.00048709
140 | 0.0011747 | 0.00029441
141 | 0.001521 | 0.00038121
142 | 0.0010091 | 0.00025291
143 | 0.00096142 | 0.00024096
144 | 0.00096214 | 0.00024113
145 | 0.0013102 | 0.00032836
146 | 0.0011065 | 0.00027732
147 | 0.0011837 | 0.00029666
148 | 0.005578 | 0.001398
149 | 0.0052684 | 0.0013204
150 | 0.0014013 | 0.00035121
151 | 0.0013699 | 0.00034333
152 | 0.0013887 | 0.00034805
153 | 0.0014221 | 0.00035642
154 | 0.0012542 | 0.00031432
155 | 0.0013677 | 0.00034278
156 | 0.0012939 | 0.00032428
157 | 0.0012545 | 0.00031441
158 | 0.0011976 | 0.00030014
159 | 0.0014199 | 0.00035586
160 | 0.0017595 | 0.00044096
161 | 0.0016972 | 0.00042535
162 | 0.0011859 | 0.00029721
163 | 0.0014293 | 0.00035822
164 | 0.0015767 | 0.00039515
165 | 0.0011877 | 0.00029767
166 | 0.0010952 | 0.00027449
167 | 0.00088267 | 0.00022122
168 | 0.0011847 | 0.0002969
169 | 0.0044024 | 0.0011033
170 | 0.001186 | 0.00029724
171 | 0.0011747 | 0.00029441
172 | 0.0010776 | 0.00027008
173 | 0.0011742 | 0.00029428
174 | 0.0010952 | 0.00027449
175 | 0.0013709 | 0.00034358
176 | 0.0013523 | 0.00033892
177 | 0.0019435 | 0.00048709
178 | 0.0011854 | 0.0002971
179 | 0.0011847 | 0.0002969
180 | 0.0012813 | 0.00032113
181 | 0.0010929 | 0.00027391
182 | 0.0011849 | 0.00029695
183 | 0.001237 | 0.00031001
184 | 0.0011852 | 0.00029705
185 | 0.0011867 | 0.00029742
186 | 0.0012945 | 0.00032442
187 | 0.001942 | 0.00048672
188 | 0.001236 | 0.00030978
189 | 0.0012948 | 0.00032451
190 | 0.0012347 | 0.00030945
191 | 0.0012359 | 0.00030974
192 | 0.0011977 | 0.00030018
193 | 0.001942 | 0.00048672
194 | 0.0013699 | 0.00034333
195 | 0.0012945 | 0.00032442
196 | 0.0012952 | 0.00032462
197 | 0.0012793 | 0.00032063
198 | 0.0010941 | 0.00027421
199 | 0.0014221 | 0.00035641
200 | 0.0011755 | 0.0002946
201 | 0.0011853 | 0.00029708
202 | 0.0011747 | 0.00029441
203 | 0.0019085 | 0.00047832
204 | 0.0019406 | 0.00048637
205 | 0.0013575 | 0.00034023
206 | 0.001352 | 0.00033885
207 | 0.0027603 | 0.00069179
208 | 0.0010932 | 0.00027397
209 | 0.0027769 | 0.00069595
210 | 0.0010949 | 0.00027441
211 | 0.0019402 | 0.00048626
212 | 0.0019074 | 0.00047803
213 | 0.0010947 | 0.00027436
214 | 0.000907 | 0.00022731
215 | 0.0012359 | 0.00030974
216 | 0.001477 | 0.00037016
217 | 0.00096195 | 0.00024109
218 | 0.00098529 | 0.00024694
219 | 0.00096143 | 0.00024096

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1