## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_230-83_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_230-83_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_230-83_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_230-83_0_5_node_138 | 0.4 | n |  | TRUE
4 | bus_LV_230-83_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_230-83_0_5_node_108 | 0.4 | n |  | TRUE
6 | bus_LV_230-83_0_5_node_117 | 0.4 | n |  | TRUE
7 | bus_LV_230-83_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_230-83_0_5_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_230-83_0_5_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_230-83_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_230-83_0_5_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_230-83_0_5_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_230-83_0_5_node_125 | 0.4 | n |  | TRUE
14 | bus_LV_230-83_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_230-83_0_5_node_127 | 0.4 | n |  | TRUE
16 | bus_LV_230-83_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_230-83_0_5_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_230-83_0_5_node_105 | 0.4 | n |  | TRUE
19 | bus_LV_230-83_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_230-83_0_5_node_158 | 0.4 | n |  | TRUE
21 | bus_LV_230-83_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_230-83_0_5_node_55 | 0.4 | n |  | TRUE
23 | bus_LV_230-83_0_5_node_63 | 0.4 | n |  | TRUE
24 | bus_LV_230-83_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_230-83_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_230-83_0_5_node_119 | 0.4 | n |  | TRUE
27 | bus_LV_230-83_0_5_node_159 | 0.4 | n |  | TRUE
28 | bus_LV_230-83_0_5_node_111 | 0.4 | n |  | TRUE
29 | bus_LV_230-83_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_230-83_0_5_node_142 | 0.4 | n |  | TRUE
31 | bus_LV_230-83_0_5_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_230-83_0_5_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_230-83_0_5_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_230-83_0_5_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_230-83_0_5_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_230-83_0_5_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_230-83_0_5_node_86 | 0.4 | n |  | TRUE
38 | bus_LV_230-83_0_5_node_94 | 0.4 | n |  | TRUE
39 | bus_LV_230-83_0_5_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_230-83_0_5_node_82 | 0.4 | n |  | TRUE
41 | bus_LV_230-83_0_5_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_230-83_0_5_node_81 | 0.4 | n |  | TRUE
43 | bus_LV_230-83_0_5_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_230-83_0_5_node_77 | 0.4 | n |  | TRUE
45 | bus_LV_230-83_0_5_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_230-83_0_5_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_230-83_0_5_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_230-83_0_5_node_146 | 0.4 | n |  | TRUE
49 | bus_LV_230-83_0_5_node_143 | 0.4 | n |  | TRUE
50 | bus_LV_230-83_0_5_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_230-83_0_5_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_230-83_0_5_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_230-83_0_5_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_230-83_0_5_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_230-83_0_5_node_144 | 0.4 | n |  | TRUE
56 | bus_LV_230-83_0_5_node_27 | 0.4 | n |  | TRUE
57 | bus_LV_230-83_0_5_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_230-83_0_5_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_230-83_0_5_node_65 | 0.4 | n |  | TRUE
60 | bus_LV_230-83_0_5_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_230-83_0_5_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_230-83_0_5_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_230-83_0_5_node_128 | 0.4 | n |  | TRUE
64 | bus_LV_230-83_0_5_node_156 | 0.4 | n |  | TRUE
65 | bus_LV_230-83_0_5_node_160 | 0.4 | n |  | TRUE
66 | bus_LV_230-83_0_5_node_36 | 0.4 | n |  | TRUE
67 | bus_LV_230-83_0_5_node_88 | 0.4 | n |  | TRUE
68 | bus_LV_230-83_0_5_node_155 | 0.4 | n |  | TRUE
69 | bus_LV_230-83_0_5_node_71 | 0.4 | n |  | TRUE
70 | bus_LV_230-83_0_5_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_230-83_0_5_node_135 | 0.4 | n |  | TRUE
72 | bus_LV_230-83_0_5_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_230-83_0_5_node_43 | 0.4 | n |  | TRUE
74 | bus_LV_230-83_0_5_node_140 | 0.4 | n |  | TRUE
75 | bus_LV_230-83_0_5_node_41 | 0.4 | n |  | TRUE
76 | bus_LV_230-83_0_5_node_102 | 0.4 | n |  | TRUE
77 | bus_LV_230-83_0_5_node_161 | 0.4 | n |  | TRUE
78 | bus_LV_230-83_0_5_node_139 | 0.4 | n |  | TRUE
79 | bus_LV_230-83_0_5_node_101 | 0.4 | n |  | TRUE
80 | bus_LV_230-83_0_5_node_99 | 0.4 | n |  | TRUE
81 | bus_LV_230-83_0_5_node_44 | 0.4 | n |  | TRUE
82 | bus_LV_230-83_0_5_node_51 | 0.4 | n |  | TRUE
83 | bus_LV_230-83_0_5_node_45 | 0.4 | n |  | TRUE
84 | bus_LV_230-83_0_5_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_230-83_0_5_node_124 | 0.4 | n |  | TRUE
86 | bus_LV_230-83_0_5_node_123 | 0.4 | n |  | TRUE
87 | bus_LV_230-83_0_5_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_230-83_0_5_node_49 | 0.4 | n |  | TRUE
89 | bus_LV_230-83_0_5_node_157 | 0.4 | n |  | TRUE
90 | bus_LV_230-83_0_5_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_230-83_0_5_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_230-83_0_5_node_136 | 0.4 | n |  | TRUE
93 | bus_LV_230-83_0_5_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_230-83_0_5_node_116 | 0.4 | n |  | TRUE
95 | bus_LV_230-83_0_5_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_230-83_0_5_node_106 | 0.4 | n |  | TRUE
97 | bus_LV_230-83_0_5_node_53 | 0.4 | n |  | TRUE
98 | bus_LV_230-83_0_5_node_61 | 0.4 | n |  | TRUE
99 | bus_LV_230-83_0_5_node_120 | 0.4 | n |  | TRUE
100 | bus_LV_230-83_0_5_node_110 | 0.4 | n |  | TRUE
101 | bus_LV_230-83_0_5_node_134 | 0.4 | n |  | TRUE
102 | bus_LV_230-83_0_5_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_230-83_0_5_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_230-83_0_5_node_76 | 0.4 | n |  | TRUE
105 | bus_LV_230-83_0_5_node_145 | 0.4 | n |  | TRUE
106 | bus_LV_230-83_0_5_node_148 | 0.4 | n |  | TRUE
107 | bus_LV_230-83_0_5_node_150 | 0.4 | n |  | TRUE
108 | bus_LV_230-83_0_5_node_149 | 0.4 | n |  | TRUE
109 | bus_LV_230-83_0_5_node_147 | 0.4 | n |  | TRUE
110 | bus_LV_230-83_0_5_node_154 | 0.4 | n |  | TRUE
111 | bus_LV_230-83_0_5_node_151 | 0.4 | n |  | TRUE
112 | bus_LV_230-83_0_5_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_230-83_0_5_node_62 | 0.4 | n |  | TRUE
114 | bus_LV_230-83_0_5_node_60 | 0.4 | n |  | TRUE
115 | bus_LV_230-83_0_5_node_122 | 0.4 | n |  | TRUE
116 | bus_LV_230-83_0_5_node_66 | 0.4 | n |  | TRUE
117 | bus_LV_230-83_0_5_node_57 | 0.4 | n |  | TRUE
118 | bus_LV_230-83_0_5_node_67 | 0.4 | n |  | TRUE
119 | bus_LV_230-83_0_5_node_129 | 0.4 | n |  | TRUE
120 | bus_LV_230-83_0_5_node_79 | 0.4 | n |  | TRUE
121 | bus_LV_230-83_0_5_node_80 | 0.4 | n |  | TRUE
122 | bus_LV_230-83_0_5_node_78 | 0.4 | n |  | TRUE
123 | bus_LV_230-83_0_5_node_130 | 0.4 | n |  | TRUE
124 | bus_LV_230-83_0_5_node_87 | 0.4 | n |  | TRUE
125 | bus_LV_230-83_0_5_node_141 | 0.4 | n |  | TRUE
126 | bus_LV_230-83_0_5_node_163 | 0.4 | n |  | TRUE
127 | bus_LV_230-83_0_5_node_137 | 0.4 | n |  | TRUE
128 | bus_LV_230-83_0_5_node_162 | 0.4 | n |  | TRUE
129 | bus_LV_230-83_0_5_node_54 | 0.4 | n |  | TRUE
130 | bus_LV_230-83_0_5_node_56 | 0.4 | n |  | TRUE
131 | bus_LV_230-83_0_5_node_126 | 0.4 | n |  | TRUE
132 | bus_LV_230-83_0_5_node_59 | 0.4 | n |  | TRUE
133 | bus_LV_230-83_0_5_node_85 | 0.4 | n |  | TRUE
134 | bus_LV_230-83_0_5_node_91 | 0.4 | n |  | TRUE
135 | bus_LV_230-83_0_5_node_93 | 0.4 | n |  | TRUE
136 | bus_LV_230-83_0_5_node_89 | 0.4 | n |  | TRUE
137 | bus_LV_230-83_0_5_node_90 | 0.4 | n |  | TRUE
138 | bus_LV_230-83_0_5_node_92 | 0.4 | n |  | TRUE
139 | bus_LV_230-83_0_5_node_103 | 0.4 | n |  | TRUE
140 | bus_LV_230-83_0_5_node_104 | 0.4 | n |  | TRUE
141 | bus_LV_230-83_0_5_node_114 | 0.4 | n |  | TRUE
142 | bus_LV_230-83_0_5_node_133 | 0.4 | n |  | TRUE
143 | bus_LV_230-83_0_5_node_113 | 0.4 | n |  | TRUE
144 | bus_LV_230-83_0_5_node_96 | 0.4 | n |  | TRUE
145 | bus_LV_230-83_0_5_node_97 | 0.4 | n |  | TRUE
146 | bus_LV_230-83_0_5_node_109 | 0.4 | n |  | TRUE
147 | bus_LV_230-83_0_5_node_112 | 0.4 | n |  | TRUE
148 | bus_LV_230-83_0_5_node_132 | 0.4 | n |  | TRUE
149 | bus_LV_230-83_0_5_node_115 | 0.4 | n |  | TRUE
150 | bus_LV_230-83_0_5_node_118 | 0.4 | n |  | TRUE
151 | bus_LV_230-83_0_5_node_131 | 0.4 | n |  | TRUE
152 | bus_LV_230-83_0_5_node_121 | 0.4 | n |  | TRUE
153 | bus_LV_230-83_0_5_node_153 | 0.4 | n |  | TRUE
154 | bus_LV_230-83_0_5_node_152 | 0.4 | n |  | TRUE
155 | bus_MV_371_0_node_164 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_230-83_0_5_load_0 | 0 | 0.0066564 | 0.0016683 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_230-83_0_5_load_138 | 3 | 0.0043829 | 0.0010985 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_230-83_0_5_load_117 | 6 | 0.0060374 | 0.0015131 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_230-83_0_5_load_50 | 9 | 0.0094346 | 0.0023645 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_230-83_0_5_load_125 | 13 | 0.0042585 | 0.0010673 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_230-83_0_5_load_127 | 15 | 0.0027125 | 0.00067981 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_230-83_0_5_load_105 | 18 | 0.0062361 | 0.0015629 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_230-83_0_5_load_158 | 20 | 0.0032108 | 0.0008047 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_230-83_0_5_load_55 | 22 | 0.0030711 | 0.00076968 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_230-83_0_5_load_63 | 23 | 0.0042287 | 0.0010598 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_230-83_0_5_load_119 | 26 | 0.0026617 | 0.0006671 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_230-83_0_5_load_159 | 27 | 0.0062233 | 0.0015597 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_230-83_0_5_load_111 | 28 | 0.0039724 | 0.00099559 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_230-83_0_5_load_142 | 30 | 0.0035132 | 0.00088048 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_230-83_0_5_load_52 | 34 | 0.0039805 | 0.0009976 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_230-83_0_5_load_98 | 36 | 0.021439 | 0.005373 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_230-83_0_5_load_86 | 37 | 0.0073761 | 0.0018486 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_230-83_0_5_load_94 | 38 | 0.011759 | 0.0029471 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_230-83_0_5_load_82 | 40 | 0.0075577 | 0.0018941 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_230-83_0_5_load_81 | 42 | 0.0088797 | 0.0022255 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_230-83_0_5_load_77 | 44 | 0.0029461 | 0.00073837 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_230-83_0_5_load_75 | 46 | 0.0082552 | 0.0020689 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_230-83_0_5_load_143 | 49 | 0.013626 | 0.003415 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_230-83_0_5_load_74 | 51 | 0.0058873 | 0.0014755 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_230-83_0_5_load_144 | 55 | 0.0057176 | 0.001433 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_230-83_0_5_load_65 | 59 | 0.0046671 | 0.0011697 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_230-83_0_5_load_58 | 60 | 0.004413 | 0.001106 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_230-83_0_5_load_128 | 63 | 0.010684 | 0.0026775 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_230-83_0_5_load_156 | 64 | 0.00024974 | 6.2592e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_230-83_0_5_load_160 | 65 | 0.020249 | 0.005075 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_230-83_0_5_load_155 | 68 | 0.0098609 | 0.0024714 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_230-83_0_5_load_71 | 69 | 0.010936 | 0.0027409 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_230-83_0_5_load_70 | 70 | 0.034284 | 0.0085923 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_230-83_0_5_load_135 | 71 | 0.0031176 | 0.00078134 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_230-83_0_5_load_140 | 74 | 0.0051089 | 0.0012804 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_230-83_0_5_load_161 | 77 | 0.011173 | 0.0028001 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_230-83_0_5_load_139 | 78 | 0.0043806 | 0.0010979 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_230-83_0_5_load_99 | 80 | 0.0079827 | 0.0020006 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_230-83_0_5_load_64 | 84 | 0.0065037 | 0.00163 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_230-83_0_5_load_124 | 85 | 0.0090053 | 0.0022569 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_230-83_0_5_load_123 | 86 | 0.0075258 | 0.0018861 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_230-83_0_5_load_73 | 87 | 0.0090035 | 0.0022565 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_230-83_0_5_load_157 | 89 | 0.00094312 | 0.00023637 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_230-83_0_5_load_136 | 92 | 0.0031148 | 0.00078064 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_230-83_0_5_load_107 | 93 | 0.0071896 | 0.0018019 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_230-83_0_5_load_84 | 95 | 0.0057846 | 0.0014498 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_230-83_0_5_load_106 | 96 | 0.0031935 | 0.00080036 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_230-83_0_5_load_53 | 97 | 0.0068965 | 0.0017284 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_230-83_0_5_load_120 | 99 | 0.0040631 | 0.0010183 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_230-83_0_5_load_110 | 100 | 0.0023822 | 0.00059704 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_230-83_0_5_load_83 | 103 | 0.017058 | 0.0042751 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_230-83_0_5_load_76 | 104 | 0.0094059 | 0.0023573 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_230-83_0_5_load_150 | 107 | 0.0002317 | 5.8069e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_230-83_0_5_load_149 | 108 | 0.00013419 | 3.3632e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_230-83_0_5_load_154 | 110 | 0.00013322 | 3.3388e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_230-83_0_5_load_151 | 111 | 0.00013066 | 3.2748e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_230-83_0_5_load_72 | 112 | 0.0098124 | 0.0024592 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_230-83_0_5_load_60 | 114 | 0.0057993 | 0.0014534 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_230-83_0_5_load_122 | 115 | 0.0042239 | 0.0010586 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_230-83_0_5_load_57 | 117 | 0.0066089 | 0.0016564 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_230-83_0_5_load_67 | 118 | 0.0046149 | 0.0011566 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_230-83_0_5_load_129 | 119 | 0.011034 | 0.0027653 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_230-83_0_5_load_78 | 122 | 0.017244 | 0.0043216 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_230-83_0_5_load_130 | 123 | 0.0015191 | 0.00038072 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_230-83_0_5_load_87 | 124 | 0.029417 | 0.0073727 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_230-83_0_5_load_141 | 125 | 0.0052842 | 0.0013243 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_230-83_0_5_load_163 | 126 | 0.0028088 | 0.00070396 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_230-83_0_5_load_137 | 127 | 0.0032246 | 0.00080815 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_230-83_0_5_load_162 | 128 | 0.0027769 | 0.00069595 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_230-83_0_5_load_54 | 129 | 0.0020501 | 0.00051381 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_230-83_0_5_load_56 | 130 | 0.0032083 | 0.00080408 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_230-83_0_5_load_126 | 131 | 0.0032092 | 0.00080429 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_230-83_0_5_load_59 | 132 | 0.010365 | 0.0025978 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_230-83_0_5_load_85 | 133 | 0.010091 | 0.0025291 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_230-83_0_5_load_89 | 136 | 0.0074245 | 0.0018608 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_230-83_0_5_load_90 | 137 | 0.0092777 | 0.0023252 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_230-83_0_5_load_104 | 140 | 0.0078729 | 0.0019731 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_230-83_0_5_load_114 | 141 | 0.0031735 | 0.00079534 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_230-83_0_5_load_133 | 142 | 0.0082747 | 0.0020738 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_230-83_0_5_load_113 | 143 | 0.0029405 | 0.00073697 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_230-83_0_5_load_96 | 144 | 0.0031714 | 0.00079483 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_230-83_0_5_load_97 | 145 | 0.0018324 | 0.00045924 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_230-83_0_5_load_109 | 146 | 0.0030362 | 0.00076095 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_230-83_0_5_load_112 | 147 | 0.0031689 | 0.00079419 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_230-83_0_5_load_115 | 149 | 0.0060356 | 0.0015127 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_230-83_0_5_load_118 | 150 | 0.0040817 | 0.001023 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_230-83_0_5_load_131 | 151 | 0.0040806 | 0.0010227 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_230-83_0_5_load_121 | 152 | 0.0063902 | 0.0016015 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_230-83_0_5_load_153 | 153 | 0.00012927 | 3.2398e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_230-83_0_5_load_152 | 154 | 0.00013051 | 3.271e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_230-83_0_5_line_0 |  | 0 | 1 | 0.025009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_230-83_0_5_line_1 |  | 1 | 2 | 0.004101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_230-83_0_5_line_2 |  | 2 | 3 | 0.044225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_230-83_0_5_line_3 |  | 3 | 90 | 0.021259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_230-83_0_5_line_4 |  | 4 | 5 | 0.004819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_230-83_0_5_line_5 |  | 4 | 6 | 0.024196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_230-83_0_5_line_6 |  | 5 | 93 | 0.0038429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_230-83_0_5_line_7 |  | 5 | 90 | 0.017419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_230-83_0_5_line_8 |  | 6 | 94 | 0.0021621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_230-83_0_5_line_9 |  | 7 | 8 | 0.011837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_230-83_0_5_line_10 |  | 7 | 9 | 0.031224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_230-83_0_5_line_11 |  | 8 | 87 | 0.02583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_230-83_0_5_line_12 |  | 9 | 81 | 0.028079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_230-83_0_5_line_13 |  | 10 | 11 | 0.006373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_230-83_0_5_line_14 |  | 10 | 12 | 0.004412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_230-83_0_5_line_15 |  | 10 | 13 | 0.012476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_230-83_0_5_line_16 |  | 11 | 22 | 0.011663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_230-83_0_5_line_17 |  | 11 | 14 | 0.052579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_230-83_0_5_line_18 |  | 12 | 86 | 0.01435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_230-83_0_5_line_19 |  | 12 | 83 | 0.029625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_230-83_0_5_line_20 |  | 13 | 95 | 0.0069833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_230-83_0_5_line_21 |  | 14 | 15 | 0.026546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_230-83_0_5_line_22 |  | 16 | 17 | 0.0046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_230-83_0_5_line_23 |  | 16 | 18 | 0.0070492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_230-83_0_5_line_24 |  | 17 | 28 | 0.016215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_230-83_0_5_line_25 |  | 17 | 25 | 0.028089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_230-83_0_5_line_26 |  | 18 | 96 | 0.013025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_230-83_0_5_line_27 |  | 19 | 20 | 0.024819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_230-83_0_5_line_28 |  | 19 | 21 | 0.011267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_230-83_0_5_line_29 |  | 21 | 23 | 0.002209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_230-83_0_5_line_30 |  | 22 | 97 | 0.0073316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_230-83_0_5_line_31 |  | 23 | 98 | 0.022949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_230-83_0_5_line_32 |  | 24 | 25 | 0.045353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_230-83_0_5_line_33 |  | 24 | 26 | 0.018853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_230-83_0_5_line_34 |  | 25 | 27 | 0.02867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_230-83_0_5_line_35 |  | 26 | 99 | 0.0031837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_230-83_0_5_line_36 |  | 28 | 100 | 0.010326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_230-83_0_5_line_37 |  | 29 | 30 | 0.026676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_230-83_0_5_line_38 |  | 29 | 31 | 0.023624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_230-83_0_5_line_39 |  | 30 | 101 | 0.013083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_230-83_0_5_line_40 |  | 31 | 78 | 0.013413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_230-83_0_5_line_41 |  | 32 | 33 | 0.098874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_230-83_0_5_line_42 |  | 32 | 34 | 0.015725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_230-83_0_5_line_43 |  | 33 | 64 | 0.023943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_230-83_0_5_line_44 |  | 34 | 56 | 0.025824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_230-83_0_5_line_45 |  | 35 | 36 | 0.029146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_230-83_0_5_line_46 |  | 35 | 37 | 0.012041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_230-83_0_5_line_47 |  | 35 | 38 | 0.01686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_230-83_0_5_line_48 |  | 36 | 41 | 0.012043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_230-83_0_5_line_49 |  | 38 | 102 | 0.030961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_230-83_0_5_line_50 |  | 39 | 40 | 0.025074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_230-83_0_5_line_51 |  | 39 | 41 | 0.022668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_230-83_0_5_line_52 |  | 39 | 42 | 0.011158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_230-83_0_5_line_53 |  | 40 | 103 | 0.026146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_230-83_0_5_line_54 |  | 41 | 61 | 0.034808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_230-83_0_5_line_55 |  | 42 | 82 | 0.024326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_230-83_0_5_line_56 |  | 43 | 44 | 0.09013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_230-83_0_5_line_57 |  | 43 | 45 | 0.024782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_230-83_0_5_line_58 |  | 43 | 46 | 0.021253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_230-83_0_5_line_59 |  | 44 | 53 | 0.023519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_230-83_0_5_line_60 |  | 45 | 62 | 0.028993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_230-83_0_5_line_61 |  | 45 | 63 | 0.025369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_230-83_0_5_line_62 |  | 45 | 50 | 0.059309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_230-83_0_5_line_63 |  | 46 | 104 | 0.050666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_230-83_0_5_line_64 |  | 47 | 48 | 0.12171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_230-83_0_5_line_65 |  | 47 | 49 | 0.21024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_230-83_0_5_line_66 |  | 48 | 108 | 0.057333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_230-83_0_5_line_67 |  | 49 | 55 | 0.01229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_230-83_0_5_line_68 |  | 50 | 51 | 0.02055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_230-83_0_5_line_69 |  | 51 | 112 | 0.025357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_230-83_0_5_line_70 |  | 52 | 53 | 0.015779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_230-83_0_5_line_71 |  | 52 | 54 | 0.064564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_230-83_0_5_line_72 |  | 52 | 55 | 0.049225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_230-83_0_5_line_73 |  | 54 | 60 | 0.019718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_230-83_0_5_line_74 |  | 54 | 56 | 0.097675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_230-83_0_5_line_75 |  | 57 | 58 | 0.003508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_230-83_0_5_line_76 |  | 57 | 59 | 0.020038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_230-83_0_5_line_77 |  | 58 | 71 | 0.024821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_230-83_0_5_line_78 |  | 59 | 116 | 0.019832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_230-83_0_5_line_79 |  | 60 | 117 | 0.096912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_230-83_0_5_line_80 |  | 61 | 69 | 0.041789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_230-83_0_5_line_81 |  | 61 | 70 | 0.014697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_230-83_0_5_line_82 |  | 61 | 66 | 0.037263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_230-83_0_5_line_83 |  | 62 | 65 | 0.03643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_230-83_0_5_line_84 |  | 63 | 119 | 0.020764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_230-83_0_5_line_85 |  | 64 | 88 | 0.013588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_230-83_0_5_line_86 |  | 66 | 67 | 0.000702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_230-83_0_5_line_87 |  | 66 | 68 | 0.035624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_230-83_0_5_line_88 |  | 67 | 124 | 0.034442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_230-83_0_5_line_89 |  | 69 | 74 | 0.02001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_230-83_0_5_line_90 |  | 71 | 92 | 0.017954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_230-83_0_5_line_91 |  | 72 | 73 | 0.075602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_230-83_0_5_line_92 |  | 72 | 74 | 0.011927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_230-83_0_5_line_93 |  | 73 | 79 | 0.006284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_230-83_0_5_line_94 |  | 73 | 80 | 0.014099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_230-83_0_5_line_95 |  | 75 | 76 | 0.004531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_230-83_0_5_line_96 |  | 75 | 77 | 0.003762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_230-83_0_5_line_97 |  | 76 | 126 | 0.013031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_230-83_0_5_line_98 |  | 76 | 79 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_230-83_0_5_line_99 |  | 78 | 127 | 0.018253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_230-83_0_5_line_100 |  | 79 | 128 | 0.018583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_230-83_0_5_line_101 |  | 81 | 82 | 0.017875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_230-83_0_5_line_102 |  | 83 | 84 | 0.018179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_230-83_0_5_line_103 |  | 83 | 85 | 0.0083419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_230-83_0_5_line_104 |  | 84 | 98 | 0.009442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_230-83_0_5_line_105 |  | 86 | 115 | 0.015503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_230-83_0_5_line_106 |  | 87 | 112 | 0.027965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_230-83_0_5_line_107 |  | 88 | 89 | 0.01148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_230-83_0_5_line_108 |  | 90 | 91 | 0.015813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_230-83_0_5_line_109 |  | 91 | 92 | 0.021649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_230-83_0_5_line_110 |  | 94 | 150 | 0.01601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_230-83_0_5_line_111 |  | 94 | 149 | 0.018339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_230-83_0_5_line_112 |  | 96 | 113 | 0.018129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_230-83_0_5_line_113 |  | 97 | 129 | 0.0032209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_230-83_0_5_line_114 |  | 98 | 132 | 0.01704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_230-83_0_5_line_115 |  | 99 | 152 | 0.025526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_230-83_0_5_line_116 |  | 100 | 146 | 0.0072271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_230-83_0_5_line_117 |  | 101 | 140 | 0.005467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_230-83_0_5_line_118 |  | 102 | 144 | 0.013602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_230-83_0_5_line_119 |  | 102 | 145 | 0.02195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_230-83_0_5_line_120 |  | 105 | 106 | 0.033526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_230-83_0_5_line_121 |  | 105 | 107 | 0.061256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_230-83_0_5_line_122 |  | 106 | 111 | 0.0193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_230-83_0_5_line_123 |  | 106 | 109 | 0.015524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_230-83_0_5_line_124 |  | 107 | 108 | 0.023786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_230-83_0_5_line_125 |  | 109 | 110 | 0.00078008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_230-83_0_5_line_126 |  | 110 | 153 | 0.011015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_230-83_0_5_line_127 |  | 111 | 154 | 0.013562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_230-83_0_5_line_128 |  | 113 | 114 | 0.0097524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_230-83_0_5_line_129 |  | 114 | 132 | 0.0085673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_230-83_0_5_line_130 |  | 116 | 118 | 0.030546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_230-83_0_5_line_131 |  | 119 | 121 | 0.0089548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_230-83_0_5_line_132 |  | 120 | 121 | 0.022296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_230-83_0_5_line_133 |  | 120 | 122 | 0.024068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_230-83_0_5_line_134 |  | 121 | 123 | 0.023463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_230-83_0_5_line_135 |  | 123 | 125 | 0.018814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_230-83_0_5_line_136 |  | 124 | 133 | 0.0059004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_230-83_0_5_line_137 |  | 129 | 130 | 0.033515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_230-83_0_5_line_138 |  | 130 | 131 | 0.0030077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_230-83_0_5_line_139 |  | 134 | 135 | 0.028942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
140 | LV_230-83_0_5_line_140 |  | 134 | 136 | 0.014674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
141 | LV_230-83_0_5_line_141 |  | 135 | 141 | 0.035738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_230-83_0_5_line_142 |  | 136 | 137 | 0.028989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_230-83_0_5_line_143 |  | 137 | 138 | 0.013389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_230-83_0_5_line_144 |  | 138 | 139 | 0.024785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_230-83_0_5_line_145 |  | 138 | 140 | 0.0065802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_230-83_0_5_line_146 |  | 139 | 142 | 0.027811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_230-83_0_5_line_147 |  | 141 | 143 | 0.0077361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
148 | LV_230-83_0_5_line_148 |  | 142 | 148 | 0.022846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_230-83_0_5_line_149 |  | 143 | 147 | 0.0066762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_230-83_0_5_line_150 |  | 144 | 146 | 0.025385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_230-83_0_5_line_151 |  | 145 | 147 | 0.0059441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
152 | LV_230-83_0_5_line_152 |  | 148 | 151 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_230-83_0_5_line_153 |  | 150 | 151 | 0.017839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_230-83_0_5_trafo_88 | 0.63 MVA 20/0.4 kV | 155 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2694282.3472 | 1263129.7322 | 2694286.2433 | 1263116.4502 | 2694281.1154 | 1263106.5299
1 | 2694283.9824 | 1263133.4946 | 2694282.3472 | 1263129.7322
2 | 2694283.9824 | 1263133.4946 | 2694314.0123 | 1263112.7566 | 2694320.3748 | 1263108.3657
3 | 2694337.8717 | 1263096.2904 | 2694320.3748 | 1263108.3657
4 | 2694333.1746 | 1263079.513 | 2694337.1511 | 1263076.7742
5 | 2694337.1511 | 1263076.7742 | 2694357.0471 | 1263063.0049
6 | 2694333.1746 | 1263079.513 | 2694332.0347 | 1263075.8431
7 | 2694337.8717 | 1263096.2904 | 2694333.1746 | 1263079.513
8 | 2694358.825 | 1263061.7745 | 2694357.0471 | 1263063.0049
9 | 2694652.3604 | 1263098.9725 | 2694641.0399 | 1263102.5387
10 | 2694652.3604 | 1263098.9725 | 2694650.5399 | 1263094.095 | 2694625.7309 | 1263101.9341
11 | 2694641.0399 | 1263102.5387 | 2694649.0092 | 1263127.1084
12 | 2694598.957 | 1263110.3941 | 2694625.7309 | 1263101.9341
13 | 2694572.7535 | 1263010.1159 | 2694566.4154 | 1263009.2917
14 | 2694562.2345 | 1263007.8459 | 2694566.4154 | 1263009.2917
15 | 2694566.4154 | 1263009.2917 | 2694561.9818 | 1263014.6919 | 2694557.7565 | 1263018.1956
16 | 2694572.7535 | 1263010.1159 | 2694576.3917 | 1263021.1971
17 | 2694572.7535 | 1263010.1159 | 2694580.5046 | 1263009.2725 | 2694588.2051 | 1263010.6523 | 2694600.8993 | 1263014.0025 | 2694605.4521 | 1263037.3943
18 | 2694562.2345 | 1263007.8459 | 2694554.3564 | 1263016.1601 | 2694551.9387 | 1263017.754
19 | 2694553.787 | 1262991.9424 | 2694556.4259 | 1262991.3508 | 2694566.6282 | 1262991.7587 | 2694565.9737 | 1262994.9953 | 2694564.4821 | 1263001.5768 | 2694562.2345 | 1263007.8459
20 | 2694552.1306 | 1263022.3247 | 2694556.2323 | 1263019.4594 | 2694557.7565 | 1263018.1956
21 | 2694605.4521 | 1263037.3943 | 2694631.9974 | 1263037.1442
22 | 2694478.1642 | 1262979.8242 | 2694473.7718 | 1262981.2329
23 | 2694478.1642 | 1262979.8242 | 2694480.4219 | 1262986.502
24 | 2694473.7718 | 1262981.2329 | 2694475.3513 | 1262986.5847 | 2694478.3017 | 1262994.3159 | 2694479.322 | 1262996.4439
25 | 2694449.5142 | 1262994.2783 | 2694454.7178 | 1262988.7792 | 2694467.1152 | 1262983.3617 | 2694473.7718 | 1262981.2329
26 | 2694480.4219 | 1262986.502 | 2694482.5453 | 1262992.7824 | 2694485.3325 | 1262998.5382
27 | 2694525.4615 | 1262964.9011 | 2694500.8797 | 1262960.9829
28 | 2694525.4615 | 1262964.9011 | 2694525.0266 | 1262967.5963 | 2694524.1061 | 1262973.3307 | 2694526.7307 | 1262974.1066
29 | 2694526.7307 | 1262974.1066 | 2694526.8211 | 1262976.3137
30 | 2694578.6787 | 1263028.1628 | 2694576.3917 | 1263021.1971
31 | 2694527.7601 | 1262999.2434 | 2694526.8211 | 1262976.3137
32 | 2694413.5251 | 1263015.8657 | 2694417.7586 | 1263015.9111 | 2694428.945 | 1263016.0231 | 2694449.5142 | 1262994.2783
33 | 2694413.5251 | 1263015.8657 | 2694413.3808 | 1263034.7179
34 | 2694449.5142 | 1262994.2783 | 2694449.9753 | 1263022.9423
35 | 2694413.3808 | 1263034.7179 | 2694413.3564 | 1263037.9015
36 | 2694484.1826 | 1263005.5395 | 2694481.8962 | 1263001.8127 | 2694479.322 | 1262996.4439
37 | 2694426.9515 | 1263162.0096 | 2694419.6112 | 1263150.8278 | 2694415.7087 | 1263138.1132
38 | 2694426.9515 | 1263162.0096 | 2694404.0068 | 1263167.9037
39 | 2694411.8699 | 1263125.606 | 2694415.7087 | 1263138.1132
40 | 2694404.0068 | 1263167.9037 | 2694396.3296 | 1263156.9054
41 | 2694492.6892 | 1263449.1815 | 2694496.4771 | 1263453.9903 | 2694498.1918 | 1263443.8095 | 2694504.8247 | 1263438.8892 | 2694508.2556 | 1263436.342 | 2694512.6936 | 1263432.9991 | 2694543.9451 | 1263471.0183 | 2694552.8908 | 1263463.7443 | 2694555.1132 | 1263466.571
42 | 2694555.1132 | 1263466.571 | 2694567.469 | 1263456.845
43 | 2694492.6892 | 1263449.1815 | 2694489.7497 | 1263439.8491 | 2694482.1359 | 1263429.786 | 2694481.2059 | 1263428.5591
44 | 2694587.7607 | 1263440.8722 | 2694567.469 | 1263456.845
45 | 2694539.5286 | 1263081.1869 | 2694552.5371 | 1263107.2683
46 | 2694539.5286 | 1263081.1869 | 2694529.9838 | 1263084.904 | 2694528.2402 | 1263085.3422
47 | 2694539.5286 | 1263081.1869 | 2694531.0137 | 1263066.6349
48 | 2694557.553 | 1263118.205 | 2694555.8877 | 1263113.9861 | 2694552.5371 | 1263107.2683
49 | 2694513.5817 | 1263041.1175 | 2694521.4983 | 1263051.1188 | 2694526.2475 | 1263058.4895 | 2694531.0137 | 1263066.6349
50 | 2694562.5539 | 1263103.7177 | 2694557.6297 | 1263094.576 | 2694552.6364 | 1263089.7589 | 2694549.0537 | 1263082.8846
51 | 2694557.553 | 1263118.205 | 2694558.433 | 1263117.8299 | 2694562.711 | 1263116.0302 | 2694566.807 | 1263114.3054 | 2694567.8917 | 1263113.8446 | 2694562.5539 | 1263103.7177
52 | 2694562.5539 | 1263103.7177 | 2694573.0036 | 1263099.8067
53 | 2694549.0537 | 1263082.8846 | 2694545.2317 | 1263075.5512 | 2694543.0283 | 1263065.8748 | 2694538.8263 | 1263059.1232
54 | 2694540.2007 | 1263139.4894 | 2694539.6803 | 1263133.8765 | 2694555.4545 | 1263129.2916 | 2694554.1725 | 1263126.0685 | 2694553.8902 | 1263125.3523 | 2694555.7296 | 1263123.8694 | 2694557.2262 | 1263121.6804 | 2694557.553 | 1263118.205
55 | 2694595.992 | 1263092.7657 | 2694589.7723 | 1263095.8465 | 2694581.6162 | 1263096.5833 | 2694573.0036 | 1263099.8067
56 | 2694586.0109 | 1263209.4118 | 2694584.9229 | 1263229.3773 | 2694581.5695 | 1263282.6225 | 2694580.6825 | 1263299.3831
57 | 2694574.9482 | 1263195.4681 | 2694575.2094 | 1263202.6892 | 2694580.4624 | 1263202.5731 | 2694580.5043 | 1263209.3682 | 2694586.0109 | 1263209.4118
58 | 2694586.0109 | 1263209.4118 | 2694590.0754 | 1263209.1766 | 2694606.6688 | 1263204.7172
59 | 2694579.6972 | 1263322.8807 | 2694580.3059 | 1263306.4994 | 2694580.6825 | 1263299.3831
60 | 2694554.5872 | 1263209.3983 | 2694573.3476 | 1263202.7484 | 2694575.2094 | 1263202.6892 | 2694574.9482 | 1263195.4681
61 | 2694574.9482 | 1263195.4681 | 2694559.5068 | 1263201.3926 | 2694551.0832 | 1263204.0415
62 | 2694574.9482 | 1263195.4681 | 2694574.2101 | 1263185.5704 | 2694573.1739 | 1263177.3472 | 2694578.8913 | 1263175.9931 | 2694574.9562 | 1263154.0123 | 2694572.8719 | 1263146.3172 | 2694577.7217 | 1263145.5052
63 | 2694606.6688 | 1263204.7172 | 2694608.7419 | 1263204.16 | 2694629.4966 | 1263194.3619 | 2694649.9756 | 1263179.0534
64 | 2694821.2844 | 1263186.6049 | 2694848.6577 | 1263235.2722 | 2694856.5158 | 1263249.3319 | 2694865.4792 | 1263265.411 | 2694874.2934 | 1263280.9205 | 2694880.9681 | 1263292.6705
65 | 2694821.2844 | 1263186.6049 | 2694815.8311 | 1263189.809 | 2694769.9314 | 1263223.345 | 2694645.4944 | 1263296.2339 | 2694643.0684 | 1263297.7347
66 | 2694880.9681 | 1263292.6705 | 2694886.7455 | 1263310.5666 | 2694895.3285 | 1263337.1815 | 2694886.6439 | 1263343.1935
67 | 2694643.0684 | 1263297.7347 | 2694632.6163 | 1263304.2004
68 | 2694577.7217 | 1263145.5052 | 2694597.9886 | 1263142.1053
69 | 2694597.9886 | 1263142.1053 | 2694612.3354 | 1263139.6985 | 2694622.5592 | 1263136.1887
70 | 2694579.6972 | 1263322.8807 | 2694579.8717 | 1263326.0973 | 2694581.3825 | 1263328.668 | 2694584.3169 | 1263329.8492 | 2694590.7543 | 1263330.0968
71 | 2694563.323 | 1263370.1684 | 2694567.2439 | 1263369.4861 | 2694575.3047 | 1263368.0917 | 2694580.3824 | 1263366.6828 | 2694577.4311 | 1263353.3804 | 2694575.3989 | 1263337.257 | 2694580.1775 | 1263336.6441 | 2694590.7543 | 1263330.0968
72 | 2694590.7543 | 1263330.0968 | 2694632.6163 | 1263304.2004
73 | 2694563.323 | 1263370.1684 | 2694543.8578 | 1263373.3129
74 | 2694563.323 | 1263370.1684 | 2694567.2439 | 1263369.4861 | 2694575.3047 | 1263368.0917 | 2694577.1365 | 1263375.0822 | 2694580.8214 | 1263386.7951 | 2694581.1016 | 1263391.8815 | 2694578.943 | 1263395.8946 | 2694579.6442 | 1263397.7407 | 2694582.8464 | 1263406.1876 | 2694586.0562 | 1263414.6347 | 2694591.4733 | 1263417.4347 | 2694593.7786 | 1263421.1969 | 2694598.3296 | 1263432.9237 | 2694587.7607 | 1263440.8722
75 | 2694360.0695 | 1263169.7485 | 2694356.658 | 1263170.6059
76 | 2694356.658 | 1263170.6059 | 2694351.7466 | 1263151.1792
77 | 2694360.0695 | 1263169.7485 | 2694354.0478 | 1263145.6692
78 | 2694346.8857 | 1263131.952 | 2694351.7466 | 1263151.1792
79 | 2694520.6349 | 1263333.1457 | 2694506.6204 | 1263343.5627 | 2694500.8501 | 1263353.423 | 2694498.8149 | 1263365.2667 | 2694500.8678 | 1263376.3419 | 2694504.6345 | 1263379.6492 | 2694543.8578 | 1263373.3129
80 | 2694540.2007 | 1263139.4894 | 2694515.2134 | 1263146.3734 | 2694511.5052 | 1263147.4038 | 2694499.9764 | 1263150.8111
81 | 2694540.2007 | 1263139.4894 | 2694540.7213 | 1263144.6241 | 2694535.7527 | 1263152.7637
82 | 2694510.5848 | 1263138.0593 | 2694513.7481 | 1263141.4237 | 2694539.6803 | 1263133.8765 | 2694540.2007 | 1263139.4894
83 | 2694548.3871 | 1263235.2757 | 2694561.9796 | 1263230.011 | 2694554.5872 | 1263209.3983
84 | 2694551.0832 | 1263204.0415 | 2694537.23 | 1263208.3978 | 2694531.2181 | 1263210.0784
85 | 2694470.728 | 1263420.4851 | 2694477.6648 | 1263423.8876 | 2694481.2059 | 1263428.5591
86 | 2694510.088 | 1263137.5621 | 2694510.5848 | 1263138.0593
87 | 2694510.5848 | 1263138.0593 | 2694476.3692 | 1263147.9755
88 | 2694510.088 | 1263137.5621 | 2694500.9094 | 1263104.3654
89 | 2694480.7871 | 1263156.4824 | 2694499.9764 | 1263150.8111
90 | 2694354.0478 | 1263145.6692 | 2694349.692 | 1263128.2512
91 | 2694469.3493 | 1263159.8627 | 2694431.4712 | 1263170.0661 | 2694440.1681 | 1263200.5408 | 2694444.6641 | 1263199.2337
92 | 2694469.3493 | 1263159.8627 | 2694480.7871 | 1263156.4824
93 | 2694444.6641 | 1263199.2337 | 2694446.3908 | 1263205.2773
94 | 2694444.6641 | 1263199.2337 | 2694458.2018 | 1263195.2951
95 | 2694430.3595 | 1263209.9362 | 2694429.1107 | 1263205.5794
96 | 2694428.0836 | 1263201.9601 | 2694429.1107 | 1263205.5794
97 | 2694430.3595 | 1263209.9362 | 2694433.9337 | 1263222.4701
98 | 2694430.3595 | 1263209.9362 | 2694446.3908 | 1263205.2773
99 | 2694396.3296 | 1263156.9054 | 2694385.8818 | 1263141.938
100 | 2694446.3908 | 1263205.2773 | 2694448.2383 | 1263211.7676 | 2694449.0946 | 1263214.7615 | 2694457.4961 | 1263212.3271
101 | 2694595.992 | 1263092.7657 | 2694598.957 | 1263110.3941
102 | 2694553.787 | 1262991.9424 | 2694540.6279 | 1262992.6882 | 2694536.1733 | 1262994.9575
103 | 2694553.787 | 1262991.9424 | 2694554.4023 | 1262983.6233
104 | 2694527.7601 | 1262999.2434 | 2694536.1733 | 1262994.9575
105 | 2694538.6957 | 1263025.7824 | 2694544.1301 | 1263022.902 | 2694551.9387 | 1263017.754
106 | 2694649.0092 | 1263127.1084 | 2694649.0092 | 1263127.1084 | 2694622.5592 | 1263136.1887
107 | 2694470.728 | 1263420.4851 | 2694473.0092 | 1263427.6496 | 2694475.4962 | 1263430.733
108 | 2694337.8717 | 1263096.2904 | 2694340.8408 | 1263108.0473 | 2694344.4398 | 1263107.2485
109 | 2694344.4398 | 1263107.2485 | 2694349.692 | 1263128.2512
110 | 2694358.825 | 1263061.7745 | 2694367.8729 | 1263074.9823
111 | 2694358.825 | 1263061.7745 | 2694373.9033 | 1263051.3365
112 | 2694495.3845 | 1263013.4599 | 2694488.7374 | 1263005.5695 | 2694485.3325 | 1262998.5382
113 | 2694578.6787 | 1263028.1628 | 2694579.6835 | 1263031.2229
114 | 2694527.7601 | 1262999.2434 | 2694512.1583 | 1263006.0944
115 | 2694399.5499 | 1263042.2418 | 2694399.5227 | 1263046.3002 | 2694412.02 | 1263046.4109 | 2694413.3031 | 1263044.8523 | 2694413.3564 | 1263037.9015
116 | 2694488.2362 | 1263011.5129 | 2694486.1403 | 1263008.7306 | 2694484.1826 | 1263005.5395
117 | 2694411.8699 | 1263125.606 | 2694417.0828 | 1263123.9584
118 | 2694513.5817 | 1263041.1175 | 2694504.7983 | 1263030.7313
119 | 2694513.5817 | 1263041.1175 | 2694493.5639 | 1263050.123
120 | 2694873.2036 | 1263406.5273 | 2694876.4832 | 1263412.4737 | 2694884.5517 | 1263423.2674 | 2694888.1798 | 1263430.0311 | 2694888.9797 | 1263435.5818
121 | 2694873.2036 | 1263406.5273 | 2694869.6122 | 1263402.1662 | 2694868.5015 | 1263400.4914 | 2694864.4754 | 1263394.5887 | 2694861.1109 | 1263388.7634 | 2694855.5175 | 1263376.775 | 2694853.7414 | 1263371.9648 | 2694853.8937 | 1263369.0427 | 2694855.2234 | 1263365.9949 | 2694858.105 | 1263362.9497 | 2694867.0871 | 1263356.7317
122 | 2694888.9797 | 1263435.5818 | 2694902.8005 | 1263425.9402 | 2694901.6997 | 1263424.121 | 2694901.9668 | 1263423.9402
123 | 2694888.9797 | 1263435.5818 | 2694876.3285 | 1263444.6307
124 | 2694886.6439 | 1263343.1935 | 2694867.0871 | 1263356.7317
125 | 2694875.6825 | 1263445.0679 | 2694876.3285 | 1263444.6307
126 | 2694866.5601 | 1263451.2421 | 2694875.6825 | 1263445.0679
127 | 2694901.9668 | 1263423.9402 | 2694912.3856 | 1263416.8866 | 2694911.8336 | 1263416.0771 | 2694911.8336 | 1263416.0771
128 | 2694495.3845 | 1263013.4599 | 2694504.3139 | 1263009.5389
129 | 2694504.3139 | 1263009.5389 | 2694512.1583 | 1263006.0944
130 | 2694346.8857 | 1263131.952 | 2694324.6265 | 1263137.3792 | 2694318.3406 | 1263141.7115
131 | 2694522.594 | 1263212.4894 | 2694531.2181 | 1263210.0784
132 | 2694516.2649 | 1263229.958 | 2694519.1121 | 1263221.9859 | 2694524.7947 | 1263219.9751 | 2694522.594 | 1263212.4894
133 | 2694516.2649 | 1263229.958 | 2694524.384 | 1263252.6147
134 | 2694522.594 | 1263212.4894 | 2694508.7603 | 1263216.3492 | 2694506.2988 | 1263207.5874
135 | 2694506.2988 | 1263207.5874 | 2694501.2103 | 1263189.4746
136 | 2694499.337 | 1263098.6784 | 2694500.9094 | 1263104.3654
137 | 2694579.6835 | 1263031.2229 | 2694584.2048 | 1263044.994 | 2694584.6048 | 1263053.8965 | 2694576.0557 | 1263059.2921
138 | 2694573.5122 | 1263060.8973 | 2694576.0557 | 1263059.2921
139 | 2694469.1725 | 1263085.1437 | 2694475.4487 | 1263113.4002
140 | 2694475.4487 | 1263113.4002 | 2694461.2435 | 1263117.0814
141 | 2694469.1725 | 1263085.1437 | 2694462.5477 | 1263064.0764 | 2694474.9995 | 1263058.4747
142 | 2694461.2435 | 1263117.0814 | 2694433.1812 | 1263124.3534
143 | 2694423.357 | 1263121.9753 | 2694424.8441 | 1263126.5139 | 2694433.1812 | 1263124.3534
144 | 2694423.357 | 1263121.9753 | 2694433.9091 | 1263099.5367
145 | 2694423.357 | 1263121.9753 | 2694417.0828 | 1263123.9584
146 | 2694433.9091 | 1263099.5367 | 2694418.4749 | 1263092.2733 | 2694410.4398 | 1263093.9242 | 2694409.5876 | 1263091.6198 | 2694409.497 | 1263091.6439
147 | 2694482.0546 | 1263055.3008 | 2694474.9995 | 1263058.4747
148 | 2694387.4187 | 1263097.5152 | 2694409.497 | 1263091.6439
149 | 2694488.143 | 1263052.5617 | 2694482.0546 | 1263055.3008
150 | 2694488.2362 | 1263011.5129 | 2694490.5152 | 1263014.5385 | 2694497.6617 | 1263022.2923 | 2694504.7983 | 1263030.7313
151 | 2694488.143 | 1263052.5617 | 2694493.5639 | 1263050.123
152 | 2694387.4187 | 1263097.5152 | 2694378.5343 | 1263090.5456 | 2694377.9547 | 1263089.6995
153 | 2694377.9547 | 1263089.6995 | 2694367.8729 | 1263074.9823

## bus_geodata
| x | y | coords
0 | 2694281.1154 | 1263106.5299
1 | 2694282.3472 | 1263129.7322
2 | 2694283.9824 | 1263133.4946
3 | 2694320.3748 | 1263108.3657
4 | 2694337.1511 | 1263076.7742
5 | 2694333.1746 | 1263079.513
6 | 2694357.0471 | 1263063.0049
7 | 2694652.3604 | 1263098.9725
8 | 2694641.0399 | 1263102.5387
9 | 2694625.7309 | 1263101.9341
10 | 2694566.4154 | 1263009.2917
11 | 2694572.7535 | 1263010.1159
12 | 2694562.2345 | 1263007.8459
13 | 2694557.7565 | 1263018.1956
14 | 2694605.4521 | 1263037.3943
15 | 2694631.9974 | 1263037.1442
16 | 2694478.1642 | 1262979.8242
17 | 2694473.7718 | 1262981.2329
18 | 2694480.4219 | 1262986.502
19 | 2694525.4615 | 1262964.9011
20 | 2694500.8797 | 1262960.9829
21 | 2694526.7307 | 1262974.1066
22 | 2694576.3917 | 1263021.1971
23 | 2694526.8211 | 1262976.3137
24 | 2694413.5251 | 1263015.8657
25 | 2694449.5142 | 1262994.2783
26 | 2694413.3807 | 1263034.7179
27 | 2694449.9753 | 1263022.9423
28 | 2694479.322 | 1262996.4439
29 | 2694426.9515 | 1263162.0096
30 | 2694415.7087 | 1263138.1132
31 | 2694404.0068 | 1263167.9037
32 | 2694555.1132 | 1263466.571
33 | 2694492.6892 | 1263449.1815
34 | 2694567.469 | 1263456.845
35 | 2694539.5286 | 1263081.1869
36 | 2694552.5371 | 1263107.2683
37 | 2694528.2402 | 1263085.3422
38 | 2694531.0137 | 1263066.6349
39 | 2694562.5539 | 1263103.7177
40 | 2694549.0537 | 1263082.8846
41 | 2694557.553 | 1263118.205
42 | 2694573.0036 | 1263099.8067
43 | 2694586.0109 | 1263209.4118
44 | 2694580.6825 | 1263299.3831
45 | 2694574.9483 | 1263195.4681
46 | 2694606.6688 | 1263204.7172
47 | 2694821.2844 | 1263186.6049
48 | 2694880.9681 | 1263292.6705
49 | 2694643.0684 | 1263297.7347
50 | 2694577.7217 | 1263145.5052
51 | 2694597.9886 | 1263142.1053
52 | 2694590.7543 | 1263330.0968
53 | 2694579.6972 | 1263322.8807
54 | 2694563.323 | 1263370.1684
55 | 2694632.6163 | 1263304.2004
56 | 2694587.7607 | 1263440.8722
57 | 2694356.658 | 1263170.6059
58 | 2694360.0695 | 1263169.7485
59 | 2694351.7466 | 1263151.1792
60 | 2694543.8578 | 1263373.3129
61 | 2694540.2007 | 1263139.4894
62 | 2694554.5872 | 1263209.3983
63 | 2694551.0832 | 1263204.0415
64 | 2694481.2059 | 1263428.5591
65 | 2694548.3871 | 1263235.2757
66 | 2694510.5848 | 1263138.0593
67 | 2694510.088 | 1263137.5621
68 | 2694476.3691 | 1263147.9755
69 | 2694499.9764 | 1263150.8111
70 | 2694535.7527 | 1263152.7637
71 | 2694354.0478 | 1263145.6692
72 | 2694469.3493 | 1263159.8627
73 | 2694444.6641 | 1263199.2337
74 | 2694480.7871 | 1263156.4824
75 | 2694429.1107 | 1263205.5794
76 | 2694430.3595 | 1263209.9362
77 | 2694428.0836 | 1263201.9601
78 | 2694396.3296 | 1263156.9054
79 | 2694446.3908 | 1263205.2773
80 | 2694458.2018 | 1263195.2951
81 | 2694598.957 | 1263110.3941
82 | 2694595.992 | 1263092.7657
83 | 2694553.787 | 1262991.9424
84 | 2694536.1733 | 1262994.9575
85 | 2694554.4023 | 1262983.6233
86 | 2694551.9387 | 1263017.754
87 | 2694649.0092 | 1263127.1084
88 | 2694470.728 | 1263420.4851
89 | 2694475.4962 | 1263430.733
90 | 2694337.8717 | 1263096.2904
91 | 2694344.4398 | 1263107.2485
92 | 2694349.692 | 1263128.2512
93 | 2694332.0347 | 1263075.8431
94 | 2694358.825 | 1263061.7745
95 | 2694552.1306 | 1263022.3247
96 | 2694485.3325 | 1262998.5382
97 | 2694578.6787 | 1263028.1628
98 | 2694527.7601 | 1262999.2434
99 | 2694413.3564 | 1263037.9015
100 | 2694484.1826 | 1263005.5395
101 | 2694411.8699 | 1263125.606
102 | 2694513.5817 | 1263041.1175
103 | 2694538.8263 | 1263059.1232
104 | 2694649.9756 | 1263179.0534
105 | 2694873.2036 | 1263406.5273
106 | 2694888.9797 | 1263435.5818
107 | 2694867.0871 | 1263356.7317
108 | 2694886.6439 | 1263343.1935
109 | 2694876.3285 | 1263444.6307
110 | 2694875.6825 | 1263445.0679
111 | 2694901.9668 | 1263423.9402
112 | 2694622.5592 | 1263136.1887
113 | 2694495.3845 | 1263013.4599
114 | 2694504.3139 | 1263009.5389
115 | 2694538.6957 | 1263025.7824
116 | 2694346.8857 | 1263131.952
117 | 2694520.6349 | 1263333.1457
118 | 2694318.3406 | 1263141.7115
119 | 2694531.2181 | 1263210.0784
120 | 2694516.2649 | 1263229.958
121 | 2694522.594 | 1263212.4894
122 | 2694524.384 | 1263252.6147
123 | 2694506.2988 | 1263207.5874
124 | 2694500.9094 | 1263104.3654
125 | 2694501.2103 | 1263189.4746
126 | 2694433.9337 | 1263222.4701
127 | 2694385.8818 | 1263141.938
128 | 2694457.4961 | 1263212.3271
129 | 2694579.6835 | 1263031.2229
130 | 2694576.0557 | 1263059.2921
131 | 2694573.5122 | 1263060.8973
132 | 2694512.1583 | 1263006.0944
133 | 2694499.337 | 1263098.6784
134 | 2694475.4487 | 1263113.4002
135 | 2694469.1725 | 1263085.1437
136 | 2694461.2435 | 1263117.0814
137 | 2694433.1812 | 1263124.3534
138 | 2694423.357 | 1263121.9753
139 | 2694433.9091 | 1263099.5367
140 | 2694417.0828 | 1263123.9584
141 | 2694474.9995 | 1263058.4747
142 | 2694409.497 | 1263091.6439
143 | 2694482.0546 | 1263055.3008
144 | 2694504.7983 | 1263030.7313
145 | 2694493.5639 | 1263050.123
146 | 2694488.2362 | 1263011.5129
147 | 2694488.143 | 1263052.5617
148 | 2694387.4187 | 1263097.5152
149 | 2694373.9033 | 1263051.3365
150 | 2694367.8729 | 1263074.9823
151 | 2694377.9547 | 1263089.6995
152 | 2694399.5499 | 1263042.2418
153 | 2694866.5601 | 1263451.2421
154 | 2694911.8336 | 1263416.0771
155 | 2694510.5848 | 1263138.0593

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97191 | -0.54203 | 0.0066564 | 0.0016683
1 | 0.97207 | -0.53896 | 0 | 0
2 | 0.97209 | -0.53846 | 0 | 0
3 | 0.97237 | -0.53303 | 0.0043829 | 0.0010985
4 | 0.97317 | -0.51719 | 0 | 0
5 | 0.97302 | -0.52018 | 0 | 0
6 | 0.97393 | -0.50217 | 0.0060374 | 0.0015131
7 | 0.98646 | -0.25823 | 0 | 0
8 | 0.98605 | -0.26606 | 0 | 0
9 | 0.98753 | -0.23758 | 0.0094346 | 0.0023645
10 | 0.97069 | -0.5657 | 0 | 0
11 | 0.97056 | -0.56819 | 0 | 0
12 | 0.97082 | -0.56315 | 0 | 0
13 | 0.97057 | -0.56801 | 0.0042585 | 0.0010673
14 | 0.97043 | -0.57083 | 0 | 0
15 | 0.97036 | -0.57216 | 0.0027125 | 0.00067981
16 | 0.97883 | -0.40562 | 0 | 0
17 | 0.97923 | -0.39797 | 0 | 0
18 | 0.97823 | -0.41736 | 0.0062361 | 0.0015629
19 | 0.9732 | -0.51602 | 0 | 0
20 | 0.97313 | -0.51749 | 0.0032108 | 0.0008047
21 | 0.97324 | -0.51536 | 0 | 0
22 | 0.97036 | -0.57217 | 0.0030711 | 0.00076968
23 | 0.97325 | -0.51522 | 0.0042287 | 0.0010598
24 | 0.97817 | -0.41868 | 0 | 0
25 | 0.97872 | -0.40785 | 0 | 0
26 | 0.97794 | -0.42318 | 0.0026617 | 0.0006671
27 | 0.97856 | -0.4111 | 0.0062233 | 0.0015597
28 | 0.9809 | -0.36536 | 0.0039724 | 0.00099559
29 | 0.97985 | -0.38621 | 0 | 0
30 | 0.98004 | -0.38252 | 0.0035132 | 0.00088048
31 | 0.97968 | -0.38947 | 0 | 0
32 | 0.97198 | -0.54122 | 0 | 0
33 | 0.97187 | -0.5434 | 0 | 0
34 | 0.97199 | -0.54087 | 0.0039805 | 0.0009976
35 | 0.98905 | -0.2081 | 0 | 0
36 | 0.99076 | -0.17549 | 0.021439 | 0.005373
37 | 0.98897 | -0.20969 | 0.0073761 | 0.0018486
38 | 0.98809 | -0.22646 | 0.011759 | 0.0029471
39 | 0.99052 | -0.18009 | 0 | 0
40 | 0.98995 | -0.19106 | 0.0075577 | 0.0018941
41 | 0.99152 | -0.1609 | 0 | 0
42 | 0.99009 | -0.18832 | 0.0088797 | 0.0022255
43 | 0.97821 | -0.41857 | 0 | 0
44 | 0.9749 | -0.4835 | 0.0029461 | 0.00073837
45 | 0.97952 | -0.39284 | 0 | 0
46 | 0.97786 | -0.42541 | 0.0082552 | 0.0020689
47 | 0.9723 | -0.53496 | 0 | 0
48 | 0.9722 | -0.53697 | 0 | 0
49 | 0.97247 | -0.53145 | 0.013626 | 0.003415
50 | 0.98292 | -0.32676 | 0 | 0
51 | 0.9835 | -0.31536 | 0.0058873 | 0.0014755
52 | 0.97356 | -0.50981 | 0 | 0
53 | 0.9741 | -0.49924 | 0 | 0
54 | 0.97259 | -0.52907 | 0 | 0
55 | 0.97264 | -0.52816 | 0.0057176 | 0.001433
56 | 0.97212 | -0.5384 | 0 | 0
57 | 0.97159 | -0.54838 | 0 | 0
58 | 0.97162 | -0.54778 | 0 | 0
59 | 0.97142 | -0.55182 | 0.0046671 | 0.0011697
60 | 0.97239 | -0.53308 | 0.004413 | 0.001106
61 | 0.99526 | -0.08961 | 0 | 0
62 | 0.97898 | -0.40352 | 0 | 0
63 | 0.97845 | -0.41396 | 0.010684 | 0.0026775
64 | 0.97184 | -0.54393 | 0.00024974 | 6.2592e-05
65 | 0.9783 | -0.41694 | 0.020249 | 0.005075
66 | 0.99991 | -0.0016789 | 0 | 0
67 | 1 | 0 | -0.59954 | -0.15358
68 | 0.99959 | -0.0078049 | 0.0098609 | 0.0024714
69 | 0.9937 | -0.11965 | 0.010936 | 0.0027409
70 | 0.9948 | -0.09848 | 0.034284 | 0.0085923
71 | 0.97183 | -0.54353 | 0.0031176 | 0.00078134
72 | 0.99289 | -0.13542 | 0 | 0
73 | 0.99118 | -0.16855 | 0 | 0
74 | 0.99316 | -0.1302 | 0.0051089 | 0.0012804
75 | 0.99082 | -0.17545 | 0 | 0
76 | 0.99087 | -0.17455 | 0 | 0
77 | 0.99078 | -0.1762 | 0.011173 | 0.0028001
78 | 0.97959 | -0.39132 | 0.0043806 | 0.0010979
79 | 0.99108 | -0.17042 | 0 | 0
80 | 0.99107 | -0.17055 | 0.0079827 | 0.0020006
81 | 0.98855 | -0.21787 | 0 | 0
82 | 0.9892 | -0.20534 | 0 | 0
83 | 0.97201 | -0.53965 | 0 | 0
84 | 0.97289 | -0.52224 | 0.0065037 | 0.00163
85 | 0.97194 | -0.54104 | 0.0090053 | 0.0022569
86 | 0.97066 | -0.56627 | 0.0075258 | 0.0018861
87 | 0.98516 | -0.28319 | 0.0090035 | 0.0022565
88 | 0.97183 | -0.54416 | 0 | 0
89 | 0.97182 | -0.54436 | 0.00094312 | 0.00023637
90 | 0.97258 | -0.5287 | 0 | 0
91 | 0.97236 | -0.53323 | 0 | 0
92 | 0.97204 | -0.53942 | 0.0031148 | 0.00078064
93 | 0.97299 | -0.52069 | 0.0071896 | 0.0018019
94 | 0.97401 | -0.50059 | 0 | 0
95 | 0.97053 | -0.56876 | 0.0057846 | 0.0014498
96 | 0.9772 | -0.43761 | 0.0031935 | 0.00080036
97 | 0.97026 | -0.57425 | 0.0068965 | 0.0017284
98 | 0.9734 | -0.51208 | 0 | 0
99 | 0.97791 | -0.42379 | 0.0040631 | 0.0010183
100 | 0.98201 | -0.3439 | 0.0023822 | 0.00059704
101 | 0.98017 | -0.37988 | 0 | 0
102 | 0.98642 | -0.25865 | 0 | 0
103 | 0.98954 | -0.19899 | 0.017058 | 0.0042751
104 | 0.97742 | -0.43411 | 0.0094059 | 0.0023573
105 | 0.9721 | -0.53885 | 0 | 0
106 | 0.97209 | -0.53918 | 0 | 0
107 | 0.97213 | -0.53826 | 0.0002317 | 5.8069e-05
108 | 0.97215 | -0.53792 | 0.00013419 | 3.3632e-05
109 | 0.97208 | -0.53925 | 0 | 0
110 | 0.97208 | -0.53926 | 0.00013322 | 3.3388e-05
111 | 0.97208 | -0.53927 | 0.00013066 | 3.2748e-05
112 | 0.98426 | -0.30063 | 0.0098124 | 0.0024592
113 | 0.97581 | -0.4648 | 0 | 0
114 | 0.97506 | -0.47946 | 0.0057993 | 0.0014534
115 | 0.9706 | -0.56748 | 0.0042239 | 0.0010586
116 | 0.97133 | -0.55351 | 0 | 0
117 | 0.97179 | -0.5449 | 0.0066089 | 0.0016564
118 | 0.9712 | -0.55612 | 0.0046149 | 0.0011566
119 | 0.97777 | -0.42723 | 0.011034 | 0.0027653
120 | 0.97722 | -0.43817 | 0 | 0
121 | 0.97757 | -0.43116 | 0 | 0
122 | 0.97683 | -0.44575 | 0.017244 | 0.0043216
123 | 0.97742 | -0.43407 | 0.0015191 | 0.00038072
124 | 0.99876 | -0.023747 | 0.029417 | 0.0073727
125 | 0.97733 | -0.43588 | 0.0052842 | 0.0013243
126 | 0.99083 | -0.1752 | 0.0028088 | 0.00070396
127 | 0.97953 | -0.39239 | 0.0032246 | 0.00080815
128 | 0.99103 | -0.17134 | 0.0027769 | 0.00069595
129 | 0.97023 | -0.57476 | 0.0020501 | 0.00051381
130 | 0.97003 | -0.57874 | 0.0032083 | 0.00080408
131 | 0.97002 | -0.57892 | 0.0032092 | 0.00080429
132 | 0.97445 | -0.49145 | 0.010365 | 0.0025978
133 | 0.99871 | -0.024787 | 0.010091 | 0.0025291
134 | 0.98324 | -0.32011 | 0 | 0
135 | 0.98456 | -0.29459 | 0 | 0
136 | 0.98258 | -0.33308 | 0.0074245 | 0.0018608
137 | 0.98136 | -0.3568 | 0.0092777 | 0.0023252
138 | 0.98034 | -0.37651 | 0 | 0
139 | 0.97891 | -0.40454 | 0 | 0
140 | 0.98023 | -0.37878 | 0.0078729 | 0.0019731
141 | 0.98537 | -0.27886 | 0.0031735 | 0.00079534
142 | 0.97729 | -0.43609 | 0.0082747 | 0.0020738
143 | 0.98556 | -0.27535 | 0.0029405 | 0.00073697
144 | 0.98564 | -0.27369 | 0.0031714 | 0.00079483
145 | 0.98586 | -0.26938 | 0.0018324 | 0.00045924
146 | 0.9828 | -0.32861 | 0.0030362 | 0.00076095
147 | 0.98572 | -0.27223 | 0.0031689 | 0.00079419
148 | 0.97614 | -0.45863 | 0 | 0
149 | 0.97391 | -0.50262 | 0.0060356 | 0.0015127
150 | 0.97469 | -0.48712 | 0.0040817 | 0.001023
151 | 0.97552 | -0.4708 | 0.0040806 | 0.0010227
152 | 0.97776 | -0.42676 | 0.0063902 | 0.0016015
153 | 0.97208 | -0.53928 | 0.00012927 | 3.2398e-05
154 | 0.97208 | -0.5393 | 0.00013051 | 3.271e-05
155 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0066564 | -0.0016683 | 0.0066574 | 0.0016686 | 9.7401e-07 | 3.1339e-07 | 0.010191 | 0.010191 | 0.010191 | 0.97191 | -0.54203 | 0.97207 | -0.53896 | 2.7998
1 | -0.0066574 | -0.0016686 | 0.0066575 | 0.0016686 | 1.5972e-07 | 5.138e-08 | 0.010191 | 0.010191 | 0.010191 | 0.97207 | -0.53896 | 0.97209 | -0.53846 | 2.7997
2 | -0.0066575 | -0.0016686 | 0.0066593 | 0.0016692 | 1.7224e-06 | 5.5389e-07 | 0.010191 | 0.010191 | 0.010191 | 0.97209 | -0.53846 | 0.97237 | -0.53303 | 2.7997
3 | -0.011042 | -0.0027676 | 0.011044 | 0.0027688 | 2.2764e-06 | 1.1931e-06 | 0.016898 | 0.016898 | 0.016898 | 0.97237 | -0.53303 | 0.97258 | -0.5287 | 4.6423
4 | 0.033779 | 0.0084764 | -0.033774 | -0.0084734 | 4.8216e-06 | 3.026e-06 | 0.051654 | 0.051654 | 0.051654 | 0.97317 | -0.51719 | 0.97302 | -0.52018 | 14.1906
5 | -0.033779 | -0.0084764 | 0.033803 | 0.0084916 | 2.4209e-05 | 1.5193e-05 | 0.051654 | 0.051654 | 0.051654 | 0.97317 | -0.51719 | 0.97393 | -0.50217 | 14.1906
6 | 0.0071898 | 0.0018019 | -0.0071896 | -0.0018019 | 1.7422e-07 | 6.3769e-08 | 0.010995 | 0.010995 | 0.010995 | 0.97302 | -0.52018 | 0.97299 | -0.52069 | 3.0207
7 | 0.026585 | 0.0066715 | -0.026574 | -0.0066648 | 1.0798e-05 | 6.6947e-06 | 0.040659 | 0.040659 | 0.040659 | 0.97302 | -0.52018 | 0.97258 | -0.5287 | 11.17
8 | -0.039841 | -0.010005 | 0.039844 | 0.010007 | 3.0049e-06 | 1.8962e-06 | 0.060878 | 0.060878 | 0.060878 | 0.97393 | -0.50217 | 0.97401 | -0.50059 | 16.7247
9 | 0.149 | 0.037803 | -0.14895 | -0.037768 | 5.6142e-05 | 3.5327e-05 | 0.22493 | 0.22493 | 0.22493 | 0.98646 | -0.25823 | 0.98605 | -0.26606 | 15.4482
10 | -0.149 | -0.037803 | 0.14915 | 0.037896 | 0.00014809 | 9.3184e-05 | 0.22493 | 0.22492 | 0.22493 | 0.98646 | -0.25823 | 0.98753 | -0.23758 | 15.4482
11 | 0.14895 | 0.037768 | -0.14882 | -0.037691 | 0.00012251 | 7.709e-05 | 0.22493 | 0.22493 | 0.22493 | 0.98605 | -0.26606 | 0.98516 | -0.28319 | 15.4482
12 | -0.15858 | -0.040261 | 0.15873 | 0.040356 | 0.00015054 | 9.4908e-05 | 0.23914 | 0.23914 | 0.23914 | 0.98753 | -0.23758 | 0.98855 | -0.21787 | 16.4245
13 | 0.021157 | 0.0053044 | -0.021155 | -0.0053029 | 2.514e-06 | 1.5302e-06 | 0.032433 | 0.032434 | 0.032434 | 0.97069 | -0.5657 | 0.97056 | -0.56819 | 8.9103
14 | -0.031202 | -0.0078221 | 0.031205 | 0.0078244 | 3.7852e-06 | 2.368e-06 | 0.047831 | 0.047831 | 0.047831 | 0.97069 | -0.5657 | 0.97082 | -0.56315 | 13.1405
15 | 0.010044 | 0.0025177 | -0.010043 | -0.0025171 | 1.1092e-06 | 5.5571e-07 | 0.015398 | 0.015398 | 0.015398 | 0.97069 | -0.5657 | 0.97057 | -0.56801 | 4.2302
16 | 0.018442 | 0.0046237 | -0.018438 | -0.0046216 | 3.4965e-06 | 2.0936e-06 | 0.028274 | 0.028274 | 0.028274 | 0.97056 | -0.56819 | 0.97036 | -0.57217 | 7.7677
17 | 0.002713 | 0.00067917 | -0.0027127 | -0.0006796 | 3.411e-07 | -4.314e-07 | 0.0041592 | 0.0041594 | 0.0041594 | 0.97056 | -0.56819 | 0.97043 | -0.57083 | 1.1427
18 | 0.011752 | 0.0029456 | -0.01175 | -0.0029447 | 1.7459e-06 | 9.3997e-07 | 0.018012 | 0.018012 | 0.018012 | 0.97082 | -0.56315 | 0.97066 | -0.56627 | 4.9485
19 | -0.042957 | -0.01077 | 0.043005 | 0.010801 | 4.8164e-05 | 3.0458e-05 | 0.065844 | 0.065844 | 0.065844 | 0.97082 | -0.56315 | 0.97201 | -0.53965 | 18.0889
20 | 0.0057848 | 0.0014498 | -0.0057846 | -0.0014498 | 2.0599e-07 | 4.5531e-08 | 0.0088689 | 0.008869 | 0.008869 | 0.97057 | -0.56801 | 0.97053 | -0.56876 | 2.4365
21 | 0.0027127 | 0.0006796 | -0.0027125 | -0.00067981 | 1.7223e-07 | -2.1773e-07 | 0.0041594 | 0.0041595 | 0.0041595 | 0.97043 | -0.57083 | 0.97036 | -0.57216 | 1.1427
22 | -0.092031 | -0.023273 | 0.092065 | 0.023295 | 3.38e-05 | 2.1574e-05 | 0.13998 | 0.13998 | 0.13998 | 0.97883 | -0.40562 | 0.97923 | -0.39797 | 38.4558
23 | 0.092031 | 0.023273 | -0.091979 | -0.02324 | 5.1796e-05 | 3.3061e-05 | 0.13998 | 0.13998 | 0.13998 | 0.97883 | -0.40562 | 0.97823 | -0.41736 | 38.4558
24 | -0.11142 | -0.028153 | 0.1116 | 0.028264 | 0.00017449 | 0.00011147 | 0.1694 | 0.1694 | 0.1694 | 0.97923 | -0.39797 | 0.9809 | -0.36536 | 46.5382
25 | 0.019359 | 0.0048581 | -0.01935 | -0.0048526 | 9.1171e-06 | 5.4818e-06 | 0.02942 | 0.02942 | 0.02942 | 0.97923 | -0.39797 | 0.97872 | -0.40785 | 8.0825
26 | 0.085743 | 0.021677 | -0.08566 | -0.021624 | 8.3172e-05 | 5.3067e-05 | 0.13049 | 0.13049 | 0.13049 | 0.97823 | -0.41736 | 0.9772 | -0.43761 | 35.8499
27 | 0.003211 | 0.00080454 | -0.0032108 | -0.0008047 | 2.2434e-07 | -1.6479e-07 | 0.0049095 | 0.0049096 | 0.0049096 | 0.9732 | -0.51602 | 0.97313 | -0.51749 | 1.3488
28 | -0.003211 | -0.00080454 | 0.0032111 | 0.00080446 | 1.0184e-07 | -7.4828e-08 | 0.0049095 | 0.0049095 | 0.0049095 | 0.9732 | -0.51602 | 0.97324 | -0.51536 | 1.3488
29 | -0.0032111 | -0.00080446 | 0.0032111 | 0.00080445 | 1.9966e-08 | -1.4672e-08 | 0.0049095 | 0.0049095 | 0.0049095 | 0.97324 | -0.51536 | 0.97325 | -0.51522 | 1.3488
30 | 0.015367 | 0.0038519 | -0.015366 | -0.003851 | 1.5267e-06 | 8.8656e-07 | 0.023565 | 0.023565 | 0.023565 | 0.97036 | -0.57217 | 0.97026 | -0.57425 | 6.4739
31 | -0.0074399 | -0.0018643 | 0.007441 | 0.0018647 | 1.1135e-06 | 4.274e-07 | 0.011375 | 0.011375 | 0.011375 | 0.97325 | -0.51522 | 0.9734 | -0.51208 | 3.125
32 | -0.013119 | -0.0032889 | 0.013126 | 0.0032927 | 6.7738e-06 | 3.7656e-06 | 0.019957 | 0.019957 | 0.019957 | 0.97817 | -0.41868 | 0.97872 | -0.40785 | 5.4828
33 | 0.013119 | 0.0032889 | -0.013116 | -0.0032873 | 2.8159e-06 | 1.5655e-06 | 0.019957 | 0.019957 | 0.019957 | 0.97817 | -0.41868 | 0.97794 | -0.42318 | 5.4828
34 | 0.0062242 | 0.00156 | -0.0062233 | -0.0015597 | 9.6279e-07 | 2.5595e-07 | 0.0094631 | 0.0094632 | 0.0094632 | 0.97872 | -0.40785 | 0.97856 | -0.4111 | 2.5998
35 | 0.010454 | 0.0026202 | -0.010454 | -0.0026201 | 3.0211e-07 | 1.534e-07 | 0.015907 | 0.015907 | 0.015907 | 0.97794 | -0.42318 | 0.97791 | -0.42379 | 4.3701
36 | -0.11557 | -0.02926 | 0.11569 | 0.029336 | 0.00011917 | 7.6137e-05 | 0.17543 | 0.17543 | 0.17543 | 0.9809 | -0.36536 | 0.98201 | -0.3439 | 48.1938
37 | -0.0076071 | -0.0019066 | 0.0076085 | 0.0019071 | 1.335e-06 | 5.1834e-07 | 0.011552 | 0.011552 | 0.011552 | 0.97985 | -0.38621 | 0.98004 | -0.38252 | 3.1737
38 | 0.0076071 | 0.0019066 | -0.007606 | -0.0019062 | 1.1823e-06 | 4.5916e-07 | 0.011552 | 0.011552 | 0.011552 | 0.97985 | -0.38621 | 0.97968 | -0.38947 | 3.1738
39 | -0.011122 | -0.0027876 | 0.011123 | 0.0027883 | 1.399e-06 | 7.3047e-07 | 0.016886 | 0.016886 | 0.016886 | 0.98004 | -0.38252 | 0.98017 | -0.37988 | 4.6391
40 | 0.007606 | 0.0019062 | -0.0076053 | -0.0019059 | 6.7128e-07 | 2.6075e-07 | 0.011552 | 0.011553 | 0.011553 | 0.97968 | -0.38947 | 0.97959 | -0.39132 | 3.1738
41 | 0.001193 | 0.00029724 | -0.0011929 | -0.00029838 | 1.2363e-07 | -1.1462e-06 | 0.0018258 | 0.0018262 | 0.0018262 | 0.97198 | -0.54122 | 0.97187 | -0.5434 | 0.50172
42 | -0.001193 | -0.00029724 | 0.0011931 | 0.00029706 | 1.9656e-08 | -1.8232e-07 | 0.0018258 | 0.0018257 | 0.0018258 | 0.97198 | -0.54122 | 0.97199 | -0.54087 | 0.5016
43 | 0.0011929 | 0.00029838 | -0.0011929 | -0.00029866 | 2.9947e-08 | -2.7751e-07 | 0.0018262 | 0.0018264 | 0.0018264 | 0.97187 | -0.5434 | 0.97184 | -0.54393 | 0.50175
44 | -0.0051735 | -0.0012947 | 0.0051741 | 0.0012947 | 6.0735e-07 | 6.8578e-08 | 0.0079194 | 0.0079193 | 0.0079194 | 0.97199 | -0.54087 | 0.97212 | -0.5384 | 2.1757
45 | -0.25451 | -0.064903 | 0.25491 | 0.065159 | 0.00040145 | 0.00025543 | 0.38331 | 0.38331 | 0.38331 | 0.98905 | -0.2081 | 0.99076 | -0.17549 | 26.326
46 | 0.0073767 | 0.0018488 | -0.0073761 | -0.0018486 | 5.5615e-07 | 2.0142e-07 | 0.011098 | 0.011098 | 0.011098 | 0.98905 | -0.2081 | 0.98897 | -0.20969 | 3.0489
47 | 0.24713 | 0.063054 | -0.24691 | -0.062915 | 0.00021898 | 0.00013928 | 0.37221 | 0.37221 | 0.37221 | 0.98905 | -0.2081 | 0.98809 | -0.22646 | 25.5638
48 | -0.27635 | -0.070532 | 0.27654 | 0.070656 | 0.00019492 | 0.00012413 | 0.4155 | 0.4155 | 0.4155 | 0.99076 | -0.17549 | 0.99152 | -0.1609 | 28.5374
49 | 0.23515 | 0.059968 | -0.23479 | -0.059736 | 0.00036477 | 0.00023187 | 0.3545 | 0.3545 | 0.3545 | 0.98809 | -0.22646 | 0.98642 | -0.25865 | 24.3476
50 | 0.024635 | 0.006181 | -0.024622 | -0.006173 | 1.2879e-05 | 7.9203e-06 | 0.037011 | 0.037011 | 0.037011 | 0.99052 | -0.18009 | 0.98995 | -0.19106 | 10.1678
51 | -0.19254 | -0.048947 | 0.19272 | 0.04906 | 0.0001781 | 0.00011282 | 0.28949 | 0.28949 | 0.28949 | 0.99052 | -0.18009 | 0.99152 | -0.1609 | 19.8829
52 | 0.16791 | 0.042766 | -0.16784 | -0.042724 | 6.6682e-05 | 4.2102e-05 | 0.25248 | 0.25248 | 0.25248 | 0.99052 | -0.18009 | 0.99009 | -0.18832 | 17.341
53 | 0.017064 | 0.0042789 | -0.017058 | -0.0042751 | 6.4511e-06 | 3.7927e-06 | 0.025651 | 0.025651 | 0.025651 | 0.98995 | -0.19106 | 0.98954 | -0.19899 | 7.0469
54 | -0.46927 | -0.11972 | 0.47089 | 0.12075 | 0.0016219 | 0.0010362 | 0.705 | 0.705 | 0.705 | 0.99152 | -0.1609 | 0.99526 | -0.08961 | 48.4202
55 | 0.15896 | 0.040499 | -0.15883 | -0.040416 | 0.00013042 | 8.222e-05 | 0.23914 | 0.23914 | 0.23914 | 0.99009 | -0.18832 | 0.9892 | -0.20534 | 16.4244
56 | 0.039587 | 0.0099891 | -0.039465 | -0.0099117 | 0.00012266 | 7.7378e-05 | 0.060243 | 0.060244 | 0.060244 | 0.97821 | -0.41857 | 0.9749 | -0.4835 | 16.5504
57 | -0.057258 | -0.014421 | 0.057329 | 0.014465 | 7.0542e-05 | 4.4835e-05 | 0.087124 | 0.087124 | 0.087124 | 0.97821 | -0.41857 | 0.97952 | -0.39284 | 23.9352
58 | 0.017671 | 0.0044316 | -0.017665 | -0.0044281 | 5.7591e-06 | 3.4191e-06 | 0.026881 | 0.026881 | 0.026881 | 0.97821 | -0.41857 | 0.97786 | -0.42541 | 7.3849
59 | 0.036519 | 0.0091733 | -0.036491 | -0.0091561 | 2.7409e-05 | 1.7249e-05 | 0.055747 | 0.055747 | 0.055747 | 0.9749 | -0.4835 | 0.9741 | -0.49924 | 15.3151
60 | 0.020273 | 0.0050891 | -0.020262 | -0.0050828 | 1.0314e-05 | 6.236e-06 | 0.0308 | 0.0308 | 0.0308 | 0.97952 | -0.39284 | 0.97898 | -0.40352 | 8.4615
61 | 0.04585 | 0.011523 | -0.045804 | -0.011494 | 4.6169e-05 | 2.9229e-05 | 0.069663 | 0.069663 | 0.069663 | 0.97952 | -0.39284 | 0.97845 | -0.41396 | 19.1383
62 | -0.12345 | -0.031077 | 0.12384 | 0.031326 | 0.00039131 | 0.00024894 | 0.18759 | 0.18759 | 0.18759 | 0.97952 | -0.39284 | 0.98292 | -0.32676 | 25.7674
63 | 0.0094098 | 0.0023592 | -0.0094059 | -0.0023573 | 3.8958e-06 | 1.858e-06 | 0.014319 | 0.014319 | 0.014319 | 0.97786 | -0.42541 | 0.97742 | -0.43411 | 3.9339
64 | 0.00088972 | 0.00021861 | -0.00088964 | -0.00022007 | 8.4458e-08 | -1.4552e-06 | 0.0013601 | 0.0013606 | 0.0013606 | 0.9723 | -0.53496 | 0.9722 | -0.53697 | 0.3738
65 | -0.00088972 | -0.00021861 | 0.00088987 | 0.0002161 | 1.4574e-07 | -2.5146e-06 | 0.0013601 | 0.0013592 | 0.0013601 | 0.9723 | -0.53496 | 0.97247 | -0.53145 | 0.37365
66 | 0.00088964 | 0.00022007 | -0.0008896 | -0.00022075 | 3.9809e-08 | -6.8541e-07 | 0.0013606 | 0.0013609 | 0.0013609 | 0.9722 | -0.53697 | 0.97215 | -0.53792 | 0.37386
67 | -0.014516 | -0.0036311 | 0.014518 | 0.0036324 | 2.2733e-06 | 1.3024e-06 | 0.022209 | 0.022209 | 0.022209 | 0.97247 | -0.53145 | 0.97264 | -0.52816 | 6.1014
68 | -0.12384 | -0.031326 | 0.12391 | 0.031369 | 6.7793e-05 | 4.2345e-05 | 0.18759 | 0.18759 | 0.18759 | 0.98292 | -0.32676 | 0.9835 | -0.31536 | 12.8837
69 | -0.1298 | -0.032844 | 0.12989 | 0.032902 | 9.1783e-05 | 5.7453e-05 | 0.19649 | 0.19649 | 0.19649 | 0.9835 | -0.31536 | 0.98426 | -0.30063 | 13.4954
70 | -0.036473 | -0.0091445 | 0.036491 | 0.0091561 | 1.8389e-05 | 1.1573e-05 | 0.055747 | 0.055747 | 0.055747 | 0.97356 | -0.50981 | 0.9741 | -0.49924 | 15.3151
71 | 0.016219 | 0.0040684 | -0.016204 | -0.0040596 | 1.488e-05 | 8.7213e-06 | 0.024791 | 0.024791 | 0.024791 | 0.97356 | -0.50981 | 0.97259 | -0.52907 | 6.8108
72 | 0.020254 | 0.0050761 | -0.020236 | -0.0050654 | 1.7689e-05 | 1.071e-05 | 0.030956 | 0.030956 | 0.030956 | 0.97356 | -0.50981 | 0.97264 | -0.52816 | 8.5045
73 | 0.011028 | 0.0027646 | -0.011026 | -0.0027635 | 2.1049e-06 | 1.1025e-06 | 0.016872 | 0.016872 | 0.016872 | 0.97259 | -0.52907 | 0.97239 | -0.53308 | 4.6353
74 | 0.0051764 | 0.001295 | -0.0051741 | -0.0012947 | 2.297e-06 | 2.5854e-07 | 0.0079189 | 0.0079193 | 0.0079193 | 0.97259 | -0.52907 | 0.97212 | -0.5384 | 2.1756
75 | -0.0092845 | -0.002327 | 0.0092848 | 0.0023271 | 2.6599e-07 | 1.2679e-07 | 0.01422 | 0.014219 | 0.01422 | 0.97159 | -0.54838 | 0.97162 | -0.54778 | 3.9065
76 | 0.0092845 | 0.002327 | -0.009283 | -0.0023263 | 1.5193e-06 | 7.2426e-07 | 0.01422 | 0.01422 | 0.01422 | 0.97159 | -0.54838 | 0.97142 | -0.55182 | 3.9065
77 | -0.0092848 | -0.0023271 | 0.0092866 | 0.002328 | 1.882e-06 | 8.9698e-07 | 0.014219 | 0.014219 | 0.014219 | 0.97162 | -0.54778 | 0.97183 | -0.54353 | 3.9065
78 | 0.0046159 | 0.0011566 | -0.0046155 | -0.0011566 | 3.718e-07 | -7.5491e-09 | 0.0070705 | 0.0070706 | 0.0070706 | 0.97142 | -0.55182 | 0.97133 | -0.55351 | 1.9425
79 | 0.0066126 | 0.0016575 | -0.0066089 | -0.0016564 | 3.7215e-06 | 1.1804e-06 | 0.010119 | 0.01012 | 0.01012 | 0.97239 | -0.53308 | 0.97179 | -0.5449 | 2.7801
80 | 0.040911 | 0.010299 | -0.040853 | -0.010262 | 5.8661e-05 | 3.7001e-05 | 0.061183 | 0.061183 | 0.061183 | 0.99526 | -0.08961 | 0.9937 | -0.11965 | 16.8085
81 | 0.034298 | 0.0086013 | -0.034284 | -0.0085923 | 1.4494e-05 | 9.0851e-06 | 0.051281 | 0.051281 | 0.051281 | 0.99526 | -0.08961 | 0.9948 | -0.09848 | 14.0882
82 | -0.5461 | -0.13965 | 0.54843 | 0.14114 | 0.0023344 | 0.0014921 | 0.81746 | 0.81746 | 0.81746 | 0.99526 | -0.08961 | 0.99991 | -0.0016789 | 56.1443
83 | 0.020262 | 0.0050828 | -0.020249 | -0.005075 | 1.296e-05 | 7.8364e-06 | 0.0308 | 0.0308 | 0.0308 | 0.97898 | -0.40352 | 0.9783 | -0.41694 | 8.4615
84 | 0.03512 | 0.0088161 | -0.035098 | -0.0088022 | 2.2217e-05 | 1.3958e-05 | 0.053416 | 0.053416 | 0.053416 | 0.97845 | -0.41396 | 0.97777 | -0.42723 | 14.6747
85 | 0.00094314 | 0.00023607 | -0.00094313 | -0.00023623 | 1.0625e-08 | -1.6157e-07 | 0.001444 | 0.001444 | 0.001444 | 0.97184 | -0.54393 | 0.97183 | -0.54416 | 0.39671
86 | -0.55829 | -0.14362 | 0.55834 | 0.14365 | 4.5572e-05 | 2.9129e-05 | 0.83214 | 0.83214 | 0.83214 | 0.99991 | -0.0016789 | 1 | 0 | 57.1524
87 | 0.0098638 | 0.0024728 | -0.0098609 | -0.0024714 | 2.8785e-06 | 1.3751e-06 | 0.014679 | 0.014679 | 0.014679 | 0.99991 | -0.0016789 | 0.99959 | -0.0078049 | 4.0328
88 | 0.039554 | 0.0099302 | -0.039509 | -0.009902 | 4.4751e-05 | 2.8189e-05 | 0.058862 | 0.058863 | 0.058863 | 1 | 0 | 0.99876 | -0.023747 | 16.171
89 | 0.029916 | 0.0075212 | -0.029901 | -0.0075119 | 1.5065e-05 | 9.3822e-06 | 0.044806 | 0.044806 | 0.044806 | 0.9937 | -0.11965 | 0.99316 | -0.1302 | 12.3095
90 | -0.012404 | -0.0031094 | 0.012407 | 0.0031107 | 2.4287e-06 | 1.3319e-06 | 0.018993 | 0.018993 | 0.018993 | 0.97183 | -0.54353 | 0.97204 | -0.53942 | 5.2178
91 | 0.024786 | 0.0062276 | -0.024747 | -0.0062036 | 3.9132e-05 | 2.4068e-05 | 0.037152 | 0.037152 | 0.037152 | 0.99289 | -0.13542 | 0.99118 | -0.16855 | 10.2067
92 | -0.024786 | -0.0062276 | 0.024792 | 0.0062314 | 6.1733e-06 | 3.7966e-06 | 0.037152 | 0.037152 | 0.037152 | 0.99289 | -0.13542 | 0.99316 | -0.1302 | 10.2066
93 | 0.016764 | 0.0042026 | -0.016762 | -0.0042018 | 1.4926e-06 | 8.7425e-07 | 0.025167 | 0.025167 | 0.025167 | 0.99118 | -0.16855 | 0.99108 | -0.17042 | 6.914
94 | 0.0079834 | 0.0020009 | -0.0079827 | -0.0020006 | 7.5947e-07 | 3.0436e-07 | 0.011985 | 0.011985 | 0.011985 | 0.99118 | -0.16855 | 0.99107 | -0.17055 | 3.2927
95 | -0.011173 | -0.0028003 | 0.011173 | 0.0028006 | 4.784e-07 | 2.4781e-07 | 0.01678 | 0.01678 | 0.01678 | 0.99082 | -0.17545 | 0.99087 | -0.17455 | 4.6098
96 | 0.011173 | 0.0028003 | -0.011173 | -0.0028001 | 3.972e-07 | 2.0576e-07 | 0.01678 | 0.01678 | 0.01678 | 0.99082 | -0.17545 | 0.99078 | -0.1762 | 4.6098
97 | 0.0028089 | 0.00070385 | -0.0028088 | -0.00070396 | 8.695e-08 | -1.122e-07 | 0.0042182 | 0.0042183 | 0.0042183 | 0.99087 | -0.17455 | 0.99083 | -0.1752 | 1.1589
98 | -0.013982 | -0.0035044 | 0.013985 | 0.003506 | 2.7527e-06 | 1.5473e-06 | 0.020998 | 0.020998 | 0.020998 | 0.99087 | -0.17455 | 0.99108 | -0.17042 | 5.7686
99 | 0.0032247 | 0.00080803 | -0.0032246 | -0.00080815 | 1.6424e-07 | -1.2467e-07 | 0.0048984 | 0.0048985 | 0.0048985 | 0.97959 | -0.39132 | 0.97953 | -0.39239 | 1.3457
100 | 0.002777 | 0.00069579 | -0.0027769 | -0.00069595 | 1.2114e-07 | -1.6192e-07 | 0.0041694 | 0.0041694 | 0.0041694 | 0.99108 | -0.17042 | 0.99103 | -0.17134 | 1.1455
101 | -0.15873 | -0.040356 | 0.15883 | 0.040416 | 9.5835e-05 | 6.0417e-05 | 0.23914 | 0.23914 | 0.23914 | 0.98855 | -0.21787 | 0.9892 | -0.20534 | 16.4245
102 | -0.052011 | -0.013058 | 0.052054 | 0.013085 | 4.3229e-05 | 2.7441e-05 | 0.07963 | 0.07963 | 0.07963 | 0.97201 | -0.53965 | 0.97289 | -0.52224 | 21.8765
103 | 0.0090059 | 0.0022572 | -0.0090053 | -0.0022569 | 5.946e-07 | 2.7716e-07 | 0.013787 | 0.013787 | 0.013787 | 0.97201 | -0.53965 | 0.97194 | -0.54104 | 3.7876
104 | -0.058558 | -0.014715 | 0.058587 | 0.014733 | 2.8412e-05 | 1.8066e-05 | 0.089578 | 0.089578 | 0.089578 | 0.97289 | -0.52224 | 0.9734 | -0.51208 | 24.6093
105 | 0.0042241 | 0.0010586 | -0.0042239 | -0.0010586 | 2.4379e-07 | -3.5599e-08 | 0.0064755 | 0.0064756 | 0.0064756 | 0.97066 | -0.56627 | 0.9706 | -0.56748 | 1.779
106 | 0.13982 | 0.035434 | -0.1397 | -0.035361 | 0.00011708 | 7.3511e-05 | 0.21133 | 0.21133 | 0.21133 | 0.98516 | -0.28319 | 0.98426 | -0.30063 | 14.5142
107 | 0.00094313 | 0.00023623 | -0.00094312 | -0.00023637 | 8.9773e-09 | -1.365e-07 | 0.001444 | 0.0014441 | 0.0014441 | 0.97183 | -0.54416 | 0.97182 | -0.54436 | 0.39672
108 | 0.015529 | 0.0038959 | -0.015526 | -0.003894 | 3.3478e-06 | 1.9464e-06 | 0.023761 | 0.023761 | 0.023761 | 0.97258 | -0.5287 | 0.97236 | -0.53323 | 6.5277
109 | 0.015526 | 0.003894 | -0.015521 | -0.0038913 | 4.5836e-06 | 2.665e-06 | 0.023761 | 0.023761 | 0.023761 | 0.97236 | -0.53323 | 0.97204 | -0.53942 | 6.5277
110 | -0.04588 | -0.011519 | 0.045909 | 0.011538 | 2.9501e-05 | 1.8682e-05 | 0.070099 | 0.070099 | 0.070099 | 0.97401 | -0.50059 | 0.97469 | -0.48712 | 19.2581
111 | 0.0060362 | 0.0015128 | -0.0060356 | -0.0015127 | 5.8481e-07 | 1.4606e-07 | 0.0092216 | 0.0092217 | 0.0092217 | 0.97401 | -0.50059 | 0.97391 | -0.50262 | 2.5334
112 | 0.082466 | 0.020824 | -0.082359 | -0.020755 | 0.0001073 | 6.8446e-05 | 0.12563 | 0.12563 | 0.12563 | 0.9772 | -0.43761 | 0.97581 | -0.4648 | 34.5139
113 | 0.0084691 | 0.0021226 | -0.0084689 | -0.0021225 | 2.0376e-07 | 9.0628e-08 | 0.012988 | 0.012988 | 0.012988 | 0.97026 | -0.57425 | 0.97023 | -0.57476 | 3.5683
114 | -0.066027 | -0.016598 | 0.066093 | 0.016639 | 6.5122e-05 | 4.1466e-05 | 0.10095 | 0.10095 | 0.10095 | 0.9734 | -0.51208 | 0.97445 | -0.49145 | 27.7342
115 | 0.0063911 | 0.0016018 | -0.0063902 | -0.0016015 | 9.0529e-07 | 2.5918e-07 | 0.0097248 | 0.009725 | 0.009725 | 0.97791 | -0.42379 | 0.97776 | -0.42676 | 2.6717
116 | -0.11807 | -0.029933 | 0.11816 | 0.029989 | 8.687e-05 | 5.5506e-05 | 0.17903 | 0.17903 | 0.17903 | 0.98201 | -0.3439 | 0.9828 | -0.32861 | 49.1854
117 | -0.011123 | -0.0027883 | 0.011124 | 0.0027887 | 5.8459e-07 | 3.0522e-07 | 0.016886 | 0.016886 | 0.016886 | 0.98017 | -0.37988 | 0.98023 | -0.37878 | 4.6391
118 | 0.12478 | 0.031807 | -0.12469 | -0.03175 | 9.0545e-05 | 5.7602e-05 | 0.18842 | 0.18842 | 0.18842 | 0.98642 | -0.25865 | 0.98564 | -0.27369 | 25.8818
119 | 0.11001 | 0.027929 | -0.10996 | -0.027894 | 5.6761e-05 | 3.5207e-05 | 0.16608 | 0.16608 | 0.16608 | 0.98642 | -0.25865 | 0.98586 | -0.26938 | 11.4067
120 | 0.00052368 | 0.00013009 | -0.00052367 | -0.0001305 | 8.0717e-09 | -4.1047e-07 | 0.00080119 | 0.00080134 | 0.00080134 | 0.9721 | -0.53885 | 0.97209 | -0.53918 | 0.22015
121 | -0.00052368 | -0.00013009 | 0.00052369 | 0.00012934 | 1.474e-08 | -7.5001e-07 | 0.00080119 | 0.00080092 | 0.00080119 | 0.9721 | -0.53885 | 0.97213 | -0.53826 | 0.22011
122 | 0.00026118 | 6.5051e-05 | -0.00026118 | -6.529e-05 | 1.1563e-09 | -2.3853e-07 | 0.00039966 | 0.00039974 | 0.00039974 | 0.97209 | -0.53918 | 0.97208 | -0.53927 | 0.10982
123 | 0.00026249 | 6.5448e-05 | -0.00026249 | -6.564e-05 | 9.3946e-10 | -1.9185e-07 | 0.00040168 | 0.00040175 | 0.00040175 | 0.97209 | -0.53918 | 0.97208 | -0.53925 | 0.11037
124 | -0.00075539 | -0.00018741 | 0.0007554 | 0.00018712 | 1.191e-08 | -2.8728e-07 | 0.0011556 | 0.0011555 | 0.0011556 | 0.97213 | -0.53826 | 0.97215 | -0.53792 | 0.31746
125 | 0.00026249 | 6.564e-05 | -0.00026249 | -6.565e-05 | 4.7263e-11 | -9.6404e-09 | 0.00040175 | 0.00040176 | 0.00040176 | 0.97208 | -0.53925 | 0.97208 | -0.53926 | 0.11037
126 | 0.00012927 | 3.2262e-05 | -0.00012927 | -3.2398e-05 | 1.6171e-10 | -1.3645e-07 | 0.00019783 | 0.00019788 | 0.00019788 | 0.97208 | -0.53926 | 0.97208 | -0.53928 | 0.054363
127 | 0.00013052 | 3.2542e-05 | -0.00013051 | -3.271e-05 | 2.0292e-10 | -1.6799e-07 | 0.00019973 | 0.00019979 | 0.00019979 | 0.97208 | -0.53927 | 0.97208 | -0.5393 | 0.054886
128 | 0.082359 | 0.020755 | -0.082301 | -0.020719 | 5.7721e-05 | 3.682e-05 | 0.12563 | 0.12563 | 0.12563 | 0.97581 | -0.4648 | 0.97506 | -0.47946 | 34.5139
129 | 0.076502 | 0.019265 | -0.076458 | -0.019237 | 4.3814e-05 | 2.7934e-05 | 0.11678 | 0.11678 | 0.11678 | 0.97506 | -0.47946 | 0.97445 | -0.49145 | 32.0826
130 | 0.0046155 | 0.0011566 | -0.0046149 | -0.0011566 | 5.7266e-07 | -1.1531e-08 | 0.0070706 | 0.0070707 | 0.0070707 | 0.97133 | -0.55351 | 0.9712 | -0.55612 | 1.9425
131 | 0.024065 | 0.0060369 | -0.02406 | -0.0060342 | 4.5044e-06 | 2.7705e-06 | 0.036625 | 0.036625 | 0.036625 | 0.97777 | -0.42723 | 0.97757 | -0.43116 | 10.0618
132 | -0.01725 | -0.0043253 | 0.017256 | 0.0043287 | 5.7687e-06 | 3.4125e-06 | 0.026267 | 0.026267 | 0.026267 | 0.97722 | -0.43817 | 0.97757 | -0.43116 | 7.2162
133 | 0.01725 | 0.0043253 | -0.017244 | -0.0043216 | 6.2272e-06 | 3.684e-06 | 0.026267 | 0.026267 | 0.026267 | 0.97722 | -0.43817 | 0.97683 | -0.44575 | 7.2163
134 | 0.0068046 | 0.0017054 | -0.0068037 | -0.0017051 | 9.4395e-07 | 3.1001e-07 | 0.010358 | 0.010358 | 0.010358 | 0.97757 | -0.43116 | 0.97742 | -0.43407 | 2.8456
135 | 0.0052846 | 0.0013244 | -0.0052842 | -0.0013243 | 4.5666e-07 | 5.6476e-08 | 0.0080452 | 0.0080453 | 0.0080453 | 0.97742 | -0.43407 | 0.97733 | -0.43588 | 2.2102
136 | 0.010092 | 0.0025293 | -0.010091 | -0.0025291 | 5.0017e-07 | 2.429e-07 | 0.015035 | 0.015035 | 0.015035 | 0.99876 | -0.023747 | 0.99871 | -0.024787 | 4.1305
137 | 0.0064187 | 0.0016087 | -0.0064175 | -0.0016083 | 1.218e-06 | 3.6568e-07 | 0.0098442 | 0.0098443 | 0.0098443 | 0.97023 | -0.57476 | 0.97003 | -0.57874 | 2.7045
138 | 0.0032092 | 0.00080427 | -0.0032092 | -0.00080429 | 2.7334e-08 | -1.9635e-08 | 0.0049228 | 0.0049229 | 0.0049229 | 0.97003 | -0.57874 | 0.97002 | -0.57892 | 1.3524
139 | -0.098597 | -0.024956 | 0.098718 | 0.025032 | 0.00012096 | 7.6682e-05 | 0.1493 | 0.1493 | 0.1493 | 0.98324 | -0.32011 | 0.98456 | -0.29459 | 20.5085
140 | 0.098597 | 0.024956 | -0.098535 | -0.024917 | 6.1333e-05 | 3.8881e-05 | 0.1493 | 0.1493 | 0.1493 | 0.98324 | -0.32011 | 0.98258 | -0.33308 | 20.5085
141 | -0.098718 | -0.025032 | 0.098792 | 0.025078 | 7.4684e-05 | 4.5978e-05 | 0.1493 | 0.1493 | 0.1493 | 0.98456 | -0.29459 | 0.98537 | -0.27886 | 10.2542
142 | 0.091111 | 0.023056 | -0.091007 | -0.02299 | 0.0001036 | 6.5571e-05 | 0.13806 | 0.13806 | 0.13806 | 0.98258 | -0.33308 | 0.98136 | -0.3568 | 18.9641
143 | 0.08173 | 0.020665 | -0.081652 | -0.020616 | 7.7187e-05 | 4.923e-05 | 0.12399 | 0.12399 | 0.12399 | 0.98136 | -0.3568 | 0.98034 | -0.37651 | 34.0634
144 | 0.062654 | 0.015853 | -0.06257 | -0.015799 | 8.4153e-05 | 5.3546e-05 | 0.095153 | 0.095153 | 0.095153 | 0.98034 | -0.37651 | 0.97891 | -0.40454 | 26.1411
145 | 0.018999 | 0.004763 | -0.018996 | -0.0047618 | 2.052e-06 | 1.2304e-06 | 0.028838 | 0.028838 | 0.028838 | 0.98034 | -0.37651 | 0.98023 | -0.37878 | 7.9224
146 | 0.06257 | 0.015799 | -0.062475 | -0.015739 | 9.4429e-05 | 6.0085e-05 | 0.095153 | 0.095154 | 0.095154 | 0.97891 | -0.40454 | 0.97729 | -0.43609 | 26.1411
147 | -0.10197 | -0.025874 | 0.10198 | 0.025884 | 1.7221e-05 | 1.0627e-05 | 0.15409 | 0.15409 | 0.15409 | 0.98537 | -0.27886 | 0.98556 | -0.27535 | 10.5833
148 | 0.054201 | 0.013666 | -0.054142 | -0.013628 | 5.8388e-05 | 3.7082e-05 | 0.082555 | 0.082555 | 0.082555 | 0.97729 | -0.43609 | 0.97614 | -0.45863 | 22.6799
149 | -0.10492 | -0.026621 | 0.10494 | 0.026631 | 1.573e-05 | 9.7271e-06 | 0.15853 | 0.15853 | 0.15853 | 0.98556 | -0.27535 | 0.98572 | -0.27223 | 10.8882
150 | 0.12152 | 0.030955 | -0.1212 | -0.03075 | 0.000321 | 0.00020512 | 0.18363 | 0.18363 | 0.18363 | 0.98564 | -0.27369 | 0.9828 | -0.32861 | 50.4483
151 | 0.10812 | 0.027434 | -0.10811 | -0.027425 | 1.4863e-05 | 9.2094e-06 | 0.16332 | 0.16332 | 0.16332 | 0.98586 | -0.26938 | 0.98572 | -0.27223 | 11.2168
152 | 0.054142 | 0.013628 | -0.054111 | -0.013608 | 3.148e-05 | 1.9993e-05 | 0.082555 | 0.082555 | 0.082555 | 0.97614 | -0.45863 | 0.97552 | -0.4708 | 22.6799
153 | -0.049991 | -0.012561 | 0.05003 | 0.012586 | 3.8977e-05 | 2.4723e-05 | 0.076331 | 0.076331 | 0.076331 | 0.97469 | -0.48712 | 0.97552 | -0.4708 | 20.97

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59954 | 0.15358

## res_load
| p_mw | q_mvar
0 | 0.0066564 | 0.0016683
1 | 0.0043829 | 0.0010985
2 | 0.0060374 | 0.0015131
3 | 0.0094346 | 0.0023645
4 | 0.0042585 | 0.0010673
5 | 0.0027125 | 0.00067981
6 | 0.0062361 | 0.0015629
7 | 0.0032108 | 0.0008047
8 | 0.0030711 | 0.00076968
9 | 0.0042287 | 0.0010598
10 | 0.0026617 | 0.0006671
11 | 0.0062233 | 0.0015597
12 | 0.0039724 | 0.00099559
13 | 0.0035132 | 0.00088048
14 | 0.0039805 | 0.0009976
15 | 0.021439 | 0.005373
16 | 0.0073761 | 0.0018486
17 | 0.011759 | 0.0029471
18 | 0.0075577 | 0.0018941
19 | 0.0088797 | 0.0022255
20 | 0.0029461 | 0.00073837
21 | 0.0082552 | 0.0020689
22 | 0.013626 | 0.003415
23 | 0.0058873 | 0.0014755
24 | 0.0057176 | 0.001433
25 | 0.0046671 | 0.0011697
26 | 0.004413 | 0.001106
27 | 0.010684 | 0.0026775
28 | 0.00024974 | 6.2592e-05
29 | 0.020249 | 0.005075
30 | 0.0098609 | 0.0024714
31 | 0.010936 | 0.0027409
32 | 0.034284 | 0.0085923
33 | 0.0031176 | 0.00078134
34 | 0.0051089 | 0.0012804
35 | 0.011173 | 0.0028001
36 | 0.0043806 | 0.0010979
37 | 0.0079827 | 0.0020006
38 | 0.0065037 | 0.00163
39 | 0.0090053 | 0.0022569
40 | 0.0075258 | 0.0018861
41 | 0.0090035 | 0.0022565
42 | 0.00094312 | 0.00023637
43 | 0.0031148 | 0.00078064
44 | 0.0071896 | 0.0018019
45 | 0.0057846 | 0.0014498
46 | 0.0031935 | 0.00080036
47 | 0.0068965 | 0.0017284
48 | 0.0040631 | 0.0010183
49 | 0.0023822 | 0.00059704
50 | 0.017058 | 0.0042751
51 | 0.0094059 | 0.0023573
52 | 0.0002317 | 5.8069e-05
53 | 0.00013419 | 3.3632e-05
54 | 0.00013322 | 3.3388e-05
55 | 0.00013066 | 3.2748e-05
56 | 0.0098124 | 0.0024592
57 | 0.0057993 | 0.0014534
58 | 0.0042239 | 0.0010586
59 | 0.0066089 | 0.0016564
60 | 0.0046149 | 0.0011566
61 | 0.011034 | 0.0027653
62 | 0.017244 | 0.0043216
63 | 0.0015191 | 0.00038072
64 | 0.029417 | 0.0073727
65 | 0.0052842 | 0.0013243
66 | 0.0028088 | 0.00070396
67 | 0.0032246 | 0.00080815
68 | 0.0027769 | 0.00069595
69 | 0.0020501 | 0.00051381
70 | 0.0032083 | 0.00080408
71 | 0.0032092 | 0.00080429
72 | 0.010365 | 0.0025978
73 | 0.010091 | 0.0025291
74 | 0.0074245 | 0.0018608
75 | 0.0092777 | 0.0023252
76 | 0.0078729 | 0.0019731
77 | 0.0031735 | 0.00079534
78 | 0.0082747 | 0.0020738
79 | 0.0029405 | 0.00073697
80 | 0.0031714 | 0.00079483
81 | 0.0018324 | 0.00045924
82 | 0.0030362 | 0.00076095
83 | 0.0031689 | 0.00079419
84 | 0.0060356 | 0.0015127
85 | 0.0040817 | 0.001023
86 | 0.0040806 | 0.0010227
87 | 0.0063902 | 0.0016015
88 | 0.00012927 | 3.2398e-05
89 | 0.00013051 | 3.271e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1