## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2407-18_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2407-18_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2407-18_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2407-18_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2407-18_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2407-18_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2407-18_0_4_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_2407-18_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_2407-18_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2407-18_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2407-18_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2407-18_0_4_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_2407-18_0_4_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_2407-18_0_4_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_2407-18_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_2407-18_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2407-18_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_2407-18_0_4_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_2407-18_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_2407-18_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_2407-18_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2407-18_0_4_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_2407-18_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_2407-18_0_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_2407-18_0_4_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_2407-18_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2407-18_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_MV_479_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2407-18_0_4_load_0 | 0 | 0.0078636 | 0.0019708 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2407-18_0_4_load_1 | 1 | 0.0059101 | 0.0014812 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2407-18_0_4_load_2 | 2 | 0.0014051 | 0.00035216 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2407-18_0_4_load_3 | 3 | 0.010393 | 0.0026048 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2407-18_0_4_load_4 | 4 | 0.0036498 | 0.00091473 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2407-18_0_4_load_18 | 6 | 0.014668 | 0.003676 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2407-18_0_4_load_13 | 7 | 0.0078377 | 0.0019643 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2407-18_0_4_load_5 | 8 | 0.0054319 | 0.0013614 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2407-18_0_4_load_35 | 12 | 0.0027572 | 0.00069103 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2407-18_0_4_load_45 | 13 | 0.0012337 | 0.0003092 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2407-18_0_4_load_37 | 17 | 0.0065068 | 0.0016308 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2407-18_0_4_load_22 | 18 | 0.036426 | 0.0091293 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2407-18_0_4_load_24 | 20 | 0.0034442 | 0.00086321 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2407-18_0_4_load_26 | 22 | 0.078753 | 0.019737 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2407-18_0_4_load_30 | 25 | 0.0021556 | 0.00054024 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2407-18_0_4_load_32 | 26 | 0.0090514 | 0.0022685 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2407-18_0_4_line_0 |  | 0 | 1 | 0.021026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2407-18_0_4_line_1 |  | 0 | 2 | 0.0062655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2407-18_0_4_line_2 |  | 1 | 3 | 0.074604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2407-18_0_4_line_3 |  | 2 | 4 | 0.0092897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2407-18_0_4_line_4 |  | 3 | 5 | 0.059167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2407-18_0_4_line_5 |  | 5 | 6 | 0.1149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2407-18_0_4_line_6 |  | 5 | 7 | 0.03077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2407-18_0_4_line_7 |  | 6 | 18 | 0.1408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2407-18_0_4_line_8 |  | 7 | 15 | 0.10854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2407-18_0_4_line_9 |  | 8 | 9 | 0.031413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2407-18_0_4_line_10 |  | 9 | 10 | 0.19759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2407-18_0_4_line_11 |  | 10 | 11 | 0.22562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2407-18_0_4_line_12 |  | 10 | 12 | 0.031282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2407-18_0_4_line_13 |  | 11 | 13 | 0.082496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2407-18_0_4_line_14 |  | 12 | 14 | 0.031079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2407-18_0_4_line_15 |  | 14 | 15 | 0.058149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2407-18_0_4_line_16 |  | 15 | 16 | 0.11245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_2407-18_0_4_line_17 |  | 16 | 17 | 0.20654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2407-18_0_4_line_18 |  | 17 | 19 | 0.077914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2407-18_0_4_line_19 |  | 19 | 23 | 0.17569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2407-18_0_4_line_20 |  | 19 | 21 | 0.009952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2407-18_0_4_line_21 |  | 20 | 21 | 0.027952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2407-18_0_4_line_22 |  | 21 | 22 | 0.035202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2407-18_0_4_line_23 |  | 23 | 24 | 0.01691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2407-18_0_4_line_24 |  | 24 | 26 | 0.10128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2407-18_0_4_line_25 |  | 24 | 25 | 0.016688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2407-18_0_4_trafo_27 | 0.63 MVA 20/0.4 kV | 27 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2621255.0213 | 1237185.323 | 2621234.6934 | 1237179.9502
1 | 2621255.0213 | 1237185.323 | 2621261.0788 | 1237186.924
2 | 2621161.3357 | 1237167.9741 | 2621172.9718 | 1237171.0961 | 2621181.8402 | 1237172.6953 | 2621207.8293 | 1237174.1554 | 2621220.5543 | 1237176.2131 | 2621234.6934 | 1237179.9502
3 | 2621270.0601 | 1237189.2978 | 2621261.0788 | 1237186.924
4 | 2621103.6289 | 1237156.0185 | 2621113.0695 | 1237156.2743 | 2621122.9146 | 1237157.6656 | 2621161.3357 | 1237167.9741
5 | 2621103.6289 | 1237156.0185 | 2621105.7648 | 1237151.0563 | 2621109.2034 | 1237147.8109 | 2621118.2797 | 1237142.0062 | 2621208.21 | 1237114.675
6 | 2621103.6289 | 1237156.0185 | 2621089.0992 | 1237159.3691 | 2621077.3974 | 1237165.298 | 2621075.1315 | 1237166.8399
7 | 2621347.6774 | 1237110.6405 | 2621330.3966 | 1237108.0967 | 2621296.219 | 1237105.2282 | 2621250.7205 | 1237105.3435 | 2621211.1008 | 1237113.7964 | 2621208.21 | 1237114.675
8 | 2620997.3177 | 1237240.6617 | 2621008.9853 | 1237225.0932 | 2621016.8991 | 1237214.2144 | 2621024.9536 | 1237204.2033 | 2621033.8376 | 1237194.9401 | 2621075.1315 | 1237166.8399
9 | 2621293.4284 | 1237206.4475 | 2621320.4116 | 1237190.3632
10 | 2621110.5439 | 1237279.6527 | 2621129.7267 | 1237276.0519 | 2621143.7282 | 1237272.2325 | 2621149.1637 | 1237269.0721 | 2621154.8924 | 1237266.413 | 2621267.2136 | 1237217.3717 | 2621293.4284 | 1237206.4475
11 | 2621110.5439 | 1237279.6527 | 2621131.4037 | 1237285.2635 | 2621144.0113 | 1237288.3769 | 2621145.3946 | 1237288.7042 | 2621178.2488 | 1237297.5375 | 2621193.5301 | 1237301.839 | 2621198.0651 | 1237302.9892 | 2621202.0236 | 1237296.0657 | 2621205.7648 | 1237290.709 | 2621210.403 | 1237286.245 | 2621213.306 | 1237282.5642 | 2621217.4122 | 1237278.7876 | 2621275.7143 | 1237232.9228 | 2621298.0786 | 1237213.4684
12 | 2621110.5439 | 1237279.6527 | 2621080.3 | 1237271.6595
13 | 2621298.0786 | 1237213.4684 | 2621368.8565 | 1237171.0881
14 | 2621050.2531 | 1237263.7184 | 2621080.3 | 1237271.6595
15 | 2620997.3177 | 1237240.6617 | 2621008.2216 | 1237248.5495 | 2621015.9314 | 1237252.6014 | 2621029.2427 | 1237257.8405 | 2621040.4053 | 1237260.993 | 2621050.2531 | 1237263.7184
16 | 2620991.4008 | 1237148.7062 | 2620970.4859 | 1237184.299 | 2620963.4941 | 1237201.8963 | 2620966.1842 | 1237207.0979 | 2620969.4206 | 1237213.958 | 2620972.9214 | 1237218.8067 | 2620983.8066 | 1237229.8518 | 2620997.3177 | 1237240.6617
17 | 2620991.4008 | 1237148.7062 | 2621002.6126 | 1237152.9706 | 2621009.6205 | 1237154.4407 | 2621017.0185 | 1237154.6891 | 2621025.5036 | 1237153.4294 | 2621034.9033 | 1237150.2718 | 2621043.3401 | 1237145.5765 | 2621065.5984 | 1237132.4359 | 2621078.3786 | 1237125.3657 | 2621091.8755 | 1237118.8539 | 2621105.1214 | 1237112.7415 | 2621118.8649 | 1237107.12 | 2621140.999 | 1237099.2159 | 2621164.6002 | 1237091.4838 | 2621179.8182 | 1237088.2248 | 2621182.811 | 1237087.6214
18 | 2621259.9587 | 1237077.5593 | 2621241.0792 | 1237078.626 | 2621217.4208 | 1237081.1432 | 2621194.2861 | 1237085.3078 | 2621182.811 | 1237087.6214
19 | 2621370.8726 | 1237059.2672 | 2621395.3683 | 1237074.3423 | 2621397.9296 | 1237077.3867 | 2621389.5033 | 1237085.3502 | 2621385.2185 | 1237088.2478 | 2621379.7984 | 1237089.1622 | 2621374.2848 | 1237088.731 | 2621359.1564 | 1237085.9417 | 2621341.3662 | 1237082.8204 | 2621327.7407 | 1237080.7926 | 2621314.2269 | 1237079.221 | 2621296.8164 | 1237077.8134 | 2621279.4783 | 1237077.3067 | 2621259.9587 | 1237077.5593
20 | 2621259.9587 | 1237077.5593 | 2621259.3208 | 1237067.6287
21 | 2621259.3208 | 1237067.6287 | 2621258.9768 | 1237062.2686 | 2621239.6429 | 1237050.6033
22 | 2621259.3208 | 1237067.6287 | 2621265.8121 | 1237067.5741 | 2621280.7358 | 1237043.0011
23 | 2621370.8726 | 1237059.2672 | 2621356.4394 | 1237050.3877
24 | 2621356.4394 | 1237050.3877 | 2621347.8564 | 1237045.1093 | 2621329.4836 | 1237018.7716 | 2621278.54 | 1236988.4929
25 | 2621356.4394 | 1237050.3877 | 2621365.0511 | 1237036.0932

## bus_geodata
| x | y | coords
0 | 2621255.0213 | 1237185.323
1 | 2621234.6934 | 1237179.9502
2 | 2621261.0788 | 1237186.924
3 | 2621161.3357 | 1237167.9741
4 | 2621270.0601 | 1237189.2978
5 | 2621103.6289 | 1237156.0185
6 | 2621208.21 | 1237114.675
7 | 2621075.1315 | 1237166.8399
8 | 2621320.4116 | 1237190.3632
9 | 2621293.4284 | 1237206.4475
10 | 2621110.5439 | 1237279.6527
11 | 2621298.0786 | 1237213.4684
12 | 2621080.3 | 1237271.6595
13 | 2621368.8565 | 1237171.0881
14 | 2621050.2531 | 1237263.7184
15 | 2620997.3177 | 1237240.6617
16 | 2620991.4008 | 1237148.7062
17 | 2621182.811 | 1237087.6214
18 | 2621347.6774 | 1237110.6405
19 | 2621259.9587 | 1237077.5593
20 | 2621239.6429 | 1237050.6033
21 | 2621259.3208 | 1237067.6287
22 | 2621280.7358 | 1237043.0011
23 | 2621370.8726 | 1237059.2672
24 | 2621356.4394 | 1237050.3877
25 | 2621365.0511 | 1237036.0932
26 | 2621278.54 | 1236988.4929
27 | 2621259.3208 | 1237067.6287

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97292 | -0.52056 | 0.0078636 | 0.0019708
1 | 0.97317 | -0.51556 | 0.0059101 | 0.0014812
2 | 0.97289 | -0.52114 | 0.0014051 | 0.00035216
3 | 0.97448 | -0.48974 | 0.010393 | 0.0026048
4 | 0.97286 | -0.52177 | 0.0036498 | 0.00091473
5 | 0.97609 | -0.45805 | 0 | 0
6 | 0.97335 | -0.51191 | 0.014668 | 0.003676
7 | 0.97724 | -0.43547 | 0.0078377 | 0.0019643
8 | 0.97958 | -0.39015 | 0.0054319 | 0.0013614
9 | 0.97974 | -0.38705 | 0 | 0
10 | 0.98073 | -0.36756 | 0 | 0
11 | 0.98048 | -0.37263 | 0 | 0
12 | 0.98093 | -0.36378 | 0.0027572 | 0.00069103
13 | 0.98038 | -0.37448 | 0.0012337 | 0.0003092
14 | 0.9812 | -0.35846 | 0 | 0
15 | 0.9817 | -0.34853 | 0 | 0
16 | 0.98682 | -0.24976 | 0 | 0
17 | 0.99622 | -0.070992 | 0.0065068 | 0.0016308
18 | 0.97096 | -0.55921 | 0.036426 | 0.0091293
19 | 1 | 0 | -0.20186 | -0.051201
20 | 0.99917 | -0.01595 | 0.0034442 | 0.00086321
21 | 0.99926 | -0.014269 | 0 | 0
22 | 0.99673 | -0.062782 | 0.078753 | 0.019737
23 | 0.99821 | -0.034403 | 0 | 0
24 | 0.99804 | -0.03772 | 0 | 0
25 | 0.99801 | -0.038349 | 0.0021556 | 0.00054024
26 | 0.9972 | -0.053776 | 0.0090514 | 0.0022685
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012919 | -0.0032376 | 0.012922 | 0.0032394 | 3.0781e-06 | 1.7088e-06 | 0.019758 | 0.019758 | 0.019758 | 0.97292 | -0.52056 | 0.97317 | -0.51556 | 5.4281
1 | 0.0050552 | 0.0012669 | -0.0050551 | -0.0012668 | 1.4045e-07 | 1.2084e-08 | 0.0077316 | 0.0077316 | 0.0077316 | 0.97292 | -0.52056 | 0.97289 | -0.52114 | 2.1241
2 | -0.018832 | -0.0047206 | 0.018855 | 0.0047345 | 2.3197e-05 | 1.3918e-05 | 0.028795 | 0.028795 | 0.028795 | 0.97317 | -0.51556 | 0.97448 | -0.48974 | 7.9107
3 | 0.0036499 | 0.00091468 | -0.0036498 | -0.00091473 | 1.0856e-07 | -4.587e-08 | 0.0055825 | 0.0055825 | 0.0055825 | 0.97289 | -0.52114 | 0.97286 | -0.52177 | 1.5337
4 | -0.029248 | -0.0073393 | 0.029293 | 0.0073669 | 4.4264e-05 | 2.759e-05 | 0.044665 | 0.044665 | 0.044665 | 0.97448 | -0.48974 | 0.97609 | -0.45805 | 12.2707
5 | 0.051308 | 0.012936 | -0.051176 | -0.012855 | 0.0001319 | 8.1549e-05 | 0.078245 | 0.078246 | 0.078246 | 0.97609 | -0.45805 | 0.97335 | -0.51191 | 10.7481
6 | -0.080601 | -0.020303 | 0.080688 | 0.020358 | 8.7157e-05 | 5.501e-05 | 0.12291 | 0.12291 | 0.12291 | 0.97609 | -0.45805 | 0.97724 | -0.43547 | 16.8833
7 | 0.036509 | 0.0091785 | -0.036426 | -0.0091293 | 8.2268e-05 | 4.916e-05 | 0.055823 | 0.055824 | 0.055824 | 0.97335 | -0.51191 | 0.97096 | -0.55921 | 7.6682
8 | -0.088526 | -0.022322 | 0.088896 | 0.022556 | 0.00037004 | 0.0002341 | 0.13484 | 0.13484 | 0.13484 | 0.97724 | -0.43547 | 0.9817 | -0.34853 | 18.5225
9 | -0.0054319 | -0.0013614 | 0.0054327 | 0.0013615 | 8.0199e-07 | 1.1775e-07 | 0.0082512 | 0.008251 | 0.0082512 | 0.97958 | -0.39015 | 0.97974 | -0.38705 | 2.2668
10 | -0.0054327 | -0.0013615 | 0.0054377 | 0.0013622 | 5.044e-06 | 7.3733e-07 | 0.008251 | 0.0082502 | 0.008251 | 0.97974 | -0.38705 | 0.98073 | -0.36756 | 2.2668
11 | 0.0012341 | 0.00030557 | -0.0012338 | -0.00030823 | 2.9638e-07 | -2.6566e-06 | 0.0018711 | 0.0018721 | 0.0018721 | 0.98073 | -0.36756 | 0.98048 | -0.37263 | 0.51432
12 | -0.0066718 | -0.0016678 | 0.006673 | 0.0016682 | 1.2017e-06 | 3.7427e-07 | 0.010121 | 0.010121 | 0.010121 | 0.98073 | -0.36756 | 0.98093 | -0.36378 | 2.7806
13 | 0.0012338 | 0.00030823 | -0.0012337 | -0.0003092 | 1.0845e-07 | -9.7093e-07 | 0.0018721 | 0.0018725 | 0.0018725 | 0.98048 | -0.37263 | 0.98038 | -0.37448 | 0.51443
14 | -0.0094303 | -0.0023592 | 0.0094326 | 0.0023603 | 2.3844e-06 | 1.1336e-06 | 0.014304 | 0.014304 | 0.014304 | 0.98093 | -0.36378 | 0.9812 | -0.35846 | 3.9296
15 | -0.0094326 | -0.0023603 | 0.0094371 | 0.0023624 | 4.4612e-06 | 2.1204e-06 | 0.014304 | 0.014303 | 0.014304 | 0.9812 | -0.35846 | 0.9817 | -0.34853 | 3.9296
16 | -0.098333 | -0.024919 | 0.098802 | 0.025216 | 0.00046901 | 0.00029731 | 0.14915 | 0.14915 | 0.14915 | 0.9817 | -0.34853 | 0.98682 | -0.24976 | 20.4871
17 | -0.098802 | -0.025216 | 0.099663 | 0.025762 | 0.00086142 | 0.00054598 | 0.14915 | 0.14914 | 0.14915 | 0.98682 | -0.24976 | 0.99622 | -0.070992 | 20.487
18 | -0.10617 | -0.027393 | 0.10654 | 0.027627 | 0.00036869 | 0.00023392 | 0.15886 | 0.15886 | 0.15886 | 0.99622 | -0.070992 | 1 | 0 | 21.8217
19 | 0.011234 | 0.0028221 | -0.011216 | -0.0028126 | 1.8417e-05 | 9.4862e-06 | 0.016719 | 0.01672 | 0.01672 | 1 | 0 | 0.99821 | -0.034403 | 4.5933
20 | 0.082436 | 0.020752 | -0.08238 | -0.020717 | 5.6185e-05 | 3.5828e-05 | 0.1227 | 0.1227 | 0.1227 | 1 | 0 | 0.99926 | -0.014269 | 33.7083
21 | -0.0034442 | -0.00086321 | 0.0034445 | 0.00086302 | 2.7577e-07 | -1.8963e-07 | 0.0051294 | 0.0051292 | 0.0051294 | 0.99917 | -0.01595 | 0.99926 | -0.014269 | 1.4092
22 | 0.078935 | 0.019854 | -0.078753 | -0.019737 | 0.00018247 | 0.00011632 | 0.11757 | 0.11757 | 0.11757 | 0.99926 | -0.014269 | 0.99673 | -0.062782 | 32.2993
23 | 0.011216 | 0.0028126 | -0.011214 | -0.0028117 | 1.7727e-06 | 9.1351e-07 | 0.01672 | 0.01672 | 0.01672 | 0.99821 | -0.034403 | 0.99804 | -0.03772 | 4.5933
24 | 0.0090583 | 0.0022716 | -0.0090514 | -0.0022685 | 6.9278e-06 | 3.1114e-06 | 0.013506 | 0.013506 | 0.013506 | 0.99804 | -0.03772 | 0.9972 | -0.053776 | 3.7105
25 | 0.0021557 | 0.00054007 | -0.0021556 | -0.00054024 | 6.4642e-08 | -1.767e-07 | 0.0032139 | 0.003214 | 0.003214 | 0.99804 | -0.03772 | 0.99801 | -0.038349 | 0.88296

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20186 | 0.051201

## res_load
| p_mw | q_mvar
0 | 0.0078636 | 0.0019708
1 | 0.0059101 | 0.0014812
2 | 0.0014051 | 0.00035216
3 | 0.010393 | 0.0026048
4 | 0.0036498 | 0.00091473
5 | 0.014668 | 0.003676
6 | 0.0078377 | 0.0019643
7 | 0.0054319 | 0.0013614
8 | 0.0027572 | 0.00069103
9 | 0.0012337 | 0.0003092
10 | 0.0065068 | 0.0016308
11 | 0.036426 | 0.0091293
12 | 0.0034442 | 0.00086321
13 | 0.078753 | 0.019737
14 | 0.0021556 | 0.00054024
15 | 0.0090514 | 0.0022685

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1