## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2407-4_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2407-4_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2407-4_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2407-4_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2407-4_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2407-4_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2407-4_0_6_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2407-4_0_6_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2407-4_0_6_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_2407-4_0_6_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_2407-4_0_6_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_2407-4_0_6_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_2407-4_0_6_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_2407-4_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2407-4_0_6_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2407-4_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2407-4_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2407-4_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2407-4_0_6_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2407-4_0_6_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2407-4_0_6_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2407-4_0_6_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_2407-4_0_6_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2407-4_0_6_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2407-4_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2407-4_0_6_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2407-4_0_6_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_2407-4_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2407-4_0_6_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2407-4_0_6_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_2407-4_0_6_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_2407-4_0_6_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2407-4_0_6_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_2407-4_0_6_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2407-4_0_6_node_26 | 0.4 | n |  | TRUE
35 | bus_MV_479_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2407-4_0_6_load_0 | 0 | 0.0012185 | 0.00030538 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2407-4_0_6_load_4 | 4 | 0.012717 | 0.0031872 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2407-4_0_6_load_5 | 5 | 0.016974 | 0.0042542 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2407-4_0_6_load_7 | 6 | 0.0034909 | 0.00087491 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2407-4_0_6_load_15 | 9 | 0.011485 | 0.0028784 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2407-4_0_6_load_31 | 11 | 0.062219 | 0.015594 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2407-4_0_6_load_34 | 12 | 0.032969 | 0.0082627 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2407-4_0_6_load_9 | 13 | 0.025604 | 0.0064171 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2407-4_0_6_load_29 | 14 | 0.076517 | 0.019177 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2407-4_0_6_load_10 | 15 | 0.0014682 | 0.00036797 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2407-4_0_6_load_11 | 16 | 0.0023038 | 0.00057739 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2407-4_0_6_load_13 | 17 | 0.002266 | 0.00056792 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2407-4_0_6_load_14 | 18 | 0.0018725 | 0.00046931 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2407-4_0_6_load_16 | 19 | 0.025599 | 0.0064157 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2407-4_0_6_load_17 | 20 | 0.008426 | 0.0021118 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2407-4_0_6_load_32 | 21 | 0.0078086 | 0.001957 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2407-4_0_6_load_18 | 22 | 0.0047986 | 0.0012026 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2407-4_0_6_load_19 | 23 | 0.0010486 | 0.00026281 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2407-4_0_6_load_22 | 26 | 0.018691 | 0.0046844 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2407-4_0_6_load_24 | 28 | 0.0798 | 0.02 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2407-4_0_6_load_36 | 30 | 0.003551 | 0.00088996 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2407-4_0_6_load_38 | 32 | 0.069173 | 0.017336 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2407-4_0_6_load_25 | 33 | 0.016591 | 0.0041581 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2407-4_0_6_load_26 | 34 | 0.033012 | 0.0082737 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2407-4_0_6_line_0 |  | 0 | 1 | 0.047725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2407-4_0_6_line_1 |  | 0 | 2 | 0.02271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2407-4_0_6_line_2 |  | 1 | 3 | 0.018544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2407-4_0_6_line_3 |  | 1 | 4 | 0.029233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2407-4_0_6_line_4 |  | 2 | 5 | 0.01064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2407-4_0_6_line_5 |  | 3 | 6 | 0.028065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2407-4_0_6_line_6 |  | 4 | 7 | 0.02582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2407-4_0_6_line_7 |  | 7 | 8 | 0.008015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2407-4_0_6_line_8 |  | 8 | 11 | 0.015776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2407-4_0_6_line_9 |  | 8 | 12 | 0.017058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2407-4_0_6_line_10 |  | 9 | 10 | 0.014502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2407-4_0_6_line_11 |  | 10 | 18 | 0.019032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2407-4_0_6_line_12 |  | 10 | 15 | 0.0090454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2407-4_0_6_line_13 |  | 11 | 14 | 0.044197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2407-4_0_6_line_14 |  | 11 | 13 | 0.065648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2407-4_0_6_line_15 |  | 12 | 20 | 0.028153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2407-4_0_6_line_16 |  | 14 | 31 | 0.023921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2407-4_0_6_line_17 |  | 15 | 16 | 0.0037772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2407-4_0_6_line_18 |  | 16 | 17 | 0.006329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2407-4_0_6_line_19 |  | 17 | 19 | 0.0035122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2407-4_0_6_line_20 |  | 18 | 20 | 0.024631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2407-4_0_6_line_21 |  | 19 | 21 | 0.024208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2407-4_0_6_line_22 |  | 22 | 23 | 0.056237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2407-4_0_6_line_23 |  | 22 | 24 | 0.0011358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2407-4_0_6_line_24 |  | 23 | 25 | 0.044367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2407-4_0_6_line_25 |  | 24 | 26 | 0.020736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2407-4_0_6_line_26 |  | 25 | 27 | 0.092448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2407-4_0_6_line_27 |  | 26 | 28 | 0.027287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2407-4_0_6_line_28 |  | 27 | 29 | 0.049392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2407-4_0_6_line_29 |  | 27 | 30 | 0.00052124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2407-4_0_6_line_30 |  | 28 | 31 | 0.0086472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2407-4_0_6_line_31 |  | 29 | 32 | 0.028423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2407-4_0_6_line_32 |  | 31 | 33 | 0.050332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2407-4_0_6_line_33 |  | 33 | 34 | 0.021972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2407-4_0_6_trafo_27 | 0.63 MVA 20/0.4 kV | 35 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2620244.9994 | 1237013.2053 | 2620261.6024 | 1236969.7016 | 2620261.7639 | 1236968.5522
1 | 2620264.9361 | 1236946.065 | 2620263.2461 | 1236958 | 2620261.7639 | 1236968.5522
2 | 2620235.1034 | 1237028.9036 | 2620244.9994 | 1237013.2053
3 | 2620244.9994 | 1237013.2053 | 2620271.2403 | 1237026.0878
4 | 2620264.9361 | 1236946.065 | 2620266.4301 | 1236935.5304
5 | 2620235.1034 | 1237028.9036 | 2620217.4202 | 1237007.1104
6 | 2620294.4176 | 1237037.4663 | 2620271.2403 | 1237026.0878
7 | 2620301.6306 | 1237041.0041 | 2620294.4176 | 1237037.4663
8 | 2620301.6306 | 1237041.0041 | 2620315.7291 | 1237048.0834
9 | 2620301.6306 | 1237041.0041 | 2620296.7632 | 1237057.3532
10 | 2620260.713 | 1237106.5386 | 2620248.1553 | 1237113.7926
11 | 2620260.713 | 1237106.5386 | 2620256.8439 | 1237100.8108 | 2620259.6662 | 1237089.0242
12 | 2620260.713 | 1237106.5386 | 2620269.5177 | 1237108.6114
13 | 2620315.7291 | 1237048.0834 | 2620355.2268 | 1237067.9161
14 | 2620315.7291 | 1237048.0834 | 2620354.4751 | 1236995.0892
15 | 2620296.7632 | 1237057.3532 | 2620296.7632 | 1237057.3532 | 2620270.2595 | 1237066.8466 | 2620270.2595 | 1237066.8466
16 | 2620376.6038 | 1237078.6501 | 2620355.2268 | 1237067.9161
17 | 2620269.5177 | 1237108.6114 | 2620271.8781 | 1237109.1671 | 2620272.8868 | 1237110.0678
18 | 2620272.8868 | 1237110.0678 | 2620277.6077 | 1237114.2831
19 | 2620280.2275 | 1237116.6224 | 2620280.2275 | 1237116.6224 | 2620277.6077 | 1237114.2831
20 | 2620259.6662 | 1237089.0242 | 2620260.1823 | 1237086.8691 | 2620270.2595 | 1237066.8466
21 | 2620275.3604 | 1237140.3356 | 2620280.2275 | 1237116.6224
22 | 2620429.4225 | 1237102.1208 | 2620438.3753 | 1237107.2905 | 2620446.4438 | 1237114.9674 | 2620450.568 | 1237121.2743 | 2620463.3382 | 1237145.3197
23 | 2620428.439 | 1237101.5529 | 2620429.4225 | 1237102.1208
24 | 2620483.9932 | 1237184.5838 | 2620479.3642 | 1237175.4956 | 2620463.3382 | 1237145.3197
25 | 2620428.439 | 1237101.5529 | 2620409.4722 | 1237093.1726
26 | 2620483.9932 | 1237184.5838 | 2620490.781 | 1237181.8833 | 2620494.765 | 1237180.5073 | 2620499.1251 | 1237179.7774 | 2620501.1534 | 1237179.5398 | 2620504.0732 | 1237179.6499 | 2620507.6024 | 1237180.7516 | 2620512.2033 | 1237182.6019 | 2620519.5793 | 1237189.2092 | 2620526.9927 | 1237195.9723 | 2620539.9635 | 1237183.865 | 2620543.1755 | 1237180.3962 | 2620556.8909 | 1237165.1897
27 | 2620409.4722 | 1237093.1726 | 2620384.5133 | 1237082.1448
28 | 2620556.8909 | 1237165.1897 | 2620562.389 | 1237159.1605 | 2620562.7688 | 1237158.7282 | 2620566.6879 | 1237154.2723 | 2620570.5265 | 1237151.217 | 2620574.8465 | 1237148.9639 | 2620575.9659 | 1237146.8331 | 2620578.54 | 1237141.9279 | 2620580.969 | 1237137.3779 | 2620585.8935 | 1237126.6105
29 | 2620557.2841 | 1237165.5318 | 2620556.8909 | 1237165.1897
30 | 2620376.6038 | 1237078.6501 | 2620384.5133 | 1237082.1448
31 | 2620585.8935 | 1237126.6105 | 2620612.8088 | 1237135.976
32 | 2620376.6038 | 1237078.6501 | 2620360.1536 | 1237090.6012 | 2620344.5107 | 1237116.1983
33 | 2620333.0532 | 1237134.9465 | 2620344.5107 | 1237116.1983

## bus_geodata
| x | y | coords
0 | 2620261.7639 | 1236968.5522
1 | 2620244.9994 | 1237013.2053
2 | 2620264.9361 | 1236946.065
3 | 2620235.1034 | 1237028.9036
4 | 2620271.2403 | 1237026.0878
5 | 2620266.4301 | 1236935.5304
6 | 2620217.4202 | 1237007.1104
7 | 2620294.4176 | 1237037.4663
8 | 2620301.6306 | 1237041.0041
9 | 2620248.1553 | 1237113.7926
10 | 2620260.713 | 1237106.5386
11 | 2620315.7291 | 1237048.0834
12 | 2620296.7632 | 1237057.3532
13 | 2620354.4751 | 1236995.0892
14 | 2620355.2268 | 1237067.9161
15 | 2620269.5177 | 1237108.6114
16 | 2620272.8868 | 1237110.0678
17 | 2620277.6077 | 1237114.2831
18 | 2620259.6662 | 1237089.0242
19 | 2620280.2275 | 1237116.6224
20 | 2620270.2595 | 1237066.8466
21 | 2620275.3604 | 1237140.3356
22 | 2620429.4225 | 1237102.1208
23 | 2620463.3382 | 1237145.3197
24 | 2620428.439 | 1237101.5529
25 | 2620483.9932 | 1237184.5838
26 | 2620409.4722 | 1237093.1726
27 | 2620556.8909 | 1237165.1897
28 | 2620384.5133 | 1237082.1448
29 | 2620585.8935 | 1237126.6105
30 | 2620557.2841 | 1237165.5318
31 | 2620376.6038 | 1237078.6501
32 | 2620612.8088 | 1237135.976
33 | 2620344.5107 | 1237116.1983
34 | 2620333.0532 | 1237134.9465
35 | 2620428.439 | 1237101.5529

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98918 | -0.20817 | 0.0012185 | 0.00030538
1 | 0.98997 | -0.19271 | 0 | 0
2 | 0.98882 | -0.21504 | 0 | 0
3 | 0.98991 | -0.19387 | 0 | 0
4 | 0.99055 | -0.18144 | 0.012717 | 0.0031872
5 | 0.98866 | -0.21826 | 0.016974 | 0.0042542
6 | 0.98982 | -0.19561 | 0.0034909 | 0.00087491
7 | 0.99137 | -0.16568 | 0 | 0
8 | 0.99162 | -0.16079 | 0 | 0
9 | 0.98632 | -0.26357 | 0.011485 | 0.0028784
10 | 0.98647 | -0.26058 | 0 | 0
11 | 0.99348 | -0.12489 | 0.062219 | 0.015594
12 | 0.99014 | -0.18931 | 0.032969 | 0.0082627
13 | 0.99195 | -0.15462 | 0.025604 | 0.0064171
14 | 0.99786 | -0.040801 | 0.076517 | 0.019177
15 | 0.98614 | -0.26697 | 0.0014682 | 0.00036797
16 | 0.98601 | -0.26955 | 0.0023038 | 0.00057739
17 | 0.9858 | -0.27359 | 0.002266 | 0.00056792
18 | 0.98736 | -0.24324 | 0.0018725 | 0.00046931
19 | 0.9857 | -0.2757 | 0.025599 | 0.0064157
20 | 0.98856 | -0.22001 | 0.008426 | 0.0021118
21 | 0.98552 | -0.27909 | 0.0078086 | 0.001957
22 | 0.99525 | -0.089987 | 0.0047986 | 0.0012026
23 | 0.9914 | -0.16328 | 0.0010486 | 0.00026281
24 | 0.99533 | -0.088417 | 0 | 0
25 | 0.9884 | -0.22068 | 0 | 0
26 | 0.99684 | -0.059794 | 0.018691 | 0.0046844
27 | 0.98216 | -0.34139 | 0 | 0
28 | 0.9993 | -0.013353 | 0.0798 | 0.02
29 | 0.97899 | -0.40333 | 0 | 0
30 | 0.98216 | -0.34143 | 0.003551 | 0.00088996
31 | 1 | 0 | -0.52518 | -0.13272
32 | 0.97716 | -0.43915 | 0.069173 | 0.017336
33 | 0.99773 | -0.043615 | 0.016591 | 0.0041581
34 | 0.99707 | -0.056323 | 0.033012 | 0.0082737
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.018201 | -0.0045644 | 0.018215 | 0.0045724 | 1.3417e-05 | 7.974e-06 | 0.027381 | 0.027381 | 0.027381 | 0.98918 | -0.20817 | 0.98997 | -0.19271 | 7.5222
1 | 0.016983 | 0.004259 | -0.016977 | -0.0042557 | 5.5585e-06 | 3.266e-06 | 0.025548 | 0.025548 | 0.025548 | 0.98918 | -0.20817 | 0.98882 | -0.21504 | 7.0187
2 | 0.0034914 | 0.00087462 | -0.0034912 | -0.00087473 | 1.9151e-07 | -1.1585e-07 | 0.0052477 | 0.0052478 | 0.0052478 | 0.98997 | -0.19271 | 0.98991 | -0.19387 | 1.4417
3 | -0.021706 | -0.005447 | 0.021718 | 0.0054541 | 1.167e-05 | 7.093e-06 | 0.032628 | 0.032628 | 0.032628 | 0.98997 | -0.19271 | 0.99055 | -0.18144 | 8.9639
4 | 0.016977 | 0.0042557 | -0.016974 | -0.0042542 | 2.6043e-06 | 1.5303e-06 | 0.025548 | 0.025548 | 0.025548 | 0.98882 | -0.21504 | 0.98866 | -0.21826 | 7.0187
5 | 0.0034912 | 0.00087473 | -0.0034909 | -0.00087491 | 2.8984e-07 | -1.7527e-07 | 0.0052478 | 0.005248 | 0.005248 | 0.98991 | -0.19387 | 0.98982 | -0.19561 | 1.4417
6 | -0.034435 | -0.0086412 | 0.03446 | 0.0086575 | 2.5912e-05 | 1.6251e-05 | 0.051732 | 0.051732 | 0.051732 | 0.99055 | -0.18144 | 0.99137 | -0.16568 | 14.212
7 | -0.03446 | -0.0086575 | 0.034468 | 0.0086625 | 8.0435e-06 | 5.0445e-06 | 0.051732 | 0.051732 | 0.051732 | 0.99137 | -0.16568 | 0.99162 | -0.16079 | 14.212
8 | -0.12902 | -0.032492 | 0.12924 | 0.032634 | 0.00022187 | 0.00014179 | 0.19366 | 0.19366 | 0.19366 | 0.99162 | -0.16079 | 0.99348 | -0.12489 | 53.2021
9 | 0.094547 | 0.02383 | -0.094418 | -0.023748 | 0.00012885 | 8.2243e-05 | 0.14192 | 0.14192 | 0.14192 | 0.99162 | -0.16079 | 0.99014 | -0.18931 | 38.9902
10 | -0.011485 | -0.0028784 | 0.011486 | 0.0028792 | 1.6326e-06 | 8.5978e-07 | 0.017327 | 0.017327 | 0.017327 | 0.98632 | -0.26357 | 0.98647 | -0.26058 | 4.7601
11 | -0.05096 | -0.012783 | 0.051002 | 0.012809 | 4.2176e-05 | 2.6749e-05 | 0.076873 | 0.076873 | 0.076873 | 0.98647 | -0.26058 | 0.98736 | -0.24324 | 21.119
12 | 0.039474 | 0.0099034 | -0.039462 | -0.0098958 | 1.2027e-05 | 7.5821e-06 | 0.059547 | 0.059547 | 0.059547 | 0.98647 | -0.26058 | 0.98614 | -0.26697 | 16.359
13 | -0.2171 | -0.054667 | 0.21797 | 0.055227 | 0.00087668 | 0.00055993 | 0.32525 | 0.32525 | 0.32525 | 0.99348 | -0.12489 | 0.99786 | -0.040801 | 44.6778
14 | 0.025641 | 0.0064395 | -0.025604 | -0.0064171 | 3.6318e-05 | 2.2394e-05 | 0.038409 | 0.038409 | 0.038409 | 0.99348 | -0.12489 | 0.99195 | -0.15462 | 10.552
15 | 0.06145 | 0.015485 | -0.06136 | -0.015428 | 9.0093e-05 | 5.7298e-05 | 0.092378 | 0.092378 | 0.092378 | 0.99014 | -0.18931 | 0.98856 | -0.22001 | 25.3786
16 | -0.29449 | -0.074404 | 0.29507 | 0.074773 | 0.00057719 | 0.00036846 | 0.43936 | 0.43936 | 0.43936 | 0.99786 | -0.040801 | 1 | 0 | 40.2341
17 | 0.037993 | 0.0095279 | -0.037989 | -0.0095249 | 4.6557e-06 | 2.9315e-06 | 0.057331 | 0.057331 | 0.057331 | 0.98614 | -0.26697 | 0.98601 | -0.26955 | 15.7504
18 | 0.035685 | 0.0089475 | -0.035678 | -0.0089432 | 6.8835e-06 | 4.3247e-06 | 0.053855 | 0.053855 | 0.053855 | 0.98601 | -0.26955 | 0.9858 | -0.27359 | 14.7952
19 | 0.033412 | 0.0083753 | -0.033409 | -0.0083732 | 3.3501e-06 | 2.0993e-06 | 0.050434 | 0.050434 | 0.050434 | 0.9858 | -0.27359 | 0.9857 | -0.2757 | 13.8555
20 | -0.052875 | -0.013279 | 0.052934 | 0.013316 | 5.8666e-05 | 3.7231e-05 | 0.079695 | 0.079695 | 0.079695 | 0.98736 | -0.24324 | 0.98856 | -0.22001 | 21.8943
21 | 0.0078098 | 0.0019575 | -0.0078086 | -0.001957 | 1.2618e-06 | 4.9906e-07 | 0.01179 | 0.01179 | 0.01179 | 0.9857 | -0.2757 | 0.98552 | -0.27909 | 3.239
22 | 0.074991 | 0.019266 | -0.074725 | -0.019096 | 0.00026591 | 0.00016945 | 0.11229 | 0.11229 | 0.11229 | 0.99525 | -0.089987 | 0.9914 | -0.16328 | 30.8487
23 | -0.07979 | -0.020468 | 0.079796 | 0.020472 | 6.0785e-06 | 3.8755e-06 | 0.11946 | 0.11946 | 0.11946 | 0.99525 | -0.089987 | 0.99533 | -0.088417 | 32.8196
24 | 0.073677 | 0.018833 | -0.073473 | -0.018703 | 0.00020394 | 0.00012995 | 0.11072 | 0.11072 | 0.11072 | 0.9914 | -0.16328 | 0.9884 | -0.22068 | 30.4164
25 | -0.079796 | -0.020472 | 0.079907 | 0.020543 | 0.00011097 | 7.0753e-05 | 0.11946 | 0.11946 | 0.11946 | 0.99533 | -0.088417 | 0.99684 | -0.059794 | 32.8196
26 | 0.073473 | 0.018703 | -0.073048 | -0.018433 | 0.00042496 | 0.0002708 | 0.11072 | 0.11072 | 0.11072 | 0.9884 | -0.22068 | 0.98216 | -0.34139 | 30.4165
27 | -0.098598 | -0.025227 | 0.09882 | 0.025369 | 0.00022221 | 0.00014186 | 0.14736 | 0.14736 | 0.14736 | 0.99684 | -0.059794 | 0.9993 | -0.013353 | 40.4844
28 | 0.069497 | 0.017543 | -0.069291 | -0.017412 | 0.00020551 | 0.00013091 | 0.10534 | 0.10534 | 0.10534 | 0.98216 | -0.34139 | 0.97899 | -0.40333 | 28.9385
29 | 0.003551 | 0.00088996 | -0.003551 | -0.00088996 | 5.6575e-09 | -2.9759e-09 | 0.0053799 | 0.0053799 | 0.0053799 | 0.98216 | -0.34139 | 0.98216 | -0.34143 | 1.478
30 | -0.17862 | -0.045369 | 0.17874 | 0.045442 | 0.00011488 | 7.3298e-05 | 0.26619 | 0.26619 | 0.26619 | 0.9993 | -0.013353 | 1 | 0 | 36.5645
31 | 0.069291 | 0.017412 | -0.069173 | -0.017336 | 0.00011827 | 7.5333e-05 | 0.10534 | 0.10534 | 0.10534 | 0.97899 | -0.40333 | 0.97716 | -0.43915 | 28.9386
32 | 0.049727 | 0.01251 | -0.049623 | -0.012444 | 0.00010339 | 6.5508e-05 | 0.07401 | 0.074011 | 0.074011 | 1 | 0 | 0.99773 | -0.043615 | 20.3326
33 | 0.033032 | 0.0082862 | -0.033012 | -0.0082737 | 1.9999e-05 | 1.2513e-05 | 0.049267 | 0.049267 | 0.049267 | 0.99773 | -0.043615 | 0.99707 | -0.056323 | 13.5349

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52518 | 0.13272

## res_load
| p_mw | q_mvar
0 | 0.0012185 | 0.00030538
1 | 0.012717 | 0.0031872
2 | 0.016974 | 0.0042542
3 | 0.0034909 | 0.00087491
4 | 0.011485 | 0.0028784
5 | 0.062219 | 0.015594
6 | 0.032969 | 0.0082627
7 | 0.025604 | 0.0064171
8 | 0.076517 | 0.019177
9 | 0.0014682 | 0.00036797
10 | 0.0023038 | 0.00057739
11 | 0.002266 | 0.00056792
12 | 0.0018725 | 0.00046931
13 | 0.025599 | 0.0064157
14 | 0.008426 | 0.0021118
15 | 0.0078086 | 0.001957
16 | 0.0047986 | 0.0012026
17 | 0.0010486 | 0.00026281
18 | 0.018691 | 0.0046844
19 | 0.0798 | 0.02
20 | 0.003551 | 0.00088996
21 | 0.069173 | 0.017336
22 | 0.016591 | 0.0041581
23 | 0.033012 | 0.0082737

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1