## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2407-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2407-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2407-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2407-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2407-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2407-8_0_4_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_2407-8_0_4_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2407-8_0_4_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_2407-8_0_4_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_2407-8_0_4_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_2407-8_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2407-8_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2407-8_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2407-8_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2407-8_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2407-8_0_4_node_77 | 0.4 | n |  | TRUE
16 | bus_LV_2407-8_0_4_node_56 | 0.4 | n |  | TRUE
17 | bus_LV_2407-8_0_4_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_2407-8_0_4_node_57 | 0.4 | n |  | TRUE
19 | bus_LV_2407-8_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2407-8_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2407-8_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2407-8_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2407-8_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2407-8_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2407-8_0_4_node_105 | 0.4 | n |  | TRUE
26 | bus_LV_2407-8_0_4_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_2407-8_0_4_node_87 | 0.4 | n |  | TRUE
28 | bus_LV_2407-8_0_4_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_2407-8_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_2407-8_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2407-8_0_4_node_85 | 0.4 | n |  | TRUE
32 | bus_LV_2407-8_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_2407-8_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_2407-8_0_4_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_2407-8_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_2407-8_0_4_node_43 | 0.4 | n |  | TRUE
37 | bus_LV_2407-8_0_4_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_2407-8_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2407-8_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2407-8_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_2407-8_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_2407-8_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_2407-8_0_4_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_2407-8_0_4_node_60 | 0.4 | n |  | TRUE
45 | bus_LV_2407-8_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_2407-8_0_4_node_92 | 0.4 | n |  | TRUE
47 | bus_LV_2407-8_0_4_node_130 | 0.4 | n |  | TRUE
48 | bus_LV_2407-8_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_2407-8_0_4_node_94 | 0.4 | n |  | TRUE
50 | bus_LV_2407-8_0_4_node_91 | 0.4 | n |  | TRUE
51 | bus_LV_2407-8_0_4_node_129 | 0.4 | n |  | TRUE
52 | bus_LV_2407-8_0_4_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_2407-8_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_2407-8_0_4_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_2407-8_0_4_node_55 | 0.4 | n |  | TRUE
56 | bus_LV_2407-8_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_2407-8_0_4_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_2407-8_0_4_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_2407-8_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_2407-8_0_4_node_69 | 0.4 | n |  | TRUE
61 | bus_LV_2407-8_0_4_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_2407-8_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_2407-8_0_4_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_2407-8_0_4_node_98 | 0.4 | n |  | TRUE
65 | bus_LV_2407-8_0_4_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_2407-8_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_2407-8_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_2407-8_0_4_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_2407-8_0_4_node_107 | 0.4 | n |  | TRUE
70 | bus_LV_2407-8_0_4_node_108 | 0.4 | n |  | TRUE
71 | bus_LV_2407-8_0_4_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_2407-8_0_4_node_89 | 0.4 | n |  | TRUE
73 | bus_LV_2407-8_0_4_node_90 | 0.4 | n |  | TRUE
74 | bus_LV_2407-8_0_4_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_2407-8_0_4_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_2407-8_0_4_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_2407-8_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_2407-8_0_4_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_2407-8_0_4_node_83 | 0.4 | n |  | TRUE
80 | bus_LV_2407-8_0_4_node_82 | 0.4 | n |  | TRUE
81 | bus_LV_2407-8_0_4_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_2407-8_0_4_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_2407-8_0_4_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_2407-8_0_4_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_2407-8_0_4_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_2407-8_0_4_node_101 | 0.4 | n |  | TRUE
87 | bus_LV_2407-8_0_4_node_100 | 0.4 | n |  | TRUE
88 | bus_LV_2407-8_0_4_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_2407-8_0_4_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_2407-8_0_4_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_2407-8_0_4_node_131 | 0.4 | n |  | TRUE
92 | bus_LV_2407-8_0_4_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_2407-8_0_4_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_2407-8_0_4_node_68 | 0.4 | n |  | TRUE
95 | bus_LV_2407-8_0_4_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_2407-8_0_4_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_2407-8_0_4_node_102 | 0.4 | n |  | TRUE
98 | bus_LV_2407-8_0_4_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_2407-8_0_4_node_103 | 0.4 | n |  | TRUE
100 | bus_LV_2407-8_0_4_node_72 | 0.4 | n |  | TRUE
101 | bus_LV_2407-8_0_4_node_73 | 0.4 | n |  | TRUE
102 | bus_LV_2407-8_0_4_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_2407-8_0_4_node_76 | 0.4 | n |  | TRUE
104 | bus_LV_2407-8_0_4_node_113 | 0.4 | n |  | TRUE
105 | bus_LV_2407-8_0_4_node_111 | 0.4 | n |  | TRUE
106 | bus_LV_2407-8_0_4_node_132 | 0.4 | n |  | TRUE
107 | bus_LV_2407-8_0_4_node_133 | 0.4 | n |  | TRUE
108 | bus_LV_2407-8_0_4_node_80 | 0.4 | n |  | TRUE
109 | bus_LV_2407-8_0_4_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_2407-8_0_4_node_86 | 0.4 | n |  | TRUE
111 | bus_LV_2407-8_0_4_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_2407-8_0_4_node_134 | 0.4 | n |  | TRUE
113 | bus_LV_2407-8_0_4_node_97 | 0.4 | n |  | TRUE
114 | bus_LV_2407-8_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_2407-8_0_4_node_126 | 0.4 | n |  | TRUE
116 | bus_LV_2407-8_0_4_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_2407-8_0_4_node_118 | 0.4 | n |  | TRUE
118 | bus_LV_2407-8_0_4_node_125 | 0.4 | n |  | TRUE
119 | bus_LV_2407-8_0_4_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_2407-8_0_4_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_2407-8_0_4_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_2407-8_0_4_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_2407-8_0_4_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_2407-8_0_4_node_128 | 0.4 | n |  | TRUE
125 | bus_LV_2407-8_0_4_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_2407-8_0_4_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_2407-8_0_4_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_2407-8_0_4_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_2407-8_0_4_node_127 | 0.4 | n |  | TRUE
130 | bus_MV_479_0_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2407-8_0_4_load_0 | 0 | 0.0038077 | 0.00095431 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2407-8_0_4_load_1 | 1 | 0.0033611 | 0.00084237 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2407-8_0_4_load_2 | 2 | 0.0034767 | 0.00087134 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2407-8_0_4_load_3 | 3 | 0.0027882 | 0.0006988 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2407-8_0_4_load_4 | 4 | 0.0029841 | 0.00074787 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2407-8_0_4_load_44 | 5 | 0.0041442 | 0.0010386 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2407-8_0_4_load_45 | 7 | 0.0024961 | 0.00062558 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2407-8_0_4_load_27 | 8 | 0.0025784 | 0.00064621 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2407-8_0_4_load_5 | 10 | 0.0017255 | 0.00043246 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2407-8_0_4_load_6 | 11 | 0.00212 | 0.00053132 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2407-8_0_4_load_7 | 12 | 0.0030212 | 0.00075719 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2407-8_0_4_load_9 | 13 | 0.0033555 | 0.00084097 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2407-8_0_4_load_8 | 14 | 0.001844 | 0.00046214 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2407-8_0_4_load_77 | 15 | 0.0010527 | 0.00026384 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2407-8_0_4_load_56 | 16 | 0.0020667 | 0.00051797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2407-8_0_4_load_57 | 18 | 0.0019881 | 0.00049826 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2407-8_0_4_load_10 | 19 | 0.0024494 | 0.00061387 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2407-8_0_4_load_11 | 20 | 0.0024378 | 0.00061096 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2407-8_0_4_load_13 | 22 | 0.0033463 | 0.00083866 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2407-8_0_4_load_14 | 23 | 0.0061392 | 0.0015386 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2407-8_0_4_load_15 | 24 | 0.0017809 | 0.00044634 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2407-8_0_4_load_105 | 25 | 0.003444 | 0.00086315 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2407-8_0_4_load_30 | 26 | 0.0028112 | 0.00070454 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2407-8_0_4_load_42 | 28 | 0.003025 | 0.00075815 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2407-8_0_4_load_29 | 29 | 0.0024578 | 0.00061597 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2407-8_0_4_load_20 | 30 | 0.0047992 | 0.0012028 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2407-8_0_4_load_85 | 31 | 0.0015927 | 0.00039917 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2407-8_0_4_load_16 | 32 | 0.0026088 | 0.00065383 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2407-8_0_4_load_17 | 33 | 0.0028113 | 0.00070457 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2407-8_0_4_load_18 | 34 | 0.0015641 | 0.00039199 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2407-8_0_4_load_19 | 35 | 0.0044229 | 0.0011085 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2407-8_0_4_load_43 | 36 | 0.006219 | 0.0015586 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2407-8_0_4_load_71 | 37 | 0.0046662 | 0.0011695 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2407-8_0_4_load_21 | 38 | 0.0031699 | 0.00079445 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2407-8_0_4_load_22 | 39 | 0.001103 | 0.00027644 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2407-8_0_4_load_23 | 40 | 0.0035566 | 0.00089137 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2407-8_0_4_load_24 | 41 | 0.0022453 | 0.00056273 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2407-8_0_4_load_25 | 42 | 0.0049085 | 0.0012302 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2407-8_0_4_load_59 | 43 | 0.0024911 | 0.00062432 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2407-8_0_4_load_60 | 44 | 0.0024898 | 0.000624 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2407-8_0_4_load_33 | 45 | 0.0032815 | 0.00082241 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2407-8_0_4_load_92 | 46 | 0.010896 | 0.0027308 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2407-8_0_4_load_130 | 47 | 0.0014618 | 0.00036636 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2407-8_0_4_load_91 | 50 | 0.0015051 | 0.00037722 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2407-8_0_4_load_129 | 51 | 0.0018732 | 0.00046948 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2407-8_0_4_load_31 | 52 | 0.0023225 | 0.00058206 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2407-8_0_4_load_32 | 53 | 0.0022053 | 0.00055269 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2407-8_0_4_load_54 | 54 | 0.0024331 | 0.00060979 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2407-8_0_4_load_55 | 55 | 0.0014148 | 0.00035457 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2407-8_0_4_load_35 | 56 | 0.0022029 | 0.0005521 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2407-8_0_4_load_36 | 57 | 0.001692 | 0.00042407 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2407-8_0_4_load_37 | 58 | 0.002582 | 0.00064712 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2407-8_0_4_load_47 | 59 | 0.0020339 | 0.00050974 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2407-8_0_4_load_69 | 60 | 0.0027827 | 0.00069741 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2407-8_0_4_load_99 | 61 | 0.0034967 | 0.00087636 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2407-8_0_4_load_48 | 62 | 0.0020298 | 0.00050872 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2407-8_0_4_load_98 | 64 | 0.0030359 | 0.00076086 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2407-8_0_4_load_38 | 65 | 0.0057989 | 0.0014533 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2407-8_0_4_load_39 | 66 | 0.0017329 | 0.00043432 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2407-8_0_4_load_40 | 67 | 0.0042569 | 0.0010669 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2407-8_0_4_load_41 | 68 | 0.0022346 | 0.00056005 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2407-8_0_4_load_107 | 69 | 0.002346 | 0.00058797 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2407-8_0_4_load_108 | 70 | 0.0023589 | 0.00059119 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2407-8_0_4_load_46 | 71 | 0.002601 | 0.00065187 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2407-8_0_4_load_89 | 72 | 0.0027396 | 0.0006866 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2407-8_0_4_load_90 | 73 | 0.0015288 | 0.00038314 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2407-8_0_4_load_49 | 74 | 0.0022087 | 0.00055356 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2407-8_0_4_load_51 | 75 | 0.0017729 | 0.00044432 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2407-8_0_4_load_50 | 76 | 0.0017619 | 0.00044156 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2407-8_0_4_load_52 | 77 | 0.0035312 | 0.000885 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2407-8_0_4_load_83 | 79 | 0.0021794 | 0.00054621 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2407-8_0_4_load_82 | 80 | 0.0023186 | 0.0005811 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2407-8_0_4_load_62 | 81 | 0.0065836 | 0.00165 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2407-8_0_4_load_63 | 82 | 0.01163 | 0.0029149 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2407-8_0_4_load_81 | 84 | 0.0014794 | 0.00037076 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2407-8_0_4_load_58 | 85 | 0.0016375 | 0.00041039 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2407-8_0_4_load_101 | 86 | 0.0021387 | 0.000536 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2407-8_0_4_load_100 | 87 | 0.0022073 | 0.00055321 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2407-8_0_4_load_61 | 88 | 0.002661 | 0.0006669 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2407-8_0_4_load_78 | 89 | 0.003385 | 0.00084836 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2407-8_0_4_load_131 | 91 | 0.005346 | 0.0013398 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2407-8_0_4_load_65 | 92 | 0.002286 | 0.00057293 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2407-8_0_4_load_66 | 93 | 0.0023093 | 0.00057875 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2407-8_0_4_load_70 | 95 | 0.0020047 | 0.00050243 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2407-8_0_4_load_95 | 96 | 0.001273 | 0.00031905 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2407-8_0_4_load_102 | 97 | 0.0029233 | 0.00073266 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2407-8_0_4_load_96 | 98 | 0.0016197 | 0.00040593 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2407-8_0_4_load_103 | 99 | 0.0043399 | 0.0010877 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2407-8_0_4_load_72 | 100 | 0.0016017 | 0.00040141 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2407-8_0_4_load_73 | 101 | 0.0022535 | 0.00056478 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2407-8_0_4_load_76 | 103 | 0.00078906 | 0.00019776 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2407-8_0_4_load_111 | 105 | 0.0069989 | 0.0017541 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2407-8_0_4_load_132 | 106 | 0.006315 | 0.0015827 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2407-8_0_4_load_133 | 107 | 0.011026 | 0.0027633 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2407-8_0_4_load_80 | 108 | 0.0022508 | 0.00056411 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2407-8_0_4_load_84 | 109 | 0.0026542 | 0.00066522 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2407-8_0_4_load_86 | 110 | 0.0015868 | 0.00039769 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2407-8_0_4_load_93 | 111 | 0.0027704 | 0.00069434 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2407-8_0_4_load_97 | 113 | 0.0020885 | 0.00052344 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2407-8_0_4_load_104 | 114 | 0.0025379 | 0.00063605 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2407-8_0_4_load_126 | 115 | 0.0021244 | 0.00053242 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2407-8_0_4_load_109 | 116 | 0.0022244 | 0.0005575 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2407-8_0_4_load_125 | 118 | 0.0016267 | 0.0004077 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2407-8_0_4_load_116 | 119 | 0.0012486 | 0.00031293 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2407-8_0_4_load_110 | 120 | 0.00079327 | 0.00019881 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2407-8_0_4_load_112 | 121 | 0.005566 | 0.001395 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2407-8_0_4_load_115 | 122 | 0.0015951 | 0.00039976 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2407-8_0_4_load_117 | 123 | 0.0015514 | 0.00038882 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2407-8_0_4_load_128 | 124 | 0.0015724 | 0.00039408 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2407-8_0_4_load_119 | 125 | 0.0019515 | 0.00048909 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2407-8_0_4_load_123 | 127 | 0.0015562 | 0.00039003 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2407-8_0_4_load_124 | 128 | 0.0023614 | 0.00059182 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2407-8_0_4_load_127 | 129 | 0.0014685 | 0.00036805 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 61 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2407-8_0_4_line_0 |  | 0 | 1 | 0.0027028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2407-8_0_4_line_1 |  | 0 | 2 | 0.022416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2407-8_0_4_line_2 |  | 1 | 3 | 0.017677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2407-8_0_4_line_3 |  | 2 | 4 | 0.014054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2407-8_0_4_line_4 |  | 3 | 5 | 0.014112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2407-8_0_4_line_5 |  | 4 | 6 | 0.02155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2407-8_0_4_line_6 |  | 5 | 7 | 0.0021265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2407-8_0_4_line_7 |  | 6 | 8 | 0.010341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2407-8_0_4_line_8 |  | 6 | 9 | 0.01707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2407-8_0_4_line_9 |  | 7 | 71 | 0.007326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2407-8_0_4_line_10 |  | 8 | 45 | 0.014595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2407-8_0_4_line_11 |  | 9 | 46 | 0.02635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2407-8_0_4_line_12 |  | 9 | 47 | 0.046781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2407-8_0_4_line_13 |  | 10 | 11 | 0.0078665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2407-8_0_4_line_14 |  | 10 | 12 | 0.019061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2407-8_0_4_line_15 |  | 12 | 13 | 0.0026317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2407-8_0_4_line_16 |  | 13 | 16 | 0.014855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2407-8_0_4_line_17 |  | 14 | 15 | 0.019576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2407-8_0_4_line_18 |  | 15 | 17 | 0.0047932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2407-8_0_4_line_19 |  | 16 | 18 | 0.01459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2407-8_0_4_line_20 |  | 17 | 103 | 0.02121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2407-8_0_4_line_21 |  | 17 | 100 | 0.034999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2407-8_0_4_line_22 |  | 18 | 85 | 0.0081659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2407-8_0_4_line_23 |  | 19 | 20 | 0.01108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2407-8_0_4_line_24 |  | 19 | 21 | 0.02131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2407-8_0_4_line_25 |  | 20 | 22 | 0.017734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2407-8_0_4_line_26 |  | 21 | 23 | 0.0088942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2407-8_0_4_line_27 |  | 21 | 24 | 0.0094075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2407-8_0_4_line_28 |  | 22 | 25 | 0.0097948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2407-8_0_4_line_29 |  | 23 | 26 | 0.027847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2407-8_0_4_line_30 |  | 24 | 27 | 0.041823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2407-8_0_4_line_31 |  | 25 | 28 | 0.0015921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2407-8_0_4_line_32 |  | 26 | 29 | 0.0050623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2407-8_0_4_line_33 |  | 27 | 30 | 0.028271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2407-8_0_4_line_34 |  | 27 | 31 | 0.01283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2407-8_0_4_line_35 |  | 28 | 67 | 0.044708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2407-8_0_4_line_36 |  | 29 | 52 | 0.015952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2407-8_0_4_line_37 |  | 30 | 34 | 0.0019554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2407-8_0_4_line_38 |  | 31 | 109 | 0.010901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2407-8_0_4_line_39 |  | 32 | 33 | 0.054241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2407-8_0_4_line_40 |  | 32 | 34 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2407-8_0_4_line_41 |  | 33 | 35 | 0.019412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2407-8_0_4_line_42 |  | 35 | 36 | 0.03008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2407-8_0_4_line_43 |  | 36 | 37 | 0.031316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2407-8_0_4_line_44 |  | 37 | 42 | 0.017469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2407-8_0_4_line_45 |  | 38 | 39 | 0.0029618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2407-8_0_4_line_46 |  | 38 | 40 | 0.029059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2407-8_0_4_line_47 |  | 39 | 41 | 0.019307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2407-8_0_4_line_48 |  | 40 | 42 | 0.013943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2407-8_0_4_line_49 |  | 41 | 43 | 0.011054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2407-8_0_4_line_50 |  | 43 | 44 | 0.0021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_2407-8_0_4_line_51 |  | 44 | 88 | 0.0017011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2407-8_0_4_line_52 |  | 45 | 48 | 0.029505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2407-8_0_4_line_53 |  | 46 | 49 | 0.025666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2407-8_0_4_line_54 |  | 46 | 50 | 0.024642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2407-8_0_4_line_55 |  | 47 | 51 | 0.026942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2407-8_0_4_line_56 |  | 48 | 56 | 0.019897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2407-8_0_4_line_57 |  | 48 | 57 | 0.029794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2407-8_0_4_line_58 |  | 48 | 58 | 0.018986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2407-8_0_4_line_59 |  | 49 | 112 | 0.01944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2407-8_0_4_line_60 |  | 50 | 111 | 0.025887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2407-8_0_4_line_61 |  | 51 | 91 | 0.0069784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2407-8_0_4_line_62 |  | 52 | 53 | 0.0078717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2407-8_0_4_line_63 |  | 53 | 54 | 0.017865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2407-8_0_4_line_64 |  | 54 | 55 | 0.012714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2407-8_0_4_line_65 |  | 56 | 59 | 0.028521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2407-8_0_4_line_66 |  | 57 | 60 | 0.00807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2407-8_0_4_line_67 |  | 58 | 61 | 0.0019827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2407-8_0_4_line_68 |  | 59 | 62 | 0.033409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2407-8_0_4_line_69 |  | 60 | 63 | 0.019932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2407-8_0_4_line_70 |  | 61 | 64 | 0.019984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2407-8_0_4_line_71 |  | 62 | 74 | 0.0054044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2407-8_0_4_line_72 |  | 63 | 95 | 0.0083249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2407-8_0_4_line_73 |  | 63 | 92 | 0.0081097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2407-8_0_4_line_74 |  | 64 | 87 | 0.022567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2407-8_0_4_line_75 |  | 65 | 66 | 0.034799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2407-8_0_4_line_76 |  | 65 | 67 | 0.008809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2407-8_0_4_line_77 |  | 66 | 68 | 0.0093048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2407-8_0_4_line_78 |  | 68 | 69 | 0.0072118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2407-8_0_4_line_79 |  | 69 | 70 | 0.039309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2407-8_0_4_line_80 |  | 70 | 116 | 0.015816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2407-8_0_4_line_81 |  | 71 | 72 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2407-8_0_4_line_82 |  | 72 | 73 | 0.0024767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2407-8_0_4_line_83 |  | 73 | 103 | 0.0065391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2407-8_0_4_line_84 |  | 74 | 75 | 0.026562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2407-8_0_4_line_85 |  | 75 | 76 | 0.0060399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2407-8_0_4_line_86 |  | 76 | 77 | 0.015532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2407-8_0_4_line_87 |  | 77 | 78 | 0.005759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2407-8_0_4_line_88 |  | 78 | 79 | 0.008064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2407-8_0_4_line_89 |  | 78 | 80 | 0.023822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2407-8_0_4_line_90 |  | 80 | 84 | 0.015513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2407-8_0_4_line_91 |  | 81 | 82 | 0.036115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2407-8_0_4_line_92 |  | 81 | 83 | 0.035238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2407-8_0_4_line_93 |  | 83 | 91 | 0.052433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2407-8_0_4_line_94 |  | 84 | 108 | 0.0098598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2407-8_0_4_line_95 |  | 85 | 86 | 0.01762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2407-8_0_4_line_96 |  | 86 | 87 | 0.00044358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2407-8_0_4_line_97 |  | 88 | 89 | 0.013417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2407-8_0_4_line_98 |  | 89 | 90 | 0.0037488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_2407-8_0_4_line_99 |  | 90 | 94 | 0.031495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_2407-8_0_4_line_100 |  | 92 | 93 | 0.03431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_2407-8_0_4_line_101 |  | 93 | 94 | 0.044913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_2407-8_0_4_line_102 |  | 94 | 96 | 0.017849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2407-8_0_4_line_103 |  | 95 | 97 | 0.019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2407-8_0_4_line_104 |  | 96 | 98 | 0.015844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2407-8_0_4_line_105 |  | 97 | 99 | 0.039557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2407-8_0_4_line_106 |  | 98 | 113 | 0.010349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2407-8_0_4_line_107 |  | 99 | 114 | 0.0053837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2407-8_0_4_line_108 |  | 100 | 101 | 0.020544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2407-8_0_4_line_109 |  | 101 | 102 | 0.023534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2407-8_0_4_line_110 |  | 102 | 104 | 0.005964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2407-8_0_4_line_111 |  | 104 | 105 | 0.012111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2407-8_0_4_line_112 |  | 105 | 120 | 0.021476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2407-8_0_4_line_113 |  | 106 | 107 | 0.030487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2407-8_0_4_line_114 |  | 107 | 112 | 0.036098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2407-8_0_4_line_115 |  | 109 | 110 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2407-8_0_4_line_116 |  | 114 | 115 | 0.010794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2407-8_0_4_line_117 |  | 116 | 117 | 0.038695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2407-8_0_4_line_118 |  | 117 | 118 | 0.031877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2407-8_0_4_line_119 |  | 117 | 119 | 0.0079464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2407-8_0_4_line_120 |  | 118 | 124 | 0.013695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2407-8_0_4_line_121 |  | 119 | 122 | 0.012468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2407-8_0_4_line_122 |  | 120 | 121 | 0.02624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2407-8_0_4_line_123 |  | 122 | 123 | 0.024452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2407-8_0_4_line_124 |  | 124 | 129 | 0.024251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2407-8_0_4_line_125 |  | 125 | 126 | 0.020573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2407-8_0_4_line_126 |  | 126 | 127 | 0.016428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2407-8_0_4_line_127 |  | 126 | 128 | 0.054291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2407-8_0_4_line_128 |  | 127 | 129 | 0.017533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2407-8_0_4_trafo_99 | 0.63 MVA 20/0.4 kV | 130 | 61 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2621949.1911 | 1237988.1767 | 2621946.554 | 1237987.5841
1 | 2621949.1911 | 1237988.1767 | 2621971.0613 | 1237993.0909
2 | 2621946.554 | 1237987.5841 | 2621929.3073 | 1237983.7088
3 | 2621984.7733 | 1237996.172 | 2621971.0613 | 1237993.0909
4 | 2621915.5386 | 1237980.615 | 2621929.3073 | 1237983.7088
5 | 2622005.7989 | 1238000.8964 | 2621984.7733 | 1237996.172
6 | 2621915.5386 | 1237980.615 | 2621913.4638 | 1237980.1488
7 | 2622005.7989 | 1238000.8964 | 2622003.4413 | 1238010.9653
8 | 2622008.093 | 1237983.9833 | 2622005.7989 | 1238000.8964
9 | 2621906.3161 | 1237978.5427 | 2621913.4638 | 1237980.1488
10 | 2622003.4413 | 1238010.9653 | 2622002.571 | 1238014.6819 | 2621998.7997 | 1238024.7782
11 | 2622008.093 | 1237983.9833 | 2622011.843 | 1237957.9032
12 | 2622008.093 | 1237983.9833 | 2622036.9422 | 1238002.5793 | 2622048.1613 | 1238007.9943
13 | 2621851.2862 | 1238027.3894 | 2621843.6419 | 1238025.5325
14 | 2621851.2862 | 1238027.3894 | 2621869.8081 | 1238031.8885
15 | 2621872.3654 | 1238032.5097 | 2621869.8081 | 1238031.8885
16 | 2621886.887 | 1238035.5934 | 2621881.024 | 1238034.613 | 2621872.3654 | 1238032.5097
17 | 2621859.0617 | 1237970.6107 | 2621846.6629 | 1237985.7593
18 | 2621862.0976 | 1237966.9015 | 2621859.0617 | 1237970.6107
19 | 2621886.887 | 1238035.5934 | 2621901.2775 | 1238037.9999
20 | 2621862.0976 | 1237966.9015 | 2621868.9691 | 1237970.1509 | 2621882.2465 | 1237973.1343
21 | 2621862.0976 | 1237966.9015 | 2621873.3856 | 1237956.0251 | 2621878.1705 | 1237948.6936 | 2621880.9585 | 1237941.3326 | 2621881.7084 | 1237938.7413
22 | 2621909.3316 | 1238039.3468 | 2621901.2775 | 1238037.9999
23 | 2621834.3955 | 1238136.5062 | 2621845.4438 | 1238137.3477
24 | 2621813.5085 | 1238132.9708 | 2621822.4697 | 1238135.6497 | 2621830.546 | 1238136.213 | 2621834.3955 | 1238136.5062
25 | 2621845.4438 | 1238137.3477 | 2621859.531 | 1238138.4207 | 2621863.0792 | 1238139.0625
26 | 2621813.5085 | 1238132.9708 | 2621806.0976 | 1238136.6014 | 2621805.4846 | 1238136.7911
27 | 2621813.5085 | 1238132.9708 | 2621807.3172 | 1238127.856 | 2621806.5041 | 1238126.7451
28 | 2621863.0792 | 1238139.0625 | 2621869.5694 | 1238140.2365 | 2621872.5358 | 1238141.4348
29 | 2621778.1607 | 1238137.6234 | 2621784.9026 | 1238138.803 | 2621796.8665 | 1238139.4583 | 2621805.4846 | 1238136.7911
30 | 2621781.8026 | 1238092.9965 | 2621806.5041 | 1238126.7451
31 | 2621874.012 | 1238142.0311 | 2621872.5358 | 1238141.4348
32 | 2621773.1742 | 1238136.7509 | 2621778.1607 | 1238137.6234
33 | 2621781.8026 | 1238092.9965 | 2621787.4587 | 1238091.4385 | 2621809.473 | 1238095.6024
34 | 2621781.8026 | 1238092.9965 | 2621771.4551 | 1238085.4104
35 | 2621874.012 | 1238142.0311 | 2621882.2355 | 1238145.3529 | 2621890.526 | 1238153.4884 | 2621901.3949 | 1238175.1368
36 | 2621757.4606 | 1238134.0016 | 2621773.1742 | 1238136.7509
37 | 2621811.3944 | 1238095.9658 | 2621809.473 | 1238095.6024
38 | 2621762.6636 | 1238078.965 | 2621771.4551 | 1238085.4104
39 | 2621821.774 | 1238097.9291 | 2621865.5039 | 1238106.2004 | 2621875.1631 | 1238104.9795
40 | 2621811.3944 | 1238095.9658 | 2621821.774 | 1238097.9291
41 | 2621894.3707 | 1238104.9939 | 2621886.103 | 1238103.5967 | 2621875.1631 | 1238104.9795
42 | 2621894.3707 | 1238104.9939 | 2621912.198 | 1238108.0066 | 2621923.8048 | 1238111.052
43 | 2621949.7291 | 1238127.316 | 2621933.9011 | 1238113.7011 | 2621923.8048 | 1238111.052
44 | 2621949.7291 | 1238127.316 | 2621952.5027 | 1238129.7018 | 2621959.8274 | 1238133.0643 | 2621965.575 | 1238133.2675
45 | 2622007.047 | 1238143.3381 | 2622009.8439 | 1238144.3125
46 | 2622007.047 | 1238143.3381 | 2621987.0685 | 1238136.378 | 2621979.49 | 1238134.1375
47 | 2622009.8439 | 1238144.3125 | 2622020.7759 | 1238148.121 | 2622027.9915 | 1238150.8943
48 | 2621965.575 | 1238133.2675 | 2621966.4981 | 1238133.3001 | 2621972.6008 | 1238133.7007 | 2621979.49 | 1238134.1375 | 2621979.49 | 1238134.1375
49 | 2622038.3098 | 1238154.8601 | 2622027.9915 | 1238150.8943
50 | 2622040.3349 | 1238155.6385 | 2622038.3098 | 1238154.8601
51 | 2622040.3349 | 1238155.6385 | 2622041.9227 | 1238156.2488
52 | 2621989.7979 | 1238052.8028 | 2621991.7301 | 1238043.7043 | 2621998.7997 | 1238024.7782
53 | 2622015.4997 | 1237932.5009 | 2622011.843 | 1237957.9032
54 | 2622011.843 | 1237957.9032 | 2622016.1767 | 1237962.144 | 2622027.8904 | 1237973.2832 | 2622029.7915 | 1237974.7705
55 | 2622048.1613 | 1238007.9943 | 2622055.6982 | 1238011.6321 | 2622073.2206 | 1238017.7906
56 | 2621989.7979 | 1238052.8028 | 2622009.448 | 1238055.9245
57 | 2621989.7979 | 1238052.8028 | 2621991.2022 | 1238061.7024 | 2621998.3488 | 1238072.3465 | 2622003.5886 | 1238078.344
58 | 2621989.7979 | 1238052.8028 | 2621971.0717 | 1238049.6713
59 | 2622015.4997 | 1237932.5009 | 2621998.9035 | 1237922.2999
60 | 2622052.6287 | 1237986.7164 | 2622040.4416 | 1237980.901 | 2622034.0299 | 1237978.0866 | 2622029.7915 | 1237974.7705
61 | 2622079.8042 | 1238020.1045 | 2622073.2206 | 1238017.7906
62 | 2621757.4606 | 1238134.0016 | 2621749.7067 | 1238132.645
63 | 2621732.1088 | 1238129.566 | 2621749.7067 | 1238132.645
64 | 2621732.1088 | 1238129.566 | 2621719.5853 | 1238127.3748
65 | 2622037.6154 | 1238060.3993 | 2622009.448 | 1238055.9245
66 | 2622003.5886 | 1238078.344 | 2622008.8982 | 1238084.4213
67 | 2621969.1162 | 1238049.3443 | 2621971.0717 | 1238049.6713
68 | 2622037.6154 | 1238060.3993 | 2622057.7975 | 1238063.6055 | 2622070.6846 | 1238062.1095
69 | 2622023.5031 | 1238097.9443 | 2622011.485 | 1238087.3822 | 2622008.8982 | 1238084.4213
70 | 2621949.406 | 1238046.0483 | 2621969.1162 | 1238049.3443
71 | 2622076.053 | 1238061.4863 | 2622070.6846 | 1238062.1095
72 | 2622023.5031 | 1238097.9443 | 2622031.567 | 1238095.876
73 | 2622023.5031 | 1238097.9443 | 2622029.9317 | 1238102.8881
74 | 2621949.406 | 1238046.0483 | 2621927.148 | 1238042.3261
75 | 2621905.6387 | 1238182.8333 | 2621913.4933 | 1238193.7868 | 2621922.4994 | 1238202.7033 | 2621929.3795 | 1238207.9403
76 | 2621901.3949 | 1238175.1368 | 2621904.3725 | 1238181.0676 | 2621905.6387 | 1238182.8333
77 | 2621937.2934 | 1238212.7507 | 2621932.8028 | 1238210.5461 | 2621929.3795 | 1238207.9403
78 | 2621943.7671 | 1238215.9289 | 2621937.2934 | 1238212.7507
79 | 2621943.7671 | 1238215.9289 | 2621959.6366 | 1238223.7199 | 2621979.3782 | 1238232.5605
80 | 2621993.4516 | 1238239.7633 | 2621982.9177 | 1238234.1456 | 2621979.3782 | 1238232.5605
81 | 2621906.3161 | 1237978.5427 | 2621891.043 | 1237975.1109
82 | 2621891.043 | 1237975.1109 | 2621888.6265 | 1237974.5679
83 | 2621888.6265 | 1237974.5679 | 2621882.2465 | 1237973.1343
84 | 2622102.5098 | 1238059.4499 | 2622091.2076 | 1238059.727 | 2622076.053 | 1238061.4863
85 | 2622108.2725 | 1238060.8511 | 2622104.5974 | 1238059.3987 | 2622102.5098 | 1238059.4499
86 | 2622122.7172 | 1238066.5593 | 2622108.2725 | 1238060.8511
87 | 2622122.7172 | 1238066.5593 | 2622127.973 | 1238068.947
88 | 2622124.5948 | 1238076.2723 | 2622127.973 | 1238068.947
89 | 2622127.973 | 1238068.947 | 2622149.4374 | 1238079.279
90 | 2622149.4374 | 1238079.279 | 2622163.4156 | 1238086.0074
91 | 2622149.8457 | 1237999.9119 | 2622182.2762 | 1238015.8049
92 | 2622118.2042 | 1237984.4027 | 2622132.0745 | 1237991.2029 | 2622149.8457 | 1237999.9119
93 | 2622079.8042 | 1238020.1045 | 2622118.2042 | 1237984.4027
94 | 2622172.2998 | 1238090.2838 | 2622163.4156 | 1238086.0074
95 | 2621909.3316 | 1238039.3468 | 2621926.7105 | 1238042.253
96 | 2621927.148 | 1238042.3261 | 2621926.7105 | 1238042.253
97 | 2622054.9057 | 1238159.6288 | 2622042.0686 | 1238156.3048 | 2622041.9227 | 1238156.2488
98 | 2622058.5348 | 1238160.5685 | 2622054.9057 | 1238159.6288
99 | 2622058.5348 | 1238160.5685 | 2622088.3979 | 1238150.3061
100 | 2622029.9317 | 1238102.8881 | 2622044.9015 | 1238114.4004 | 2622058.6363 | 1238121.4227
101 | 2622088.3979 | 1238150.3061 | 2622083.7601 | 1238134.2679 | 2622058.6363 | 1238121.4227
102 | 2622088.3979 | 1238150.3061 | 2622103.1884 | 1238147.526 | 2622105.949 | 1238147.9895
103 | 2622050.8672 | 1238095.2154 | 2622048.8012 | 1238094.9027 | 2622034.0575 | 1238095.2373 | 2622031.567 | 1238095.876
104 | 2622120.22 | 1238154.0813 | 2622112.5997 | 1238149.1064 | 2622105.949 | 1238147.9895
105 | 2622050.8672 | 1238095.2154 | 2622064.7676 | 1238097.3189 | 2622089.6257 | 1238102.9958
106 | 2622120.22 | 1238154.0813 | 2622128.886 | 1238159.7391
107 | 2622089.6257 | 1238102.9958 | 2622094.8743 | 1238104.1944
108 | 2621886.0161 | 1237918.7155 | 2621884.8277 | 1237927.9608 | 2621881.7084 | 1237938.7413
109 | 2621885.9996 | 1237895.2003 | 2621886.2761 | 1237916.6925 | 2621886.0161 | 1237918.7155
110 | 2621880.1031 | 1237894.2003 | 2621885.9996 | 1237895.2003
111 | 2621880.1031 | 1237894.2003 | 2621867.9965 | 1237893.8767
112 | 2621846.5283 | 1237893.303 | 2621867.9965 | 1237893.8767
113 | 2621935.0894 | 1237904.6616 | 2621965.0259 | 1237910.4314
114 | 2621998.9035 | 1237922.2999 | 2621989.0126 | 1237917.3269 | 2621975.0974 | 1237912.3725 | 2621965.0259 | 1237910.4314
115 | 2621762.6636 | 1238078.965 | 2621753.3018 | 1238072.1016
116 | 2622105.3978 | 1238106.5977 | 2622094.8743 | 1238104.1944
117 | 2622028.678 | 1238254.9832 | 2622017.7036 | 1238252.6968 | 2621993.4516 | 1238239.7633
118 | 2622028.678 | 1238254.9832 | 2622038.5071 | 1238235.6298 | 2622042.0822 | 1238232.2521 | 2622047.274 | 1238231.4597 | 2622047.274 | 1238231.4597
119 | 2622028.678 | 1238254.9832 | 2622036.134 | 1238257.7318
120 | 2622060.8292 | 1238233.4141 | 2622047.274 | 1238231.4597
121 | 2622047.8322 | 1238262.0441 | 2622036.134 | 1238257.7318
122 | 2621846.5283 | 1237893.303 | 2621820.2975 | 1237892.602
123 | 2622047.8322 | 1238262.0441 | 2622056.9813 | 1238265.4167 | 2622070.715 | 1238270.6623
124 | 2622084.8832 | 1238236.3025 | 2622079.4867 | 1238236.1042 | 2622060.8292 | 1238233.4141
125 | 2622118.7118 | 1238236.5167 | 2622120.3747 | 1238238.8465 | 2622121.7826 | 1238242.643 | 2622121.8767 | 1238245.8343 | 2622120.238 | 1238249.1636 | 2622117.7364 | 1238252.7009 | 2622117.4698 | 1238255.1113
126 | 2622118.7118 | 1238236.5167 | 2622115.1685 | 1238237.4152 | 2622102.4044 | 1238236.9462
127 | 2622114.1604 | 1238193.2173 | 2622108.7079 | 1238199.0118 | 2622106.4089 | 1238202.9501 | 2622107.1659 | 1238204.8208 | 2622109.0327 | 1238207.2626 | 2622114.4416 | 1238211.174 | 2622118.7402 | 1238214.6254 | 2622122.9371 | 1238218.9882 | 2622123.082 | 1238220.712 | 2622121.2495 | 1238223.2846 | 2622119.8694 | 1238226.2591 | 2622119.4447 | 1238230.6046 | 2622118.7118 | 1238236.5167
128 | 2622084.8832 | 1238236.3025 | 2622102.4044 | 1238236.9462

## bus_geodata
| x | y | coords
0 | 2621949.1911 | 1237988.1767
1 | 2621946.554 | 1237987.5841
2 | 2621971.0613 | 1237993.0909
3 | 2621929.3073 | 1237983.7088
4 | 2621984.7733 | 1237996.1719
5 | 2621915.5386 | 1237980.615
6 | 2622005.7989 | 1238000.8964
7 | 2621913.4638 | 1237980.1488
8 | 2622003.4413 | 1238010.9653
9 | 2622008.093 | 1237983.9833
10 | 2621851.2862 | 1238027.3894
11 | 2621843.6419 | 1238025.5325
12 | 2621869.8081 | 1238031.8885
13 | 2621872.3654 | 1238032.5097
14 | 2621846.6629 | 1237985.7593
15 | 2621859.0617 | 1237970.6107
16 | 2621886.887 | 1238035.5934
17 | 2621862.0976 | 1237966.9015
18 | 2621901.2775 | 1238037.9999
19 | 2621834.3955 | 1238136.5062
20 | 2621845.4438 | 1238137.3477
21 | 2621813.5085 | 1238132.9708
22 | 2621863.0792 | 1238139.0625
23 | 2621805.4846 | 1238136.7911
24 | 2621806.5041 | 1238126.7451
25 | 2621872.5358 | 1238141.4348
26 | 2621778.1607 | 1238137.6234
27 | 2621781.8026 | 1238092.9965
28 | 2621874.012 | 1238142.0311
29 | 2621773.1742 | 1238136.7509
30 | 2621809.473 | 1238095.6024
31 | 2621771.4551 | 1238085.4104
32 | 2621821.774 | 1238097.9291
33 | 2621875.1631 | 1238104.9795
34 | 2621811.3944 | 1238095.9658
35 | 2621894.3707 | 1238104.9939
36 | 2621923.8048 | 1238111.052
37 | 2621949.7291 | 1238127.316
38 | 2622007.047 | 1238143.3381
39 | 2622009.8439 | 1238144.3125
40 | 2621979.49 | 1238134.1375
41 | 2622027.9915 | 1238150.8943
42 | 2621965.575 | 1238133.2675
43 | 2622038.3098 | 1238154.8601
44 | 2622040.3349 | 1238155.6385
45 | 2621998.7997 | 1238024.7782
46 | 2622011.843 | 1237957.9032
47 | 2622048.1613 | 1238007.9943
48 | 2621989.7979 | 1238052.8028
49 | 2622015.4997 | 1237932.5009
50 | 2622029.7915 | 1237974.7705
51 | 2622073.2206 | 1238017.7906
52 | 2621757.4606 | 1238134.0016
53 | 2621749.7067 | 1238132.645
54 | 2621732.1088 | 1238129.566
55 | 2621719.5853 | 1238127.3748
56 | 2622009.448 | 1238055.9245
57 | 2622003.5886 | 1238078.344
58 | 2621971.0717 | 1238049.6713
59 | 2622037.6154 | 1238060.3993
60 | 2622008.8982 | 1238084.4213
61 | 2621969.1162 | 1238049.3443
62 | 2622070.6846 | 1238062.1095
63 | 2622023.5031 | 1238097.9443
64 | 2621949.406 | 1238046.0483
65 | 2621905.6387 | 1238182.8333
66 | 2621929.3795 | 1238207.9403
67 | 2621901.3949 | 1238175.1368
68 | 2621937.2934 | 1238212.7507
69 | 2621943.7671 | 1238215.9289
70 | 2621979.3782 | 1238232.5605
71 | 2621906.3161 | 1237978.5427
72 | 2621891.043 | 1237975.1109
73 | 2621888.6265 | 1237974.5679
74 | 2622076.053 | 1238061.4863
75 | 2622102.5098 | 1238059.4499
76 | 2622108.2725 | 1238060.8511
77 | 2622122.7172 | 1238066.5593
78 | 2622127.973 | 1238068.947
79 | 2622124.5948 | 1238076.2724
80 | 2622149.4374 | 1238079.279
81 | 2622149.8457 | 1237999.9119
82 | 2622182.2762 | 1238015.8049
83 | 2622118.2042 | 1237984.4027
84 | 2622163.4156 | 1238086.0074
85 | 2621909.3316 | 1238039.3468
86 | 2621926.7105 | 1238042.253
87 | 2621927.148 | 1238042.3261
88 | 2622041.9227 | 1238156.2488
89 | 2622054.9057 | 1238159.6288
90 | 2622058.5348 | 1238160.5685
91 | 2622079.8042 | 1238020.1045
92 | 2622029.9317 | 1238102.8881
93 | 2622058.6363 | 1238121.4227
94 | 2622088.3979 | 1238150.3061
95 | 2622031.567 | 1238095.876
96 | 2622105.949 | 1238147.9895
97 | 2622050.8672 | 1238095.2154
98 | 2622120.22 | 1238154.0813
99 | 2622089.6257 | 1238102.9958
100 | 2621881.7084 | 1237938.7413
101 | 2621886.0161 | 1237918.7155
102 | 2621885.9996 | 1237895.2003
103 | 2621882.2465 | 1237973.1343
104 | 2621880.1031 | 1237894.2003
105 | 2621867.9965 | 1237893.8767
106 | 2621935.0894 | 1237904.6616
107 | 2621965.0259 | 1237910.4314
108 | 2622172.2998 | 1238090.2838
109 | 2621762.6636 | 1238078.965
110 | 2621753.3018 | 1238072.1016
111 | 2622052.6287 | 1237986.7164
112 | 2621998.9035 | 1237922.2999
113 | 2622128.886 | 1238159.7391
114 | 2622094.8743 | 1238104.1944
115 | 2622105.3978 | 1238106.5977
116 | 2621993.4516 | 1238239.7633
117 | 2622028.678 | 1238254.9832
118 | 2622047.274 | 1238231.4597
119 | 2622036.134 | 1238257.7318
120 | 2621846.5283 | 1237893.303
121 | 2621820.2975 | 1237892.602
122 | 2622047.8322 | 1238262.0441
123 | 2622070.715 | 1238270.6623
124 | 2622060.8292 | 1238233.4141
125 | 2622117.4698 | 1238255.1113
126 | 2622118.7118 | 1238236.5167
127 | 2622102.4044 | 1238236.9462
128 | 2622114.1604 | 1238193.2173
129 | 2622084.8832 | 1238236.3025
130 | 2621989.7979 | 1238052.8028

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98984 | -0.19488 | 0.0038077 | 0.00095431
1 | 0.98974 | -0.19683 | 0.0033611 | 0.00084237
2 | 0.99075 | -0.17721 | 0.0034767 | 0.00087134
3 | 0.98914 | -0.20854 | 0.0027882 | 0.0006988
4 | 0.99137 | -0.16527 | 0.0029841 | 0.00074787
5 | 0.98869 | -0.2172 | 0.0041442 | 0.0010386
6 | 0.99238 | -0.14586 | 0 | 0
7 | 0.98863 | -0.21835 | 0.0024961 | 0.00062558
8 | 0.99342 | -0.1257 | 0.0025784 | 0.00064621
9 | 0.99145 | -0.16383 | 0 | 0
10 | 0.99841 | -0.03056 | 0.0017255 | 0.00043246
11 | 0.9984 | -0.030852 | 0.00212 | 0.00053132
12 | 0.99848 | -0.029278 | 0.0030212 | 0.00075719
13 | 0.99849 | -0.028962 | 0.0033555 | 0.00084097
14 | 0.98747 | -0.24096 | 0.001844 | 0.00046214
15 | 0.9875 | -0.24031 | 0.0010527 | 0.00026384
16 | 0.99863 | -0.026308 | 0.0020667 | 0.00051797
17 | 0.98751 | -0.24006 | 0 | 0
18 | 0.99879 | -0.023174 | 0.0019881 | 0.00049826
19 | 0.97796 | -0.42392 | 0.0024494 | 0.00061387
20 | 0.97747 | -0.43365 | 0.0024378 | 0.00061096
21 | 0.97897 | -0.40429 | 0 | 0
22 | 0.97671 | -0.44845 | 0.0033463 | 0.00083866
23 | 0.9788 | -0.40749 | 0.0061392 | 0.0015386
24 | 0.97958 | -0.39226 | 0.0017809 | 0.00044634
25 | 0.97632 | -0.45604 | 0.003444 | 0.00086315
26 | 0.97845 | -0.41441 | 0.0028112 | 0.00070454
27 | 0.98098 | -0.36488 | 0 | 0
28 | 0.97627 | -0.45717 | 0.003025 | 0.00075815
29 | 0.9784 | -0.41541 | 0.0024578 | 0.00061597
30 | 0.98201 | -0.34493 | 0.0047992 | 0.0012028
31 | 0.98092 | -0.36624 | 0.0015927 | 0.00039917
32 | 0.98234 | -0.33859 | 0.0026088 | 0.00065383
33 | 0.9838 | -0.31023 | 0.0028113 | 0.00070457
34 | 0.98206 | -0.34396 | 0.0015641 | 0.00039199
35 | 0.98434 | -0.29977 | 0.0044229 | 0.0011085
36 | 0.98521 | -0.28279 | 0.006219 | 0.0015586
37 | 0.98619 | -0.26398 | 0.0046662 | 0.0011695
38 | 0.98825 | -0.22421 | 0.0031699 | 0.00079445
39 | 0.98835 | -0.22215 | 0.001103 | 0.00027644
40 | 0.98723 | -0.24387 | 0.0035566 | 0.00089137
41 | 0.98906 | -0.20863 | 0.0022453 | 0.00056273
42 | 0.98675 | -0.25301 | 0.0049085 | 0.0012302
43 | 0.98947 | -0.20075 | 0.0024911 | 0.00062432
44 | 0.98955 | -0.19917 | 0.0024898 | 0.000624
45 | 0.99493 | -0.096664 | 0.0032815 | 0.00082241
46 | 0.99066 | -0.17904 | 0.010896 | 0.0027308
47 | 0.99029 | -0.18617 | 0.0014618 | 0.00036636
48 | 0.99807 | -0.03653 | 0 | 0
49 | 0.99025 | -0.18695 | 0 | 0
50 | 0.99057 | -0.18091 | 0.0015051 | 0.00037722
51 | 0.98966 | -0.19836 | 0.0018732 | 0.00046948
52 | 0.97828 | -0.41784 | 0.0023225 | 0.00058206
53 | 0.97823 | -0.41871 | 0.0022053 | 0.00055269
54 | 0.97817 | -0.41996 | 0.0024331 | 0.00060979
55 | 0.97815 | -0.42029 | 0.0014148 | 0.00035457
56 | 0.99764 | -0.044811 | 0.0022029 | 0.0005521
57 | 0.99661 | -0.064224 | 0.001692 | 0.00042407
58 | 0.99982 | -0.0034751 | 0.002582 | 0.00064712
59 | 0.99708 | -0.055591 | 0.0020339 | 0.00050974
60 | 0.99622 | -0.071659 | 0.0027827 | 0.00069741
61 | 1 | 0 | -0.33035 | -0.083849
62 | 0.99649 | -0.067041 | 0.0020298 | 0.00050872
63 | 0.99527 | -0.089722 | 0 | 0
64 | 0.99958 | -0.0081191 | 0.0030359 | 0.00076086
65 | 0.97451 | -0.49168 | 0.0057989 | 0.0014533
66 | 0.97367 | -0.5082 | 0.0017329 | 0.00043432
67 | 0.97477 | -0.48656 | 0.0042569 | 0.0010669
68 | 0.97346 | -0.51232 | 0.0022346 | 0.00056005
69 | 0.97332 | -0.51522 | 0.002346 | 0.00058797
70 | 0.9726 | -0.52935 | 0.0023589 | 0.00059119
71 | 0.98844 | -0.22198 | 0.002601 | 0.00065187
72 | 0.98808 | -0.22901 | 0.0027396 | 0.0006866
73 | 0.98803 | -0.23 | 0.0015288 | 0.00038314
74 | 0.9964 | -0.068702 | 0.0022087 | 0.00055356
75 | 0.99603 | -0.075837 | 0.0017729 | 0.00044432
76 | 0.99596 | -0.077273 | 0.0017619 | 0.00044156
77 | 0.99579 | -0.080483 | 0.0035312 | 0.000885
78 | 0.99575 | -0.081316 | 0 | 0
79 | 0.99573 | -0.081625 | 0.0021794 | 0.00054621
80 | 0.99562 | -0.08385 | 0.0023186 | 0.0005811
81 | 0.98805 | -0.22976 | 0.0065836 | 0.00165
82 | 0.98766 | -0.23726 | 0.01163 | 0.0029149
83 | 0.98864 | -0.2183 | 0 | 0
84 | 0.99557 | -0.084868 | 0.0014794 | 0.00037076
85 | 0.9989 | -0.021137 | 0.0016375 | 0.00041039
86 | 0.99916 | -0.016239 | 0.0021387 | 0.000536
87 | 0.99916 | -0.0161 | 0.0022073 | 0.00055321
88 | 0.98962 | -0.19791 | 0.002661 | 0.0006669
89 | 0.99014 | -0.18774 | 0.003385 | 0.00084836
90 | 0.9903 | -0.18483 | 0 | 0
91 | 0.98951 | -0.20129 | 0.005346 | 0.0013398
92 | 0.99492 | -0.096418 | 0.002286 | 0.00057293
93 | 0.99346 | -0.12434 | 0.0023093 | 0.00057875
94 | 0.99157 | -0.16039 | 0 | 0
95 | 0.99517 | -0.091763 | 0.0020047 | 0.00050243
96 | 0.99149 | -0.16197 | 0.001273 | 0.00031905
97 | 0.99496 | -0.095838 | 0.0029233 | 0.00073266
98 | 0.99144 | -0.16301 | 0.0016197 | 0.00040593
99 | 0.99463 | -0.10211 | 0.0043399 | 0.0010877
100 | 0.98696 | -0.25084 | 0.0016017 | 0.00040141
101 | 0.98667 | -0.25658 | 0.0022535 | 0.00056478
102 | 0.98638 | -0.26221 | 0 | 0
103 | 0.98791 | -0.23244 | 0.00078906 | 0.00019776
104 | 0.9863 | -0.26364 | 0 | 0
105 | 0.98615 | -0.26654 | 0.0069989 | 0.0017541
106 | 0.9892 | -0.20751 | 0.006315 | 0.0015827
107 | 0.98937 | -0.20408 | 0.011026 | 0.0027633
108 | 0.99555 | -0.085258 | 0.0022508 | 0.00056411
109 | 0.98087 | -0.36708 | 0.0026542 | 0.00066522
110 | 0.98086 | -0.36741 | 0.0015868 | 0.00039769
111 | 0.9905 | -0.18218 | 0.0027704 | 0.00069434
112 | 0.98995 | -0.19294 | 0 | 0
113 | 0.99142 | -0.1634 | 0.0020885 | 0.00052344
114 | 0.99461 | -0.10255 | 0.0025379 | 0.00063605
115 | 0.99459 | -0.10296 | 0.0021244 | 0.00053242
116 | 0.97235 | -0.53436 | 0.0022244 | 0.0005575
117 | 0.97181 | -0.54502 | 0 | 0
118 | 0.97149 | -0.55122 | 0.0016267 | 0.0004077
119 | 0.97178 | -0.54566 | 0.0012486 | 0.00031293
120 | 0.98603 | -0.26899 | 0.00079327 | 0.00019881
121 | 0.98589 | -0.27161 | 0.005566 | 0.001395
122 | 0.97174 | -0.54639 | 0.0015951 | 0.00039976
123 | 0.9717 | -0.54709 | 0.0015514 | 0.00038882
124 | 0.97138 | -0.55348 | 0.0015724 | 0.00039408
125 | 0.97101 | -0.56072 | 0.0019515 | 0.00048909
126 | 0.97105 | -0.55998 | 0 | 0
127 | 0.97112 | -0.55867 | 0.0015562 | 0.00039003
128 | 0.97093 | -0.56235 | 0.0023614 | 0.00059182
129 | 0.97121 | -0.55677 | 0.0014685 | 0.00036805
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.040644 | 0.010216 | -0.04064 | -0.010214 | 3.785e-06 | 2.3877e-06 | 0.06111 | 0.06111 | 0.06111 | 0.98984 | -0.19488 | 0.98974 | -0.19683 | 16.7884
1 | -0.044451 | -0.011171 | 0.044489 | 0.011194 | 3.7547e-05 | 2.3742e-05 | 0.066834 | 0.066834 | 0.066834 | 0.98984 | -0.19488 | 0.99075 | -0.17721 | 18.3609
2 | 0.037279 | 0.0093715 | -0.037258 | -0.0093584 | 2.083e-05 | 1.3104e-05 | 0.056057 | 0.056057 | 0.056057 | 0.98974 | -0.19683 | 0.98914 | -0.20854 | 15.4002
3 | -0.047966 | -0.012066 | 0.047993 | 0.012083 | 2.7363e-05 | 1.7331e-05 | 0.072055 | 0.072055 | 0.072055 | 0.99075 | -0.17721 | 0.99137 | -0.16527 | 19.7954
4 | 0.03447 | 0.0086596 | -0.034455 | -0.0086507 | 1.4234e-05 | 8.9286e-06 | 0.051862 | 0.051862 | 0.051862 | 0.98914 | -0.20854 | 0.98869 | -0.2172 | 14.2478
5 | -0.050977 | -0.012831 | 0.051024 | 0.012861 | 4.7336e-05 | 3.0017e-05 | 0.076534 | 0.076534 | 0.076534 | 0.99137 | -0.16527 | 0.99238 | -0.14586 | 21.0259
6 | 0.030311 | 0.007612 | -0.03031 | -0.007611 | 1.66e-06 | 1.0351e-06 | 0.045625 | 0.045625 | 0.045625 | 0.98869 | -0.2172 | 0.98863 | -0.21835 | 12.5343
7 | -0.1106 | -0.027855 | 0.11071 | 0.027923 | 0.00010672 | 6.817e-05 | 0.16589 | 0.16589 | 0.16589 | 0.99238 | -0.14586 | 0.99342 | -0.1257 | 45.5751
8 | 0.05958 | 0.014994 | -0.059529 | -0.014962 | 5.1114e-05 | 3.2493e-05 | 0.089359 | 0.089359 | 0.089359 | 0.99238 | -0.14586 | 0.99145 | -0.16383 | 24.5492
9 | 0.027814 | 0.0069854 | -0.027809 | -0.0069824 | 4.8157e-06 | 2.9882e-06 | 0.041868 | 0.041868 | 0.041868 | 0.98863 | -0.21835 | 0.98844 | -0.22198 | 11.5022
10 | -0.11329 | -0.028569 | 0.11345 | 0.02867 | 0.00015772 | 0.00010075 | 0.16976 | 0.16976 | 0.16976 | 0.99342 | -0.1257 | 0.99493 | -0.096664 | 46.6361
11 | 0.032558 | 0.0081753 | -0.032534 | -0.0081605 | 2.36e-05 | 1.4764e-05 | 0.04887 | 0.04887 | 0.04887 | 0.99145 | -0.16383 | 0.99066 | -0.17904 | 13.4259
12 | 0.026971 | 0.0067864 | -0.026942 | -0.0067686 | 2.8759e-05 | 1.7803e-05 | 0.040489 | 0.040489 | 0.040489 | 0.99145 | -0.16383 | 0.99029 | -0.18617 | 11.1234
13 | 0.00212 | 0.00053123 | -0.00212 | -0.00053132 | 2.945e-08 | -8.4026e-08 | 0.0031596 | 0.0031596 | 0.0031596 | 0.99841 | -0.03056 | 0.9984 | -0.030852 | 0.86803
14 | -0.0038456 | -0.0009637 | 0.0038458 | 0.0009636 | 2.3478e-07 | -9.9021e-08 | 0.0057313 | 0.0057312 | 0.0057313 | 0.99841 | -0.03056 | 0.99848 | -0.029278 | 1.5745
15 | -0.006867 | -0.0017208 | 0.0068671 | 0.0017208 | 1.0336e-07 | 3.1726e-08 | 0.010234 | 0.010234 | 0.010234 | 0.99848 | -0.029278 | 0.99849 | -0.028962 | 2.8115
16 | -0.010223 | -0.0025618 | 0.010224 | 0.0025624 | 1.2928e-06 | 6.3308e-07 | 0.015234 | 0.015234 | 0.015234 | 0.99849 | -0.028962 | 0.99863 | -0.026308 | 4.1852
17 | -0.001844 | -0.00046214 | 0.001844 | 0.00046193 | 5.6677e-08 | -2.1416e-07 | 0.0027787 | 0.0027786 | 0.0027787 | 0.98747 | -0.24096 | 0.9875 | -0.24031 | 0.76337
18 | -0.0028967 | -0.00072576 | 0.0028968 | 0.00072572 | 3.4245e-08 | -3.9405e-08 | 0.0043649 | 0.0043648 | 0.0043649 | 0.9875 | -0.24031 | 0.98751 | -0.24006 | 1.1991
19 | -0.012291 | -0.0030804 | 0.012292 | 0.0030814 | 1.8351e-06 | 9.8352e-07 | 0.018314 | 0.018314 | 0.018314 | 0.99863 | -0.026308 | 0.99879 | -0.023174 | 5.0313
20 | -0.020131 | -0.0050513 | 0.020138 | 0.0050557 | 7.3195e-06 | 4.413e-06 | 0.030336 | 0.030336 | 0.030336 | 0.98751 | -0.24006 | 0.98791 | -0.23244 | 8.3341
21 | 0.017234 | 0.0043256 | -0.017225 | -0.0043204 | 8.8527e-06 | 5.2182e-06 | 0.025971 | 0.025971 | 0.025971 | 0.98751 | -0.24006 | 0.98696 | -0.25084 | 7.135
22 | -0.014281 | -0.0035796 | 0.014282 | 0.0035804 | 1.3861e-06 | 7.8023e-07 | 0.021276 | 0.021276 | 0.021276 | 0.99879 | -0.023174 | 0.9989 | -0.021137 | 5.8449
23 | 0.048328 | 0.012181 | -0.048306 | -0.012166 | 2.2482e-05 | 1.425e-05 | 0.073558 | 0.073558 | 0.073558 | 0.97796 | -0.42392 | 0.97747 | -0.43365 | 20.2083
24 | -0.050777 | -0.012794 | 0.050825 | 0.012825 | 4.773e-05 | 3.028e-05 | 0.077285 | 0.077285 | 0.077285 | 0.97796 | -0.42392 | 0.97897 | -0.40429 | 21.2321
25 | 0.045868 | 0.011555 | -0.045835 | -0.011535 | 3.2444e-05 | 2.0542e-05 | 0.069847 | 0.069847 | 0.069847 | 0.97747 | -0.43365 | 0.97671 | -0.44845 | 19.1888
26 | 0.019793 | 0.0049632 | -0.01979 | -0.0049613 | 3.0191e-06 | 1.8204e-06 | 0.030086 | 0.030086 | 0.030086 | 0.97897 | -0.40429 | 0.9788 | -0.40749 | 8.2655
27 | -0.070618 | -0.017788 | 0.070659 | 0.017814 | 4.0671e-05 | 2.5911e-05 | 0.10737 | 0.10737 | 0.10737 | 0.97897 | -0.40429 | 0.97958 | -0.39226 | 29.4976
28 | 0.042489 | 0.010696 | -0.042474 | -0.010686 | 1.5399e-05 | 9.7328e-06 | 0.064749 | 0.064749 | 0.064749 | 0.97671 | -0.44845 | 0.97632 | -0.45604 | 17.7882
29 | 0.013651 | 0.0034227 | -0.013647 | -0.0034202 | 4.4977e-06 | 2.5287e-06 | 0.020753 | 0.020753 | 0.020753 | 0.9788 | -0.40749 | 0.97845 | -0.41441 | 5.7015
30 | -0.07244 | -0.01826 | 0.072535 | 0.01832 | 9.5017e-05 | 5.9756e-05 | 0.11008 | 0.11008 | 0.11008 | 0.97958 | -0.39226 | 0.98098 | -0.36488 | 15.1204
31 | 0.03903 | 0.0098232 | -0.039028 | -0.0098219 | 2.1136e-06 | 1.3328e-06 | 0.0595 | 0.0595 | 0.0595 | 0.97632 | -0.45604 | 0.97627 | -0.45717 | 16.3462
32 | 0.010835 | 0.0027156 | -0.010835 | -0.0027154 | 5.1547e-07 | 2.6632e-07 | 0.016478 | 0.016478 | 0.016478 | 0.97845 | -0.41441 | 0.9784 | -0.41541 | 4.527
33 | -0.078369 | -0.019782 | 0.078444 | 0.019829 | 7.4972e-05 | 4.7268e-05 | 0.11893 | 0.11893 | 0.11893 | 0.98098 | -0.36488 | 0.98201 | -0.34493 | 16.336
34 | 0.0058343 | 0.001462 | -0.0058339 | -0.0014619 | 3.7682e-07 | 7.9192e-08 | 0.0088497 | 0.0088498 | 0.0088498 | 0.98098 | -0.36488 | 0.98092 | -0.36624 | 2.4313
35 | 0.036003 | 0.0090638 | -0.035952 | -0.009032 | 5.0512e-05 | 3.177e-05 | 0.054889 | 0.05489 | 0.05489 | 0.97627 | -0.45717 | 0.97477 | -0.48656 | 15.0795
36 | 0.0083771 | 0.0020994 | -0.0083761 | -0.002099 | 9.71e-07 | 4.2113e-07 | 0.01274 | 0.01274 | 0.01274 | 0.9784 | -0.41541 | 0.97828 | -0.41784 | 3.5001
37 | -0.083244 | -0.021032 | 0.083247 | 0.021034 | 3.8928e-06 | 2.4171e-06 | 0.1262 | 0.1262 | 0.1262 | 0.98201 | -0.34493 | 0.98206 | -0.34396 | 11.5566
38 | 0.0042412 | 0.0010627 | -0.0042411 | -0.0010628 | 1.6921e-07 | -2.9306e-08 | 0.0064337 | 0.0064338 | 0.0064338 | 0.98092 | -0.36624 | 0.98087 | -0.36708 | 1.7675
39 | -0.087442 | -0.022094 | 0.087561 | 0.022168 | 0.00011907 | 7.414e-05 | 0.13252 | 0.13252 | 0.13252 | 0.98234 | -0.33859 | 0.9838 | -0.31023 | 12.1354
40 | 0.084833 | 0.02144 | -0.084811 | -0.021426 | 2.1827e-05 | 1.3568e-05 | 0.12857 | 0.12857 | 0.12857 | 0.98234 | -0.33859 | 0.98206 | -0.34396 | 11.7736
41 | -0.090372 | -0.022872 | 0.090418 | 0.022901 | 4.539e-05 | 2.831e-05 | 0.13677 | 0.13677 | 0.13677 | 0.9838 | -0.31023 | 0.98434 | -0.29977 | 12.5248
42 | -0.094841 | -0.024009 | 0.094918 | 0.024058 | 7.7379e-05 | 4.8374e-05 | 0.14346 | 0.14346 | 0.14346 | 0.98434 | -0.29977 | 0.98521 | -0.28279 | 13.137
43 | -0.10114 | -0.025616 | 0.10123 | 0.025674 | 9.1453e-05 | 5.7333e-05 | 0.15285 | 0.15285 | 0.15285 | 0.98521 | -0.28279 | 0.98619 | -0.26398 | 13.9971
44 | -0.10589 | -0.026843 | 0.10595 | 0.026878 | 5.5824e-05 | 3.5058e-05 | 0.15989 | 0.15989 | 0.15989 | 0.98619 | -0.26398 | 0.98675 | -0.25301 | 14.6418
45 | -0.11774 | -0.029893 | 0.11775 | 0.0299 | 1.1654e-05 | 7.3449e-06 | 0.17742 | 0.17742 | 0.17742 | 0.98825 | -0.22421 | 0.98835 | -0.22215 | 16.2476
46 | 0.11457 | 0.029098 | -0.11446 | -0.02903 | 0.00010827 | 6.818e-05 | 0.17265 | 0.17265 | 0.17265 | 0.98825 | -0.22421 | 0.98723 | -0.24387 | 15.8105
47 | -0.11886 | -0.030177 | 0.11893 | 0.030225 | 7.7398e-05 | 4.8792e-05 | 0.17908 | 0.17908 | 0.17908 | 0.98835 | -0.22215 | 0.98906 | -0.20863 | 16.3996
48 | 0.11091 | 0.028139 | -0.11086 | -0.028108 | 4.8775e-05 | 3.0681e-05 | 0.16729 | 0.16729 | 0.16729 | 0.98723 | -0.24387 | 0.98675 | -0.25301 | 15.3196
49 | -0.12118 | -0.030788 | 0.12123 | 0.030817 | 4.6002e-05 | 2.9016e-05 | 0.18246 | 0.18246 | 0.18246 | 0.98906 | -0.20863 | 0.98947 | -0.20075 | 16.709
50 | -0.12372 | -0.031442 | 0.12373 | 0.031447 | 9.4031e-06 | 5.9344e-06 | 0.18621 | 0.18621 | 0.18621 | 0.98947 | -0.20075 | 0.98955 | -0.19917 | 17.052
51 | -0.12622 | -0.032071 | 0.12622 | 0.032076 | 7.6722e-06 | 4.8446e-06 | 0.18995 | 0.18995 | 0.18995 | 0.98955 | -0.19917 | 0.98962 | -0.19791 | 17.3948
52 | -0.11673 | -0.029493 | 0.11707 | 0.029708 | 0.00033754 | 0.00021564 | 0.17466 | 0.17466 | 0.17466 | 0.99493 | -0.096664 | 0.99807 | -0.03653 | 47.9843
53 | 0.017362 | 0.0043584 | -0.017356 | -0.0043546 | 6.5472e-06 | 3.8599e-06 | 0.026081 | 0.026082 | 0.026082 | 0.99066 | -0.17904 | 0.99025 | -0.18695 | 7.1652
54 | 0.0042761 | 0.0010713 | -0.0042758 | -0.0010713 | 3.812e-07 | -7.3273e-08 | 0.0064228 | 0.0064229 | 0.0064229 | 0.99066 | -0.17904 | 0.99057 | -0.18091 | 1.7645
55 | 0.02548 | 0.0064023 | -0.025466 | -0.0063931 | 1.4815e-05 | 9.135e-06 | 0.038293 | 0.038293 | 0.038293 | 0.99029 | -0.18617 | 0.98966 | -0.19836 | 10.52
56 | 0.023811 | 0.0059814 | -0.023802 | -0.0059756 | 9.4055e-06 | 5.7596e-06 | 0.035505 | 0.035505 | 0.035505 | 0.99807 | -0.03653 | 0.99764 | -0.044811 | 9.7541
57 | 0.16138 | 0.041318 | -0.16116 | -0.041181 | 0.00021615 | 0.00013717 | 0.24091 | 0.24091 | 0.24091 | 0.99807 | -0.03653 | 0.99661 | -0.064224 | 22.0614
58 | -0.30226 | -0.077008 | 0.30274 | 0.077316 | 0.00048289 | 0.0003083 | 0.45108 | 0.45108 | 0.45108 | 0.99807 | -0.03653 | 0.99982 | -0.0034751 | 41.3075
59 | 0.017356 | 0.0043546 | -0.017351 | -0.0043517 | 4.959e-06 | 2.9237e-06 | 0.026082 | 0.026082 | 0.026082 | 0.99025 | -0.18695 | 0.98995 | -0.19294 | 7.1653
60 | 0.0027706 | 0.00069411 | -0.0027704 | -0.00069434 | 1.6815e-07 | -2.256e-07 | 0.0041619 | 0.004162 | 0.004162 | 0.99057 | -0.18091 | 0.9905 | -0.18218 | 1.1434
61 | 0.023592 | 0.0059236 | -0.023589 | -0.0059216 | 3.2935e-06 | 2.0182e-06 | 0.035476 | 0.035476 | 0.035476 | 0.98966 | -0.19836 | 0.98951 | -0.20129 | 9.7462
62 | 0.0060536 | 0.0015169 | -0.0060534 | -0.0015168 | 2.5027e-07 | 6.1347e-08 | 0.0092078 | 0.0092079 | 0.0092079 | 0.97828 | -0.41784 | 0.97823 | -0.41871 | 2.5296
63 | 0.0038481 | 0.00096414 | -0.0038479 | -0.00096422 | 2.2954e-07 | -7.7366e-08 | 0.0058534 | 0.0058535 | 0.0058535 | 0.97823 | -0.41871 | 0.97817 | -0.41996 | 1.6081
64 | 0.0014148 | 0.00035443 | -0.0014148 | -0.00035457 | 2.2083e-08 | -1.4546e-07 | 0.0021522 | 0.0021522 | 0.0021522 | 0.97817 | -0.41996 | 0.97815 | -0.42029 | 0.59127
65 | 0.021599 | 0.0054235 | -0.021588 | -0.0054168 | 1.1102e-05 | 6.7334e-06 | 0.032219 | 0.032219 | 0.032219 | 0.99764 | -0.044811 | 0.99708 | -0.055591 | 8.8514
66 | 0.15947 | 0.040757 | -0.15942 | -0.040721 | 5.7325e-05 | 3.6372e-05 | 0.23838 | 0.23838 | 0.23838 | 0.99661 | -0.064224 | 0.99622 | -0.071659 | 21.8301
67 | -0.30532 | -0.077963 | 0.30537 | 0.077996 | 5.1291e-05 | 3.2748e-05 | 0.45492 | 0.45492 | 0.45492 | 0.99982 | -0.0034751 | 1 | 0 | 41.6593
68 | 0.019554 | 0.004907 | -0.019543 | -0.0049006 | 1.067e-05 | 6.3936e-06 | 0.029184 | 0.029184 | 0.029184 | 0.99708 | -0.055591 | 0.99649 | -0.067041 | 8.0176
69 | 0.15663 | 0.040023 | -0.1565 | -0.039936 | 0.00013669 | 8.6702e-05 | 0.23423 | 0.23423 | 0.23423 | 0.99622 | -0.071659 | 0.99527 | -0.089722 | 21.4495
70 | 0.023322 | 0.0058532 | -0.023313 | -0.0058477 | 9.0266e-06 | 5.515e-06 | 0.034706 | 0.034706 | 0.034706 | 1 | 0 | 0.99958 | -0.0081191 | 9.5347
71 | 0.017513 | 0.0043919 | -0.017512 | -0.0043911 | 1.3862e-06 | 8.1676e-07 | 0.026153 | 0.026153 | 0.026153 | 0.99649 | -0.067041 | 0.9964 | -0.068702 | 7.1849
72 | 0.013937 | 0.0034943 | -0.013935 | -0.0034936 | 1.3555e-06 | 7.5932e-07 | 0.020837 | 0.020837 | 0.020837 | 0.99527 | -0.089722 | 0.99517 | -0.091763 | 5.7245
73 | 0.14256 | 0.036442 | -0.14251 | -0.036413 | 4.6161e-05 | 2.9227e-05 | 0.21339 | 0.21339 | 0.21339 | 0.99527 | -0.089722 | 0.99492 | -0.096418 | 19.5414
74 | 0.020277 | 0.0050869 | -0.020269 | -0.0050822 | 7.7117e-06 | 4.6398e-06 | 0.030187 | 0.030187 | 0.030187 | 0.99958 | -0.0081191 | 0.99916 | -0.0161 | 8.2932
75 | 0.025888 | 0.0065069 | -0.025868 | -0.0064943 | 2.0398e-05 | 1.2622e-05 | 0.039537 | 0.039537 | 0.039537 | 0.97451 | -0.49168 | 0.97367 | -0.5082 | 10.8618
76 | -0.031687 | -0.0079603 | 0.031695 | 0.0079651 | 7.7356e-06 | 4.841e-06 | 0.048391 | 0.048391 | 0.048391 | 0.97451 | -0.49168 | 0.97477 | -0.48656 | 13.2943
77 | 0.024135 | 0.00606 | -0.02413 | -0.0060571 | 4.7481e-06 | 2.9231e-06 | 0.036889 | 0.036889 | 0.036889 | 0.97367 | -0.5082 | 0.97346 | -0.51232 | 10.1342
78 | 0.021896 | 0.005497 | -0.021893 | -0.0054952 | 3.0301e-06 | 1.8496e-06 | 0.033473 | 0.033473 | 0.033473 | 0.97346 | -0.51232 | 0.97332 | -0.51522 | 9.1958
79 | 0.019547 | 0.0049072 | -0.019534 | -0.0048993 | 1.3167e-05 | 7.9384e-06 | 0.029886 | 0.029886 | 0.029886 | 0.97332 | -0.51522 | 0.9726 | -0.52935 | 8.2105
80 | 0.017175 | 0.0043081 | -0.017171 | -0.0043056 | 4.0955e-06 | 2.4249e-06 | 0.026277 | 0.026278 | 0.026278 | 0.9726 | -0.52935 | 0.97235 | -0.53436 | 7.2191
81 | 0.025208 | 0.0063306 | -0.025199 | -0.0063254 | 8.4554e-06 | 5.2109e-06 | 0.037953 | 0.037953 | 0.037953 | 0.98844 | -0.22198 | 0.98808 | -0.22901 | 10.4265
82 | 0.02246 | 0.0056388 | -0.022459 | -0.0056381 | 1.0627e-06 | 6.4844e-07 | 0.033827 | 0.033827 | 0.033827 | 0.98808 | -0.22901 | 0.98803 | -0.23 | 9.2931
83 | 0.02093 | 0.005255 | -0.020927 | -0.0052535 | 2.437e-06 | 1.4759e-06 | 0.031525 | 0.031525 | 0.031525 | 0.98803 | -0.23 | 0.98791 | -0.23244 | 8.6606
84 | 0.015303 | 0.0038375 | -0.015298 | -0.0038345 | 5.2028e-06 | 2.984e-06 | 0.022855 | 0.022855 | 0.022855 | 0.9964 | -0.068702 | 0.99603 | -0.075837 | 6.2787
85 | 0.013525 | 0.0033902 | -0.013524 | -0.0033897 | 9.2476e-07 | 5.1324e-07 | 0.020206 | 0.020206 | 0.020206 | 0.99603 | -0.075837 | 0.99596 | -0.077273 | 5.5511
86 | 0.011762 | 0.0029481 | -0.011761 | -0.0029472 | 1.7988e-06 | 9.4915e-07 | 0.017574 | 0.017574 | 0.017574 | 0.99596 | -0.077273 | 0.99579 | -0.080483 | 4.828
87 | 0.0082295 | 0.0020622 | -0.0082292 | -0.0020621 | 3.2658e-07 | 1.341e-07 | 0.012297 | 0.012297 | 0.012297 | 0.99579 | -0.080483 | 0.99575 | -0.081316 | 3.3784
88 | 0.0021794 | 0.00054613 | -0.0021794 | -0.00054621 | 3.2076e-08 | -8.4366e-08 | 0.0032568 | 0.0032569 | 0.0032569 | 0.99575 | -0.081316 | 0.99573 | -0.081625 | 0.89475
89 | 0.0060497 | 0.0015159 | -0.006049 | -0.0015158 | 7.301e-07 | 1.5743e-07 | 0.0090404 | 0.0090405 | 0.0090405 | 0.99575 | -0.081316 | 0.99562 | -0.08385 | 2.4837
90 | 0.0037304 | 0.00093468 | -0.0037302 | -0.00093477 | 1.8083e-07 | -8.6004e-08 | 0.0055752 | 0.0055753 | 0.0055753 | 0.99562 | -0.08385 | 0.99557 | -0.084868 | 1.5317
91 | 0.011635 | 0.0029171 | -0.01163 | -0.0029149 | 4.1582e-06 | 2.1989e-06 | 0.017522 | 0.017522 | 0.017522 | 0.98805 | -0.22976 | 0.98766 | -0.23726 | 4.8139
92 | -0.018218 | -0.0045671 | 0.018228 | 0.004573 | 9.9477e-06 | 5.9149e-06 | 0.027437 | 0.027437 | 0.027437 | 0.98805 | -0.22976 | 0.98864 | -0.2183 | 7.5377
93 | -0.018228 | -0.004573 | 0.018243 | 0.0045818 | 1.4802e-05 | 8.8001e-06 | 0.027437 | 0.027437 | 0.027437 | 0.98864 | -0.2183 | 0.98951 | -0.20129 | 7.5377
94 | 0.0022509 | 0.000564 | -0.0022508 | -0.00056411 | 4.1847e-08 | -1.0142e-07 | 0.0033642 | 0.0033642 | 0.0033642 | 0.99557 | -0.084868 | 0.99555 | -0.085258 | 0.92424
95 | -0.015919 | -0.0039908 | 0.015923 | 0.003993 | 3.716e-06 | 2.1475e-06 | 0.023715 | 0.023715 | 0.023715 | 0.9989 | -0.021137 | 0.99916 | -0.016239 | 6.5151
96 | -0.018062 | -0.004529 | 0.018062 | 0.004529 | 1.2037e-07 | 7.1224e-08 | 0.0269 | 0.0269 | 0.0269 | 0.99916 | -0.016239 | 0.99916 | -0.0161 | 7.39
97 | -0.12888 | -0.032743 | 0.12895 | 0.032783 | 6.3088e-05 | 3.9859e-05 | 0.19395 | 0.19395 | 0.19395 | 0.98962 | -0.19791 | 0.99014 | -0.18774 | 17.7612
98 | -0.13233 | -0.033631 | 0.13235 | 0.033643 | 1.8564e-05 | 1.1736e-05 | 0.19904 | 0.19904 | 0.19904 | 0.99014 | -0.18774 | 0.9903 | -0.18483 | 18.2271
99 | -0.13235 | -0.033643 | 0.13251 | 0.033742 | 0.00015597 | 9.8601e-05 | 0.19904 | 0.19904 | 0.19904 | 0.9903 | -0.18483 | 0.99157 | -0.16039 | 18.2271
100 | 0.14023 | 0.03584 | -0.14004 | -0.03572 | 0.00018909 | 0.00011968 | 0.20997 | 0.20997 | 0.20997 | 0.99492 | -0.096418 | 0.99346 | -0.12434 | 19.2283
101 | 0.13773 | 0.035142 | -0.13749 | -0.03499 | 0.00023943 | 0.00015149 | 0.20651 | 0.20652 | 0.20652 | 0.99346 | -0.12434 | 0.99157 | -0.16039 | 18.9116
102 | 0.0049819 | 0.0012482 | -0.0049815 | -0.0012482 | 3.741e-07 | 9.2083e-09 | 0.007476 | 0.0074761 | 0.0074761 | 0.99157 | -0.16039 | 0.99149 | -0.16197 | 2.0539
103 | 0.011931 | 0.0029911 | -0.011928 | -0.0029899 | 2.3162e-06 | 1.2303e-06 | 0.01784 | 0.01784 | 0.01784 | 0.99517 | -0.091763 | 0.99496 | -0.095838 | 4.901
104 | 0.0037085 | 0.00092918 | -0.0037083 | -0.00092926 | 1.8405e-07 | -8.6543e-08 | 0.0055655 | 0.0055656 | 0.0055656 | 0.99149 | -0.16197 | 0.99144 | -0.16301 | 1.529
105 | 0.009005 | 0.0022572 | -0.0090023 | -0.002256 | 2.6905e-06 | 1.2084e-06 | 0.013468 | 0.013468 | 0.013468 | 0.99496 | -0.095838 | 0.99463 | -0.10211 | 3.6999
106 | 0.0020886 | 0.00052333 | -0.0020885 | -0.00052344 | 3.8136e-08 | -1.0905e-07 | 0.0031347 | 0.0031347 | 0.0031347 | 0.99144 | -0.16301 | 0.99142 | -0.1634 | 0.86118
107 | 0.0046624 | 0.0011684 | -0.0046623 | -0.0011684 | 9.8224e-08 | -7.0095e-09 | 0.0069751 | 0.0069751 | 0.0069751 | 0.99463 | -0.10211 | 0.99461 | -0.10255 | 1.9162
108 | 0.015624 | 0.003919 | -0.015619 | -0.0039165 | 4.2751e-06 | 2.4736e-06 | 0.023557 | 0.023557 | 0.023557 | 0.98696 | -0.25084 | 0.98667 | -0.25658 | 6.4716
109 | 0.013366 | 0.0033517 | -0.013362 | -0.0033497 | 3.5861e-06 | 1.9946e-06 | 0.020158 | 0.020158 | 0.020158 | 0.98667 | -0.25658 | 0.98638 | -0.26221 | 5.538
110 | 0.013362 | 0.0033497 | -0.013361 | -0.0033492 | 9.0882e-07 | 5.0553e-07 | 0.020158 | 0.020158 | 0.020158 | 0.98638 | -0.26221 | 0.9863 | -0.26364 | 5.538
111 | 0.013361 | 0.0033492 | -0.01336 | -0.0033482 | 1.8455e-06 | 1.0266e-06 | 0.020158 | 0.020158 | 0.020158 | 0.9863 | -0.26364 | 0.98615 | -0.26654 | 5.538
112 | 0.0063607 | 0.0015941 | -0.00636 | -0.0015939 | 7.4186e-07 | 2.0083e-07 | 0.0095977 | 0.0095978 | 0.0095978 | 0.98615 | -0.26654 | 0.98603 | -0.26899 | 2.6368
113 | -0.006315 | -0.0015827 | 0.0063161 | 0.001583 | 1.0317e-06 | 2.6883e-07 | 0.0094995 | 0.0094994 | 0.0094995 | 0.9892 | -0.20751 | 0.98937 | -0.20408 | 2.6098
114 | -0.017342 | -0.0043462 | 0.017351 | 0.0043517 | 9.2085e-06 | 5.4296e-06 | 0.026082 | 0.026082 | 0.026082 | 0.98937 | -0.20408 | 0.98995 | -0.19294 | 7.1653
115 | 0.0015868 | 0.00039756 | -0.0015868 | -0.00039769 | 2.5225e-08 | -1.3037e-07 | 0.0024072 | 0.0024073 | 0.0024073 | 0.98087 | -0.36708 | 0.98086 | -0.36741 | 0.66133
116 | 0.0021244 | 0.0005323 | -0.0021244 | -0.00053242 | 4.089e-08 | -1.1392e-07 | 0.0031782 | 0.0031783 | 0.0031783 | 0.99461 | -0.10255 | 0.99459 | -0.10296 | 0.87316
117 | 0.014946 | 0.0037481 | -0.014939 | -0.0037438 | 7.5919e-06 | 4.3791e-06 | 0.022873 | 0.022874 | 0.022874 | 0.97235 | -0.53436 | 0.97181 | -0.54502 | 6.2839
118 | 0.010543 | 0.0026426 | -0.01054 | -0.002641 | 3.1154e-06 | 1.599e-06 | 0.016144 | 0.016144 | 0.016144 | 0.97181 | -0.54502 | 0.97149 | -0.55122 | 4.4351
119 | 0.0043954 | 0.0011011 | -0.0043952 | -0.0011012 | 1.3497e-07 | -1.2073e-08 | 0.00673 | 0.00673 | 0.00673 | 0.97181 | -0.54502 | 0.97178 | -0.54566 | 1.8489
120 | 0.0089133 | 0.0022333 | -0.0089123 | -0.0022329 | 9.572e-07 | 4.4305e-07 | 0.013652 | 0.013652 | 0.013652 | 0.97149 | -0.55122 | 0.97138 | -0.55348 | 3.7506
121 | 0.0031466 | 0.00078822 | -0.0031465 | -0.00078831 | 1.0854e-07 | -8.4997e-08 | 0.0048181 | 0.0048181 | 0.0048181 | 0.97178 | -0.54566 | 0.97174 | -0.54639 | 1.3237
122 | 0.0055667 | 0.0013951 | -0.005566 | -0.001395 | 6.9444e-07 | 1.0979e-07 | 0.0084007 | 0.0084008 | 0.0084008 | 0.98603 | -0.26899 | 0.98589 | -0.27161 | 2.3079
123 | 0.0015515 | 0.00038855 | -0.0015514 | -0.00038882 | 5.1753e-08 | -2.6979e-07 | 0.0023756 | 0.0023758 | 0.0023758 | 0.97174 | -0.54639 | 0.9717 | -0.54709 | 0.65268
124 | 0.0073399 | 0.0018388 | -0.0073388 | -0.0018384 | 1.1496e-06 | 4.3561e-07 | 0.011243 | 0.011244 | 0.011244 | 0.97138 | -0.55348 | 0.97121 | -0.55677 | 3.0889
125 | -0.0019515 | -0.00048909 | 0.0019516 | 0.00048888 | 6.8993e-08 | -2.1033e-07 | 0.0029905 | 0.0029904 | 0.0029905 | 0.97101 | -0.56072 | 0.97105 | -0.55998 | 0.82158
126 | -0.0043132 | -0.0010802 | 0.0043135 | 0.0010802 | 2.691e-07 | -3.102e-08 | 0.0066092 | 0.0066091 | 0.0066092 | 0.97105 | -0.55998 | 0.97112 | -0.55867 | 1.8157
127 | 0.0023616 | 0.00059132 | -0.0023614 | -0.00059182 | 2.6662e-07 | -5.009e-07 | 0.0036187 | 0.003619 | 0.003619 | 0.97105 | -0.55998 | 0.97093 | -0.56235 | 0.99422
128 | -0.0058697 | -0.0014702 | 0.0058702 | 0.0014703 | 5.3181e-07 | 1.2341e-07 | 0.0089936 | 0.0089936 | 0.0089936 | 0.97112 | -0.55867 | 0.97121 | -0.55677 | 2.4708

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33384 | 0.084726

## res_load
| p_mw | q_mvar
0 | 0.0038077 | 0.00095431
1 | 0.0033611 | 0.00084237
2 | 0.0034767 | 0.00087134
3 | 0.0027882 | 0.0006988
4 | 0.0029841 | 0.00074787
5 | 0.0041442 | 0.0010386
6 | 0.0024961 | 0.00062558
7 | 0.0025784 | 0.00064621
8 | 0.0017255 | 0.00043246
9 | 0.00212 | 0.00053132
10 | 0.0030212 | 0.00075719
11 | 0.0033555 | 0.00084097
12 | 0.001844 | 0.00046214
13 | 0.0010527 | 0.00026384
14 | 0.0020667 | 0.00051797
15 | 0.0019881 | 0.00049826
16 | 0.0024494 | 0.00061387
17 | 0.0024378 | 0.00061096
18 | 0.0033463 | 0.00083866
19 | 0.0061392 | 0.0015386
20 | 0.0017809 | 0.00044634
21 | 0.003444 | 0.00086315
22 | 0.0028112 | 0.00070454
23 | 0.003025 | 0.00075815
24 | 0.0024578 | 0.00061597
25 | 0.0047992 | 0.0012028
26 | 0.0015927 | 0.00039917
27 | 0.0026088 | 0.00065383
28 | 0.0028113 | 0.00070457
29 | 0.0015641 | 0.00039199
30 | 0.0044229 | 0.0011085
31 | 0.006219 | 0.0015586
32 | 0.0046662 | 0.0011695
33 | 0.0031699 | 0.00079445
34 | 0.001103 | 0.00027644
35 | 0.0035566 | 0.00089137
36 | 0.0022453 | 0.00056273
37 | 0.0049085 | 0.0012302
38 | 0.0024911 | 0.00062432
39 | 0.0024898 | 0.000624
40 | 0.0032815 | 0.00082241
41 | 0.010896 | 0.0027308
42 | 0.0014618 | 0.00036636
43 | 0.0015051 | 0.00037722
44 | 0.0018732 | 0.00046948
45 | 0.0023225 | 0.00058206
46 | 0.0022053 | 0.00055269
47 | 0.0024331 | 0.00060979
48 | 0.0014148 | 0.00035457
49 | 0.0022029 | 0.0005521
50 | 0.001692 | 0.00042407
51 | 0.002582 | 0.00064712
52 | 0.0020339 | 0.00050974
53 | 0.0027827 | 0.00069741
54 | 0.0034967 | 0.00087636
55 | 0.0020298 | 0.00050872
56 | 0.0030359 | 0.00076086
57 | 0.0057989 | 0.0014533
58 | 0.0017329 | 0.00043432
59 | 0.0042569 | 0.0010669
60 | 0.0022346 | 0.00056005
61 | 0.002346 | 0.00058797
62 | 0.0023589 | 0.00059119
63 | 0.002601 | 0.00065187
64 | 0.0027396 | 0.0006866
65 | 0.0015288 | 0.00038314
66 | 0.0022087 | 0.00055356
67 | 0.0017729 | 0.00044432
68 | 0.0017619 | 0.00044156
69 | 0.0035312 | 0.000885
70 | 0.0021794 | 0.00054621
71 | 0.0023186 | 0.0005811
72 | 0.0065836 | 0.00165
73 | 0.01163 | 0.0029149
74 | 0.0014794 | 0.00037076
75 | 0.0016375 | 0.00041039
76 | 0.0021387 | 0.000536
77 | 0.0022073 | 0.00055321
78 | 0.002661 | 0.0006669
79 | 0.003385 | 0.00084836
80 | 0.005346 | 0.0013398
81 | 0.002286 | 0.00057293
82 | 0.0023093 | 0.00057875
83 | 0.0020047 | 0.00050243
84 | 0.001273 | 0.00031905
85 | 0.0029233 | 0.00073266
86 | 0.0016197 | 0.00040593
87 | 0.0043399 | 0.0010877
88 | 0.0016017 | 0.00040141
89 | 0.0022535 | 0.00056478
90 | 0.00078906 | 0.00019776
91 | 0.0069989 | 0.0017541
92 | 0.006315 | 0.0015827
93 | 0.011026 | 0.0027633
94 | 0.0022508 | 0.00056411
95 | 0.0026542 | 0.00066522
96 | 0.0015868 | 0.00039769
97 | 0.0027704 | 0.00069434
98 | 0.0020885 | 0.00052344
99 | 0.0025379 | 0.00063605
100 | 0.0021244 | 0.00053242
101 | 0.0022244 | 0.0005575
102 | 0.0016267 | 0.0004077
103 | 0.0012486 | 0.00031293
104 | 0.00079327 | 0.00019881
105 | 0.005566 | 0.001395
106 | 0.0015951 | 0.00039976
107 | 0.0015514 | 0.00038882
108 | 0.0015724 | 0.00039408
109 | 0.0019515 | 0.00048909
110 | 0.0015562 | 0.00039003
111 | 0.0023614 | 0.00059182
112 | 0.0014685 | 0.00036805

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1