## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_243-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_243-13_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_243-13_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_243-13_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_243-13_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_243-13_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_243-13_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_243-13_0_4_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_243-13_0_4_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_243-13_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_243-13_0_4_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_243-13_0_4_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_243-13_0_4_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_243-13_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_243-13_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_243-13_0_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_243-13_0_4_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_243-13_0_4_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_243-13_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_243-13_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_243-13_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_243-13_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_243-13_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_243-13_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_243-13_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_243-13_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_243-13_0_4_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_243-13_0_4_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_243-13_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_243-13_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_243-13_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_243-13_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_243-13_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_243-13_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_243-13_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_MV_515_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-13_0_4_load_0 | 0 | 0.047663 | 0.011945 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-13_0_4_load_8 | 5 | 0.016264 | 0.0040761 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-13_0_4_load_9 | 8 | 0.027116 | 0.0067959 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-13_0_4_load_38 | 9 | 0.044595 | 0.011177 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-13_0_4_load_37 | 10 | 0.0236 | 0.0059147 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-13_0_4_load_19 | 12 | 0.045774 | 0.011472 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-13_0_4_load_36 | 14 | 0.0049638 | 0.001244 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-13_0_4_load_18 | 16 | 0.013134 | 0.0032918 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-13_0_4_load_23 | 18 | 0.0085844 | 0.0021515 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-13_0_4_load_20 | 19 | 0.0031215 | 0.00078231 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-13_0_4_load_28 | 20 | 0.031826 | 0.0079763 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-13_0_4_load_12 | 22 | 0.015518 | 0.0038892 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-13_0_4_load_17 | 23 | 0.022616 | 0.0056682 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-13_0_4_load_13 | 26 | 0.071437 | 0.017904 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-13_0_4_load_33 | 29 | 0.012696 | 0.0031818 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-13_0_4_load_35 | 30 | 0.0033872 | 0.00084891 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-13_0_4_load_29 | 34 | 0.0030606 | 0.00076706 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-13_0_4_load_31 | 35 | 0.023543 | 0.0059005 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-13_0_4_load_32 | 36 | 0.0094928 | 0.0023791 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-13_0_4_line_0 |  | 0 | 1 | 0.033792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-13_0_4_line_1 |  | 0 | 2 | 0.013737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_243-13_0_4_line_2 |  | 1 | 3 | 0.049424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_243-13_0_4_line_3 |  | 1 | 4 | 0.0838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_243-13_0_4_line_4 |  | 2 | 5 | 0.012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_243-13_0_4_line_5 |  | 3 | 9 | 0.0075773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_243-13_0_4_line_6 |  | 4 | 10 | 0.031971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_243-13_0_4_line_7 |  | 5 | 14 | 0.010889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_243-13_0_4_line_8 |  | 6 | 7 | 0.025875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_243-13_0_4_line_9 |  | 6 | 8 | 0.015394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_243-13_0_4_line_10 |  | 7 | 14 | 0.010171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-13_0_4_line_11 |  | 8 | 15 | 0.012878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_243-13_0_4_line_12 |  | 11 | 12 | 0.018536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_243-13_0_4_line_13 |  | 11 | 13 | 0.040922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_243-13_0_4_line_14 |  | 13 | 16 | 0.017617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_243-13_0_4_line_15 |  | 15 | 22 | 0.012023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_243-13_0_4_line_16 |  | 16 | 27 | 0.015364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_243-13_0_4_line_17 |  | 17 | 18 | 0.022817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_243-13_0_4_line_18 |  | 17 | 19 | 0.02076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-13_0_4_line_19 |  | 19 | 21 | 0.016827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-13_0_4_line_20 |  | 20 | 21 | 0.012839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_243-13_0_4_line_21 |  | 21 | 32 | 0.022961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-13_0_4_line_22 |  | 22 | 23 | 0.038305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_243-13_0_4_line_23 |  | 23 | 24 | 0.031938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_243-13_0_4_line_24 |  | 24 | 25 | 0.01347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_243-13_0_4_line_25 |  | 24 | 26 | 0.027124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_243-13_0_4_line_26 |  | 25 | 28 | 0.058668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-13_0_4_line_27 |  | 25 | 29 | 0.1169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_243-13_0_4_line_28 |  | 26 | 27 | 0.022843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_243-13_0_4_line_29 |  | 28 | 30 | 0.011558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_243-13_0_4_line_30 |  | 29 | 31 | 0.0076509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_243-13_0_4_line_31 |  | 31 | 33 | 0.028815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_243-13_0_4_line_32 |  | 32 | 35 | 0.02668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_243-13_0_4_line_33 |  | 32 | 34 | 0.015901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_243-13_0_4_line_34 |  | 33 | 34 | 0.011447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_243-13_0_4_line_35 |  | 35 | 36 | 0.044309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-13_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 37 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2672878.6816 | 1250816.5938 | 2672882.8323 | 1250816.6894 | 2672883.5049 | 1250808.0358 | 2672884.6379 | 1250806.76 | 2672903.883 | 1250807.3473
1 | 2672915.2258 | 1250809.8606 | 2672911.9202 | 1250809.7865 | 2672912.1133 | 1250807.5984 | 2672903.883 | 1250807.3473
2 | 2672867.9525 | 1250859.7153 | 2672875.4685 | 1250858.0954 | 2672876.6239 | 1250854.3736 | 2672877.8908 | 1250835.4644 | 2672878.6816 | 1250816.5938
3 | 2672878.6816 | 1250816.5938 | 2672878.5432 | 1250805.751 | 2672878.2105 | 1250805.1798 | 2672875.9636 | 1250801.2827 | 2672858.5647 | 1250788.2816 | 2672882.5758 | 1250760.8459 | 2672887.3138 | 1250752.4758
4 | 2672915.2258 | 1250809.8606 | 2672920.7802 | 1250816.1223 | 2672923.4583 | 1250819.1049
5 | 2672867.9525 | 1250859.7153 | 2672860.407 | 1250860.4084
6 | 2672887.3138 | 1250752.4758 | 2672908.5113 | 1250776.4094
7 | 2672930.7332 | 1250827.2069 | 2672923.4583 | 1250819.1049
8 | 2672931.8751 | 1250836.518 | 2672905.9281 | 1250836.0207
9 | 2672905.9281 | 1250836.0207 | 2672905.0114 | 1250851.3877
10 | 2672931.8751 | 1250836.518 | 2672932.8143 | 1250829.5245 | 2672930.7332 | 1250827.2069
11 | 2672904.2446 | 1250864.2426 | 2672905.0114 | 1250851.3877
12 | 2672980.6652 | 1250744.4853 | 2672975.3344 | 1250750.713 | 2672968.9472 | 1250758.8428
13 | 2672980.6652 | 1250744.4853 | 2672994.1288 | 1250756.4375 | 2672999.5589 | 1250761.7637 | 2673003.6824 | 1250767.1295 | 2673005.5308 | 1250770.8994 | 2673006.9439 | 1250775.0643
14 | 2673006.9439 | 1250775.0643 | 2673007.3552 | 1250779.0611 | 2673007.3243 | 1250784.0199 | 2673005.907 | 1250789.9845 | 2673005.0385 | 1250792.3393
15 | 2672904.2446 | 1250864.2426 | 2672911.2946 | 1250864.9076 | 2672914.73 | 1250868.4597
16 | 2672999.7216 | 1250806.7538 | 2673005.0385 | 1250792.3393
17 | 2672834.601 | 1250971.4974 | 2672848.4564 | 1250989.6254
18 | 2672834.601 | 1250971.4974 | 2672838.0791 | 1250955.6842 | 2672840.8287 | 1250952.0356
19 | 2672850.9561 | 1250938.5968 | 2672840.8287 | 1250952.0356
20 | 2672850.9561 | 1250938.5968 | 2672842.0681 | 1250929.3321
21 | 2672850.9561 | 1250938.5968 | 2672861.6492 | 1250949.3138 | 2672867.7557 | 1250954.2591
22 | 2672947.9577 | 1250864.352 | 2672943.8699 | 1250866.5873 | 2672937.1888 | 1250870.2967 | 2672926.6949 | 1250875.2823 | 2672919.8816 | 1250873.7863 | 2672914.73 | 1250868.4597
23 | 2672976.5987 | 1250850.9122 | 2672966.3232 | 1250853.4764 | 2672951.8044 | 1250862.2485 | 2672947.9577 | 1250864.352
24 | 2672970.9975 | 1250863.1632 | 2672973.555 | 1250857.157 | 2672976.5987 | 1250850.9122
25 | 2672976.5987 | 1250850.9122 | 2672979.1415 | 1250846.7182 | 2672982.4127 | 1250841.6104 | 2672987.5996 | 1250832.968 | 2672990.5641 | 1250827.6665
26 | 2672946.4915 | 1250909.9398 | 2672952.9419 | 1250893.0848 | 2672962.2733 | 1250868.493 | 2672965.5083 | 1250860.805 | 2672969.3593 | 1250862.5537 | 2672970.9975 | 1250863.1632
27 | 2672970.9975 | 1250863.1632 | 2672947.0747 | 1250924.4909 | 2672941.0146 | 1250942.7517 | 2672937.7347 | 1250951.0285 | 2672936.1207 | 1250955.2005 | 2672934.316 | 1250958.9255 | 2672932.169 | 1250962.2459 | 2672927.4091 | 1250966.8796 | 2672924.3712 | 1250969.0313
28 | 2672999.7216 | 1250806.7538 | 2672993.5903 | 1250821.5779 | 2672991.2738 | 1250826.3973 | 2672990.5641 | 1250827.6665
29 | 2672946.4915 | 1250909.9398 | 2672942.902 | 1250920.9259
30 | 2672917.6971 | 1250972.7532 | 2672923.3045 | 1250969.7867 | 2672924.3712 | 1250969.0313
31 | 2672917.6971 | 1250972.7532 | 2672910.6065 | 1250974.7786 | 2672901.5309 | 1250974.3333 | 2672895.7208 | 1250972.9053 | 2672889.7185 | 1250970.5409
32 | 2672867.7557 | 1250954.2591 | 2672883.3689 | 1250932.6247
33 | 2672867.7557 | 1250954.2591 | 2672877.3555 | 1250961.8048 | 2672880.3698 | 1250963.9347
34 | 2672889.7185 | 1250970.5409 | 2672880.3698 | 1250963.9347
35 | 2672909.6375 | 1250896.9427 | 2672891.8162 | 1250920.9197 | 2672883.3689 | 1250932.6247

## bus_geodata
| x | y | coords
0 | 2672903.883 | 1250807.3473
1 | 2672878.6816 | 1250816.5938
2 | 2672915.2258 | 1250809.8606
3 | 2672867.9525 | 1250859.7153
4 | 2672887.3138 | 1250752.4758
5 | 2672923.4583 | 1250819.1049
6 | 2672905.9281 | 1250836.0207
7 | 2672931.8751 | 1250836.518
8 | 2672905.0114 | 1250851.3877
9 | 2672860.407 | 1250860.4084
10 | 2672908.5113 | 1250776.4094
11 | 2672980.6652 | 1250744.4853
12 | 2672968.9472 | 1250758.8428
13 | 2673006.9439 | 1250775.0643
14 | 2672930.7332 | 1250827.2069
15 | 2672904.2446 | 1250864.2426
16 | 2673005.0385 | 1250792.3393
17 | 2672834.601 | 1250971.4974
18 | 2672848.4564 | 1250989.6254
19 | 2672840.8287 | 1250952.0356
20 | 2672842.0681 | 1250929.3321
21 | 2672850.9561 | 1250938.5968
22 | 2672914.73 | 1250868.4597
23 | 2672947.9577 | 1250864.352
24 | 2672976.5987 | 1250850.9122
25 | 2672970.9975 | 1250863.1632
26 | 2672990.5641 | 1250827.6665
27 | 2672999.7216 | 1250806.7538
28 | 2672946.4915 | 1250909.9398
29 | 2672924.3712 | 1250969.0313
30 | 2672942.902 | 1250920.9259
31 | 2672917.6971 | 1250972.7532
32 | 2672867.7557 | 1250954.2591
33 | 2672889.7185 | 1250970.5409
34 | 2672880.3698 | 1250963.9347
35 | 2672883.3689 | 1250932.6247
36 | 2672909.6375 | 1250896.9427
37 | 2672905.9281 | 1250836.0207

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99464 | -0.10267 | 0.047663 | 0.011945
1 | 0.99253 | -0.14336 | 0 | 0
2 | 0.9961 | -0.074669 | 0 | 0
3 | 0.99052 | -0.18243 | 0 | 0
4 | 0.99072 | -0.17842 | 0 | 0
5 | 0.99741 | -0.049508 | 0.016264 | 0.0040761
6 | 0.99768 | -0.043898 | 0 | 0
7 | 1 | 0 | -0.43591 | -0.11111
8 | 0.99629 | -0.070113 | 0.027116 | 0.0067959
9 | 0.99021 | -0.18844 | 0.044595 | 0.011177
10 | 0.99003 | -0.19182 | 0.0236 | 0.0059147
11 | 0.98014 | -0.38148 | 0 | 0
12 | 0.97936 | -0.39689 | 0.045774 | 0.011472
13 | 0.98188 | -0.34756 | 0 | 0
14 | 0.99873 | -0.024334 | 0.0049638 | 0.001244
15 | 0.99524 | -0.090049 | 0 | 0
16 | 0.98262 | -0.33299 | 0.013134 | 0.0032918
17 | 0.9707 | -0.56517 | 0 | 0
18 | 0.97051 | -0.56879 | 0.0085844 | 0.0021515
19 | 0.97086 | -0.56187 | 0.0031215 | 0.00078231
20 | 0.97067 | -0.56579 | 0.031826 | 0.0079763
21 | 0.97105 | -0.55823 | 0 | 0
22 | 0.99426 | -0.1087 | 0.015518 | 0.0038892
23 | 0.99132 | -0.16485 | 0.022616 | 0.0056682
24 | 0.98797 | -0.2291 | 0 | 0
25 | 0.98676 | -0.25215 | 0 | 0
26 | 0.9847 | -0.29244 | 0.071437 | 0.017904
27 | 0.98346 | -0.31666 | 0 | 0
28 | 0.98658 | -0.25571 | 0 | 0
29 | 0.97668 | -0.44736 | 0.012696 | 0.0031818
30 | 0.98655 | -0.25641 | 0.0033872 | 0.00084891
31 | 0.97611 | -0.4585 | 0 | 0
32 | 0.97198 | -0.53977 | 0 | 0
33 | 0.97397 | -0.50057 | 0 | 0
34 | 0.97312 | -0.51733 | 0.0030606 | 0.00076706
35 | 0.97116 | -0.55605 | 0.023543 | 0.0059005
36 | 0.97077 | -0.56382 | 0.0094928 | 0.0023791
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.068479 | 0.01727 | -0.068345 | -0.017185 | 0.00013309 | 8.4742e-05 | 0.10248 | 0.10248 | 0.10248 | 0.99464 | -0.10267 | 0.99253 | -0.14336 | 28.155
1 | -0.11614 | -0.029216 | 0.1163 | 0.029315 | 0.00015559 | 9.9396e-05 | 0.17379 | 0.17379 | 0.17379 | 0.99464 | -0.10267 | 0.9961 | -0.074669 | 47.7442
2 | 0.044691 | 0.011237 | -0.044608 | -0.011185 | 8.3235e-05 | 5.2633e-05 | 0.067014 | 0.067014 | 0.067014 | 0.99253 | -0.14336 | 0.99052 | -0.18243 | 18.4106
3 | 0.023654 | 0.0059481 | -0.023615 | -0.0059239 | 3.9537e-05 | 2.4222e-05 | 0.03547 | 0.03547 | 0.03547 | 0.99253 | -0.14336 | 0.99072 | -0.17842 | 9.7446
4 | -0.1163 | -0.029315 | 0.11644 | 0.029405 | 0.0001402 | 8.9567e-05 | 0.17379 | 0.17379 | 0.17379 | 0.9961 | -0.074669 | 0.99741 | -0.049508 | 47.7442
5 | 0.044608 | 0.011185 | -0.044595 | -0.011177 | 1.2761e-05 | 8.0695e-06 | 0.067014 | 0.067014 | 0.067014 | 0.99052 | -0.18243 | 0.99021 | -0.18844 | 18.4106
6 | 0.023615 | 0.0059239 | -0.0236 | -0.0059147 | 1.5084e-05 | 9.2424e-06 | 0.03547 | 0.03547 | 0.03547 | 0.99072 | -0.17842 | 0.99003 | -0.19182 | 9.7446
7 | -0.1327 | -0.033481 | 0.13286 | 0.033583 | 0.00016017 | 0.00010236 | 0.19805 | 0.19805 | 0.19805 | 0.99741 | -0.049508 | 0.99873 | -0.024334 | 54.41
8 | -0.29564 | -0.075773 | 0.29628 | 0.076176 | 0.00063058 | 0.00040256 | 0.44155 | 0.44154 | 0.44155 | 0.99768 | -0.043898 | 1 | 0 | 40.4345
9 | 0.29564 | 0.075773 | -0.29527 | -0.075534 | 0.00037516 | 0.0002395 | 0.44155 | 0.44155 | 0.44155 | 0.99768 | -0.043898 | 0.99629 | -0.070113 | 40.4346
10 | 0.13799 | 0.03493 | -0.13783 | -0.034827 | 0.00016099 | 0.0001029 | 0.20545 | 0.20545 | 0.20545 | 1 | 0 | 0.99873 | -0.024334 | 56.4417
11 | 0.26815 | 0.068738 | -0.26789 | -0.068573 | 0.00025891 | 0.0001652 | 0.40105 | 0.40105 | 0.40105 | 0.99629 | -0.070113 | 0.99524 | -0.090049 | 36.7259
12 | 0.045808 | 0.011493 | -0.045774 | -0.011472 | 3.3623e-05 | 2.1285e-05 | 0.069548 | 0.069549 | 0.069549 | 0.98014 | -0.38148 | 0.97936 | -0.39689 | 19.1067
13 | -0.045808 | -0.011493 | 0.045882 | 0.01154 | 7.4227e-05 | 4.6989e-05 | 0.069548 | 0.069548 | 0.069548 | 0.98014 | -0.38148 | 0.98188 | -0.34756 | 19.1067
14 | -0.045882 | -0.01154 | 0.045914 | 0.011561 | 3.1955e-05 | 2.0228e-05 | 0.069548 | 0.069548 | 0.069548 | 0.98188 | -0.34756 | 0.98262 | -0.33299 | 19.1067
15 | 0.26789 | 0.068573 | -0.26765 | -0.068418 | 0.00024172 | 0.00015423 | 0.40105 | 0.40105 | 0.40105 | 0.99524 | -0.090049 | 0.99426 | -0.1087 | 36.7259
16 | -0.059048 | -0.014852 | 0.059095 | 0.014882 | 4.6087e-05 | 2.9301e-05 | 0.089438 | 0.089438 | 0.089438 | 0.98262 | -0.33299 | 0.98346 | -0.31666 | 24.5709
17 | 0.0085859 | 0.0021521 | -0.0085844 | -0.0021515 | 1.4822e-06 | 6.6661e-07 | 0.013162 | 0.013162 | 0.013162 | 0.9707 | -0.56517 | 0.97051 | -0.56879 | 3.6159
18 | -0.0085859 | -0.0021521 | 0.0085872 | 0.0021527 | 1.3486e-06 | 6.0642e-07 | 0.013162 | 0.013162 | 0.013162 | 0.9707 | -0.56517 | 0.97086 | -0.56187 | 3.6159
19 | -0.011709 | -0.002935 | 0.011711 | 0.0029361 | 2.0322e-06 | 1.0925e-06 | 0.017946 | 0.017946 | 0.017946 | 0.97086 | -0.56187 | 0.97105 | -0.55823 | 4.9302
20 | -0.031826 | -0.0079763 | 0.031837 | 0.0079835 | 1.146e-05 | 7.1756e-06 | 0.048788 | 0.048788 | 0.048788 | 0.97067 | -0.56579 | 0.97105 | -0.55823 | 13.4034
21 | -0.043548 | -0.01092 | 0.043586 | 0.010944 | 3.8346e-05 | 2.4257e-05 | 0.066734 | 0.066734 | 0.066734 | 0.97105 | -0.55823 | 0.97198 | -0.53977 | 18.3335
22 | 0.25213 | 0.064529 | -0.25145 | -0.064093 | 0.0006835 | 0.00043595 | 0.37782 | 0.37782 | 0.37782 | 0.99426 | -0.1087 | 0.99132 | -0.16485 | 34.5992
23 | 0.22883 | 0.058425 | -0.22813 | -0.057973 | 0.00070813 | 0.00045238 | 0.34388 | 0.34388 | 0.34388 | 0.99132 | -0.16485 | 0.98797 | -0.2291 | 47.2357
24 | 0.09713 | 0.02489 | -0.097022 | -0.024821 | 0.00010839 | 6.9199e-05 | 0.14649 | 0.14649 | 0.14649 | 0.98797 | -0.2291 | 0.98676 | -0.25215 | 40.2439
25 | 0.131 | 0.033082 | -0.1306 | -0.032829 | 0.0003963 | 0.00025329 | 0.19739 | 0.19739 | 0.19739 | 0.98797 | -0.2291 | 0.9847 | -0.29244 | 54.2278
26 | 0.0033879 | 0.00084845 | -0.0033873 | -0.00084884 | 5.742e-07 | -3.8182e-07 | 0.0051086 | 0.0051089 | 0.0051089 | 0.98676 | -0.25215 | 0.98658 | -0.25571 | 1.4035
27 | 0.093634 | 0.023972 | -0.092757 | -0.023413 | 0.00087626 | 0.00055933 | 0.14138 | 0.14138 | 0.14138 | 0.98676 | -0.25215 | 0.97668 | -0.44736 | 38.8406
28 | 0.059163 | 0.014925 | -0.059095 | -0.014882 | 6.8523e-05 | 4.3564e-05 | 0.089438 | 0.089438 | 0.089438 | 0.9847 | -0.29244 | 0.98346 | -0.31666 | 24.5709
29 | 0.0033873 | 0.00084884 | -0.0033872 | -0.00084891 | 1.1312e-07 | -7.518e-08 | 0.0051089 | 0.0051089 | 0.0051089 | 0.98658 | -0.25571 | 0.98655 | -0.25641 | 1.4036
30 | 0.080062 | 0.020231 | -0.080019 | -0.020204 | 4.273e-05 | 2.7251e-05 | 0.12204 | 0.12204 | 0.12204 | 0.97668 | -0.44736 | 0.97611 | -0.4585 | 33.5268
31 | 0.080019 | 0.020204 | -0.079858 | -0.020101 | 0.00016093 | 0.00010264 | 0.12204 | 0.12204 | 0.12204 | 0.97611 | -0.4585 | 0.97397 | -0.50057 | 33.5268
32 | 0.033065 | 0.0082974 | -0.03304 | -0.0082814 | 2.5641e-05 | 1.608e-05 | 0.050624 | 0.050624 | 0.050624 | 0.97198 | -0.53977 | 0.97116 | -0.55605 | 13.9077
33 | -0.076652 | -0.019241 | 0.076734 | 0.019294 | 8.2127e-05 | 5.2364e-05 | 0.11736 | 0.11736 | 0.11736 | 0.97198 | -0.53977 | 0.97312 | -0.51733 | 32.2411
34 | 0.079858 | 0.020101 | -0.079794 | -0.020061 | 6.3932e-05 | 4.0774e-05 | 0.12204 | 0.12204 | 0.12204 | 0.97397 | -0.50057 | 0.97312 | -0.51733 | 33.5268
35 | 0.0094964 | 0.0023808 | -0.0094928 | -0.0023791 | 3.518e-06 | 1.7035e-06 | 0.014551 | 0.014551 | 0.014551 | 0.97116 | -0.55605 | 0.97077 | -0.56382 | 3.9975

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43591 | 0.11111

## res_load
| p_mw | q_mvar
0 | 0.047663 | 0.011945
1 | 0.016264 | 0.0040761
2 | 0.027116 | 0.0067959
3 | 0.044595 | 0.011177
4 | 0.0236 | 0.0059147
5 | 0.045774 | 0.011472
6 | 0.0049638 | 0.001244
7 | 0.013134 | 0.0032918
8 | 0.0085844 | 0.0021515
9 | 0.0031215 | 0.00078231
10 | 0.031826 | 0.0079763
11 | 0.015518 | 0.0038892
12 | 0.022616 | 0.0056682
13 | 0.071437 | 0.017904
14 | 0.012696 | 0.0031818
15 | 0.0033872 | 0.00084891
16 | 0.0030606 | 0.00076706
17 | 0.023543 | 0.0059005
18 | 0.0094928 | 0.0023791

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1