## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-18_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-18_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_243-18_0_5_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_243-18_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_243-18_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_243-18_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_243-18_0_5_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_243-18_0_5_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_243-18_0_5_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_243-18_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_243-18_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_243-18_0_5_node_46 | 0.4 | n |  | TRUE
12 | bus_LV_243-18_0_5_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_243-18_0_5_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_243-18_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_243-18_0_5_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_243-18_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_243-18_0_5_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_243-18_0_5_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_243-18_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_243-18_0_5_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_243-18_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_243-18_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_243-18_0_5_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_243-18_0_5_node_43 | 0.4 | n |  | TRUE
25 | bus_LV_243-18_0_5_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_243-18_0_5_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_243-18_0_5_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_243-18_0_5_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_243-18_0_5_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_243-18_0_5_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_243-18_0_5_node_49 | 0.4 | n |  | TRUE
32 | bus_LV_243-18_0_5_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_243-18_0_5_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_243-18_0_5_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_243-18_0_5_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_243-18_0_5_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_243-18_0_5_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_243-18_0_5_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_243-18_0_5_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_243-18_0_5_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_243-18_0_5_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_243-18_0_5_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_243-18_0_5_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_243-18_0_5_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_243-18_0_5_node_36 | 0.4 | n |  | TRUE
46 | bus_MV_516_0_node_159 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-18_0_5_load_0 | 0 | 0.058179 | 0.014581 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-18_0_5_load_20 | 6 | 0.056458 | 0.01415 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-18_0_5_load_47 | 8 | 0.0025079 | 0.00062853 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-18_0_5_load_46 | 11 | 0.0023191 | 0.00058122 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-18_0_5_load_19 | 12 | 0.027707 | 0.006944 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-18_0_5_load_18 | 13 | 0.03277 | 0.0082129 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-18_0_5_load_21 | 15 | 0.0069794 | 0.0017492 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-18_0_5_load_23 | 17 | 0.034158 | 0.0085608 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-18_0_5_load_22 | 18 | 0.0046317 | 0.0011608 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-18_0_5_load_28 | 23 | 0.00066675 | 0.0001671 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-18_0_5_load_43 | 24 | 0.0019355 | 0.00048509 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-18_0_5_load_30 | 26 | 0.0032846 | 0.00082321 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-18_0_5_load_33 | 27 | 0.0016237 | 0.00040693 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-18_0_5_load_35 | 28 | 0.029636 | 0.0074275 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-18_0_5_load_29 | 29 | 0.0067138 | 0.0016826 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-18_0_5_load_49 | 31 | 0.0057389 | 0.0014383 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-18_0_5_load_48 | 33 | 0.041276 | 0.010345 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-18_0_5_load_26 | 34 | 0.0020277 | 0.00050818 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-18_0_5_load_44 | 35 | 0.00058223 | 0.00014592 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_243-18_0_5_load_31 | 36 | 0.0010465 | 0.00026227 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_243-18_0_5_load_34 | 37 | 0.0012203 | 0.00030583 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_243-18_0_5_load_45 | 38 | 0.034721 | 0.0087018 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_243-18_0_5_load_27 | 40 | 0.020642 | 0.0051734 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_243-18_0_5_load_24 | 41 | 0.00073114 | 0.00018324 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_243-18_0_5_load_25 | 42 | 0.00069343 | 0.00017379 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_243-18_0_5_load_40 | 43 | 0.0024114 | 0.00060435 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_243-18_0_5_load_39 | 44 | 0.010869 | 0.0027239 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_243-18_0_5_load_36 | 45 | 0.016085 | 0.0040313 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-18_0_5_line_0 |  | 0 | 1 | 0.028003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-18_0_5_line_1 |  | 1 | 3 | 0.031473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_243-18_0_5_line_2 |  | 2 | 3 | 0.061375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_243-18_0_5_line_3 |  | 2 | 4 | 0.038992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_243-18_0_5_line_4 |  | 3 | 5 | 0.0098644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_243-18_0_5_line_5 |  | 3 | 6 | 0.033071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_243-18_0_5_line_6 |  | 4 | 7 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_243-18_0_5_line_7 |  | 4 | 8 | 0.0352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_243-18_0_5_line_8 |  | 5 | 13 | 0.040363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_243-18_0_5_line_9 |  | 6 | 14 | 0.0092962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_243-18_0_5_line_10 |  | 7 | 28 | 0.021608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-18_0_5_line_11 |  | 9 | 10 | 0.1292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_243-18_0_5_line_12 |  | 9 | 11 | 0.0080959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_243-18_0_5_line_13 |  | 10 | 12 | 0.036342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_243-18_0_5_line_14 |  | 10 | 13 | 0.026768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_243-18_0_5_line_15 |  | 14 | 15 | 0.029881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_243-18_0_5_line_16 |  | 14 | 16 | 0.03326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_243-18_0_5_line_17 |  | 15 | 29 | 0.01931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_243-18_0_5_line_18 |  | 16 | 17 | 0.039335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-18_0_5_line_19 |  | 16 | 18 | 0.088398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-18_0_5_line_20 |  | 19 | 20 | 0.061651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_243-18_0_5_line_21 |  | 19 | 21 | 0.048276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-18_0_5_line_22 |  | 19 | 22 | 0.058554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_243-18_0_5_line_23 |  | 19 | 23 | 0.001651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_243-18_0_5_line_24 |  | 20 | 24 | 0.02915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_243-18_0_5_line_25 |  | 21 | 27 | 0.020466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_243-18_0_5_line_26 |  | 22 | 25 | 0.048201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-18_0_5_line_27 |  | 22 | 26 | 0.049174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_243-18_0_5_line_28 |  | 23 | 34 | 0.021113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_243-18_0_5_line_29 |  | 24 | 35 | 0.0256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_243-18_0_5_line_30 |  | 25 | 32 | 0.05649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_243-18_0_5_line_31 |  | 26 | 36 | 0.0055415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_243-18_0_5_line_32 |  | 27 | 37 | 0.03536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_243-18_0_5_line_33 |  | 28 | 45 | 0.028493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_243-18_0_5_line_34 |  | 29 | 40 | 0.024446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_243-18_0_5_line_35 |  | 30 | 31 | 0.10648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_243-18_0_5_line_36 |  | 30 | 32 | 0.085553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_243-18_0_5_line_37 |  | 31 | 33 | 0.034767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_243-18_0_5_line_38 |  | 32 | 43 | 0.010882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_243-18_0_5_line_39 |  | 34 | 41 | 0.026928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_243-18_0_5_line_40 |  | 38 | 39 | 0.059012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_243-18_0_5_line_41 |  | 39 | 45 | 0.019521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_243-18_0_5_line_42 |  | 40 | 42 | 0.041707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_243-18_0_5_line_43 |  | 41 | 42 | 0.021609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_243-18_0_5_line_44 |  | 43 | 44 | 0.030064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-18_0_5_trafo_9 | 0.63 MVA 20/0.4 kV | 46 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2672677.1155 | 1251809.0487 | 2672675.6772 | 1251807.5522 | 2672672.9866 | 1251804.7728 | 2672666.8729 | 1251804.164 | 2672655.3512 | 1251815.1429
1 | 2672700.5084 | 1251787.9203 | 2672677.1155 | 1251809.0487
2 | 2672657.2143 | 1251744.2911 | 2672700.5084 | 1251787.9203
3 | 2672655.7833 | 1251716.9648 | 2672645.3581 | 1251726.9554 | 2672642.5939 | 1251729.5567 | 2672657.2143 | 1251744.2911
4 | 2672700.5084 | 1251787.9203 | 2672704.0422 | 1251791.4884 | 2672707.3194 | 1251795.0534
5 | 2672700.5084 | 1251787.9203 | 2672724.6934 | 1251765.3644
6 | 2672667.0634 | 1251706.2064 | 2672657.8379 | 1251714.9886 | 2672655.7833 | 1251716.9648
7 | 2672655.7833 | 1251716.9648 | 2672675.9196 | 1251720.7478 | 2672684.627 | 1251725.2801 | 2672686.1755 | 1251725.7994 | 2672687.8051 | 1251725.8528 | 2672689.3803 | 1251725.4274
8 | 2672707.3194 | 1251795.0534 | 2672677.1791 | 1251821.9004
9 | 2672731.4918 | 1251759.0239 | 2672724.6934 | 1251765.3644
10 | 2672667.0634 | 1251706.2064 | 2672678.809 | 1251695.0312 | 2672682.7026 | 1251691.2957
11 | 2672570.4009 | 1251910.5481 | 2672599.2484 | 1251912.9364 | 2672604.1653 | 1251905.8804 | 2672608.3112 | 1251900.7719 | 2672605.358 | 1251891.707 | 2672605.7171 | 1251886.4298 | 2672606.6554 | 1251882.5384 | 2672627.6609 | 1251864.6384 | 2672631.5199 | 1251861.3833 | 2672657.191 | 1251839.7044
12 | 2672570.4009 | 1251910.5481 | 2672562.9536 | 1251913.7231
13 | 2672657.191 | 1251839.7044 | 2672681.3123 | 1251866.8873
14 | 2672657.191 | 1251839.7044 | 2672677.1791 | 1251821.9004
15 | 2672731.4918 | 1251759.0239 | 2672753.3567 | 1251738.657
16 | 2672731.4918 | 1251759.0239 | 2672734.9426 | 1251762.5911 | 2672738.3064 | 1251765.868 | 2672741.5012 | 1251762.616 | 2672755.5768 | 1251749.7906
17 | 2672767.4862 | 1251725.4955 | 2672753.3567 | 1251738.657
18 | 2672755.5768 | 1251749.7906 | 2672784.2865 | 1251722.9017
19 | 2672755.5768 | 1251749.7906 | 2672761.842 | 1251757.1173 | 2672767.3078 | 1251756.3949 | 2672788.6887 | 1251746.7171 | 2672816.8913 | 1251737.1677 | 2672832.3953 | 1251724.534
20 | 2672836.6677 | 1251673.8426 | 2672833.5232 | 1251670.5349 | 2672871.1934 | 1251635.0388 | 2672867.4969 | 1251631.2017
21 | 2672854.0206 | 1251601.4033 | 2672867.059 | 1251609.1248 | 2672879.303 | 1251616.9921 | 2672877.3838 | 1251620.2264 | 2672874.1606 | 1251624.5455 | 2672867.4969 | 1251631.2017
22 | 2672867.4969 | 1251631.2017 | 2672874.1606 | 1251624.5455 | 2672877.3838 | 1251620.2264 | 2672879.303 | 1251616.9921 | 2672884.8566 | 1251620.1961 | 2672910.5325 | 1251641.8275
23 | 2672867.4969 | 1251631.2017 | 2672866.298 | 1251632.3368
24 | 2672836.6677 | 1251673.8426 | 2672856.746 | 1251694.9757
25 | 2672854.0206 | 1251601.4033 | 2672840.6253 | 1251616.8764
26 | 2672910.5325 | 1251641.8275 | 2672948.4776 | 1251671.6939
27 | 2672910.5325 | 1251641.8275 | 2672897.342 | 1251660.5789 | 2672891.8943 | 1251673.9216 | 2672884.9179 | 1251683.4826
28 | 2672850.9661 | 1251646.8523 | 2672866.298 | 1251632.3368
29 | 2672874.3789 | 1251713.5349 | 2672856.746 | 1251694.9757
30 | 2672948.4776 | 1251671.6939 | 2672963.8116 | 1251686.0486 | 2672984.9338 | 1251714.5627
31 | 2672884.9179 | 1251683.4826 | 2672881.6515 | 1251687.9592
32 | 2672840.6253 | 1251616.8764 | 2672838.6383 | 1251619.1716 | 2672815.2814 | 1251641.5163
33 | 2672682.7026 | 1251691.2957 | 2672703.2628 | 1251671.5697
34 | 2672767.4862 | 1251725.4955 | 2672774.0117 | 1251719.4171 | 2672785.3173 | 1251708.773
35 | 2672984.557 | 1251789.2345 | 2672971.6876 | 1251818.6863 | 2672967.2834 | 1251833.0981 | 2672951.8479 | 1251890.3191
36 | 2672984.557 | 1251789.2345 | 2672998.5331 | 1251766.1454 | 2673001.3531 | 1251761.4767 | 2673003.5009 | 1251755.6212 | 2673004.3151 | 1251750.8055 | 2673004.2957 | 1251747.4806 | 2673002.7911 | 1251741.5689 | 2673000.4209 | 1251735.4575 | 2672984.9338 | 1251714.5627
37 | 2672942.793 | 1251923.8863 | 2672951.8479 | 1251890.3191
38 | 2672984.9338 | 1251714.5627 | 2672979.0958 | 1251718.527 | 2672975.5988 | 1251719.329 | 2672975.3637 | 1251719.2926
39 | 2672850.9661 | 1251646.8523 | 2672831.4117 | 1251665.3654
40 | 2672717.3492 | 1251658.0549 | 2672726.0375 | 1251650.6228 | 2672760.4887 | 1251617.8079
41 | 2672717.3492 | 1251658.0549 | 2672703.2628 | 1251671.5697
42 | 2672815.6837 | 1251680.1832 | 2672785.3173 | 1251708.773
43 | 2672815.6837 | 1251680.1832 | 2672829.5268 | 1251667.15 | 2672831.4117 | 1251665.3654
44 | 2672945.6535 | 1251714.6903 | 2672945.6535 | 1251714.6903 | 2672975.3637 | 1251719.2926

## bus_geodata
| x | y | coords
0 | 2672655.3512 | 1251815.1429
1 | 2672677.1155 | 1251809.0487
2 | 2672657.2143 | 1251744.2911
3 | 2672700.5084 | 1251787.9203
4 | 2672655.7833 | 1251716.9648
5 | 2672707.3194 | 1251795.0534
6 | 2672724.6934 | 1251765.3644
7 | 2672667.0634 | 1251706.2064
8 | 2672689.3803 | 1251725.4274
9 | 2672570.4009 | 1251910.5481
10 | 2672657.191 | 1251839.7044
11 | 2672562.9536 | 1251913.7231
12 | 2672681.3123 | 1251866.8873
13 | 2672677.1791 | 1251821.9004
14 | 2672731.4918 | 1251759.0239
15 | 2672753.3567 | 1251738.657
16 | 2672755.5768 | 1251749.7906
17 | 2672784.2865 | 1251722.9017
18 | 2672832.3953 | 1251724.534
19 | 2672867.4969 | 1251631.2017
20 | 2672836.6677 | 1251673.8426
21 | 2672854.0206 | 1251601.4033
22 | 2672910.5325 | 1251641.8275
23 | 2672866.298 | 1251632.3368
24 | 2672856.746 | 1251694.9757
25 | 2672948.4776 | 1251671.6939
26 | 2672884.9179 | 1251683.4826
27 | 2672840.6253 | 1251616.8764
28 | 2672682.7026 | 1251691.2957
29 | 2672767.4862 | 1251725.4955
30 | 2672984.557 | 1251789.2345
31 | 2672951.8479 | 1251890.3191
32 | 2672984.9338 | 1251714.5627
33 | 2672942.793 | 1251923.8863
34 | 2672850.9661 | 1251646.8523
35 | 2672874.3789 | 1251713.5349
36 | 2672881.6515 | 1251687.9592
37 | 2672815.2814 | 1251641.5163
38 | 2672760.4887 | 1251617.8079
39 | 2672717.3492 | 1251658.0549
40 | 2672785.3173 | 1251708.773
41 | 2672831.4117 | 1251665.3654
42 | 2672815.6837 | 1251680.1832
43 | 2672975.3637 | 1251719.2926
44 | 2672945.6535 | 1251714.6903
45 | 2672703.2628 | 1251671.5697
46 | 2672752.5113 | 1251746.1948

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98922 | -0.20667 | 0.058179 | 0.014581
1 | 0.99071 | -0.17769 | 0 | 0
2 | 0.98767 | -0.23577 | 0 | 0
3 | 0.99239 | -0.14523 | 0 | 0
4 | 0.98468 | -0.29374 | 0 | 0
5 | 0.99182 | -0.1562 | 0 | 0
6 | 0.99549 | -0.085734 | 0.056458 | 0.01415
7 | 0.98352 | -0.31627 | 0 | 0
8 | 0.9846 | -0.29533 | 0.0025079 | 0.00062853
9 | 0.98848 | -0.22089 | 0 | 0
10 | 0.98876 | -0.21554 | 0 | 0
11 | 0.98847 | -0.22122 | 0.0023191 | 0.00058122
12 | 0.98783 | -0.23351 | 0.027707 | 0.006944
13 | 0.9895 | -0.20122 | 0.03277 | 0.0082129
14 | 0.99623 | -0.071552 | 0 | 0
15 | 0.99524 | -0.090546 | 0.0069794 | 0.0017492
16 | 1 | 0 | -0.41416 | -0.10526
17 | 0.99878 | -0.023447 | 0.034158 | 0.0085608
18 | 0.99963 | -0.0071412 | 0.0046317 | 0.0011608
19 | 0.99006 | -0.18911 | 0 | 0
20 | 0.98992 | -0.19187 | 0 | 0
21 | 0.98993 | -0.19155 | 0 | 0
22 | 0.98653 | -0.25665 | 0 | 0
23 | 0.99017 | -0.18705 | 0.00066675 | 0.0001671
24 | 0.98985 | -0.19318 | 0.0019355 | 0.00048509
25 | 0.98382 | -0.30885 | 0 | 0
26 | 0.98633 | -0.26046 | 0.0032846 | 0.00082321
27 | 0.98988 | -0.19259 | 0.0016237 | 0.00040693
28 | 0.98191 | -0.34765 | 0.029636 | 0.0074275
29 | 0.99463 | -0.10205 | 0.0067138 | 0.0016826
30 | 0.97688 | -0.44358 | 0 | 0
31 | 0.97221 | -0.53546 | 0.0057389 | 0.0014383
32 | 0.98064 | -0.37039 | 0 | 0
33 | 0.97087 | -0.56196 | 0.041276 | 0.010345
34 | 0.99155 | -0.16056 | 0.0020277 | 0.00050818
35 | 0.98983 | -0.19344 | 0.00058223 | 0.00014592
36 | 0.98633 | -0.26057 | 0.0010465 | 0.00026227
37 | 0.98984 | -0.19336 | 0.0012203 | 0.00030583
38 | 0.97804 | -0.42341 | 0.034721 | 0.0087018
39 | 0.97994 | -0.38615 | 0 | 0
40 | 0.99392 | -0.11567 | 0.020642 | 0.0051734
41 | 0.99247 | -0.14322 | 0.00073114 | 0.00018324
42 | 0.99296 | -0.13387 | 0.00069343 | 0.00017379
43 | 0.98051 | -0.37301 | 0.0024114 | 0.00060435
44 | 0.98021 | -0.37894 | 0.010869 | 0.0027239
45 | 0.98057 | -0.37385 | 0.016085 | 0.0040313
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.058179 | -0.014581 | 0.05826 | 0.014632 | 8.0427e-05 | 5.1114e-05 | 0.087516 | 0.087515 | 0.087516 | 0.98922 | -0.20667 | 0.99071 | -0.17769 | 24.0428
1 | -0.05826 | -0.014632 | 0.05835 | 0.01469 | 9.0394e-05 | 5.7446e-05 | 0.087515 | 0.087515 | 0.087515 | 0.99071 | -0.17769 | 0.99239 | -0.14523 | 24.0427
2 | -0.083536 | -0.021161 | 0.083901 | 0.021394 | 0.00036501 | 0.00023282 | 0.12593 | 0.12593 | 0.12593 | 0.98767 | -0.23577 | 0.99239 | -0.14523 | 34.5973
3 | 0.083536 | 0.021161 | -0.083304 | -0.021013 | 0.0002319 | 0.00014792 | 0.12593 | 0.12593 | 0.12593 | 0.98767 | -0.23577 | 0.98468 | -0.29374 | 34.5973
4 | 0.063009 | 0.015871 | -0.062976 | -0.01585 | 3.3038e-05 | 2.1017e-05 | 0.094506 | 0.094506 | 0.094506 | 0.99239 | -0.14523 | 0.99182 | -0.1562 | 25.9631
5 | -0.20526 | -0.051955 | 0.20585 | 0.052331 | 0.00058806 | 0.0003755 | 0.30795 | 0.30795 | 0.30795 | 0.99239 | -0.14523 | 0.99549 | -0.085734 | 42.3014
6 | 0.080796 | 0.020385 | -0.080709 | -0.02033 | 8.7082e-05 | 5.5535e-05 | 0.12214 | 0.12214 | 0.12214 | 0.98468 | -0.29374 | 0.98352 | -0.31627 | 33.5561
7 | 0.002508 | 0.0006282 | -0.0025079 | -0.00062853 | 1.8961e-07 | -3.2637e-07 | 0.0037899 | 0.0037901 | 0.0037901 | 0.98468 | -0.29374 | 0.9846 | -0.29533 | 1.0412
8 | 0.062976 | 0.01585 | -0.062841 | -0.015764 | 0.00013519 | 8.6e-05 | 0.094506 | 0.094506 | 0.094506 | 0.99182 | -0.1562 | 0.9895 | -0.20122 | 25.9632
9 | -0.26231 | -0.066481 | 0.26249 | 0.066595 | 0.00017888 | 0.00011412 | 0.39235 | 0.39235 | 0.39235 | 0.99549 | -0.085734 | 0.99623 | -0.071552 | 35.9291
10 | 0.080709 | 0.02033 | -0.080588 | -0.020253 | 0.00012089 | 7.7097e-05 | 0.12214 | 0.12214 | 0.12214 | 0.98352 | -0.31627 | 0.98191 | -0.34765 | 33.5562
11 | -0.0023191 | -0.00058114 | 0.0023197 | 0.00057986 | 5.9038e-07 | -1.2788e-06 | 0.0034911 | 0.0034905 | 0.0034911 | 0.98848 | -0.22089 | 0.98876 | -0.21554 | 0.95908
12 | 0.0023191 | 0.00058114 | -0.0023191 | -0.00058122 | 3.7001e-08 | -8.0097e-08 | 0.0034911 | 0.0034911 | 0.0034911 | 0.98848 | -0.22089 | 0.98847 | -0.22122 | 0.95909
13 | 0.027731 | 0.0069587 | -0.027707 | -0.006944 | 2.3739e-05 | 1.4727e-05 | 0.041736 | 0.041736 | 0.041736 | 0.98876 | -0.21554 | 0.98783 | -0.23351 | 11.466
14 | -0.03005 | -0.0075386 | 0.030071 | 0.0075514 | 2.0532e-05 | 1.2797e-05 | 0.045226 | 0.045226 | 0.045226 | 0.98876 | -0.21554 | 0.9895 | -0.20122 | 12.4248
15 | 0.1099 | 0.028099 | -0.1098 | -0.028036 | 0.0001009 | 6.3408e-05 | 0.16436 | 0.16436 | 0.16436 | 0.99623 | -0.071552 | 0.99524 | -0.090546 | 15.0509
16 | -0.37239 | -0.094694 | 0.37368 | 0.095517 | 0.0012885 | 0.00082333 | 0.5567 | 0.5567 | 0.5567 | 0.99623 | -0.071552 | 1 | 0 | 50.9799
17 | 0.10282 | 0.026287 | -0.10277 | -0.026251 | 5.7185e-05 | 3.5846e-05 | 0.15392 | 0.15392 | 0.15392 | 0.99524 | -0.090546 | 0.99463 | -0.10205 | 14.0953
18 | 0.034196 | 0.0085847 | -0.034158 | -0.0085608 | 3.8201e-05 | 2.3933e-05 | 0.05089 | 0.05089 | 0.05089 | 1 | 0 | 0.99878 | -0.023447 | 13.9807
19 | 0.0046333 | 0.0011607 | -0.0046317 | -0.0011608 | 1.5757e-06 | -1.5084e-07 | 0.0068943 | 0.0068947 | 0.0068947 | 1 | 0 | 0.99963 | -0.0071412 | 1.8941
20 | 0.0025183 | 0.00062983 | -0.0025179 | -0.00063041 | 3.3112e-07 | -5.8078e-07 | 0.0037844 | 0.0037847 | 0.0037847 | 0.99006 | -0.18911 | 0.98992 | -0.19187 | 1.0397
21 | 0.0028445 | 0.00071175 | -0.0028441 | -0.00071216 | 3.3082e-07 | -4.0901e-07 | 0.0042747 | 0.0042749 | 0.0042749 | 0.99006 | -0.18911 | 0.98993 | -0.19155 | 1.1744
22 | 0.065605 | 0.016817 | -0.065391 | -0.016681 | 0.00021406 | 0.00013625 | 0.098736 | 0.098736 | 0.098736 | 0.99006 | -0.18911 | 0.98653 | -0.25665 | 27.1254
23 | -0.070968 | -0.018159 | 0.070975 | 0.018163 | 7.0614e-06 | 4.4981e-06 | 0.1068 | 0.1068 | 0.1068 | 0.99006 | -0.18911 | 0.99017 | -0.18705 | 29.3393
24 | 0.0025179 | 0.00063041 | -0.0025178 | -0.00063069 | 1.5658e-07 | -2.7452e-07 | 0.0037847 | 0.0037848 | 0.0037848 | 0.98992 | -0.19187 | 0.98985 | -0.19318 | 1.0398
25 | 0.0028441 | 0.00071216 | -0.002844 | -0.00071234 | 1.4026e-07 | -1.7334e-07 | 0.0042749 | 0.004275 | 0.004275 | 0.98993 | -0.19155 | 0.98988 | -0.19259 | 1.1745
26 | 0.061059 | 0.015596 | -0.060906 | -0.015498 | 0.00015367 | 9.7732e-05 | 0.092203 | 0.092203 | 0.092203 | 0.98653 | -0.25665 | 0.98382 | -0.30885 | 25.3305
27 | 0.0043319 | 0.0010853 | -0.0043311 | -0.0010854 | 7.8724e-07 | -1.239e-07 | 0.0065338 | 0.006534 | 0.006534 | 0.98653 | -0.25665 | 0.98633 | -0.26046 | 1.7951
28 | -0.071642 | -0.018331 | 0.071734 | 0.018389 | 9.2002e-05 | 5.8609e-05 | 0.1078 | 0.1078 | 0.1078 | 0.99017 | -0.18705 | 0.99155 | -0.16056 | 29.6146
29 | 0.00058224 | 0.0001456 | -0.00058223 | -0.00014592 | 7.3536e-09 | -3.2436e-07 | 0.00087516 | 0.00087527 | 0.00087527 | 0.98985 | -0.19318 | 0.98983 | -0.19344 | 0.24046
30 | 0.060906 | 0.015498 | -0.060725 | -0.015384 | 0.00018009 | 0.00011454 | 0.092203 | 0.092203 | 0.092203 | 0.98382 | -0.30885 | 0.98064 | -0.37039 | 25.3306
31 | 0.0010465 | 0.0002622 | -0.0010465 | -0.00026227 | 5.1793e-09 | -6.7412e-08 | 0.0015787 | 0.0015787 | 0.0015787 | 0.98633 | -0.26046 | 0.98633 | -0.26057 | 0.43372
32 | 0.0012203 | 0.00030541 | -0.0012203 | -0.00030583 | 4.4618e-08 | -4.2598e-07 | 0.0018343 | 0.0018345 | 0.0018345 | 0.98988 | -0.19259 | 0.98984 | -0.19336 | 0.50397
33 | 0.050952 | 0.012825 | -0.050888 | -0.012785 | 6.3735e-05 | 4.043e-05 | 0.077233 | 0.077233 | 0.077233 | 0.98191 | -0.34765 | 0.98057 | -0.37385 | 21.218
34 | 0.096054 | 0.024568 | -0.09599 | -0.024529 | 6.3255e-05 | 3.9532e-05 | 0.14388 | 0.14388 | 0.14388 | 0.99463 | -0.10205 | 0.99392 | -0.11567 | 13.1756
35 | 0.047274 | 0.011947 | -0.047067 | -0.011816 | 0.00020725 | 0.00013131 | 0.072045 | 0.072046 | 0.072046 | 0.97688 | -0.44358 | 0.97221 | -0.53546 | 19.7928
36 | -0.047274 | -0.011947 | 0.047441 | 0.012053 | 0.00016652 | 0.0001055 | 0.072045 | 0.072045 | 0.072045 | 0.97688 | -0.44358 | 0.98064 | -0.37039 | 19.7926
37 | 0.041328 | 0.010378 | -0.041276 | -0.010345 | 5.2178e-05 | 3.2963e-05 | 0.063262 | 0.063262 | 0.063262 | 0.97221 | -0.53546 | 0.97087 | -0.56196 | 17.3797
38 | 0.013285 | 0.0033308 | -0.013283 | -0.0033299 | 1.6584e-06 | 9.2408e-07 | 0.020159 | 0.020159 | 0.020159 | 0.98064 | -0.37039 | 0.98051 | -0.37301 | 5.5381
39 | -0.073761 | -0.018897 | 0.073823 | 0.018936 | 6.2029e-05 | 3.9003e-05 | 0.11084 | 0.11084 | 0.11084 | 0.99155 | -0.16056 | 0.99247 | -0.14322 | 15.2253
40 | -0.034721 | -0.0087018 | 0.034782 | 0.0087406 | 6.1751e-05 | 3.8778e-05 | 0.052825 | 0.052824 | 0.052825 | 0.97804 | -0.42341 | 0.97994 | -0.38615 | 14.5123
41 | -0.034782 | -0.0087406 | 0.034803 | 0.0087534 | 2.0427e-05 | 1.2827e-05 | 0.052824 | 0.052824 | 0.052824 | 0.97994 | -0.38615 | 0.98057 | -0.37385 | 14.5122
42 | 0.075348 | 0.019355 | -0.075282 | -0.019314 | 6.654e-05 | 4.0965e-05 | 0.11297 | 0.11297 | 0.11297 | 0.99392 | -0.11567 | 0.99296 | -0.13387 | 10.3457
43 | -0.074555 | -0.01912 | 0.074588 | 0.01914 | 3.3844e-05 | 2.0822e-05 | 0.11194 | 0.11194 | 0.11194 | 0.99247 | -0.14322 | 0.99296 | -0.13387 | 10.2505
44 | 0.010872 | 0.0027255 | -0.010869 | -0.0027239 | 3.0691e-06 | 1.5851e-06 | 0.016499 | 0.016499 | 0.016499 | 0.98051 | -0.37301 | 0.98021 | -0.37894 | 4.5328

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41416 | 0.10526

## res_load
| p_mw | q_mvar
0 | 0.058179 | 0.014581
1 | 0.056458 | 0.01415
2 | 0.0025079 | 0.00062853
3 | 0.0023191 | 0.00058122
4 | 0.027707 | 0.006944
5 | 0.03277 | 0.0082129
6 | 0.0069794 | 0.0017492
7 | 0.034158 | 0.0085608
8 | 0.0046317 | 0.0011608
9 | 0.00066675 | 0.0001671
10 | 0.0019355 | 0.00048509
11 | 0.0032846 | 0.00082321
12 | 0.0016237 | 0.00040693
13 | 0.029636 | 0.0074275
14 | 0.0067138 | 0.0016826
15 | 0.0057389 | 0.0014383
16 | 0.041276 | 0.010345
17 | 0.0020277 | 0.00050818
18 | 0.00058223 | 0.00014592
19 | 0.0010465 | 0.00026227
20 | 0.0012203 | 0.00030583
21 | 0.034721 | 0.0087018
22 | 0.020642 | 0.0051734
23 | 0.00073114 | 0.00018324
24 | 0.00069343 | 0.00017379
25 | 0.0024114 | 0.00060435
26 | 0.010869 | 0.0027239
27 | 0.016085 | 0.0040313

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1