## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-19_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-19_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_243-19_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_243-19_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_243-19_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_243-19_0_6_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_243-19_0_6_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_243-19_0_6_node_109 | 0.4 | n |  | TRUE
8 | bus_LV_243-19_0_6_node_92 | 0.4 | n |  | TRUE
9 | bus_LV_243-19_0_6_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_243-19_0_6_node_117 | 0.4 | n |  | TRUE
11 | bus_LV_243-19_0_6_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_243-19_0_6_node_48 | 0.4 | n |  | TRUE
13 | bus_LV_243-19_0_6_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_243-19_0_6_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_243-19_0_6_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_243-19_0_6_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_243-19_0_6_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_243-19_0_6_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_243-19_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_243-19_0_6_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_243-19_0_6_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_243-19_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_243-19_0_6_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_243-19_0_6_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_243-19_0_6_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_243-19_0_6_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_243-19_0_6_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_243-19_0_6_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_243-19_0_6_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_243-19_0_6_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_243-19_0_6_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_243-19_0_6_node_51 | 0.4 | n |  | TRUE
33 | bus_LV_243-19_0_6_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_243-19_0_6_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_243-19_0_6_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_243-19_0_6_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_243-19_0_6_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_243-19_0_6_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_243-19_0_6_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_243-19_0_6_node_57 | 0.4 | n |  | TRUE
41 | bus_LV_243-19_0_6_node_61 | 0.4 | n |  | TRUE
42 | bus_LV_243-19_0_6_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_243-19_0_6_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_243-19_0_6_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_243-19_0_6_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_243-19_0_6_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_243-19_0_6_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_243-19_0_6_node_62 | 0.4 | n |  | TRUE
49 | bus_LV_243-19_0_6_node_110 | 0.4 | n |  | TRUE
50 | bus_LV_243-19_0_6_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_243-19_0_6_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_243-19_0_6_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_243-19_0_6_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_243-19_0_6_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_243-19_0_6_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_243-19_0_6_node_127 | 0.4 | n |  | TRUE
57 | bus_LV_243-19_0_6_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_243-19_0_6_node_81 | 0.4 | n |  | TRUE
59 | bus_LV_243-19_0_6_node_79 | 0.4 | n |  | TRUE
60 | bus_LV_243-19_0_6_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_243-19_0_6_node_124 | 0.4 | n |  | TRUE
62 | bus_LV_243-19_0_6_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_243-19_0_6_node_122 | 0.4 | n |  | TRUE
64 | bus_LV_243-19_0_6_node_84 | 0.4 | n |  | TRUE
65 | bus_LV_243-19_0_6_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_243-19_0_6_node_78 | 0.4 | n |  | TRUE
67 | bus_LV_243-19_0_6_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_243-19_0_6_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_243-19_0_6_node_83 | 0.4 | n |  | TRUE
70 | bus_LV_243-19_0_6_node_82 | 0.4 | n |  | TRUE
71 | bus_LV_243-19_0_6_node_87 | 0.4 | n |  | TRUE
72 | bus_LV_243-19_0_6_node_121 | 0.4 | n |  | TRUE
73 | bus_LV_243-19_0_6_node_126 | 0.4 | n |  | TRUE
74 | bus_LV_243-19_0_6_node_80 | 0.4 | n |  | TRUE
75 | bus_LV_243-19_0_6_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_243-19_0_6_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_243-19_0_6_node_125 | 0.4 | n |  | TRUE
78 | bus_LV_243-19_0_6_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_243-19_0_6_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_243-19_0_6_node_119 | 0.4 | n |  | TRUE
81 | bus_LV_243-19_0_6_node_120 | 0.4 | n |  | TRUE
82 | bus_LV_243-19_0_6_node_85 | 0.4 | n |  | TRUE
83 | bus_LV_243-19_0_6_node_53 | 0.4 | n |  | TRUE
84 | bus_LV_243-19_0_6_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_243-19_0_6_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_243-19_0_6_node_116 | 0.4 | n |  | TRUE
87 | bus_LV_243-19_0_6_node_115 | 0.4 | n |  | TRUE
88 | bus_LV_243-19_0_6_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_243-19_0_6_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_243-19_0_6_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_243-19_0_6_node_65 | 0.4 | n |  | TRUE
92 | bus_LV_243-19_0_6_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_243-19_0_6_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_243-19_0_6_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_243-19_0_6_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_243-19_0_6_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_243-19_0_6_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_243-19_0_6_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_243-19_0_6_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_243-19_0_6_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_243-19_0_6_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_243-19_0_6_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_243-19_0_6_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_243-19_0_6_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_243-19_0_6_node_113 | 0.4 | n |  | TRUE
106 | bus_LV_243-19_0_6_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_243-19_0_6_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_243-19_0_6_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_243-19_0_6_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_243-19_0_6_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_243-19_0_6_node_118 | 0.4 | n |  | TRUE
112 | bus_LV_243-19_0_6_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_243-19_0_6_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_243-19_0_6_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_243-19_0_6_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_243-19_0_6_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_243-19_0_6_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_243-19_0_6_node_108 | 0.4 | n |  | TRUE
119 | bus_MV_516_0_node_9 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-19_0_6_load_0 | 0 | 0.015622 | 0.0039152 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-19_0_6_load_1 | 1 | 0.0091103 | 0.0022833 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-19_0_6_load_5 | 4 | 0.0088467 | 0.0022172 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-19_0_6_load_3 | 5 | 0.0024307 | 0.0006092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-19_0_6_load_60 | 6 | 0.017588 | 0.0044079 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-19_0_6_load_92 | 8 | 0.0051218 | 0.0012836 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-19_0_6_load_59 | 9 | 0.0021335 | 0.00053471 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-19_0_6_load_117 | 10 | 0.021112 | 0.0052912 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-19_0_6_load_49 | 11 | 0.021684 | 0.0054344 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-19_0_6_load_6 | 14 | 0.0061606 | 0.001544 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-19_0_6_load_7 | 15 | 0.010465 | 0.0026228 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-19_0_6_load_9 | 17 | 0.0069891 | 0.0017516 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-19_0_6_load_10 | 18 | 0.0016116 | 0.00040391 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-19_0_6_load_11 | 19 | 0.013383 | 0.0033542 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-19_0_6_load_31 | 20 | 0.0076033 | 0.0019056 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-19_0_6_load_24 | 21 | 0.010565 | 0.002648 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-19_0_6_load_30 | 23 | 0.0039627 | 0.00099313 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-19_0_6_load_23 | 24 | 0.007148 | 0.0017915 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-19_0_6_load_58 | 25 | 0.0037747 | 0.00094603 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_243-19_0_6_load_13 | 26 | 0.0026933 | 0.000675 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_243-19_0_6_load_12 | 27 | 0.0056493 | 0.0014159 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_243-19_0_6_load_16 | 29 | 0.009976 | 0.0025002 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_243-19_0_6_load_17 | 30 | 0.0029531 | 0.00074011 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_243-19_0_6_load_47 | 31 | 0.0063893 | 0.0016013 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_243-19_0_6_load_51 | 32 | 0.0030048 | 0.00075308 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_243-19_0_6_load_54 | 33 | 0.012008 | 0.0030096 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_243-19_0_6_load_52 | 34 | 0.0023386 | 0.00058612 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_243-19_0_6_load_18 | 35 | 0.002927 | 0.00073356 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_243-19_0_6_load_19 | 36 | 0.0065068 | 0.0016308 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_243-19_0_6_load_20 | 37 | 0.0027759 | 0.0006957 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_243-19_0_6_load_21 | 38 | 0.0082225 | 0.0020608 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_243-19_0_6_load_22 | 39 | 0.0096512 | 0.0024188 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_243-19_0_6_load_61 | 41 | 0.0075405 | 0.0018898 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_243-19_0_6_load_26 | 44 | 0.0084679 | 0.0021223 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_243-19_0_6_load_33 | 47 | 0.0020662 | 0.00051783 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_243-19_0_6_load_62 | 48 | 0.0043667 | 0.0010944 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_243-19_0_6_load_110 | 49 | 0.015695 | 0.0039334 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_243-19_0_6_load_50 | 50 | 0.01776 | 0.004451 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_243-19_0_6_load_63 | 51 | 0.005478 | 0.0013729 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_243-19_0_6_load_32 | 52 | 0.011881 | 0.0029776 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_243-19_0_6_load_127 | 56 | 0.0016864 | 0.00042265 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_243-19_0_6_load_81 | 58 | 0.0048723 | 0.0012211 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_243-19_0_6_load_79 | 59 | 0.006051 | 0.0015165 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_243-19_0_6_load_122 | 63 | 0.0016428 | 0.00041172 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_243-19_0_6_load_84 | 64 | 0.019909 | 0.0049897 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_243-19_0_6_load_78 | 66 | 0.00051254 | 0.00012845 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_243-19_0_6_load_76 | 67 | 0.00098416 | 0.00024665 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_243-19_0_6_load_83 | 69 | 0.0035653 | 0.00089355 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_243-19_0_6_load_82 | 70 | 0.0043892 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_243-19_0_6_load_87 | 71 | 0.00021359 | 5.353e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_243-19_0_6_load_121 | 72 | 0.00037072 | 9.291e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_243-19_0_6_load_126 | 73 | 0.00088441 | 0.00022165 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_243-19_0_6_load_80 | 74 | 0.0039753 | 0.0009963 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_243-19_0_6_load_70 | 75 | 0.0010712 | 0.00026847 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_243-19_0_6_load_69 | 76 | 0.00097803 | 0.00024512 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_243-19_0_6_load_125 | 77 | 0.0034467 | 0.00086383 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_243-19_0_6_load_68 | 78 | 0.00040074 | 0.00010043 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_243-19_0_6_load_77 | 79 | 0.0070924 | 0.0017775 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_243-19_0_6_load_119 | 80 | 0.0089539 | 0.0022441 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_243-19_0_6_load_120 | 81 | 0.00032597 | 8.1695e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_243-19_0_6_load_85 | 82 | 0.0033109 | 0.0008298 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_243-19_0_6_load_53 | 83 | 0.0060304 | 0.0015114 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_243-19_0_6_load_55 | 84 | 0.0093097 | 0.0023332 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_243-19_0_6_load_56 | 85 | 0.0064645 | 0.0016201 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_243-19_0_6_load_116 | 86 | 0.0062452 | 0.0015652 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_243-19_0_6_load_115 | 87 | 0.0089051 | 0.0022318 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_243-19_0_6_load_64 | 88 | 0.0008238 | 0.00020646 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_243-19_0_6_load_75 | 89 | 0.00090656 | 0.00022721 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_243-19_0_6_load_73 | 90 | 0.0011139 | 0.00027917 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_243-19_0_6_load_65 | 91 | 0.0013923 | 0.00034894 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_243-19_0_6_load_66 | 92 | 0.006958 | 0.0017438 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_243-19_0_6_load_67 | 93 | 0.0020176 | 0.00050566 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_243-19_0_6_load_71 | 94 | 0.0077162 | 0.0019339 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_243-19_0_6_load_72 | 95 | 0.0065084 | 0.0016312 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_243-19_0_6_load_74 | 96 | 0.0085579 | 0.0021448 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_243-19_0_6_load_86 | 97 | 0.00090471 | 0.00022674 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_243-19_0_6_load_88 | 98 | 0.0075213 | 0.001885 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_243-19_0_6_load_89 | 99 | 0.018103 | 0.0045371 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_243-19_0_6_load_93 | 101 | 0.0035942 | 0.0009008 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_243-19_0_6_load_94 | 102 | 0.0027071 | 0.00067846 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_243-19_0_6_load_95 | 103 | 0.0022917 | 0.00057435 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_243-19_0_6_load_104 | 104 | 0.0015477 | 0.00038789 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_243-19_0_6_load_102 | 106 | 0.005473 | 0.0013717 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_243-19_0_6_load_112 | 107 | 0.008969 | 0.0022478 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_243-19_0_6_load_98 | 108 | 0.0047263 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_243-19_0_6_load_99 | 109 | 0.0089249 | 0.0022368 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_243-19_0_6_load_118 | 111 | 0.011465 | 0.0028735 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_243-19_0_6_load_100 | 112 | 0.0054577 | 0.0013678 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_243-19_0_6_load_106 | 113 | 0.0062033 | 0.0015547 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_243-19_0_6_load_107 | 114 | 0.0069434 | 0.0017402 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_243-19_0_6_load_101 | 115 | 0.011528 | 0.0028891 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_243-19_0_6_load_103 | 116 | 0.0058685 | 0.0014708 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_243-19_0_6_load_105 | 117 | 0.012094 | 0.003031 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-19_0_6_line_0 |  | 0 | 1 | 0.022532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-19_0_6_line_1 |  | 0 | 2 | 0.018654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_243-19_0_6_line_2 |  | 2 | 3 | 0.013141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_243-19_0_6_line_3 |  | 2 | 4 | 0.036366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_243-19_0_6_line_4 |  | 3 | 7 | 0.064714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_243-19_0_6_line_5 |  | 4 | 8 | 0.02985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_243-19_0_6_line_6 |  | 5 | 6 | 0.006682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_243-19_0_6_line_7 |  | 6 | 9 | 0.013987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_243-19_0_6_line_8 |  | 7 | 10 | 0.0037735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_243-19_0_6_line_9 |  | 8 | 13 | 0.023927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_243-19_0_6_line_10 |  | 9 | 40 | 0.048273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-19_0_6_line_11 |  | 10 | 110 | 0.016046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_243-19_0_6_line_12 |  | 11 | 12 | 0.039802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_243-19_0_6_line_13 |  | 12 | 50 | 0.012478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_243-19_0_6_line_14 |  | 12 | 31 | 0.024626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_243-19_0_6_line_15 |  | 13 | 101 | 0.031612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_243-19_0_6_line_16 |  | 13 | 102 | 0.019294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_243-19_0_6_line_17 |  | 13 | 99 | 0.036997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_243-19_0_6_line_18 |  | 14 | 15 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-19_0_6_line_19 |  | 14 | 16 | 0.013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-19_0_6_line_20 |  | 15 | 17 | 0.028337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_243-19_0_6_line_21 |  | 16 | 18 | 0.01227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-19_0_6_line_22 |  | 16 | 19 | 0.016104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_243-19_0_6_line_23 |  | 17 | 20 | 0.0022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_243-19_0_6_line_24 |  | 18 | 21 | 0.0018662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_243-19_0_6_line_25 |  | 19 | 22 | 0.039269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_243-19_0_6_line_26 |  | 20 | 23 | 0.019788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-19_0_6_line_27 |  | 21 | 24 | 0.0069333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_243-19_0_6_line_28 |  | 22 | 25 | 0.03398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_243-19_0_6_line_29 |  | 22 | 26 | 0.010728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_243-19_0_6_line_30 |  | 23 | 52 | 0.027381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_243-19_0_6_line_31 |  | 24 | 43 | 0.014855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_243-19_0_6_line_32 |  | 25 | 33 | 0.017426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_243-19_0_6_line_33 |  | 26 | 27 | 0.0090893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_243-19_0_6_line_34 |  | 27 | 28 | 0.021693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_243-19_0_6_line_35 |  | 28 | 29 | 0.022952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_243-19_0_6_line_36 |  | 28 | 30 | 0.013266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_243-19_0_6_line_37 |  | 29 | 31 | 0.021571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_243-19_0_6_line_38 |  | 30 | 32 | 0.0047724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_243-19_0_6_line_39 |  | 32 | 34 | 0.015362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_243-19_0_6_line_40 |  | 33 | 38 | 0.029919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_243-19_0_6_line_41 |  | 34 | 83 | 0.023554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_243-19_0_6_line_42 |  | 35 | 36 | 0.0053239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_243-19_0_6_line_43 |  | 35 | 37 | 0.025424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_243-19_0_6_line_44 |  | 36 | 38 | 0.020091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_243-19_0_6_line_45 |  | 37 | 39 | 0.010678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_243-19_0_6_line_46 |  | 39 | 40 | 0.016591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_243-19_0_6_line_47 |  | 40 | 41 | 0.018469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_243-19_0_6_line_48 |  | 40 | 42 | 0.034879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_243-19_0_6_line_49 |  | 41 | 86 | 0.0071523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_243-19_0_6_line_50 |  | 42 | 70 | 0.0098215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_243-19_0_6_line_51 |  | 43 | 44 | 0.013638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_243-19_0_6_line_52 |  | 44 | 45 | 0.013262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_243-19_0_6_line_53 |  | 45 | 46 | 0.052405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_243-19_0_6_line_54 |  | 45 | 47 | 0.027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_243-19_0_6_line_55 |  | 46 | 48 | 0.036449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_243-19_0_6_line_56 |  | 48 | 51 | 0.015904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_243-19_0_6_line_57 |  | 49 | 50 | 0.048428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_243-19_0_6_line_58 |  | 51 | 88 | 0.013465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_243-19_0_6_line_59 |  | 53 | 54 | 0.022533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_243-19_0_6_line_60 |  | 53 | 55 | 0.071765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_243-19_0_6_line_61 |  | 53 | 56 | 0.046004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_243-19_0_6_line_62 |  | 54 | 64 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_243-19_0_6_line_63 |  | 55 | 71 | 0.031728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_243-19_0_6_line_64 |  | 55 | 72 | 0.011051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_243-19_0_6_line_65 |  | 56 | 73 | 0.026108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_243-19_0_6_line_66 |  | 57 | 58 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_243-19_0_6_line_67 |  | 57 | 59 | 0.045934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_243-19_0_6_line_68 |  | 58 | 69 | 0.02331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_243-19_0_6_line_69 |  | 59 | 74 | 0.038397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_243-19_0_6_line_70 |  | 60 | 61 | 0.1531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_243-19_0_6_line_71 |  | 60 | 62 | 0.12457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_243-19_0_6_line_72 |  | 60 | 63 | 0.11241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_243-19_0_6_line_73 |  | 61 | 77 | 0.091518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_243-19_0_6_line_74 |  | 62 | 64 | 0.03501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_243-19_0_6_line_75 |  | 62 | 68 | 0.024337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_243-19_0_6_line_76 |  | 65 | 66 | 0.028408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_243-19_0_6_line_77 |  | 65 | 67 | 0.024944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_243-19_0_6_line_78 |  | 66 | 78 | 0.022122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_243-19_0_6_line_79 |  | 67 | 79 | 0.035607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_243-19_0_6_line_80 |  | 68 | 69 | 0.018486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_243-19_0_6_line_81 |  | 68 | 70 | 0.033086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_243-19_0_6_line_82 |  | 71 | 82 | 0.0018324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_243-19_0_6_line_83 |  | 72 | 81 | 0.0032566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_243-19_0_6_line_84 |  | 75 | 76 | 0.018655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_243-19_0_6_line_85 |  | 76 | 93 | 0.023695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_243-19_0_6_line_86 |  | 78 | 92 | 0.023093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_243-19_0_6_line_87 |  | 79 | 96 | 0.027311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_243-19_0_6_line_88 |  | 80 | 81 | 0.036329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_243-19_0_6_line_89 |  | 82 | 97 | 0.021649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_243-19_0_6_line_90 |  | 83 | 84 | 0.0048474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_243-19_0_6_line_91 |  | 84 | 85 | 0.010833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_243-19_0_6_line_92 |  | 86 | 87 | 0.038758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_243-19_0_6_line_93 |  | 87 | 118 | 0.0029201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_243-19_0_6_line_94 |  | 88 | 89 | 0.0077516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_243-19_0_6_line_95 |  | 89 | 90 | 0.017187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_243-19_0_6_line_96 |  | 90 | 94 | 0.02275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_243-19_0_6_line_97 |  | 91 | 92 | 0.02198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_243-19_0_6_line_98 |  | 91 | 93 | 0.027359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_243-19_0_6_line_99 |  | 94 | 95 | 0.022822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_243-19_0_6_line_100 |  | 95 | 96 | 0.02321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_243-19_0_6_line_101 |  | 97 | 98 | 0.013536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_243-19_0_6_line_102 |  | 99 | 100 | 0.029747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_243-19_0_6_line_103 |  | 100 | 103 | 0.030777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_243-19_0_6_line_104 |  | 101 | 104 | 0.012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_243-19_0_6_line_105 |  | 102 | 105 | 0.018641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_243-19_0_6_line_106 |  | 104 | 106 | 0.011563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_243-19_0_6_line_107 |  | 105 | 107 | 0.010078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_243-19_0_6_line_108 |  | 106 | 115 | 0.0095502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
109 | LV_243-19_0_6_line_109 |  | 108 | 109 | 0.0018983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_243-19_0_6_line_110 |  | 109 | 112 | 0.01676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_243-19_0_6_line_111 |  | 110 | 111 | 0.061435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_243-19_0_6_line_112 |  | 112 | 113 | 0.016641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_243-19_0_6_line_113 |  | 113 | 114 | 0.0040783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_243-19_0_6_line_114 |  | 114 | 118 | 0.030648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_243-19_0_6_line_115 |  | 115 | 116 | 0.013524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
116 | LV_243-19_0_6_line_116 |  | 116 | 117 | 0.032118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_243-19_0_6_line_117 |  | 117 | 118 | 0.024023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-19_0_6_trafo_21 | 0.63 MVA 20/0.4 kV | 119 | 38 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2672382.3803 | 1251233.5937 | 2672382.7283 | 1251256.1227
1 | 2672382.0921 | 1251214.9417 | 2672382.3803 | 1251233.5937
2 | 2672381.5279 | 1251201.8142 | 2672382.0921 | 1251214.9417
3 | 2672382.0921 | 1251214.9417 | 2672371.9987 | 1251218.1318 | 2672349.141 | 1251230.0546
4 | 2672381.5279 | 1251201.8142 | 2672380.2955 | 1251137.119
5 | 2672322.6746 | 1251243.8596 | 2672349.141 | 1251230.0546
6 | 2672383.6123 | 1251305.6963 | 2672383.9866 | 1251312.3678
7 | 2672385.284 | 1251326.2901 | 2672384.2425 | 1251316.9306 | 2672383.9866 | 1251312.3678
8 | 2672380.2955 | 1251137.119 | 2672380.1375 | 1251133.3489
9 | 2672301.4626 | 1251254.931 | 2672309.8647 | 1251250.5414 | 2672322.6746 | 1251243.8596
10 | 2672395.5017 | 1251373.3645 | 2672392.3526 | 1251364.2194 | 2672390.1259 | 1251353.7179 | 2672388.4611 | 1251344.8022 | 2672385.8817 | 1251331.6612 | 2672385.284 | 1251326.2901
11 | 2672379.4656 | 1251117.3168 | 2672380.1375 | 1251133.3489
12 | 2672459.7879 | 1251173.5944 | 2672423.6269 | 1251190.2258
13 | 2672459.7879 | 1251173.5944 | 2672470.7827 | 1251167.6946
14 | 2672459.7879 | 1251173.5944 | 2672470.7414 | 1251195.6503
15 | 2672301.4626 | 1251254.931 | 2672308.2853 | 1251285.7981
16 | 2672301.4626 | 1251254.931 | 2672296.9426 | 1251236.174
17 | 2672301.4626 | 1251254.931 | 2672268.5861 | 1251271.8984
18 | 2672561.2621 | 1251255.9499 | 2672546.7374 | 1251267.9929 | 2672543.0286 | 1251270.9375
19 | 2672564.7183 | 1251244.5182 | 2672565.4426 | 1251251.3209 | 2672561.4857 | 1251255.7645 | 2672561.2621 | 1251255.9499
20 | 2672543.0286 | 1251270.9375 | 2672536.752 | 1251275.9208 | 2672530.2668 | 1251283.4136 | 2672525.9532 | 1251289.8654 | 2672524.7997 | 1251292.253
21 | 2672564.7183 | 1251244.5182 | 2672575.9499 | 1251239.5783
22 | 2672564.7183 | 1251244.5182 | 2672549.9765 | 1251250.9996
23 | 2672524.7997 | 1251292.253 | 2672523.8356 | 1251294.2487
24 | 2672577.6582 | 1251238.8269 | 2672575.9499 | 1251239.5783
25 | 2672514.9794 | 1251268.7826 | 2672543.7796 | 1251253.7241 | 2672549.9765 | 1251250.9996
26 | 2672515.3903 | 1251312.1441 | 2672521.6704 | 1251298.7306 | 2672523.8356 | 1251294.2487
27 | 2672584.0047 | 1251236.0355 | 2672577.6582 | 1251238.8269
28 | 2672514.9794 | 1251268.7826 | 2672487.4366 | 1251287.1924 | 2672486.7977 | 1251287.7548
29 | 2672514.9794 | 1251268.7826 | 2672508.0565 | 1251260.5872
30 | 2672508.938 | 1251338.6815 | 2672511.6639 | 1251325.0383 | 2672514.1442 | 1251314.8057 | 2672515.3903 | 1251312.1441
31 | 2672597.6027 | 1251230.0548 | 2672584.0047 | 1251236.0355
32 | 2672486.7977 | 1251287.7548 | 2672473.7183 | 1251299.27
33 | 2672508.0565 | 1251260.5872 | 2672502.1911 | 1251253.6437
34 | 2672490.5448 | 1251235.5263 | 2672495.7605 | 1251246.0311 | 2672502.1911 | 1251253.6437
35 | 2672490.5448 | 1251235.5263 | 2672480.3359 | 1251214.9696
36 | 2672490.5448 | 1251235.5263 | 2672480.2937 | 1251243.9465
37 | 2672480.3359 | 1251214.9696 | 2672470.7414 | 1251195.6503
38 | 2672476.6059 | 1251246.9757 | 2672480.2937 | 1251243.9465
39 | 2672476.6059 | 1251246.9757 | 2672464.7352 | 1251256.7262
40 | 2672473.7183 | 1251299.27 | 2672459.509 | 1251311.7798 | 2672451.8342 | 1251319.6431
41 | 2672446.5345 | 1251271.6762 | 2672464.7352 | 1251256.7262
42 | 2672437.801 | 1251334.021 | 2672434.0824 | 1251337.8309
43 | 2672416.3244 | 1251356.0251 | 2672434.0824 | 1251337.8309
44 | 2672437.801 | 1251334.021 | 2672451.8342 | 1251319.6431
45 | 2672416.3244 | 1251356.0251 | 2672408.8662 | 1251363.6664
46 | 2672395.5017 | 1251373.3645 | 2672405.9932 | 1251366.6099 | 2672408.8662 | 1251363.6664
47 | 2672395.5017 | 1251373.3645 | 2672378.2886 | 1251380.0578
48 | 2672395.5017 | 1251373.3645 | 2672396.8792 | 1251377.3842 | 2672402.9281 | 1251407.4131
49 | 2672378.2886 | 1251380.0578 | 2672371.6226 | 1251382.6499
50 | 2672402.9281 | 1251407.4131 | 2672404.1331 | 1251417.1604
51 | 2672597.6027 | 1251230.0548 | 2672599.3687 | 1251232.5449 | 2672607.3877 | 1251239.4541
52 | 2672617.3379 | 1251248.2208 | 2672611.6485 | 1251243.1252 | 2672607.3877 | 1251239.4541
53 | 2672617.3379 | 1251248.2208 | 2672618.5661 | 1251249.6258 | 2672633.9982 | 1251263.5249 | 2672649.6586 | 1251247.7165 | 2672653.7988 | 1251247.4226 | 2672657.0373 | 1251248.6299
54 | 2672617.3379 | 1251248.2208 | 2672599.1153 | 1251268.1444
55 | 2672657.0373 | 1251248.6299 | 2672640.6071 | 1251281.1659
56 | 2672640.6071 | 1251281.1659 | 2672633.438 | 1251295.3625
57 | 2672513.4553 | 1251144.7965 | 2672470.7827 | 1251167.6946
58 | 2672633.438 | 1251295.3625 | 2672631.384 | 1251299.43 | 2672626.5565 | 1251306.9174
59 | 2672460.9765 | 1251486.135 | 2672461.7852 | 1251480.4964 | 2672453.2295 | 1251479.5689 | 2672445.1737 | 1251477.8803
60 | 2672460.9765 | 1251486.135 | 2672461.7852 | 1251480.4964 | 2672488.1996 | 1251480.8085 | 2672494.508 | 1251480.3409 | 2672512.1636 | 1251477.8217 | 2672519.3837 | 1251475.6306 | 2672521.6681 | 1251483.2419
61 | 2672460.9765 | 1251486.135 | 2672451.2263 | 1251523.6208 | 2672449.167 | 1251530.5946
62 | 2672445.1737 | 1251477.8803 | 2672439.9975 | 1251480.8192 | 2672432.5244 | 1251479.1182
63 | 2672521.6681 | 1251483.2419 | 2672513.2799 | 1251495.1479 | 2672508.3011 | 1251511.5736
64 | 2672521.6681 | 1251483.2419 | 2672532.1262 | 1251479.6703
65 | 2672441.7734 | 1251555.6334 | 2672449.167 | 1251530.5946
66 | 2672460.0447 | 1251458.6482 | 2672457.5824 | 1251459.3964 | 2672452.0027 | 1251459.5283 | 2672445.345 | 1251458.2315
67 | 2672460.0447 | 1251458.6482 | 2672462.241 | 1251454.9613 | 2672475.8801 | 1251415.616
68 | 2672422.4719 | 1251453.7422 | 2672432.7557 | 1251455.7792 | 2672445.345 | 1251458.2315
69 | 2672491.6446 | 1251380.6448 | 2672478.2808 | 1251408.6905 | 2672475.8801 | 1251415.616
70 | 2672358.0857 | 1251532.734 | 2672367.5152 | 1251539.9766 | 2672372.0043 | 1251566.0836 | 2672378.4278 | 1251586.4546 | 2672383.362 | 1251595.2768 | 2672387.052 | 1251599.6695 | 2672389.3349 | 1251604.3341 | 2672392.0195 | 1251595.2714 | 2672389.6422 | 1251584.1343 | 2672387.045 | 1251559.4848 | 2672387.1823 | 1251549.4903 | 2672387.7788 | 1251532.7966
71 | 2672387.7788 | 1251532.7966 | 2672393.9951 | 1251533.0616 | 2672395.2888 | 1251516.143 | 2672393.9264 | 1251508.4207 | 2672389.9548 | 1251500.4998 | 2672382.4788 | 1251492.1358 | 2672370.7042 | 1251483.4635 | 2672366.7964 | 1251478.3454 | 2672366.5913 | 1251471.6603 | 2672368.8053 | 1251460.9574 | 2672399.0598 | 1251467.6094 | 2672398.3876 | 1251471.3484
72 | 2672387.7788 | 1251532.7966 | 2672388.391 | 1251520.3729 | 2672386.9601 | 1251513.9396 | 2672382.9194 | 1251506.7295 | 2672374.492 | 1251500.2441 | 2672358.1783 | 1251495.4971 | 2672341.848 | 1251493.9633 | 2672321.6109 | 1251494.0275 | 2672300.9249 | 1251496.6719
73 | 2672358.0857 | 1251532.734 | 2672343.6736 | 1251544.0997 | 2672308.4115 | 1251580.4068 | 2672292.2487 | 1251596.133
74 | 2672398.3876 | 1251471.3484 | 2672432.5244 | 1251479.1182
75 | 2672398.3876 | 1251471.3484 | 2672399.0598 | 1251467.6094 | 2672400.6109 | 1251461.1237 | 2672402.877 | 1251461.6073 | 2672403.6401 | 1251456.6019 | 2672404.1074 | 1251452.3378 | 2672404.338 | 1251450.1502
76 | 2672549.2364 | 1251448.5097 | 2672564.532 | 1251438.4007 | 2672571.9832 | 1251431.6209
77 | 2672549.2364 | 1251448.5097 | 2672531.4254 | 1251431.0457 | 2672531.4254 | 1251431.0457
78 | 2672587.9704 | 1251416.3449 | 2672581.7144 | 1251422.7664 | 2672571.9832 | 1251431.6209
79 | 2672531.4254 | 1251431.0457 | 2672535.7169 | 1251425.7722 | 2672554.9908 | 1251404.3616
80 | 2672404.338 | 1251450.1502 | 2672422.4719 | 1251453.7422
81 | 2672404.338 | 1251450.1502 | 2672405.0431 | 1251443.0981 | 2672405.3407 | 1251436.0411 | 2672404.8926 | 1251423.3042 | 2672404.1331 | 1251417.1604
82 | 2672507.7695 | 1251513.3272 | 2672508.3011 | 1251511.5736
83 | 2672532.1262 | 1251479.6703 | 2672535.208 | 1251478.6178
84 | 2672668.3911 | 1251334.4549 | 2672657.4778 | 1251345.0161 | 2672655.0556 | 1251347.4982
85 | 2672638.5137 | 1251364.464 | 2672647.1198 | 1251355.6302 | 2672655.0556 | 1251347.4982
86 | 2672604.0847 | 1251399.8042 | 2672587.9704 | 1251416.3449
87 | 2672572.0962 | 1251383.0912 | 2672559.9134 | 1251398.8933 | 2672554.9908 | 1251404.3616
88 | 2672567.8921 | 1251462.9485 | 2672543.7329 | 1251475.7064 | 2672535.208 | 1251478.6178
89 | 2672507.7695 | 1251513.3272 | 2672501.4896 | 1251534.0453
90 | 2672442.7887 | 1251274.7529 | 2672446.5345 | 1251271.6762
91 | 2672434.4174 | 1251281.6291 | 2672442.7887 | 1251274.7529
92 | 2672333.3926 | 1251386.4711 | 2672341.5145 | 1251387.1597 | 2672353.5693 | 1251386.5175 | 2672367.5841 | 1251384.2203 | 2672371.6226 | 1251382.6499
93 | 2672330.4829 | 1251386.2244 | 2672333.3926 | 1251386.4711
94 | 2672622.3561 | 1251313.4323 | 2672626.5565 | 1251306.9174
95 | 2672622.3561 | 1251313.4323 | 2672613.0427 | 1251327.8772
96 | 2672600.2022 | 1251346.6353 | 2672604.7607 | 1251340.7226 | 2672613.0427 | 1251327.8772
97 | 2672619.4225 | 1251384.0605 | 2672604.0847 | 1251399.8042
98 | 2672619.4225 | 1251384.0605 | 2672638.5137 | 1251364.464
99 | 2672600.2022 | 1251346.6353 | 2672586.2676 | 1251364.7097
100 | 2672572.0962 | 1251383.0912 | 2672586.2676 | 1251364.7097
101 | 2672497.563 | 1251546.9997 | 2672501.4896 | 1251534.0453
102 | 2672242.1518 | 1251285.5411 | 2672268.5861 | 1251271.8984
103 | 2672242.1518 | 1251285.5411 | 2672256.875 | 1251312.5679
104 | 2672308.2853 | 1251285.7981 | 2672310.8908 | 1251297.5858
105 | 2672292.5754 | 1251218.0515 | 2672296.9426 | 1251236.174
106 | 2672313.3864 | 1251308.8766 | 2672310.8908 | 1251297.5858
107 | 2672292.5754 | 1251218.0515 | 2672289.366 | 1251208.4977
108 | 2672315.4476 | 1251318.2018 | 2672313.3864 | 1251308.8766
109 | 2672262.1937 | 1251370.9905 | 2672264.0371 | 1251371.4434
110 | 2672280.3135 | 1251375.4417 | 2672264.0371 | 1251371.4434
111 | 2672379.4656 | 1251117.3168 | 2672332.0498 | 1251156.5441
112 | 2672280.3135 | 1251375.4417 | 2672296.4741 | 1251379.4117
113 | 2672296.4741 | 1251379.4117 | 2672300.4346 | 1251380.3846
114 | 2672330.4829 | 1251386.2244 | 2672315.4957 | 1251384.0845 | 2672300.4346 | 1251380.3846
115 | 2672315.4476 | 1251318.2018 | 2672318.3664 | 1251331.4068
116 | 2672325.2982 | 1251362.7678 | 2672318.3664 | 1251331.4068
117 | 2672330.4829 | 1251386.2244 | 2672325.2982 | 1251362.7678

## bus_geodata
| x | y | coords
0 | 2672382.3803 | 1251233.5937
1 | 2672382.7283 | 1251256.1227
2 | 2672382.0921 | 1251214.9417
3 | 2672381.5279 | 1251201.8142
4 | 2672349.141 | 1251230.0546
5 | 2672383.6123 | 1251305.6963
6 | 2672383.9866 | 1251312.3678
7 | 2672380.2955 | 1251137.119
8 | 2672322.6746 | 1251243.8596
9 | 2672385.284 | 1251326.2901
10 | 2672380.1375 | 1251133.3489
11 | 2672423.6269 | 1251190.2258
12 | 2672459.7879 | 1251173.5944
13 | 2672301.4626 | 1251254.931
14 | 2672561.2621 | 1251255.9499
15 | 2672543.0286 | 1251270.9375
16 | 2672564.7183 | 1251244.5182
17 | 2672524.7997 | 1251292.253
18 | 2672575.9499 | 1251239.5783
19 | 2672549.9765 | 1251250.9996
20 | 2672523.8356 | 1251294.2487
21 | 2672577.6582 | 1251238.8269
22 | 2672514.9794 | 1251268.7826
23 | 2672515.3903 | 1251312.1441
24 | 2672584.0047 | 1251236.0355
25 | 2672486.7977 | 1251287.7548
26 | 2672508.0565 | 1251260.5872
27 | 2672502.1911 | 1251253.6437
28 | 2672490.5448 | 1251235.5263
29 | 2672480.3359 | 1251214.9696
30 | 2672480.2937 | 1251243.9465
31 | 2672470.7414 | 1251195.6503
32 | 2672476.6059 | 1251246.9757
33 | 2672473.7183 | 1251299.27
34 | 2672464.7352 | 1251256.7262
35 | 2672434.0824 | 1251337.8309
36 | 2672437.801 | 1251334.021
37 | 2672416.3244 | 1251356.0251
38 | 2672451.8342 | 1251319.6431
39 | 2672408.8662 | 1251363.6664
40 | 2672395.5017 | 1251373.3645
41 | 2672378.2886 | 1251380.0578
42 | 2672402.9281 | 1251407.4131
43 | 2672597.6027 | 1251230.0548
44 | 2672607.3877 | 1251239.4541
45 | 2672617.3379 | 1251248.2208
46 | 2672657.0373 | 1251248.6299
47 | 2672599.1153 | 1251268.1444
48 | 2672640.6071 | 1251281.1659
49 | 2672513.4553 | 1251144.7965
50 | 2672470.7827 | 1251167.6946
51 | 2672633.438 | 1251295.3625
52 | 2672508.938 | 1251338.6815
53 | 2672460.9765 | 1251486.135
54 | 2672445.1737 | 1251477.8803
55 | 2672521.6681 | 1251483.2419
56 | 2672449.167 | 1251530.5946
57 | 2672460.0447 | 1251458.6482
58 | 2672445.345 | 1251458.2315
59 | 2672475.8801 | 1251415.616
60 | 2672387.7788 | 1251532.7966
61 | 2672358.0857 | 1251532.734
62 | 2672398.3876 | 1251471.3484
63 | 2672300.9249 | 1251496.6719
64 | 2672432.5244 | 1251479.1182
65 | 2672549.2364 | 1251448.5097
66 | 2672571.9832 | 1251431.6209
67 | 2672531.4254 | 1251431.0457
68 | 2672404.338 | 1251450.1502
69 | 2672422.4719 | 1251453.7422
70 | 2672404.1331 | 1251417.1604
71 | 2672508.3011 | 1251511.5736
72 | 2672532.1262 | 1251479.6703
73 | 2672441.7734 | 1251555.6334
74 | 2672491.6446 | 1251380.6448
75 | 2672668.3911 | 1251334.4549
76 | 2672655.0556 | 1251347.4982
77 | 2672292.2487 | 1251596.133
78 | 2672587.9704 | 1251416.3449
79 | 2672554.9908 | 1251404.3616
80 | 2672567.8921 | 1251462.9485
81 | 2672535.208 | 1251478.6178
82 | 2672507.7695 | 1251513.3272
83 | 2672446.5345 | 1251271.6762
84 | 2672442.7887 | 1251274.7529
85 | 2672434.4174 | 1251281.6291
86 | 2672371.6226 | 1251382.6499
87 | 2672333.3926 | 1251386.4711
88 | 2672626.5565 | 1251306.9174
89 | 2672622.3561 | 1251313.4323
90 | 2672613.0427 | 1251327.8772
91 | 2672619.4225 | 1251384.0605
92 | 2672604.0847 | 1251399.8042
93 | 2672638.5137 | 1251364.464
94 | 2672600.2022 | 1251346.6353
95 | 2672586.2676 | 1251364.7097
96 | 2672572.0962 | 1251383.0912
97 | 2672501.4896 | 1251534.0453
98 | 2672497.563 | 1251546.9997
99 | 2672268.5861 | 1251271.8984
100 | 2672242.1518 | 1251285.541
101 | 2672308.2853 | 1251285.7981
102 | 2672296.9426 | 1251236.174
103 | 2672256.875 | 1251312.5679
104 | 2672310.8908 | 1251297.5858
105 | 2672292.5754 | 1251218.0515
106 | 2672313.3864 | 1251308.8766
107 | 2672289.366 | 1251208.4977
108 | 2672262.1937 | 1251370.9905
109 | 2672264.0371 | 1251371.4434
110 | 2672379.4656 | 1251117.3168
111 | 2672332.0498 | 1251156.5441
112 | 2672280.3135 | 1251375.4417
113 | 2672296.4741 | 1251379.4117
114 | 2672300.4346 | 1251380.3846
115 | 2672315.4476 | 1251318.2018
116 | 2672318.3664 | 1251331.4068
117 | 2672325.2982 | 1251362.7678
118 | 2672330.4829 | 1251386.2244
119 | 2672395.5017 | 1251373.3645

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97322 | -0.51678 | 0.015622 | 0.0039152
1 | 0.97302 | -0.52056 | 0.0091103 | 0.0022833
2 | 0.97365 | -0.50829 | 0 | 0
3 | 0.97325 | -0.51617 | 0 | 0
4 | 0.97559 | -0.47005 | 0.0088467 | 0.0022172
5 | 0.99143 | -0.16347 | 0.0024307 | 0.0006092
6 | 0.99144 | -0.16318 | 0.017588 | 0.0044079
7 | 0.97128 | -0.55504 | 0 | 0
8 | 0.97743 | -0.43395 | 0.0051218 | 0.0012836
9 | 0.9917 | -0.15822 | 0.0021335 | 0.00053471
10 | 0.97116 | -0.55732 | 0.021112 | 0.0052912
11 | 0.98326 | -0.32183 | 0.021684 | 0.0054344
12 | 0.98405 | -0.30628 | 0 | 0
13 | 0.97902 | -0.40288 | 0 | 0
14 | 0.98682 | -0.25201 | 0.0061606 | 0.001544
15 | 0.98593 | -0.2693 | 0.010465 | 0.0026228
16 | 0.98739 | -0.24099 | 0 | 0
17 | 0.98514 | -0.28478 | 0.0069891 | 0.0017516
18 | 0.9864 | -0.26004 | 0.0016116 | 0.00040391
19 | 0.98938 | -0.20254 | 0.013383 | 0.0033542
20 | 0.98509 | -0.28571 | 0.0076033 | 0.0019056
21 | 0.98625 | -0.26289 | 0.010565 | 0.002648
22 | 0.99205 | -0.15122 | 0 | 0
23 | 0.9848 | -0.29134 | 0.0039627 | 0.00099313
24 | 0.98577 | -0.27216 | 0.007148 | 0.0017915
25 | 0.99609 | -0.074154 | 0.0037747 | 0.00094603
26 | 0.99097 | -0.17213 | 0.0026933 | 0.000675
27 | 0.99007 | -0.18945 | 0.0056493 | 0.0014159
28 | 0.98804 | -0.22873 | 0 | 0
29 | 0.98653 | -0.25807 | 0.009976 | 0.0025002
30 | 0.98767 | -0.23586 | 0.0029531 | 0.00074011
31 | 0.9853 | -0.28187 | 0.0063893 | 0.0016013
32 | 0.98756 | -0.23817 | 0.0030048 | 0.00075308
33 | 0.99749 | -0.047565 | 0.012008 | 0.0030096
34 | 0.98721 | -0.24481 | 0.0023386 | 0.00058612
35 | 0.99755 | -0.046352 | 0.002927 | 0.00073356
36 | 0.99806 | -0.036783 | 0.0065068 | 0.0016308
37 | 0.99516 | -0.091744 | 0.0027759 | 0.0006957
38 | 1 | 0 | -0.59795 | -0.15289
39 | 0.99417 | -0.1107 | 0.0096512 | 0.0024188
40 | 0.99268 | -0.13928 | 0 | 0
41 | 0.99154 | -0.16091 | 0.0075405 | 0.0018898
42 | 0.99036 | -0.18384 | 0 | 0
43 | 0.98484 | -0.29014 | 0 | 0
44 | 0.98399 | -0.30668 | 0.0084679 | 0.0021223
45 | 0.98326 | -0.32077 | 0 | 0
46 | 0.98048 | -0.37467 | 0 | 0
47 | 0.98321 | -0.32177 | 0.0020662 | 0.00051783
48 | 0.97855 | -0.41234 | 0.0043667 | 0.0010944
49 | 0.98297 | -0.3275 | 0.015695 | 0.0039334
50 | 0.98367 | -0.3138 | 0.01776 | 0.004451
51 | 0.97778 | -0.42755 | 0.005478 | 0.0013729
52 | 0.9845 | -0.29719 | 0.011881 | 0.0029776
53 | 0.98432 | -0.30116 | 0 | 0
54 | 0.98482 | -0.29136 | 0 | 0
55 | 0.98289 | -0.32909 | 0 | 0
56 | 0.98421 | -0.30329 | 0.0016864 | 0.00042265
57 | 0.98688 | -0.25134 | 0 | 0
58 | 0.98702 | -0.24866 | 0.0048723 | 0.0012211
59 | 0.98646 | -0.25959 | 0.006051 | 0.0015165
60 | 0.98596 | -0.26915 | 0 | 0
61 | 0.98548 | -0.27863 | 0 | 0
62 | 0.98655 | -0.25776 | 0 | 0
63 | 0.98579 | -0.27247 | 0.0016428 | 0.00041172
64 | 0.98512 | -0.28545 | 0.019909 | 0.0049897
65 | 0.97244 | -0.53262 | 0 | 0
66 | 0.97208 | -0.53961 | 0.00051254 | 0.00012845
67 | 0.97275 | -0.52649 | 0.00098416 | 0.00024665
68 | 0.98765 | -0.23634 | 0 | 0
69 | 0.98734 | -0.24245 | 0.0035653 | 0.00089355
70 | 0.98971 | -0.19642 | 0.0043892 | 0.0011
71 | 0.98254 | -0.33594 | 0.00021359 | 5.353e-05
72 | 0.98279 | -0.33102 | 0.00037072 | 9.291e-05
73 | 0.98419 | -0.3037 | 0.00088441 | 0.00022165
74 | 0.98632 | -0.26232 | 0.0039753 | 0.0009963
75 | 0.97127 | -0.55568 | 0.0010712 | 0.00026847
76 | 0.97129 | -0.55531 | 0.00097803 | 0.00024512
77 | 0.98519 | -0.2843 | 0.0034467 | 0.00086383
78 | 0.97182 | -0.54484 | 0.00040074 | 0.00010043
79 | 0.97322 | -0.51711 | 0.0070924 | 0.0017775
80 | 0.98246 | -0.33743 | 0.0089539 | 0.0022441
81 | 0.98276 | -0.33156 | 0.00032597 | 8.1695e-05
82 | 0.98252 | -0.33632 | 0.0033109 | 0.0008298
83 | 0.98674 | -0.25399 | 0.0060304 | 0.0015114
84 | 0.98667 | -0.25536 | 0.0093097 | 0.0023332
85 | 0.98661 | -0.25662 | 0.0064645 | 0.0016201
86 | 0.99112 | -0.16898 | 0.0062452 | 0.0015652
87 | 0.98891 | -0.2114 | 0.0089051 | 0.0022318
88 | 0.97719 | -0.43911 | 0.0008238 | 0.00020646
89 | 0.97685 | -0.44565 | 0.00090656 | 0.00022721
90 | 0.97613 | -0.45989 | 0.0011139 | 0.00027917
91 | 0.97144 | -0.55235 | 0.0013923 | 0.00034894
92 | 0.97155 | -0.55014 | 0.006958 | 0.0017438
93 | 0.97133 | -0.55441 | 0.0020176 | 0.00050566
94 | 0.97519 | -0.4783 | 0.0077162 | 0.0019339
95 | 0.97441 | -0.49357 | 0.0065084 | 0.0016312
96 | 0.97377 | -0.50635 | 0.0085579 | 0.0021448
97 | 0.98235 | -0.33962 | 0.00090471 | 0.00022674
98 | 0.98225 | -0.34146 | 0.0075213 | 0.001885
99 | 0.97832 | -0.41661 | 0.018103 | 0.0045371
100 | 0.97826 | -0.41785 | 0 | 0
101 | 0.98206 | -0.34365 | 0.0035942 | 0.0009008
102 | 0.97881 | -0.40698 | 0.0027071 | 0.00067846
103 | 0.97819 | -0.41914 | 0.0022917 | 0.00057435
104 | 0.98327 | -0.32034 | 0.0015477 | 0.00038789
105 | 0.97866 | -0.41002 | 0 | 0
106 | 0.98443 | -0.29775 | 0.005473 | 0.0013717
107 | 0.97857 | -0.41166 | 0.008969 | 0.0022478
108 | 0.98724 | -0.24387 | 0.0047263 | 0.0011845
109 | 0.98725 | -0.24371 | 0.0089249 | 0.0022368
110 | 0.97099 | -0.56072 | 0 | 0
111 | 0.97033 | -0.57375 | 0.011465 | 0.0028735
112 | 0.98746 | -0.23962 | 0.0054577 | 0.0013678
113 | 0.98775 | -0.23394 | 0.0062033 | 0.0015547
114 | 0.98785 | -0.23209 | 0.0069434 | 0.0017402
115 | 0.98494 | -0.28796 | 0.011528 | 0.0028891
116 | 0.98573 | -0.27273 | 0.0058685 | 0.0014708
117 | 0.98769 | -0.23496 | 0.012094 | 0.003031
118 | 0.98876 | -0.21445 | 0 | 0
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.009112 | 0.002284 | -0.0091103 | -0.0022833 | 1.64e-06 | 7.6971e-07 | 0.013932 | 0.013932 | 0.013932 | 0.97322 | -0.51678 | 0.97302 | -0.52056 | 3.8275
1 | -0.024734 | -0.0061992 | 0.024744 | 0.0062053 | 1.0004e-05 | 6.1708e-06 | 0.037817 | 0.037817 | 0.037817 | 0.97322 | -0.51678 | 0.97365 | -0.50829 | 10.3893
2 | 0.032663 | 0.0082173 | -0.032651 | -0.0082096 | 1.2285e-05 | 7.6991e-06 | 0.04993 | 0.04993 | 0.04993 | 0.97365 | -0.50829 | 0.97325 | -0.51617 | 13.717
3 | -0.057406 | -0.014423 | 0.057511 | 0.014489 | 0.000105 | 6.6746e-05 | 0.087747 | 0.087746 | 0.087747 | 0.97365 | -0.50829 | 0.97559 | -0.47005 | 24.1062
4 | 0.032651 | 0.0082096 | -0.03259 | -0.0081717 | 6.0499e-05 | 3.7917e-05 | 0.04993 | 0.04993 | 0.04993 | 0.97325 | -0.51617 | 0.97128 | -0.55504 | 13.717
5 | -0.066358 | -0.016707 | 0.066473 | 0.01678 | 0.00011473 | 7.3055e-05 | 0.10124 | 0.10124 | 0.10124 | 0.97559 | -0.47005 | 0.97743 | -0.43395 | 27.8132
6 | -0.0024307 | -0.0006092 | 0.0024308 | 0.00060913 | 3.335e-08 | -6.4823e-08 | 0.0036482 | 0.0036482 | 0.0036482 | 0.99143 | -0.16347 | 0.99144 | -0.16318 | 1.0023
7 | -0.020018 | -0.005017 | 0.020023 | 0.0050198 | 4.7348e-06 | 2.8498e-06 | 0.030045 | 0.030045 | 0.030045 | 0.99144 | -0.16318 | 0.9917 | -0.15822 | 8.2541
8 | 0.03259 | 0.0081717 | -0.032587 | -0.0081695 | 3.5277e-06 | 2.2111e-06 | 0.04993 | 0.04993 | 0.04993 | 0.97128 | -0.55504 | 0.97116 | -0.55732 | 13.7171
9 | -0.071595 | -0.018063 | 0.071701 | 0.018131 | 0.00010668 | 6.7974e-05 | 0.10904 | 0.10904 | 0.10904 | 0.97743 | -0.43395 | 0.97902 | -0.40288 | 29.9552
10 | -0.022157 | -0.0055546 | 0.022177 | 0.0055667 | 2.0008e-05 | 1.2182e-05 | 0.033246 | 0.033246 | 0.033246 | 0.9917 | -0.15822 | 0.99268 | -0.13928 | 9.1335
11 | 0.011474 | 0.0028783 | -0.011473 | -0.0028773 | 1.8601e-06 | 9.9198e-07 | 0.017582 | 0.017582 | 0.017582 | 0.97116 | -0.55732 | 0.97099 | -0.56072 | 4.8303
12 | -0.021684 | -0.0054344 | 0.0217 | 0.0054442 | 1.6072e-05 | 9.7811e-06 | 0.032815 | 0.032815 | 0.032815 | 0.98326 | -0.32183 | 0.98405 | -0.30628 | 9.0151
13 | 0.033476 | 0.0083979 | -0.033464 | -0.0083903 | 1.1991e-05 | 7.516e-06 | 0.050623 | 0.050624 | 0.050624 | 0.98405 | -0.30628 | 0.98367 | -0.3138 | 13.9076
14 | -0.055176 | -0.013842 | 0.05524 | 0.013883 | 6.4292e-05 | 4.0833e-05 | 0.083438 | 0.083438 | 0.083438 | 0.98405 | -0.30628 | 0.9853 | -0.28187 | 22.9226
15 | -0.10379 | -0.026179 | 0.10409 | 0.026367 | 0.00029523 | 0.00018855 | 0.15781 | 0.15781 | 0.15781 | 0.97902 | -0.40288 | 0.98206 | -0.34365 | 43.3546
16 | 0.01168 | 0.0029284 | -0.011678 | -0.0029272 | 2.2804e-06 | 1.2169e-06 | 0.017753 | 0.017753 | 0.017753 | 0.97902 | -0.40288 | 0.97881 | -0.40698 | 4.8773
17 | 0.020409 | 0.005119 | -0.020395 | -0.0051109 | 1.3351e-05 | 8.0795e-06 | 0.031021 | 0.031021 | 0.031021 | 0.97902 | -0.40288 | 0.97832 | -0.41661 | 8.5222
18 | 0.040966 | 0.010291 | -0.040932 | -0.01027 | 3.3784e-05 | 2.132e-05 | 0.06178 | 0.06178 | 0.06178 | 0.98682 | -0.25201 | 0.98593 | -0.2693 | 16.9726
19 | -0.047126 | -0.011835 | 0.047151 | 0.011851 | 2.4778e-05 | 1.5691e-05 | 0.07107 | 0.07107 | 0.07107 | 0.98682 | -0.25201 | 0.98739 | -0.24099 | 19.5247
20 | 0.030467 | 0.0076468 | -0.030444 | -0.0076328 | 2.2471e-05 | 1.4021e-05 | 0.045986 | 0.045986 | 0.045986 | 0.98593 | -0.2693 | 0.98514 | -0.28478 | 12.6335
21 | 0.087495 | 0.022216 | -0.087415 | -0.022165 | 8.0122e-05 | 5.1122e-05 | 0.13196 | 0.13196 | 0.13196 | 0.98739 | -0.24099 | 0.9864 | -0.26004 | 36.2526
22 | -0.13465 | -0.034067 | 0.13489 | 0.034226 | 0.00024893 | 0.00015911 | 0.20303 | 0.20303 | 0.20303 | 0.98739 | -0.24099 | 0.98938 | -0.20254 | 55.7772
23 | 0.023455 | 0.0058812 | -0.023454 | -0.0058805 | 1.0433e-06 | 6.3948e-07 | 0.035429 | 0.035429 | 0.035429 | 0.98514 | -0.28478 | 0.98509 | -0.28571 | 9.7333
24 | 0.085803 | 0.021761 | -0.085791 | -0.021754 | 1.1742e-05 | 7.4908e-06 | 0.12953 | 0.12953 | 0.12953 | 0.9864 | -0.26004 | 0.98625 | -0.26289 | 35.5847
25 | -0.14828 | -0.03758 | 0.14864 | 0.037814 | 0.00036667 | 0.00023365 | 0.22316 | 0.22316 | 0.22316 | 0.98938 | -0.20254 | 0.99205 | -0.15122 | 30.6535
26 | 0.015851 | 0.003975 | -0.015847 | -0.0039725 | 4.2544e-06 | 2.471e-06 | 0.023944 | 0.023944 | 0.023944 | 0.98509 | -0.28571 | 0.9848 | -0.29134 | 6.5781
27 | 0.075226 | 0.019106 | -0.075192 | -0.019084 | 3.3545e-05 | 2.1381e-05 | 0.11359 | 0.11359 | 0.11359 | 0.98625 | -0.26289 | 0.98577 | -0.27216 | 31.2054
28 | -0.25929 | -0.065812 | 0.26025 | 0.066428 | 0.00096515 | 0.00061681 | 0.38921 | 0.38921 | 0.38921 | 0.99205 | -0.15122 | 0.99609 | -0.074154 | 53.463
29 | 0.11064 | 0.027998 | -0.11053 | -0.027927 | 0.00011093 | 7.0857e-05 | 0.16605 | 0.16605 | 0.16605 | 0.99205 | -0.15122 | 0.99097 | -0.17213 | 45.6192
30 | 0.011884 | 0.0029794 | -0.011881 | -0.0029776 | 3.3108e-06 | 1.7707e-06 | 0.017957 | 0.017957 | 0.017957 | 0.9848 | -0.29134 | 0.9845 | -0.29719 | 4.9332
31 | 0.068044 | 0.017293 | -0.067985 | -0.017255 | 5.8867e-05 | 3.7486e-05 | 0.1028 | 0.1028 | 0.1028 | 0.98577 | -0.27216 | 0.98484 | -0.29014 | 28.2412
32 | -0.26403 | -0.067374 | 0.26437 | 0.067591 | 0.0003396 | 0.00021667 | 0.39485 | 0.39485 | 0.39485 | 0.99609 | -0.074154 | 0.99749 | -0.047565 | 36.1583
33 | 0.10784 | 0.027252 | -0.10775 | -0.027195 | 8.9463e-05 | 5.7139e-05 | 0.16201 | 0.16201 | 0.16201 | 0.99097 | -0.17213 | 0.99007 | -0.18945 | 44.5082
34 | 0.1021 | 0.025779 | -0.10191 | -0.025657 | 0.00019173 | 0.00012243 | 0.15352 | 0.15352 | 0.15352 | 0.99007 | -0.18945 | 0.98804 | -0.22873 | 42.1756
35 | 0.071776 | 0.018093 | -0.071676 | -0.018029 | 0.00010064 | 6.4118e-05 | 0.10813 | 0.10813 | 0.10813 | 0.98804 | -0.22873 | 0.98653 | -0.25807 | 29.7072
36 | 0.030133 | 0.0075635 | -0.030123 | -0.0075571 | 1.0247e-05 | 6.3882e-06 | 0.045385 | 0.045385 | 0.045385 | 0.98804 | -0.22873 | 0.98767 | -0.23586 | 12.4684
37 | 0.0617 | 0.015529 | -0.06163 | -0.015484 | 7.0093e-05 | 4.4584e-05 | 0.093087 | 0.093087 | 0.093087 | 0.98653 | -0.25807 | 0.9853 | -0.28187 | 25.5734
38 | 0.02717 | 0.006817 | -0.027167 | -0.0068151 | 2.999e-06 | 1.8583e-06 | 0.040936 | 0.040936 | 0.040936 | 0.98767 | -0.23586 | 0.98756 | -0.23817 | 11.2462
39 | 0.024162 | 0.0060621 | -0.024154 | -0.0060574 | 7.6363e-06 | 4.6907e-06 | 0.036409 | 0.036409 | 0.036409 | 0.98756 | -0.23817 | 0.98721 | -0.24481 | 10.0024
40 | -0.27638 | -0.070601 | 0.27701 | 0.071007 | 0.00063718 | 0.00040662 | 0.41276 | 0.41276 | 0.41276 | 0.99749 | -0.047565 | 1 | 0 | 37.7987
41 | 0.021816 | 0.0054713 | -0.021806 | -0.0054654 | 9.551e-06 | 5.8116e-06 | 0.032884 | 0.032884 | 0.032884 | 0.98721 | -0.24481 | 0.98674 | -0.25399 | 9.034
42 | -0.31207 | -0.079795 | 0.31221 | 0.079888 | 0.00014456 | 9.2307e-05 | 0.46607 | 0.46607 | 0.46607 | 0.99755 | -0.046352 | 0.99806 | -0.036783 | 42.6801
43 | 0.30914 | 0.079062 | -0.30847 | -0.078629 | 0.00067744 | 0.00043257 | 0.4617 | 0.4617 | 0.4617 | 0.99755 | -0.046352 | 0.99516 | -0.091744 | 42.2803
44 | -0.31872 | -0.081518 | 0.31929 | 0.081881 | 0.00056846 | 0.00036303 | 0.47577 | 0.47577 | 0.47577 | 0.99806 | -0.036783 | 1 | 0 | 43.5685
45 | 0.30569 | 0.077934 | -0.30541 | -0.077755 | 0.00027943 | 0.00017842 | 0.45755 | 0.45755 | 0.45755 | 0.99516 | -0.091744 | 0.99417 | -0.1107 | 41.9002
46 | 0.29576 | 0.075336 | -0.29535 | -0.075076 | 0.00040719 | 0.00025996 | 0.44311 | 0.44311 | 0.44311 | 0.99417 | -0.1107 | 0.99268 | -0.13928 | 40.5774
47 | 0.20064 | 0.051143 | -0.20043 | -0.05101 | 0.00020924 | 0.0001332 | 0.30106 | 0.30106 | 0.30106 | 0.99268 | -0.13928 | 0.99154 | -0.16091 | 27.5695
48 | 0.072538 | 0.018367 | -0.072384 | -0.018268 | 0.00015483 | 9.8643e-05 | 0.1088 | 0.1088 | 0.1088 | 0.99268 | -0.13928 | 0.99036 | -0.18384 | 29.8905
49 | 0.19289 | 0.04912 | -0.19281 | -0.049072 | 7.5055e-05 | 4.7759e-05 | 0.28974 | 0.28974 | 0.28974 | 0.99154 | -0.16091 | 0.99112 | -0.16898 | 26.5333
50 | 0.072384 | 0.018268 | -0.07234 | -0.01824 | 4.3599e-05 | 2.7777e-05 | 0.1088 | 0.1088 | 0.1088 | 0.99036 | -0.18384 | 0.98971 | -0.19642 | 29.8905
51 | 0.067985 | 0.017255 | -0.067931 | -0.017221 | 5.4043e-05 | 3.4414e-05 | 0.1028 | 0.1028 | 0.1028 | 0.98484 | -0.29014 | 0.98399 | -0.30668 | 28.2412
52 | 0.059463 | 0.015099 | -0.059423 | -0.015073 | 4.0276e-05 | 2.5609e-05 | 0.089993 | 0.089993 | 0.089993 | 0.98399 | -0.30668 | 0.98326 | -0.32077 | 24.7233
53 | 0.057357 | 0.014555 | -0.057209 | -0.014461 | 0.00014829 | 9.4241e-05 | 0.086866 | 0.086866 | 0.086866 | 0.98326 | -0.32077 | 0.98048 | -0.37467 | 23.8643
54 | 0.0020663 | 0.00051755 | -0.0020662 | -0.00051783 | 9.8999e-08 | -2.7909e-07 | 0.0031269 | 0.003127 | 0.003127 | 0.98326 | -0.32077 | 0.98321 | -0.32177 | 0.85906
55 | 0.057209 | 0.014461 | -0.057105 | -0.014396 | 0.00010314 | 6.555e-05 | 0.086866 | 0.086866 | 0.086866 | 0.98048 | -0.37467 | 0.97855 | -0.41234 | 23.8644
56 | 0.052739 | 0.013301 | -0.0527 | -0.013277 | 3.8386e-05 | 2.4367e-05 | 0.080226 | 0.080226 | 0.080226 | 0.97855 | -0.41234 | 0.97778 | -0.42755 | 22.0401
57 | -0.015695 | -0.0039334 | 0.015705 | 0.0039394 | 1.0251e-05 | 5.9462e-06 | 0.023758 | 0.023758 | 0.023758 | 0.98297 | -0.3275 | 0.98367 | -0.3138 | 6.527
58 | 0.047222 | 0.011904 | -0.047196 | -0.011887 | 2.6097e-05 | 1.6533e-05 | 0.071889 | 0.07189 | 0.07189 | 0.97778 | -0.42755 | 0.97719 | -0.43911 | 19.7499
59 | -0.024211 | -0.0060796 | 0.024222 | 0.0060865 | 1.1322e-05 | 6.9593e-06 | 0.036604 | 0.036604 | 0.036604 | 0.98432 | -0.30116 | 0.98482 | -0.29136 | 10.0561
60 | 0.02164 | 0.005436 | -0.021611 | -0.0054185 | 2.8808e-05 | 1.7526e-05 | 0.032718 | 0.032718 | 0.032718 | 0.98432 | -0.30116 | 0.98289 | -0.32909 | 8.9885
61 | 0.0025711 | 0.00064357 | -0.0025708 | -0.00064398 | 2.606e-07 | -4.1792e-07 | 0.0038865 | 0.0038867 | 0.0038867 | 0.98432 | -0.30116 | 0.98421 | -0.30329 | 1.0678
62 | -0.024222 | -0.0060865 | 0.024229 | 0.0060907 | 6.8416e-06 | 4.2053e-06 | 0.036604 | 0.036604 | 0.036604 | 0.98482 | -0.29136 | 0.98512 | -0.28545 | 10.0561
63 | 0.011957 | 0.0029981 | -0.011953 | -0.002996 | 3.8988e-06 | 2.0933e-06 | 0.018102 | 0.018102 | 0.018102 | 0.98289 | -0.32909 | 0.98254 | -0.33594 | 4.9731
64 | 0.0096542 | 0.0024204 | -0.0096534 | -0.0024199 | 8.8532e-07 | 4.2656e-07 | 0.014616 | 0.014616 | 0.014616 | 0.98289 | -0.32909 | 0.98279 | -0.33102 | 4.0154
65 | 0.00088442 | 0.00022133 | -0.00088441 | -0.00022165 | 1.7503e-08 | -3.2057e-07 | 0.001337 | 0.0013372 | 0.0013372 | 0.98421 | -0.30329 | 0.98419 | -0.3037 | 0.36735
66 | -0.010031 | -0.0025146 | 0.010032 | 0.0025152 | 1.2814e-06 | 6.2919e-07 | 0.015125 | 0.015125 | 0.015125 | 0.98688 | -0.25134 | 0.98702 | -0.24866 | 4.1551
67 | 0.010031 | 0.0025146 | -0.010027 | -0.0025127 | 3.9404e-06 | 1.9352e-06 | 0.015125 | 0.015125 | 0.015125 | 0.98688 | -0.25134 | 0.98646 | -0.25959 | 4.1552
68 | -0.014904 | -0.0037364 | 0.014909 | 0.0037389 | 4.4134e-06 | 2.5265e-06 | 0.02247 | 0.02247 | 0.02247 | 0.98702 | -0.24866 | 0.98734 | -0.24245 | 6.1731
69 | 0.0039758 | 0.00099614 | -0.0039753 | -0.0009963 | 5.1788e-07 | -1.5867e-07 | 0.0059972 | 0.0059974 | 0.0059974 | 0.98646 | -0.25959 | 0.98632 | -0.26232 | 1.6476
70 | 0.0034492 | 0.0008623 | -0.0034476 | -0.00086326 | 1.5555e-06 | -9.5613e-07 | 0.0052048 | 0.0052055 | 0.0052055 | 0.98596 | -0.26915 | 0.98548 | -0.27863 | 1.4301
71 | -0.0050922 | -0.0012728 | 0.005095 | 0.0012729 | 2.7579e-06 | 1.7542e-07 | 0.007684 | 0.0076834 | 0.007684 | 0.98596 | -0.26915 | 0.98655 | -0.25776 | 2.111
72 | 0.001643 | 0.00041045 | -0.0016428 | -0.00041172 | 2.5916e-07 | -1.2676e-06 | 0.0024792 | 0.0024797 | 0.0024797 | 0.98596 | -0.26915 | 0.98579 | -0.27247 | 0.68124
73 | 0.0034476 | 0.00086326 | -0.0034467 | -0.00086383 | 9.3001e-07 | -5.7048e-07 | 0.0052055 | 0.0052059 | 0.0052059 | 0.98548 | -0.27863 | 0.98519 | -0.2843 | 1.4302
74 | 0.044196 | 0.011117 | -0.044138 | -0.01108 | 5.8367e-05 | 3.6908e-05 | 0.066676 | 0.066676 | 0.066676 | 0.98655 | -0.25776 | 0.98512 | -0.28545 | 18.3177
75 | -0.049291 | -0.01239 | 0.049342 | 0.012422 | 5.0463e-05 | 3.1985e-05 | 0.07436 | 0.074359 | 0.07436 | 0.98655 | -0.25776 | 0.98765 | -0.23634 | 20.4284
76 | 0.013342 | 0.0033464 | -0.013338 | -0.003344 | 4.4409e-06 | 2.4899e-06 | 0.020417 | 0.020417 | 0.020417 | 0.97244 | -0.53262 | 0.97208 | -0.53961 | 5.6091
77 | -0.013342 | -0.0033464 | 0.013346 | 0.0033486 | 3.8994e-06 | 2.186e-06 | 0.020417 | 0.020417 | 0.020417 | 0.97244 | -0.53262 | 0.97275 | -0.52649 | 5.6091
78 | 0.012825 | 0.0032155 | -0.012822 | -0.0032137 | 3.1975e-06 | 1.7723e-06 | 0.019633 | 0.019633 | 0.019633 | 0.97208 | -0.53961 | 0.97182 | -0.54484 | 5.3936
79 | -0.01433 | -0.0035953 | 0.014337 | 0.003599 | 6.4172e-06 | 3.6648e-06 | 0.021923 | 0.021922 | 0.021923 | 0.97275 | -0.52649 | 0.97322 | -0.51711 | 6.0227
80 | 0.018479 | 0.0046356 | -0.018474 | -0.0046324 | 5.3742e-06 | 3.203e-06 | 0.027843 | 0.027843 | 0.027843 | 0.98765 | -0.23634 | 0.98734 | -0.24245 | 7.6492
81 | -0.067821 | -0.017058 | 0.067951 | 0.01714 | 0.0001296 | 8.2518e-05 | 0.1022 | 0.1022 | 0.1022 | 0.98765 | -0.23634 | 0.98971 | -0.19642 | 28.0776
82 | 0.011739 | 0.0029425 | -0.011739 | -0.0029424 | 2.1719e-07 | 1.158e-07 | 0.017779 | 0.017779 | 0.017779 | 0.98254 | -0.33594 | 0.98252 | -0.33632 | 4.8843
83 | 0.0092826 | 0.002327 | -0.0092824 | -0.0023269 | 2.4123e-07 | 1.1313e-07 | 0.014055 | 0.014055 | 0.014055 | 0.98279 | -0.33102 | 0.98276 | -0.33156 | 3.8612
84 | -0.0010712 | -0.00026847 | 0.0010712 | 0.00026825 | 1.884e-08 | -2.1883e-07 | 0.0016411 | 0.001641 | 0.0016411 | 0.97127 | -0.55568 | 0.97129 | -0.55531 | 0.45085
85 | -0.0020492 | -0.00051336 | 0.0020493 | 0.00051313 | 8.7572e-08 | -2.3724e-07 | 0.0031394 | 0.0031393 | 0.0031394 | 0.97129 | -0.55531 | 0.97133 | -0.55441 | 0.86246
86 | 0.012421 | 0.0031133 | -0.012418 | -0.0031116 | 3.1325e-06 | 1.7188e-06 | 0.019019 | 0.019019 | 0.019019 | 0.97182 | -0.54484 | 0.97155 | -0.55014 | 5.2251
87 | -0.021429 | -0.0053765 | 0.02144 | 0.0053832 | 1.0996e-05 | 6.6976e-06 | 0.032766 | 0.032766 | 0.032766 | 0.97322 | -0.51711 | 0.97377 | -0.50635 | 9.0017
88 | -0.0089539 | -0.0022441 | 0.0089564 | 0.0022452 | 2.5055e-06 | 1.1433e-06 | 0.013561 | 0.013561 | 0.013561 | 0.98246 | -0.33743 | 0.98276 | -0.33156 | 3.7257
89 | 0.008428 | 0.0021126 | -0.0084267 | -0.002112 | 1.3227e-06 | 5.7241e-07 | 0.012764 | 0.012764 | 0.012764 | 0.98252 | -0.33632 | 0.98235 | -0.33962 | 3.5067
90 | 0.015776 | 0.0039541 | -0.015775 | -0.0039535 | 1.0288e-06 | 5.9651e-07 | 0.02379 | 0.02379 | 0.02379 | 0.98674 | -0.25399 | 0.98667 | -0.25536 | 6.5357
91 | 0.0064648 | 0.0016203 | -0.0064645 | -0.0016201 | 3.8617e-07 | 1.088e-07 | 0.0097497 | 0.0097498 | 0.0097498 | 0.98667 | -0.25536 | 0.98661 | -0.25662 | 2.6785
92 | 0.18657 | 0.047507 | -0.18619 | -0.047265 | 0.00038082 | 0.00024223 | 0.28037 | 0.28037 | 0.28037 | 0.99112 | -0.16898 | 0.98891 | -0.2114 | 25.6747
93 | 0.17728 | 0.045033 | -0.17725 | -0.045016 | 2.6015e-05 | 1.6537e-05 | 0.26697 | 0.26697 | 0.26697 | 0.98891 | -0.2114 | 0.98876 | -0.21445 | 24.4477
94 | 0.046372 | 0.011681 | -0.046358 | -0.011672 | 1.4503e-05 | 9.1849e-06 | 0.070635 | 0.070635 | 0.070635 | 0.97719 | -0.43911 | 0.97685 | -0.44565 | 19.4052
95 | 0.045451 | 0.011445 | -0.04542 | -0.011425 | 3.0912e-05 | 1.9569e-05 | 0.069254 | 0.069254 | 0.069254 | 0.97685 | -0.44565 | 0.97613 | -0.45989 | 19.0259
96 | 0.044307 | 0.011146 | -0.044268 | -0.011121 | 3.8935e-05 | 2.4634e-05 | 0.067556 | 0.067556 | 0.067556 | 0.97613 | -0.45989 | 0.97519 | -0.4783 | 18.5594
97 | -0.0054596 | -0.0013676 | 0.0054602 | 0.0013677 | 5.7642e-07 | 9.6755e-08 | 0.0083627 | 0.0083626 | 0.0083627 | 0.97144 | -0.55235 | 0.97155 | -0.55014 | 2.2974
98 | 0.0040673 | 0.0010187 | -0.004067 | -0.0010188 | 3.9821e-07 | -8.3827e-08 | 0.00623 | 0.0062301 | 0.0062301 | 0.97144 | -0.55235 | 0.97133 | -0.55441 | 1.7116
99 | 0.036551 | 0.0091873 | -0.036525 | -0.0091706 | 2.6631e-05 | 1.6759e-05 | 0.055782 | 0.055782 | 0.055782 | 0.97519 | -0.4783 | 0.97441 | -0.49357 | 15.3248
100 | 0.030016 | 0.0075394 | -0.029998 | -0.007528 | 1.8292e-05 | 1.1418e-05 | 0.045844 | 0.045844 | 0.045844 | 0.97441 | -0.49357 | 0.97377 | -0.50635 | 12.5944
101 | 0.007522 | 0.0018853 | -0.0075213 | -0.001885 | 6.5901e-07 | 2.5041e-07 | 0.011394 | 0.011394 | 0.011394 | 0.98235 | -0.33962 | 0.98225 | -0.34146 | 3.1302
102 | 0.0022919 | 0.00057376 | -0.0022918 | -0.00057405 | 1.3555e-07 | -2.8675e-07 | 0.0034858 | 0.0034859 | 0.0034859 | 0.97832 | -0.41661 | 0.97826 | -0.41785 | 0.95767
103 | 0.0022918 | 0.00057405 | -0.0022917 | -0.00057435 | 1.4025e-07 | -2.9662e-07 | 0.0034859 | 0.0034861 | 0.0034861 | 0.97826 | -0.41785 | 0.97819 | -0.41914 | 0.95771
104 | -0.10768 | -0.027268 | 0.1078 | 0.027345 | 0.00012066 | 7.7069e-05 | 0.16326 | 0.16326 | 0.16326 | 0.98206 | -0.34365 | 0.98327 | -0.32034 | 44.8507
105 | 0.008971 | 0.0022488 | -0.0089697 | -0.0022482 | 1.3002e-06 | 5.9786e-07 | 0.013638 | 0.013638 | 0.013638 | 0.97881 | -0.40698 | 0.97866 | -0.41002 | 3.7467
106 | -0.10935 | -0.027733 | 0.10947 | 0.027809 | 0.00011891 | 7.5958e-05 | 0.1656 | 0.1656 | 0.1656 | 0.98327 | -0.32034 | 0.98443 | -0.29775 | 45.4942
107 | 0.0089697 | 0.0022482 | -0.008969 | -0.0022478 | 7.0297e-07 | 3.2327e-07 | 0.013638 | 0.013638 | 0.013638 | 0.97866 | -0.41002 | 0.97857 | -0.41166 | 3.7467
108 | -0.11494 | -0.029181 | 0.11499 | 0.029215 | 5.4134e-05 | 3.4403e-05 | 0.17387 | 0.17387 | 0.17387 | 0.98443 | -0.29775 | 0.98494 | -0.28796 | 23.8834
109 | -0.0047263 | -0.0011845 | 0.0047264 | 0.0011845 | 3.6125e-08 | -1.1529e-09 | 0.0071238 | 0.0071237 | 0.0071238 | 0.98724 | -0.24387 | 0.98725 | -0.24371 | 1.9571
110 | -0.013651 | -0.0034213 | 0.013654 | 0.0034228 | 2.6608e-06 | 1.4886e-06 | 0.020576 | 0.020576 | 0.020576 | 0.98725 | -0.24371 | 0.98746 | -0.23962 | 5.6526
111 | 0.011473 | 0.0028773 | -0.011465 | -0.0028735 | 7.122e-06 | 3.7987e-06 | 0.017582 | 0.017582 | 0.017582 | 0.97099 | -0.56072 | 0.97033 | -0.57375 | 4.8304
112 | -0.019112 | -0.0047906 | 0.019117 | 0.0047937 | 5.176e-06 | 3.0997e-06 | 0.0288 | 0.0288 | 0.0288 | 0.98746 | -0.23962 | 0.98775 | -0.23394 | 7.912
113 | -0.02532 | -0.0063484 | 0.025322 | 0.0063498 | 2.2253e-06 | 1.372e-06 | 0.038145 | 0.038145 | 0.038145 | 0.98775 | -0.23394 | 0.98785 | -0.23209 | 10.4793
114 | -0.032266 | -0.00809 | 0.032293 | 0.0081069 | 2.715e-05 | 1.6983e-05 | 0.048604 | 0.048604 | 0.048604 | 0.98785 | -0.23209 | 0.98876 | -0.21445 | 13.3527
115 | -0.12652 | -0.032104 | 0.12661 | 0.032163 | 9.2783e-05 | 5.9037e-05 | 0.19129 | 0.19129 | 0.19129 | 0.98494 | -0.28796 | 0.98573 | -0.27273 | 26.2757
116 | -0.13248 | -0.033634 | 0.13272 | 0.033788 | 0.00024124 | 0.00015357 | 0.20015 | 0.20015 | 0.20015 | 0.98573 | -0.27273 | 0.98769 | -0.23496 | 27.4926
117 | -0.14482 | -0.036819 | 0.14496 | 0.036909 | 0.00014319 | 9.0716e-05 | 0.21837 | 0.21837 | 0.21837 | 0.98769 | -0.23496 | 0.98876 | -0.21445 | 19.9968

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60618 | 0.15495

## res_load
| p_mw | q_mvar
0 | 0.015622 | 0.0039152
1 | 0.0091103 | 0.0022833
2 | 0.0088467 | 0.0022172
3 | 0.0024307 | 0.0006092
4 | 0.017588 | 0.0044079
5 | 0.0051218 | 0.0012836
6 | 0.0021335 | 0.00053471
7 | 0.021112 | 0.0052912
8 | 0.021684 | 0.0054344
9 | 0.0061606 | 0.001544
10 | 0.010465 | 0.0026228
11 | 0.0069891 | 0.0017516
12 | 0.0016116 | 0.00040391
13 | 0.013383 | 0.0033542
14 | 0.0076033 | 0.0019056
15 | 0.010565 | 0.002648
16 | 0.0039627 | 0.00099313
17 | 0.007148 | 0.0017915
18 | 0.0037747 | 0.00094603
19 | 0.0026933 | 0.000675
20 | 0.0056493 | 0.0014159
21 | 0.009976 | 0.0025002
22 | 0.0029531 | 0.00074011
23 | 0.0063893 | 0.0016013
24 | 0.0030048 | 0.00075308
25 | 0.012008 | 0.0030096
26 | 0.0023386 | 0.00058612
27 | 0.002927 | 0.00073356
28 | 0.0065068 | 0.0016308
29 | 0.0027759 | 0.0006957
30 | 0.0082225 | 0.0020608
31 | 0.0096512 | 0.0024188
32 | 0.0075405 | 0.0018898
33 | 0.0084679 | 0.0021223
34 | 0.0020662 | 0.00051783
35 | 0.0043667 | 0.0010944
36 | 0.015695 | 0.0039334
37 | 0.01776 | 0.004451
38 | 0.005478 | 0.0013729
39 | 0.011881 | 0.0029776
40 | 0.0016864 | 0.00042265
41 | 0.0048723 | 0.0012211
42 | 0.006051 | 0.0015165
43 | 0.0016428 | 0.00041172
44 | 0.019909 | 0.0049897
45 | 0.00051254 | 0.00012845
46 | 0.00098416 | 0.00024665
47 | 0.0035653 | 0.00089355
48 | 0.0043892 | 0.0011
49 | 0.00021359 | 5.353e-05
50 | 0.00037072 | 9.291e-05
51 | 0.00088441 | 0.00022165
52 | 0.0039753 | 0.0009963
53 | 0.0010712 | 0.00026847
54 | 0.00097803 | 0.00024512
55 | 0.0034467 | 0.00086383
56 | 0.00040074 | 0.00010043
57 | 0.0070924 | 0.0017775
58 | 0.0089539 | 0.0022441
59 | 0.00032597 | 8.1695e-05
60 | 0.0033109 | 0.0008298
61 | 0.0060304 | 0.0015114
62 | 0.0093097 | 0.0023332
63 | 0.0064645 | 0.0016201
64 | 0.0062452 | 0.0015652
65 | 0.0089051 | 0.0022318
66 | 0.0008238 | 0.00020646
67 | 0.00090656 | 0.00022721
68 | 0.0011139 | 0.00027917
69 | 0.0013923 | 0.00034894
70 | 0.006958 | 0.0017438
71 | 0.0020176 | 0.00050566
72 | 0.0077162 | 0.0019339
73 | 0.0065084 | 0.0016312
74 | 0.0085579 | 0.0021448
75 | 0.00090471 | 0.00022674
76 | 0.0075213 | 0.001885
77 | 0.018103 | 0.0045371
78 | 0.0035942 | 0.0009008
79 | 0.0027071 | 0.00067846
80 | 0.0022917 | 0.00057435
81 | 0.0015477 | 0.00038789
82 | 0.005473 | 0.0013717
83 | 0.008969 | 0.0022478
84 | 0.0047263 | 0.0011845
85 | 0.0089249 | 0.0022368
86 | 0.011465 | 0.0028735
87 | 0.0054577 | 0.0013678
88 | 0.0062033 | 0.0015547
89 | 0.0069434 | 0.0017402
90 | 0.011528 | 0.0028891
91 | 0.0058685 | 0.0014708
92 | 0.012094 | 0.003031

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1