## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-27_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-27_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_243-27_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_243-27_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_243-27_0_4_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_243-27_0_4_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_243-27_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_243-27_0_4_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_243-27_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_243-27_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_243-27_0_4_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_243-27_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_243-27_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_243-27_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_243-27_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_243-27_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_243-27_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_243-27_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_243-27_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_243-27_0_4_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_243-27_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_243-27_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_243-27_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_243-27_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_243-27_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_243-27_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_243-27_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_243-27_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_243-27_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_243-27_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_243-27_0_4_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_243-27_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_243-27_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_243-27_0_4_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_243-27_0_4_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_243-27_0_4_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_243-27_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_243-27_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_243-27_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_243-27_0_4_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_243-27_0_4_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_243-27_0_4_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_243-27_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_243-27_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_243-27_0_4_node_45 | 0.4 | n |  | TRUE
45 | bus_MV_515_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-27_0_4_load_0 | 0 | 0.031293 | 0.0078428 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-27_0_4_load_3 | 3 | 0.018693 | 0.0046849 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-27_0_4_load_31 | 5 | 0.023664 | 0.0059307 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-27_0_4_load_21 | 7 | 0.013551 | 0.0033963 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-27_0_4_load_5 | 8 | 0.017793 | 0.0044593 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-27_0_4_load_24 | 10 | 0.012095 | 0.0030312 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-27_0_4_load_7 | 11 | 0.009701 | 0.0024313 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-27_0_4_load_8 | 12 | 0.014172 | 0.0035519 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-27_0_4_load_9 | 13 | 0.0055038 | 0.0013794 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-27_0_4_load_14 | 17 | 0.01271 | 0.0031855 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-27_0_4_load_19 | 18 | 0.013853 | 0.0034718 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-27_0_4_load_20 | 19 | 0.029835 | 0.0074773 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-27_0_4_load_30 | 20 | 0.0091621 | 0.0022962 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-27_0_4_load_35 | 21 | 0.0075664 | 0.0018963 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-27_0_4_load_13 | 22 | 0.0075249 | 0.0018859 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-27_0_4_load_12 | 23 | 0.010471 | 0.0026243 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-27_0_4_load_15 | 24 | 0.016613 | 0.0041637 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-27_0_4_load_16 | 25 | 0.0085203 | 0.0021354 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-27_0_4_load_27 | 27 | 0.0067311 | 0.001687 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_243-27_0_4_load_29 | 28 | 0.0070682 | 0.0017715 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_243-27_0_4_load_28 | 29 | 0.0068593 | 0.0017191 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_243-27_0_4_load_33 | 30 | 0.0088108 | 0.0022082 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_243-27_0_4_load_38 | 32 | 0.0053265 | 0.0013349 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_243-27_0_4_load_39 | 33 | 0.0058589 | 0.0014684 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_243-27_0_4_load_37 | 34 | 0.0047131 | 0.0011812 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_243-27_0_4_load_32 | 36 | 0.0068274 | 0.0017111 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_243-27_0_4_load_34 | 37 | 0.0046303 | 0.0011605 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_243-27_0_4_load_36 | 38 | 0.0039301 | 0.00098497 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_243-27_0_4_load_41 | 39 | 0.0047775 | 0.0011974 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_243-27_0_4_load_46 | 40 | 0.0065404 | 0.0016392 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_243-27_0_4_load_44 | 41 | 0.009613 | 0.0024092 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_243-27_0_4_load_42 | 42 | 0.0083399 | 0.0020902 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_243-27_0_4_load_43 | 43 | 0.0040049 | 0.0010037 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_243-27_0_4_load_45 | 44 | 0.0057481 | 0.0014406 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-27_0_4_line_0 |  | 0 | 1 | 0.038623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-27_0_4_line_1 |  | 1 | 2 | 0.024511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_243-27_0_4_line_2 |  | 1 | 3 | 0.027236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_243-27_0_4_line_3 |  | 2 | 4 | 0.034813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_243-27_0_4_line_4 |  | 2 | 5 | 0.010593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_243-27_0_4_line_5 |  | 3 | 6 | 0.026942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_243-27_0_4_line_6 |  | 4 | 7 | 0.028666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_243-27_0_4_line_7 |  | 6 | 8 | 0.0093808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_243-27_0_4_line_8 |  | 6 | 9 | 0.033396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_243-27_0_4_line_9 |  | 7 | 18 | 0.021808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_243-27_0_4_line_10 |  | 9 | 10 | 0.024089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-27_0_4_line_11 |  | 11 | 12 | 0.018132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_243-27_0_4_line_12 |  | 11 | 13 | 0.036919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_243-27_0_4_line_13 |  | 12 | 14 | 0.030532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_243-27_0_4_line_14 |  | 13 | 15 | 0.016247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_243-27_0_4_line_15 |  | 14 | 16 | 0.019233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_243-27_0_4_line_16 |  | 14 | 17 | 0.0040457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_243-27_0_4_line_17 |  | 15 | 18 | 0.0049749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_243-27_0_4_line_18 |  | 15 | 19 | 0.067343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-27_0_4_line_19 |  | 16 | 20 | 0.044764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-27_0_4_line_20 |  | 16 | 21 | 0.032555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_243-27_0_4_line_21 |  | 17 | 22 | 0.015491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-27_0_4_line_22 |  | 20 | 29 | 0.010054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_243-27_0_4_line_23 |  | 21 | 30 | 0.00066074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_243-27_0_4_line_24 |  | 22 | 23 | 0.015585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_243-27_0_4_line_25 |  | 24 | 25 | 0.04638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_243-27_0_4_line_26 |  | 25 | 26 | 0.02029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-27_0_4_line_27 |  | 26 | 27 | 0.0024173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_243-27_0_4_line_28 |  | 27 | 28 | 0.00019924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_243-27_0_4_line_29 |  | 28 | 29 | 0.024741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_243-27_0_4_line_30 |  | 30 | 36 | 0.025018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_243-27_0_4_line_31 |  | 31 | 32 | 0.051654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_243-27_0_4_line_32 |  | 31 | 33 | 0.024793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_243-27_0_4_line_33 |  | 32 | 34 | 0.036417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_243-27_0_4_line_34 |  | 33 | 35 | 0.031342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_243-27_0_4_line_35 |  | 35 | 39 | 0.022291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_243-27_0_4_line_36 |  | 35 | 38 | 0.023733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_243-27_0_4_line_37 |  | 36 | 37 | 0.011356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_243-27_0_4_line_38 |  | 37 | 38 | 0.013964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_243-27_0_4_line_39 |  | 39 | 40 | 0.025489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_243-27_0_4_line_40 |  | 40 | 41 | 0.0050766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_243-27_0_4_line_41 |  | 41 | 42 | 0.02592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_243-27_0_4_line_42 |  | 42 | 43 | 0.0025414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_243-27_0_4_line_43 |  | 43 | 44 | 0.01107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-27_0_4_trafo_37 | 0.63 MVA 20/0.4 kV | 45 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2672021.0864 | 1250999.1885 | 2672039.8629 | 1251017.5633 | 2672047.1686 | 1251027.5226
1 | 2672021.0864 | 1250999.1885 | 2672027.9223 | 1250988.8975 | 2672034.853 | 1250978.8856
2 | 2672021.0864 | 1250999.1885 | 2672002.5384 | 1251019.1332
3 | 2672034.853 | 1250978.8856 | 2672049.7938 | 1250956.3843 | 2672053.591 | 1250949.5366
4 | 2672034.853 | 1250978.8856 | 2672025.4726 | 1250977.4261 | 2672024.8034 | 1250978.299
5 | 2671982.2065 | 1251036.8101 | 2672002.5384 | 1251019.1332
6 | 2672053.591 | 1250949.5366 | 2672030.2754 | 1250932.8595
7 | 2671982.2065 | 1251036.8101 | 2671979.9317 | 1251027.7092
8 | 2671960.3714 | 1251062.0299 | 2671976.3418 | 1251042.9767 | 2671979.6048 | 1251039.0802 | 2671982.2065 | 1251036.8101
9 | 2672012.8824 | 1250919.7119 | 2672023.5442 | 1250928.0449 | 2672030.2754 | 1250932.8595
10 | 2671960.3714 | 1251062.0299 | 2671955.02 | 1251058.8849 | 2671950.2281 | 1251055.035 | 2671941.9963 | 1251046.6709
11 | 2671967.9764 | 1250882.8821 | 2671955.0808 | 1250870.1354
12 | 2671967.9764 | 1250882.8821 | 2671976.4267 | 1250891.2349 | 2671996.1584 | 1250906.6471
13 | 2671931.3477 | 1250851.2478 | 2671943.524 | 1250858.712 | 2671955.0808 | 1250870.1354
14 | 2672008.9627 | 1250916.6484 | 2671996.1584 | 1250906.6471
15 | 2671919.2463 | 1250866.2228 | 2671931.3477 | 1250851.2478
16 | 2671931.3477 | 1250851.2478 | 2671933.7899 | 1250848.0223
17 | 2672008.9627 | 1250916.6484 | 2672012.8824 | 1250919.7119
18 | 2672008.9627 | 1250916.6484 | 2671971.2263 | 1250953.3054 | 2671960.8301 | 1250963.7451
19 | 2671919.2463 | 1250866.2228 | 2671902.695 | 1250855.3809 | 2671881.8021 | 1250841.6924
20 | 2671919.2463 | 1250866.2228 | 2671897.1335 | 1250890.1156
21 | 2671933.7899 | 1250848.0223 | 2671943.1409 | 1250835.6716
22 | 2671873.3927 | 1250836.1828 | 2671881.8021 | 1250841.6924
23 | 2671896.6847 | 1250890.6006 | 2671897.1335 | 1250890.1156
24 | 2671952.5488 | 1250823.2459 | 2671943.1409 | 1250835.6716
25 | 2671859.3663 | 1250802.9683 | 2671865.0369 | 1250789.7881 | 2671866.8525 | 1250778.2684 | 2671869.3749 | 1250766.9798 | 2671875.2536 | 1250760.4279
26 | 2671850.5093 | 1250821.1902 | 2671854.7288 | 1250813.7471 | 2671859.3663 | 1250802.9683
27 | 2671850.5093 | 1250821.1902 | 2671852.5313 | 1250822.5149
28 | 2671852.6979 | 1250822.6241 | 2671852.5313 | 1250822.5149
29 | 2671873.3927 | 1250836.1828 | 2671852.6979 | 1250822.6241
30 | 2671879.6912 | 1250908.962 | 2671896.6847 | 1250890.6006
31 | 2671884.5501 | 1250988.29 | 2671902.8655 | 1250968.8203 | 2671914.2272 | 1250965.6336 | 2671923.0269 | 1250955.8981
32 | 2671884.5501 | 1250988.29 | 2671867.0304 | 1250970.7472
33 | 2671947.4462 | 1250928.8816 | 2671923.0269 | 1250955.8981
34 | 2671848.7635 | 1250946.4482 | 2671848.6836 | 1250948.6822 | 2671849.1325 | 1250950.8781 | 2671849.8822 | 1250952.5551 | 2671850.9434 | 1250954.0579 | 2671855.5605 | 1250959.2621 | 2671867.0304 | 1250970.7472
35 | 2671848.7635 | 1250946.4482 | 2671840.5794 | 1250943.4468 | 2671828.6943 | 1250936.8901
36 | 2671848.7635 | 1250946.4482 | 2671849.9003 | 1250942.3479 | 2671853.0281 | 1250937.7714 | 2671862.4929 | 1250927.5447
37 | 2671879.6912 | 1250908.962 | 2671871.9776 | 1250917.2965
38 | 2671871.9776 | 1250917.2965 | 2671862.4929 | 1250927.5447
39 | 2671806.3764 | 1250924.5779 | 2671828.6943 | 1250936.8901
40 | 2671801.9314 | 1250922.1257 | 2671806.3764 | 1250924.5779
41 | 2671779.2363 | 1250909.6054 | 2671801.9314 | 1250922.1257
42 | 2671779.2363 | 1250909.6054 | 2671777.0111 | 1250908.3778
43 | 2671767.3179 | 1250903.0303 | 2671777.0111 | 1250908.3778

## bus_geodata
| x | y | coords
0 | 2672047.1686 | 1251027.5226
1 | 2672021.0864 | 1250999.1885
2 | 2672034.853 | 1250978.8856
3 | 2672002.5384 | 1251019.1332
4 | 2672053.591 | 1250949.5366
5 | 2672024.8033 | 1250978.299
6 | 2671982.2065 | 1251036.8101
7 | 2672030.2754 | 1250932.8595
8 | 2671979.9317 | 1251027.7092
9 | 2671960.3714 | 1251062.0299
10 | 2671941.9963 | 1251046.6709
11 | 2671967.9764 | 1250882.8821
12 | 2671955.0808 | 1250870.1354
13 | 2671996.1584 | 1250906.6471
14 | 2671931.3477 | 1250851.2478
15 | 2672008.9627 | 1250916.6484
16 | 2671919.2463 | 1250866.2228
17 | 2671933.7899 | 1250848.0223
18 | 2672012.8824 | 1250919.7119
19 | 2671960.8301 | 1250963.7451
20 | 2671881.8021 | 1250841.6924
21 | 2671897.1335 | 1250890.1156
22 | 2671943.1409 | 1250835.6716
23 | 2671952.5488 | 1250823.2459
24 | 2671875.2536 | 1250760.4279
25 | 2671859.3663 | 1250802.9683
26 | 2671850.5093 | 1250821.1902
27 | 2671852.5313 | 1250822.5149
28 | 2671852.6979 | 1250822.6241
29 | 2671873.3927 | 1250836.1828
30 | 2671896.6847 | 1250890.6006
31 | 2671884.5501 | 1250988.29
32 | 2671923.0269 | 1250955.8981
33 | 2671867.0304 | 1250970.7472
34 | 2671947.4462 | 1250928.8816
35 | 2671848.7635 | 1250946.4482
36 | 2671879.6912 | 1250908.962
37 | 2671871.9776 | 1250917.2965
38 | 2671862.4929 | 1250927.5447
39 | 2671828.6943 | 1250936.8901
40 | 2671806.3764 | 1250924.5779
41 | 2671801.9314 | 1250922.1257
42 | 2671779.2363 | 1250909.6054
43 | 2671777.0111 | 1250908.3778
44 | 2671767.3179 | 1250903.0303
45 | 2671952.9975 | 1250922.7398

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97115 | -0.55632 | 0.031293 | 0.0078428
1 | 0.97228 | -0.53401 | 0 | 0
2 | 0.97319 | -0.51598 | 0 | 0
3 | 0.97166 | -0.54621 | 0.018693 | 0.0046849
4 | 0.97432 | -0.49389 | 0 | 0
5 | 0.97296 | -0.52059 | 0.023664 | 0.0059307
6 | 0.97091 | -0.56109 | 0 | 0
7 | 0.97501 | -0.48027 | 0.013551 | 0.0033963
8 | 0.97075 | -0.56418 | 0.017793 | 0.0044593
9 | 0.97053 | -0.56856 | 0 | 0
10 | 0.97026 | -0.57396 | 0.012095 | 0.0030312
11 | 0.9778 | -0.42562 | 0.009701 | 0.0024313
12 | 0.97854 | -0.41109 | 0.014172 | 0.0035519
13 | 0.97636 | -0.45364 | 0.0055038 | 0.0013794
14 | 0.97989 | -0.3847 | 0 | 0
15 | 0.97576 | -0.46559 | 0 | 0
16 | 0.98088 | -0.36544 | 0 | 0
17 | 0.97978 | -0.38696 | 0.01271 | 0.0031855
18 | 0.9756 | -0.46858 | 0.013853 | 0.0034718
19 | 0.97389 | -0.50244 | 0.029835 | 0.0074773
20 | 0.9786 | -0.41011 | 0.0091621 | 0.0022962
21 | 0.98297 | -0.32485 | 0.0075664 | 0.0018963
22 | 0.97952 | -0.39202 | 0.0075249 | 0.0018859
23 | 0.97937 | -0.39498 | 0.010471 | 0.0026243
24 | 0.97603 | -0.46068 | 0.016613 | 0.0041637
25 | 0.97674 | -0.44659 | 0.0085203 | 0.0021354
26 | 0.97721 | -0.43728 | 0 | 0
27 | 0.97727 | -0.43617 | 0.0067311 | 0.001687
28 | 0.97728 | -0.43606 | 0.0070682 | 0.0017715
29 | 0.97817 | -0.41849 | 0.0068593 | 0.0017191
30 | 0.98301 | -0.32401 | 0.0088108 | 0.0022082
31 | 0.99274 | -0.13713 | 0 | 0
32 | 0.99697 | -0.056959 | 0.0053265 | 0.0013349
33 | 0.99071 | -0.17585 | 0.0058589 | 0.0014684
34 | 1 | 0 | -0.36698 | -0.094466
35 | 0.98819 | -0.22421 | 0 | 0
36 | 0.98471 | -0.2911 | 0.0068274 | 0.0017111
37 | 0.9855 | -0.27585 | 0.0046303 | 0.0011605
38 | 0.98649 | -0.25684 | 0.0039301 | 0.00098497
39 | 0.98739 | -0.23975 | 0.0047775 | 0.0011974
40 | 0.98659 | -0.25537 | 0.0065404 | 0.0016392
41 | 0.98646 | -0.25788 | 0.009613 | 0.0024092
42 | 0.98603 | -0.26629 | 0.0083399 | 0.0020902
43 | 0.986 | -0.26673 | 0.0040049 | 0.0010037
44 | 0.98594 | -0.26787 | 0.0057481 | 0.0014406
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031293 | -0.0078428 | 0.031326 | 0.0078636 | 3.3298e-05 | 2.0832e-05 | 0.047948 | 0.047948 | 0.047948 | 0.97115 | -0.55632 | 0.97228 | -0.53401 | 13.1725
1 | -0.079966 | -0.020075 | 0.080035 | 0.020119 | 6.8848e-05 | 4.3454e-05 | 0.1224 | 0.1224 | 0.1224 | 0.97228 | -0.53401 | 0.97319 | -0.51598 | 16.8125
2 | 0.04864 | 0.012212 | -0.048611 | -0.012194 | 2.8304e-05 | 1.744e-05 | 0.074448 | 0.074448 | 0.074448 | 0.97228 | -0.53401 | 0.97166 | -0.54621 | 10.2264
3 | -0.1037 | -0.026053 | 0.10381 | 0.026121 | 0.00010944 | 6.8743e-05 | 0.15859 | 0.15859 | 0.15859 | 0.97319 | -0.51598 | 0.97432 | -0.49389 | 14.5225
4 | 0.023669 | 0.0059339 | -0.023664 | -0.0059307 | 5.203e-06 | 3.1983e-06 | 0.036191 | 0.036191 | 0.036191 | 0.97319 | -0.51598 | 0.97296 | -0.52059 | 9.9425
5 | 0.029918 | 0.0075093 | -0.029897 | -0.007496 | 2.1213e-05 | 1.3243e-05 | 0.045822 | 0.045822 | 0.045822 | 0.97166 | -0.54621 | 0.97091 | -0.56109 | 12.5884
6 | -0.10381 | -0.026121 | 0.10388 | 0.026163 | 6.7587e-05 | 4.1827e-05 | 0.15859 | 0.15858 | 0.15859 | 0.97432 | -0.49389 | 0.97501 | -0.48027 | 10.8919
7 | 0.017795 | 0.0044608 | -0.017793 | -0.0044593 | 2.6167e-06 | 1.5587e-06 | 0.027273 | 0.027273 | 0.027273 | 0.97091 | -0.56109 | 0.97075 | -0.56418 | 7.4927
8 | 0.012102 | 0.0030352 | -0.012098 | -0.0030329 | 4.3086e-06 | 2.3447e-06 | 0.018548 | 0.018548 | 0.018548 | 0.97091 | -0.56109 | 0.97053 | -0.56856 | 5.0957
9 | -0.11743 | -0.029559 | 0.1175 | 0.0296 | 6.5702e-05 | 4.0961e-05 | 0.17927 | 0.17927 | 0.17927 | 0.97501 | -0.48027 | 0.9756 | -0.46858 | 12.3123
10 | 0.012098 | 0.0030329 | -0.012095 | -0.0030312 | 3.108e-06 | 1.6915e-06 | 0.018548 | 0.018549 | 0.018549 | 0.97053 | -0.56856 | 0.97026 | -0.57396 | 5.0958
11 | -0.17678 | -0.044604 | 0.1769 | 0.044682 | 0.00012312 | 7.7888e-05 | 0.26913 | 0.26913 | 0.26913 | 0.9778 | -0.42562 | 0.97854 | -0.41109 | 18.4841
12 | 0.16708 | 0.042173 | -0.16685 | -0.042032 | 0.00022395 | 0.00014148 | 0.25437 | 0.25437 | 0.25437 | 0.9778 | -0.42562 | 0.97636 | -0.45364 | 17.4702
13 | -0.19107 | -0.048234 | 0.19131 | 0.048387 | 0.00024185 | 0.00015325 | 0.29068 | 0.29068 | 0.29068 | 0.97854 | -0.41109 | 0.97989 | -0.3847 | 19.9643
14 | 0.16135 | 0.040652 | -0.16126 | -0.040594 | 9.2161e-05 | 5.8171e-05 | 0.24598 | 0.24598 | 0.24598 | 0.97636 | -0.45364 | 0.97576 | -0.46559 | 16.8941
15 | -0.22203 | -0.056088 | 0.22224 | 0.056219 | 0.00020517 | 0.00013034 | 0.33732 | 0.33732 | 0.33732 | 0.97989 | -0.3847 | 0.98088 | -0.36544 | 23.1678
16 | 0.030715 | 0.0077011 | -0.030712 | -0.007699 | 3.3007e-06 | 2.0615e-06 | 0.046644 | 0.046644 | 0.046644 | 0.97989 | -0.3847 | 0.97978 | -0.38696 | 12.8142
17 | 0.13137 | 0.033084 | -0.13135 | -0.033072 | 1.873e-05 | 1.1738e-05 | 0.20039 | 0.20039 | 0.20039 | 0.97576 | -0.46559 | 0.9756 | -0.46858 | 13.7633
18 | 0.029887 | 0.00751 | -0.029835 | -0.0074773 | 5.2476e-05 | 3.2745e-05 | 0.045585 | 0.045585 | 0.045585 | 0.97576 | -0.46559 | 0.97389 | -0.50244 | 12.5233
19 | 0.055147 | 0.013894 | -0.055029 | -0.013819 | 0.00011756 | 7.4674e-05 | 0.083685 | 0.083685 | 0.083685 | 0.98088 | -0.36544 | 0.9786 | -0.41011 | 22.9905
20 | -0.27738 | -0.070113 | 0.27792 | 0.070457 | 0.00054097 | 0.00034457 | 0.42101 | 0.42101 | 0.42101 | 0.98088 | -0.36544 | 0.98297 | -0.32485 | 28.9153
21 | 0.018002 | 0.0045135 | -0.017997 | -0.0045109 | 4.3424e-06 | 2.5841e-06 | 0.02734 | 0.02734 | 0.02734 | 0.97978 | -0.38696 | 0.97952 | -0.39202 | 7.5111
22 | 0.045867 | 0.011523 | -0.045849 | -0.011512 | 1.8344e-05 | 1.1614e-05 | 0.069754 | 0.069754 | 0.069754 | 0.9786 | -0.41011 | 0.97817 | -0.41849 | 19.1631
23 | -0.28549 | -0.072354 | 0.2855 | 0.072361 | 1.1585e-05 | 7.3809e-06 | 0.43246 | 0.43246 | 0.43246 | 0.98297 | -0.32485 | 0.98301 | -0.32401 | 29.702
24 | 0.010472 | 0.002625 | -0.010471 | -0.0026243 | 1.4793e-06 | 7.5057e-07 | 0.015909 | 0.015909 | 0.015909 | 0.97952 | -0.39202 | 0.97937 | -0.39498 | 4.3707
25 | -0.016613 | -0.0041637 | 0.016625 | 0.0041703 | 1.1158e-05 | 6.5608e-06 | 0.025328 | 0.025328 | 0.025328 | 0.97603 | -0.46068 | 0.97674 | -0.44659 | 6.9583
26 | -0.025145 | -0.0063057 | 0.025156 | 0.0063126 | 1.1166e-05 | 6.8922e-06 | 0.038308 | 0.038308 | 0.038308 | 0.97674 | -0.44659 | 0.97721 | -0.43728 | 10.5243
27 | -0.025156 | -0.0063126 | 0.025157 | 0.0063134 | 1.3303e-06 | 8.211e-07 | 0.038308 | 0.038308 | 0.038308 | 0.97721 | -0.43728 | 0.97727 | -0.43617 | 10.5242
28 | -0.031889 | -0.0080004 | 0.031889 | 0.0080005 | 1.7617e-07 | 1.1025e-07 | 0.048557 | 0.048557 | 0.048557 | 0.97727 | -0.43617 | 0.97728 | -0.43606 | 13.3399
29 | -0.038957 | -0.0097719 | 0.03899 | 0.0097925 | 3.2647e-05 | 2.0584e-05 | 0.059319 | 0.059319 | 0.059319 | 0.97728 | -0.43606 | 0.97817 | -0.41849 | 16.2965
30 | -0.29431 | -0.074569 | 0.29478 | 0.074866 | 0.00046613 | 0.00029705 | 0.4458 | 0.4458 | 0.4458 | 0.98301 | -0.32401 | 0.98471 | -0.2911 | 30.618
31 | -0.35759 | -0.091594 | 0.35899 | 0.092484 | 0.0013949 | 0.00089004 | 0.5367 | 0.5367 | 0.5367 | 0.99274 | -0.13713 | 0.99697 | -0.056959 | 36.8613
32 | 0.35759 | 0.091594 | -0.35692 | -0.091167 | 0.00066952 | 0.00042721 | 0.5367 | 0.5367 | 0.5367 | 0.99274 | -0.13713 | 0.99071 | -0.17585 | 36.8613
33 | -0.36432 | -0.093819 | 0.36533 | 0.094465 | 0.0010128 | 0.00064626 | 0.54465 | 0.54465 | 0.54465 | 0.99697 | -0.056959 | 1 | 0 | 37.4072
34 | 0.35107 | 0.089699 | -0.35025 | -0.089176 | 0.00081885 | 0.00052246 | 0.5279 | 0.5279 | 0.5279 | 0.99071 | -0.17585 | 0.98819 | -0.22421 | 36.257
35 | 0.039089 | 0.0098211 | -0.03906 | -0.0098028 | 2.8969e-05 | 1.8255e-05 | 0.05887 | 0.05887 | 0.05887 | 0.98819 | -0.22421 | 0.98739 | -0.23975 | 16.173
36 | 0.31116 | 0.079355 | -0.31067 | -0.079043 | 0.00048947 | 0.00031205 | 0.46903 | 0.46903 | 0.46903 | 0.98819 | -0.22421 | 0.98649 | -0.25684 | 32.2138
37 | -0.30161 | -0.076578 | 0.30183 | 0.076719 | 0.00022149 | 0.00014117 | 0.45611 | 0.45611 | 0.45611 | 0.98471 | -0.2911 | 0.9855 | -0.27585 | 31.3265
38 | -0.30646 | -0.077879 | 0.30674 | 0.078058 | 0.00028076 | 0.00017897 | 0.46311 | 0.46311 | 0.46311 | 0.9855 | -0.27585 | 0.98649 | -0.25684 | 31.8067
39 | 0.034283 | 0.0086055 | -0.034257 | -0.0085895 | 2.5518e-05 | 1.6006e-05 | 0.05167 | 0.05167 | 0.05167 | 0.98739 | -0.23975 | 0.98659 | -0.25537 | 14.195
40 | 0.027717 | 0.0069503 | -0.027714 | -0.0069482 | 3.3271e-06 | 2.0646e-06 | 0.041805 | 0.041805 | 0.041805 | 0.98659 | -0.25537 | 0.98646 | -0.25788 | 11.485
41 | 0.018101 | 0.004539 | -0.018093 | -0.0045347 | 7.2466e-06 | 4.3071e-06 | 0.027305 | 0.027305 | 0.027305 | 0.98646 | -0.25788 | 0.98603 | -0.26629 | 7.5013
42 | 0.0097535 | 0.0024445 | -0.0097533 | -0.0024444 | 2.0648e-07 | 9.9729e-08 | 0.014719 | 0.014719 | 0.014719 | 0.98603 | -0.26629 | 0.986 | -0.26673 | 4.0437
43 | 0.0057484 | 0.0014407 | -0.0057481 | -0.0014406 | 3.1243e-07 | 5.8763e-08 | 0.0086751 | 0.0086752 | 0.0086752 | 0.986 | -0.26673 | 0.98594 | -0.26787 | 2.3833

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37169 | 0.095647

## res_load
| p_mw | q_mvar
0 | 0.031293 | 0.0078428
1 | 0.018693 | 0.0046849
2 | 0.023664 | 0.0059307
3 | 0.013551 | 0.0033963
4 | 0.017793 | 0.0044593
5 | 0.012095 | 0.0030312
6 | 0.009701 | 0.0024313
7 | 0.014172 | 0.0035519
8 | 0.0055038 | 0.0013794
9 | 0.01271 | 0.0031855
10 | 0.013853 | 0.0034718
11 | 0.029835 | 0.0074773
12 | 0.0091621 | 0.0022962
13 | 0.0075664 | 0.0018963
14 | 0.0075249 | 0.0018859
15 | 0.010471 | 0.0026243
16 | 0.016613 | 0.0041637
17 | 0.0085203 | 0.0021354
18 | 0.0067311 | 0.001687
19 | 0.0070682 | 0.0017715
20 | 0.0068593 | 0.0017191
21 | 0.0088108 | 0.0022082
22 | 0.0053265 | 0.0013349
23 | 0.0058589 | 0.0014684
24 | 0.0047131 | 0.0011812
25 | 0.0068274 | 0.0017111
26 | 0.0046303 | 0.0011605
27 | 0.0039301 | 0.00098497
28 | 0.0047775 | 0.0011974
29 | 0.0065404 | 0.0016392
30 | 0.009613 | 0.0024092
31 | 0.0083399 | 0.0020902
32 | 0.0040049 | 0.0010037
33 | 0.0057481 | 0.0014406

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1