## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-33_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-33_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_243-33_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_243-33_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_243-33_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_243-33_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_243-33_0_8_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_243-33_0_8_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_243-33_0_8_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_243-33_0_8_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_243-33_0_8_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_243-33_0_8_node_60 | 0.4 | n |  | TRUE
12 | bus_LV_243-33_0_8_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_243-33_0_8_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_243-33_0_8_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_243-33_0_8_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_243-33_0_8_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_243-33_0_8_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_243-33_0_8_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_243-33_0_8_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_243-33_0_8_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_243-33_0_8_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_243-33_0_8_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_243-33_0_8_node_7 | 0.4 | n |  | TRUE
24 | bus_LV_243-33_0_8_node_8 | 0.4 | n |  | TRUE
25 | bus_LV_243-33_0_8_node_9 | 0.4 | n |  | TRUE
26 | bus_LV_243-33_0_8_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_243-33_0_8_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_243-33_0_8_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_243-33_0_8_node_43 | 0.4 | n |  | TRUE
30 | bus_LV_243-33_0_8_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_243-33_0_8_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_243-33_0_8_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_243-33_0_8_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_243-33_0_8_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_243-33_0_8_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_243-33_0_8_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_243-33_0_8_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_243-33_0_8_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_243-33_0_8_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_243-33_0_8_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_243-33_0_8_node_19 | 0.4 | n |  | TRUE
42 | bus_LV_243-33_0_8_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_243-33_0_8_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_243-33_0_8_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_243-33_0_8_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_243-33_0_8_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_243-33_0_8_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_243-33_0_8_node_59 | 0.4 | n |  | TRUE
49 | bus_LV_243-33_0_8_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_243-33_0_8_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_243-33_0_8_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_243-33_0_8_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_243-33_0_8_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_243-33_0_8_node_61 | 0.4 | n |  | TRUE
55 | bus_LV_243-33_0_8_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_243-33_0_8_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_243-33_0_8_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_243-33_0_8_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_243-33_0_8_node_57 | 0.4 | n |  | TRUE
60 | bus_MV_515_0_node_124 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-33_0_8_load_0 | 0 | 0.013282 | 0.0033289 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-33_0_8_load_1 | 1 | 0.0097334 | 0.0024394 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-33_0_8_load_3 | 3 | 0.037313 | 0.0093515 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-33_0_8_load_4 | 4 | 0.028307 | 0.0070943 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-33_0_8_load_38 | 7 | 0.0067393 | 0.001689 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-33_0_8_load_36 | 8 | 0.0095531 | 0.0023942 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-33_0_8_load_60 | 11 | 0.0095318 | 0.0023889 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-33_0_8_load_12 | 12 | 0.0039523 | 0.00099054 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-33_0_8_load_13 | 13 | 0.0048224 | 0.0012086 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-33_0_8_load_15 | 15 | 0.0095923 | 0.0024041 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-33_0_8_load_37 | 19 | 0.0073442 | 0.0018406 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-33_0_8_load_50 | 20 | 0.016321 | 0.0040904 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-33_0_8_load_41 | 22 | 0.0076758 | 0.0019237 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-33_0_8_load_7 | 23 | 0.0062478 | 0.0015659 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-33_0_8_load_8 | 24 | 0.012651 | 0.0031707 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-33_0_8_load_9 | 25 | 0.012918 | 0.0032376 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-33_0_8_load_11 | 27 | 0.012812 | 0.0032111 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-33_0_8_load_42 | 28 | 0.016851 | 0.0042232 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-33_0_8_load_43 | 29 | 0.007615 | 0.0019085 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_243-33_0_8_load_39 | 30 | 0.012305 | 0.0030838 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_243-33_0_8_load_53 | 32 | 0.034821 | 0.0087269 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_243-33_0_8_load_40 | 33 | 0.0063685 | 0.0015961 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_243-33_0_8_load_26 | 35 | 0.010854 | 0.0027202 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_243-33_0_8_load_20 | 37 | 0.012231 | 0.0030653 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_243-33_0_8_load_17 | 38 | 0.0098109 | 0.0024588 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_243-33_0_8_load_24 | 39 | 0.0086434 | 0.0021662 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_243-33_0_8_load_22 | 40 | 0.0086985 | 0.00218 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_243-33_0_8_load_21 | 42 | 0.0087313 | 0.0021883 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_243-33_0_8_load_46 | 43 | 0.0097591 | 0.0024459 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_243-33_0_8_load_45 | 44 | 0.012859 | 0.0032228 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_243-33_0_8_load_30 | 45 | 0.036596 | 0.0091718 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_243-33_0_8_load_34 | 47 | 0.053211 | 0.013336 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_243-33_0_8_load_58 | 50 | 0.053225 | 0.013339 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_243-33_0_8_load_47 | 51 | 0.036056 | 0.0090365 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_243-33_0_8_load_51 | 52 | 0.007213 | 0.0018078 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_243-33_0_8_load_52 | 53 | 0.0069305 | 0.001737 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_243-33_0_8_load_61 | 54 | 0.0070179 | 0.0017588 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_243-33_0_8_load_63 | 55 | 0.0061204 | 0.0015339 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_243-33_0_8_load_62 | 56 | 0.0058043 | 0.0014547 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_243-33_0_8_load_55 | 57 | 0.016318 | 0.0040897 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_243-33_0_8_load_56 | 58 | 0.0089633 | 0.0022464 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_243-33_0_8_load_57 | 59 | 0.0047762 | 0.001197 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-33_0_8_line_0 |  | 0 | 1 | 0.050227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-33_0_8_line_1 |  | 0 | 2 | 0.03003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_243-33_0_8_line_2 |  | 1 | 3 | 0.0072141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_243-33_0_8_line_3 |  | 2 | 4 | 0.049859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_243-33_0_8_line_4 |  | 2 | 5 | 0.056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_243-33_0_8_line_5 |  | 4 | 6 | 0.037973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_243-33_0_8_line_6 |  | 5 | 7 | 0.006221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_243-33_0_8_line_7 |  | 5 | 8 | 0.014633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_243-33_0_8_line_8 |  | 6 | 17 | 0.03502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_243-33_0_8_line_9 |  | 6 | 18 | 0.070822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_243-33_0_8_line_10 |  | 8 | 19 | 0.014483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-33_0_8_line_11 |  | 9 | 10 | 0.028854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_243-33_0_8_line_12 |  | 9 | 11 | 0.021924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_243-33_0_8_line_13 |  | 10 | 20 | 0.030137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_243-33_0_8_line_14 |  | 10 | 21 | 0.016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_243-33_0_8_line_15 |  | 11 | 22 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_243-33_0_8_line_16 |  | 12 | 13 | 0.038113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_243-33_0_8_line_17 |  | 12 | 14 | 0.05998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_243-33_0_8_line_18 |  | 13 | 15 | 0.017097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-33_0_8_line_19 |  | 14 | 16 | 0.05404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-33_0_8_line_20 |  | 16 | 36 | 0.05717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_243-33_0_8_line_21 |  | 16 | 37 | 0.022008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-33_0_8_line_22 |  | 17 | 43 | 0.033414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_243-33_0_8_line_23 |  | 17 | 44 | 0.028015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_243-33_0_8_line_24 |  | 18 | 39 | 0.018989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_243-33_0_8_line_25 |  | 18 | 40 | 0.003855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_243-33_0_8_line_26 |  | 20 | 49 | 0.069524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-33_0_8_line_27 |  | 21 | 45 | 0.012868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_243-33_0_8_line_28 |  | 22 | 33 | 0.011135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_243-33_0_8_line_29 |  | 23 | 24 | 0.034436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_243-33_0_8_line_30 |  | 23 | 25 | 0.0052425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_243-33_0_8_line_31 |  | 24 | 26 | 0.042541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_243-33_0_8_line_32 |  | 25 | 27 | 0.022244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_243-33_0_8_line_33 |  | 26 | 28 | 0.023882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_243-33_0_8_line_34 |  | 26 | 29 | 0.025196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_243-33_0_8_line_35 |  | 26 | 30 | 0.020529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_243-33_0_8_line_36 |  | 27 | 31 | 0.028042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_243-33_0_8_line_37 |  | 29 | 32 | 0.0054457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_243-33_0_8_line_38 |  | 30 | 33 | 0.035015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_243-33_0_8_line_39 |  | 31 | 34 | 0.061004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_243-33_0_8_line_40 |  | 31 | 35 | 0.024407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_243-33_0_8_line_41 |  | 34 | 44 | 0.0030225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_243-33_0_8_line_42 |  | 36 | 38 | 0.018107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_243-33_0_8_line_43 |  | 38 | 41 | 0.038078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_243-33_0_8_line_44 |  | 39 | 41 | 0.05612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_243-33_0_8_line_45 |  | 40 | 42 | 0.030114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_243-33_0_8_line_46 |  | 45 | 46 | 0.0067863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_243-33_0_8_line_47 |  | 46 | 47 | 0.020314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_243-33_0_8_line_48 |  | 47 | 48 | 0.051299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_243-33_0_8_line_49 |  | 48 | 50 | 0.0052976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_243-33_0_8_line_50 |  | 49 | 52 | 0.025628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_243-33_0_8_line_51 |  | 49 | 53 | 0.02531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_243-33_0_8_line_52 |  | 49 | 51 | 0.080206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_243-33_0_8_line_53 |  | 52 | 54 | 0.0071111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_243-33_0_8_line_54 |  | 53 | 55 | 0.018784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_243-33_0_8_line_55 |  | 54 | 56 | 0.011021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_243-33_0_8_line_56 |  | 56 | 59 | 0.024171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_243-33_0_8_line_57 |  | 57 | 58 | 0.0045686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_243-33_0_8_line_58 |  | 58 | 59 | 0.010051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-33_0_8_trafo_6 | 0.63 MVA 20/0.4 kV | 60 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2671830.5889 | 1250572.3299 | 2671788.7082 | 1250544.6043
1 | 2671855.6293 | 1250588.9071 | 2671830.5889 | 1250572.3299
2 | 2671782.6929 | 1250540.622 | 2671788.7082 | 1250544.6043
3 | 2671855.6293 | 1250588.9071 | 2671881.4704 | 1250547.2014 | 2671881.8897 | 1250546.5243
4 | 2671855.6293 | 1250588.9071 | 2671846.4223 | 1250602.9723 | 2671879.6662 | 1250623.7236
5 | 2671902.3255 | 1250514.5197 | 2671885.5884 | 1250540.68 | 2671883.0489 | 1250544.6521 | 2671881.8897 | 1250546.5243
6 | 2671879.6662 | 1250623.7236 | 2671875.8395 | 1250628.6363
7 | 2671879.6662 | 1250623.7236 | 2671888.8043 | 1250612.2948
8 | 2671902.3255 | 1250514.5197 | 2671916.2295 | 1250524.6179 | 2671922.8977 | 1250530.6587 | 2671930.0517 | 1250535.8492
9 | 2671850.151 | 1250476.0483 | 2671905.5905 | 1250509.2444 | 2671902.3255 | 1250514.5197
10 | 2671897.8487 | 1250600.9832 | 2671888.8043 | 1250612.2948
11 | 2671804.5469 | 1250666.5107 | 2671820.5705 | 1250642.4875
12 | 2671820.5705 | 1250642.4875 | 2671839.193 | 1250654.057
13 | 2671804.5469 | 1250666.5107 | 2671787.8267 | 1250691.5836
14 | 2671804.5469 | 1250666.5107 | 2671790.1011 | 1250657.5293
15 | 2671839.193 | 1250654.057 | 2671854.6 | 1250663.6287
16 | 2671686.2245 | 1250471.2863 | 2671667.8858 | 1250504.6974
17 | 2671699.1975 | 1250415.933 | 2671701.9456 | 1250424.6503 | 2671702.8152 | 1250433.267 | 2671702.0188 | 1250442.931 | 2671698.8205 | 1250449.5749 | 2671692.6833 | 1250459.5189 | 2671686.2245 | 1250471.2863
18 | 2671659.6594 | 1250519.6851 | 2671667.8858 | 1250504.6974
19 | 2671699.1975 | 1250415.933 | 2671708.5833 | 1250412.0326 | 2671721.9254 | 1250407.4796 | 2671750.9791 | 1250400.9487
20 | 2671750.9791 | 1250400.9487 | 2671762.3267 | 1250398.3953 | 2671785.4665 | 1250396.4519 | 2671807.9508 | 1250396.2796
21 | 2671750.9791 | 1250400.9487 | 2671750.7005 | 1250417.7241 | 2671749.9206 | 1250422.8961
22 | 2671930.0517 | 1250535.8492 | 2671909.8285 | 1250562.4897
23 | 2671930.0517 | 1250535.8492 | 2671951.1837 | 1250554.2414
24 | 2671850.151 | 1250476.0483 | 2671860.5614 | 1250460.1669
25 | 2671850.151 | 1250476.0483 | 2671847.8689 | 1250479.1553
26 | 2671751.6671 | 1250750.5198 | 2671753.8012 | 1250742.6066 | 2671787.8267 | 1250691.5836
27 | 2671790.1011 | 1250657.5293 | 2671790.4246 | 1250655.7541 | 2671789.7071 | 1250652.6654 | 2671787.1709 | 1250650.1551 | 2671782.8821 | 1250649.6028
28 | 2671864.0586 | 1250669.505 | 2671854.6 | 1250663.6287
29 | 2671961.1049 | 1250640.1758 | 2671938.8603 | 1250666.4627
30 | 2671961.1049 | 1250640.1758 | 2671964.4914 | 1250636.174
31 | 2671911.2386 | 1250698.8161 | 2671929.6318 | 1250677.3683 | 2671938.8603 | 1250666.4627
32 | 2671964.4914 | 1250636.174 | 2671978.8605 | 1250619.1937
33 | 2671911.2386 | 1250698.8161 | 2671919.5889 | 1250703.6987 | 2671931.2771 | 1250711.7775
34 | 2671911.2386 | 1250698.8161 | 2671900.6603 | 1250721.6835
35 | 2671911.2386 | 1250698.8161 | 2671893.8009 | 1250687.9828
36 | 2671997.598 | 1250598.3364 | 2671983.138 | 1250614.1388 | 2671978.8605 | 1250619.1937
37 | 2671898.374 | 1250726.626 | 2671900.6603 | 1250721.6835
38 | 2671893.8009 | 1250687.9828 | 2671864.0586 | 1250669.505
39 | 2671953.4636 | 1250556.2258 | 2671991.6617 | 1250592.9604 | 2671997.598 | 1250598.3364
40 | 2671997.598 | 1250598.3364 | 2672016.0988 | 1250614.2554
41 | 2671953.4636 | 1250556.2258 | 2671951.1837 | 1250554.2414
42 | 2671807.9508 | 1250396.2796 | 2671825.9698 | 1250398.0581
43 | 2671863.5327 | 1250404.1254 | 2671836.4611 | 1250399.0937 | 2671825.9698 | 1250398.0581
44 | 2671860.5614 | 1250460.1669 | 2671863.5327 | 1250404.1254
45 | 2671847.8689 | 1250479.1553 | 2671830.0423 | 1250503.4257
46 | 2671778.2965 | 1250654.2395 | 2671779.9255 | 1250651.2571 | 2671782.8821 | 1250649.6028
47 | 2671778.2965 | 1250654.2395 | 2671757.9821 | 1250654.2868
48 | 2671706.6837 | 1250654.4063 | 2671757.9821 | 1250654.2868
49 | 2671706.6837 | 1250654.4063 | 2671706.334 | 1250652.1115 | 2671704.787 | 1250649.5687
50 | 2671751.6671 | 1250750.5198 | 2671756.3013 | 1250757.4476 | 2671767.4159 | 1250764.7207 | 2671770.8004 | 1250766.8717
51 | 2671751.6671 | 1250750.5198 | 2671733.7811 | 1250768.4282
52 | 2671751.6671 | 1250750.5198 | 2671692.0138 | 1250719.4423 | 2671680.7131 | 1250713.133
53 | 2671770.8004 | 1250766.8717 | 2671776.802 | 1250770.686
54 | 2671721.9949 | 1250782.9519 | 2671727.8788 | 1250774.338 | 2671733.7811 | 1250768.4282
55 | 2671786.1032 | 1250776.5975 | 2671776.802 | 1250770.686
56 | 2671786.1032 | 1250776.5975 | 2671806.5028 | 1250789.5625
57 | 2671818.4777 | 1250797.9398 | 2671814.7805 | 1250795.2562
58 | 2671806.5028 | 1250789.5625 | 2671809.9886 | 1250791.778 | 2671814.7805 | 1250795.2562

## bus_geodata
| x | y | coords
0 | 2671830.5889 | 1250572.3299
1 | 2671788.7082 | 1250544.6043
2 | 2671855.6293 | 1250588.9071
3 | 2671782.6929 | 1250540.622
4 | 2671881.8897 | 1250546.5243
5 | 2671879.6662 | 1250623.7236
6 | 2671902.3255 | 1250514.5197
7 | 2671875.8395 | 1250628.6363
8 | 2671888.8043 | 1250612.2948
9 | 2671820.5705 | 1250642.4875
10 | 2671804.5469 | 1250666.5107
11 | 2671839.193 | 1250654.057
12 | 2671686.2245 | 1250471.2863
13 | 2671667.8858 | 1250504.6974
14 | 2671699.1975 | 1250415.933
15 | 2671659.6594 | 1250519.6851
16 | 2671750.9791 | 1250400.9487
17 | 2671930.0517 | 1250535.8492
18 | 2671850.151 | 1250476.0483
19 | 2671897.8487 | 1250600.9832
20 | 2671787.8267 | 1250691.5836
21 | 2671790.1011 | 1250657.5293
22 | 2671854.6 | 1250663.6287
23 | 2671961.1049 | 1250640.1758
24 | 2671938.8603 | 1250666.4627
25 | 2671964.4914 | 1250636.174
26 | 2671911.2386 | 1250698.8161
27 | 2671978.8605 | 1250619.1937
28 | 2671931.2771 | 1250711.7775
29 | 2671900.6603 | 1250721.6835
30 | 2671893.8009 | 1250687.9828
31 | 2671997.598 | 1250598.3364
32 | 2671898.374 | 1250726.626
33 | 2671864.0586 | 1250669.505
34 | 2671953.4636 | 1250556.2258
35 | 2672016.0988 | 1250614.2554
36 | 2671807.9508 | 1250396.2796
37 | 2671749.9206 | 1250422.8961
38 | 2671825.9698 | 1250398.0581
39 | 2671860.5614 | 1250460.1669
40 | 2671847.8689 | 1250479.1553
41 | 2671863.5327 | 1250404.1254
42 | 2671830.0423 | 1250503.4257
43 | 2671909.8285 | 1250562.4897
44 | 2671951.1837 | 1250554.2414
45 | 2671782.8821 | 1250649.6028
46 | 2671778.2965 | 1250654.2395
47 | 2671757.9821 | 1250654.2868
48 | 2671706.6837 | 1250654.4063
49 | 2671751.6671 | 1250750.5198
50 | 2671704.787 | 1250649.5687
51 | 2671680.7131 | 1250713.133
52 | 2671770.8004 | 1250766.8717
53 | 2671733.7811 | 1250768.4282
54 | 2671776.802 | 1250770.686
55 | 2671721.9949 | 1250782.9519
56 | 2671786.1032 | 1250776.5975
57 | 2671818.4777 | 1250797.9398
58 | 2671814.7805 | 1250795.2562
59 | 2671806.5028 | 1250789.5625
60 | 2671804.5469 | 1250666.5107

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9741 | -0.49889 | 0.013282 | 0.0033289
1 | 0.97189 | -0.54239 | 0.0097334 | 0.0024394
2 | 0.97579 | -0.46567 | 0 | 0
3 | 0.97164 | -0.54736 | 0.037313 | 0.0093515
4 | 0.97774 | -0.42742 | 0.028307 | 0.0070943
5 | 0.97456 | -0.48993 | 0 | 0
6 | 0.97873 | -0.40801 | 0 | 0
7 | 0.97452 | -0.4907 | 0.0067393 | 0.001689
8 | 0.97433 | -0.49447 | 0.0095531 | 0.0023942
9 | 1 | 0 | -0.62041 | -0.15822
10 | 0.99829 | -0.032565 | 0 | 0
11 | 0.99821 | -0.033697 | 0.0095318 | 0.0023889
12 | 0.97082 | -0.5636 | 0.0039523 | 0.00099054
13 | 0.97031 | -0.57376 | 0.0048224 | 0.0012086
14 | 0.97185 | -0.54324 | 0 | 0
15 | 0.97015 | -0.5768 | 0.0095923 | 0.0024041
16 | 0.97278 | -0.52494 | 0 | 0
17 | 0.98019 | -0.37957 | 0 | 0
18 | 0.97764 | -0.42946 | 0 | 0
19 | 0.97423 | -0.49642 | 0.0073442 | 0.0018406
20 | 0.99509 | -0.093652 | 0.016321 | 0.0040904
21 | 0.99774 | -0.043186 | 0 | 0
22 | 0.99678 | -0.060909 | 0.0076758 | 0.0019237
23 | 0.98726 | -0.24274 | 0.0062478 | 0.0015659
24 | 0.98921 | -0.20521 | 0.012651 | 0.0031707
25 | 0.98697 | -0.24832 | 0.012918 | 0.0032376
26 | 0.99175 | -0.15667 | 0 | 0
27 | 0.9858 | -0.27075 | 0.012812 | 0.0032111
28 | 0.99138 | -0.1638 | 0.016851 | 0.0042232
29 | 0.99077 | -0.17563 | 0.007615 | 0.0019085
30 | 0.99325 | -0.12795 | 0.012305 | 0.0030838
31 | 0.98442 | -0.29748 | 0 | 0
32 | 0.9906 | -0.179 | 0.034821 | 0.0087269
33 | 0.99591 | -0.077278 | 0.0063685 | 0.0015961
34 | 0.98156 | -0.35289 | 0 | 0
35 | 0.98417 | -0.30224 | 0.010854 | 0.0027202
36 | 0.97441 | -0.49277 | 0 | 0
37 | 0.97252 | -0.5299 | 0.012231 | 0.0030653
38 | 0.97493 | -0.4826 | 0.0098109 | 0.0024588
39 | 0.97742 | -0.4337 | 0.0086434 | 0.0021662
40 | 0.97757 | -0.43068 | 0.0086985 | 0.00218
41 | 0.97636 | -0.45442 | 0 | 0
42 | 0.97733 | -0.43548 | 0.0087313 | 0.0021883
43 | 0.97989 | -0.38549 | 0.0097591 | 0.0024459
44 | 0.98142 | -0.35564 | 0.012859 | 0.0032228
45 | 0.9969 | -0.059313 | 0.036596 | 0.0091718
46 | 0.99624 | -0.071989 | 0 | 0
47 | 0.99426 | -0.11004 | 0.053211 | 0.013336
48 | 0.99177 | -0.1583 | 0 | 0
49 | 0.98875 | -0.21583 | 0 | 0
50 | 0.99151 | -0.1633 | 0.053225 | 0.013339
51 | 0.98609 | -0.26753 | 0.036056 | 0.0090365
52 | 0.98757 | -0.23875 | 0.007213 | 0.0018078
53 | 0.98845 | -0.22173 | 0.0069305 | 0.001737
54 | 0.98729 | -0.2442 | 0.0070179 | 0.0017588
55 | 0.98835 | -0.22378 | 0.0061204 | 0.0015339
56 | 0.98693 | -0.25127 | 0.0058043 | 0.0014547
57 | 0.98596 | -0.27017 | 0.016318 | 0.0040897
58 | 0.98603 | -0.26884 | 0.0089633 | 0.0022464
59 | 0.98626 | -0.26428 | 0.0047762 | 0.001197
60 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.047153 | 0.011858 | -0.047055 | -0.011796 | 9.7762e-05 | 6.1944e-05 | 0.072045 | 0.072045 | 0.072045 | 0.9741 | -0.49889 | 0.97189 | -0.54239 | 19.7925
1 | -0.060435 | -0.015187 | 0.060531 | 0.015248 | 9.6011e-05 | 6.1073e-05 | 0.092335 | 0.092335 | 0.092335 | 0.9741 | -0.49889 | 0.97579 | -0.46567 | 25.3667
2 | 0.037322 | 0.009357 | -0.037313 | -0.0093515 | 8.8334e-06 | 5.564e-06 | 0.057142 | 0.057142 | 0.057142 | 0.97189 | -0.54239 | 0.97164 | -0.54736 | 15.6985
3 | -0.0842 | -0.021192 | 0.084354 | 0.021289 | 0.0001542 | 9.744e-05 | 0.12843 | 0.12843 | 0.12843 | 0.97579 | -0.46567 | 0.97774 | -0.42742 | 17.6417
4 | 0.023669 | 0.0059432 | -0.023641 | -0.0059264 | 2.7363e-05 | 1.6814e-05 | 0.036097 | 0.036097 | 0.036097 | 0.97579 | -0.46567 | 0.97456 | -0.48993 | 9.9169
5 | -0.11266 | -0.028383 | 0.11277 | 0.028448 | 0.00010472 | 6.5113e-05 | 0.17151 | 0.17151 | 0.17151 | 0.97774 | -0.42742 | 0.97873 | -0.40801 | 11.7796
6 | 0.0067395 | 0.0016891 | -0.0067393 | -0.001689 | 2.4703e-07 | 8.0588e-08 | 0.01029 | 0.01029 | 0.01029 | 0.97456 | -0.48993 | 0.97452 | -0.4907 | 2.827
7 | 0.016902 | 0.0042373 | -0.016898 | -0.0042351 | 3.6546e-06 | 2.1567e-06 | 0.025807 | 0.025807 | 0.025807 | 0.97456 | -0.48993 | 0.97433 | -0.49447 | 7.0899
8 | -0.17953 | -0.045282 | 0.17978 | 0.045437 | 0.00024479 | 0.0001549 | 0.27305 | 0.27305 | 0.27305 | 0.97873 | -0.40801 | 0.98019 | -0.37957 | 18.7537
9 | 0.066766 | 0.016833 | -0.066697 | -0.016793 | 6.8462e-05 | 4.0259e-05 | 0.10154 | 0.10154 | 0.10154 | 0.97873 | -0.40801 | 0.97764 | -0.42946 | 6.9742
10 | 0.0073449 | 0.0018409 | -0.0073442 | -0.0018406 | 6.8339e-07 | 2.5702e-07 | 0.011217 | 0.011217 | 0.011217 | 0.97433 | -0.49447 | 0.97423 | -0.49642 | 3.0817
11 | 0.26066 | 0.066141 | -0.26025 | -0.065881 | 0.00040756 | 0.00025932 | 0.38815 | 0.38815 | 0.38815 | 1 | 0 | 0.99829 | -0.032565 | 26.659
12 | 0.3581 | 0.092079 | -0.35751 | -0.091705 | 0.00058541 | 0.00037351 | 0.53369 | 0.53369 | 0.53369 | 1 | 0 | 0.99821 | -0.033697 | 36.6543
13 | 0.11664 | 0.029667 | -0.1163 | -0.029448 | 0.00034222 | 0.00021863 | 0.17402 | 0.17402 | 0.17402 | 0.99829 | -0.032565 | 0.99509 | -0.093652 | 47.807
14 | 0.14361 | 0.036215 | -0.14354 | -0.036169 | 7.297e-05 | 4.5813e-05 | 0.21414 | 0.21414 | 0.21414 | 0.99829 | -0.032565 | 0.99774 | -0.043186 | 14.7073
15 | 0.34798 | 0.089316 | -0.34752 | -0.089024 | 0.00045888 | 0.00029274 | 0.51948 | 0.51948 | 0.51948 | 0.99821 | -0.033697 | 0.99678 | -0.060909 | 35.6785
16 | 0.014423 | 0.0036174 | -0.014416 | -0.0036134 | 6.9856e-06 | 3.9998e-06 | 0.022108 | 0.022108 | 0.022108 | 0.97082 | -0.5636 | 0.97031 | -0.57376 | 6.0737
17 | -0.018375 | -0.0046079 | 0.018393 | 0.0046186 | 1.7843e-05 | 1.0677e-05 | 0.028166 | 0.028166 | 0.028166 | 0.97082 | -0.5636 | 0.97185 | -0.54324 | 7.7379
18 | 0.0095937 | 0.0024047 | -0.0095923 | -0.0024041 | 1.3878e-06 | 6.7706e-07 | 0.014713 | 0.014713 | 0.014713 | 0.97031 | -0.57376 | 0.97015 | -0.5768 | 4.042
19 | -0.018393 | -0.0046186 | 0.018409 | 0.0046282 | 1.6076e-05 | 9.6185e-06 | 0.028166 | 0.028165 | 0.028166 | 0.97185 | -0.54324 | 0.97278 | -0.52494 | 7.7378
20 | -0.030643 | -0.0076951 | 0.03069 | 0.0077246 | 4.7115e-05 | 2.9442e-05 | 0.046879 | 0.046879 | 0.046879 | 0.97278 | -0.52494 | 0.97441 | -0.49277 | 12.8789
21 | 0.012234 | 0.0030669 | -0.012231 | -0.0030653 | 2.8903e-06 | 1.5766e-06 | 0.018714 | 0.018714 | 0.018714 | 0.97278 | -0.52494 | 0.97252 | -0.5299 | 5.1412
22 | 0.0097618 | 0.0024472 | -0.0097591 | -0.0024459 | 2.7519e-06 | 1.3402e-06 | 0.01482 | 0.01482 | 0.01482 | 0.98019 | -0.37957 | 0.97989 | -0.38549 | 4.0713
23 | -0.18954 | -0.047884 | 0.18976 | 0.048022 | 0.00021765 | 0.00013788 | 0.28787 | 0.28787 | 0.28787 | 0.98019 | -0.37957 | 0.98142 | -0.35564 | 19.7715
24 | 0.049264 | 0.012423 | -0.049254 | -0.012418 | 1.0017e-05 | 5.4585e-06 | 0.075011 | 0.075011 | 0.075011 | 0.97764 | -0.42946 | 0.97742 | -0.4337 | 5.1519
25 | 0.017433 | 0.0043698 | -0.017432 | -0.0043692 | 1.0178e-06 | 6.0305e-07 | 0.026534 | 0.026534 | 0.026534 | 0.97764 | -0.42946 | 0.97757 | -0.43068 | 7.2896
26 | 0.09998 | 0.025358 | -0.099397 | -0.024985 | 0.00058358 | 0.00037259 | 0.14961 | 0.14961 | 0.14961 | 0.99509 | -0.093652 | 0.98875 | -0.21583 | 41.1023
27 | 0.14354 | 0.036169 | -0.14343 | -0.036098 | 0.00011064 | 7.0472e-05 | 0.21414 | 0.21414 | 0.21414 | 0.99774 | -0.043186 | 0.9969 | -0.059313 | 29.4146
28 | 0.33985 | 0.0871 | -0.33958 | -0.086928 | 0.00026943 | 0.00017185 | 0.50802 | 0.50802 | 0.50802 | 0.99678 | -0.060909 | 0.99591 | -0.077278 | 34.8915
29 | -0.2466 | -0.062712 | 0.24705 | 0.062996 | 0.00044677 | 0.00028417 | 0.37201 | 0.37201 | 0.37201 | 0.98726 | -0.24274 | 0.98921 | -0.20521 | 25.5501
30 | 0.24035 | 0.061146 | -0.24029 | -0.061105 | 6.4617e-05 | 4.1087e-05 | 0.36259 | 0.36259 | 0.36259 | 0.98726 | -0.24274 | 0.98697 | -0.24832 | 24.9033
31 | -0.2597 | -0.066167 | 0.26031 | 0.066555 | 0.00060984 | 0.00038811 | 0.39104 | 0.39104 | 0.39104 | 0.98921 | -0.20521 | 0.99175 | -0.15667 | 26.8571
32 | 0.22737 | 0.057868 | -0.22713 | -0.057712 | 0.00024551 | 0.00015599 | 0.34312 | 0.34312 | 0.34312 | 0.98697 | -0.24832 | 0.9858 | -0.27075 | 23.5657
33 | 0.016857 | 0.0042266 | -0.016851 | -0.0042232 | 5.7289e-06 | 3.3585e-06 | 0.025292 | 0.025292 | 0.025292 | 0.99175 | -0.15667 | 0.99138 | -0.1638 | 6.9485
34 | 0.04248 | 0.010663 | -0.042441 | -0.010639 | 3.839e-05 | 2.4245e-05 | 0.063742 | 0.063743 | 0.063743 | 0.99175 | -0.15667 | 0.99077 | -0.17563 | 17.5117
35 | -0.31965 | -0.081445 | 0.32009 | 0.081728 | 0.00044356 | 0.00028281 | 0.48007 | 0.48007 | 0.48007 | 0.99175 | -0.15667 | 0.99325 | -0.12795 | 32.972
36 | 0.21431 | 0.054501 | -0.21404 | -0.054326 | 0.00027559 | 0.00017495 | 0.32378 | 0.32378 | 0.32378 | 0.9858 | -0.27075 | 0.98442 | -0.29748 | 22.2375
37 | 0.034826 | 0.0087304 | -0.034821 | -0.0087269 | 5.5871e-06 | 3.5056e-06 | 0.052306 | 0.052306 | 0.052306 | 0.99077 | -0.17563 | 0.9906 | -0.179 | 14.3697
38 | -0.33239 | -0.084812 | 0.33321 | 0.085332 | 0.00081576 | 0.00052027 | 0.49851 | 0.4985 | 0.49851 | 0.99325 | -0.12795 | 0.99591 | -0.077278 | 34.238
39 | 0.20318 | 0.051604 | -0.20264 | -0.051262 | 0.00054032 | 0.00034271 | 0.30737 | 0.30737 | 0.30737 | 0.98442 | -0.29748 | 0.98156 | -0.35289 | 21.1105
40 | 0.010856 | 0.0027215 | -0.010854 | -0.0027202 | 2.4648e-06 | 1.2672e-06 | 0.01641 | 0.01641 | 0.01641 | 0.98442 | -0.29748 | 0.98417 | -0.30224 | 4.5084
41 | 0.20264 | 0.051262 | -0.20261 | -0.051245 | 2.6771e-05 | 1.698e-05 | 0.30737 | 0.30737 | 0.30737 | 0.98156 | -0.35289 | 0.98142 | -0.35564 | 21.1105
42 | -0.03069 | -0.0077246 | 0.030705 | 0.0077339 | 1.4922e-05 | 9.3243e-06 | 0.046879 | 0.046879 | 0.046879 | 0.97441 | -0.49277 | 0.97493 | -0.4826 | 12.8788
43 | -0.040516 | -0.010193 | 0.040571 | 0.010227 | 5.4629e-05 | 3.4487e-05 | 0.061853 | 0.061853 | 0.061853 | 0.97493 | -0.4826 | 0.97636 | -0.45442 | 16.9926
44 | 0.040611 | 0.010252 | -0.040571 | -0.010227 | 4.0256e-05 | 2.4359e-05 | 0.061852 | 0.061853 | 0.061853 | 0.97742 | -0.4337 | 0.97636 | -0.45442 | 8.4963
45 | 0.0087333 | 0.0021892 | -0.0087313 | -0.0021883 | 1.9957e-06 | 8.9977e-07 | 0.013294 | 0.013294 | 0.013294 | 0.97757 | -0.43068 | 0.97733 | -0.43548 | 3.6521
46 | 0.10683 | 0.026927 | -0.10677 | -0.026885 | 6.4753e-05 | 4.1353e-05 | 0.15951 | 0.15951 | 0.15951 | 0.9969 | -0.059313 | 0.99624 | -0.071989 | 43.8224
47 | 0.10677 | 0.026885 | -0.10657 | -0.026761 | 0.00019383 | 0.00012379 | 0.15951 | 0.15951 | 0.15951 | 0.99624 | -0.071989 | 0.99426 | -0.11004 | 43.8224
48 | 0.05336 | 0.013425 | -0.053238 | -0.013347 | 0.00012274 | 7.789e-05 | 0.079877 | 0.079878 | 0.079878 | 0.99426 | -0.11004 | 0.99177 | -0.1583 | 21.9444
49 | 0.053238 | 0.013347 | -0.053225 | -0.013339 | 1.2675e-05 | 8.0439e-06 | 0.079878 | 0.079878 | 0.079878 | 0.99177 | -0.1583 | 0.99151 | -0.1633 | 21.9444
50 | 0.050196 | 0.01262 | -0.050141 | -0.012585 | 5.4864e-05 | 3.4785e-05 | 0.075556 | 0.075557 | 0.075557 | 0.98875 | -0.21583 | 0.98757 | -0.23875 | 20.7573
51 | 0.013055 | 0.003273 | -0.013051 | -0.003271 | 3.664e-06 | 2.0204e-06 | 0.019648 | 0.019648 | 0.019648 | 0.98875 | -0.21583 | 0.98845 | -0.22173 | 5.3977
52 | 0.036145 | 0.0090925 | -0.036056 | -0.0090365 | 8.9037e-05 | 5.5958e-05 | 0.054408 | 0.054409 | 0.054409 | 0.98875 | -0.21583 | 0.98609 | -0.26753 | 14.9474
53 | 0.042928 | 0.010777 | -0.042917 | -0.01077 | 1.1159e-05 | 7.0507e-06 | 0.064688 | 0.064688 | 0.064688 | 0.98757 | -0.23875 | 0.98729 | -0.2442 | 17.7716
54 | 0.006121 | 0.0015341 | -0.0061204 | -0.0015339 | 5.9809e-07 | 1.4203e-07 | 0.0092145 | 0.0092146 | 0.0092146 | 0.98845 | -0.22173 | 0.98835 | -0.22378 | 2.5315
55 | 0.035899 | 0.0090111 | -0.035887 | -0.0090035 | 1.2101e-05 | 7.6038e-06 | 0.054111 | 0.054111 | 0.054111 | 0.98729 | -0.2442 | 0.98693 | -0.25127 | 14.8658
56 | 0.030083 | 0.0075488 | -0.030064 | -0.0075372 | 1.865e-05 | 1.1627e-05 | 0.04536 | 0.04536 | 0.04536 | 0.98693 | -0.25127 | 0.98626 | -0.26428 | 12.4616
57 | -0.016318 | -0.0040897 | 0.016319 | 0.0040903 | 1.0391e-06 | 6.0675e-07 | 0.024628 | 0.024628 | 0.024628 | 0.98596 | -0.27017 | 0.98603 | -0.26884 | 6.7658
58 | -0.025283 | -0.0063368 | 0.025288 | 0.0063402 | 5.4871e-06 | 3.3835e-06 | 0.038154 | 0.038154 | 0.038154 | 0.98603 | -0.26884 | 0.98626 | -0.26428 | 10.4819

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.62041 | 0.15822

## res_load
| p_mw | q_mvar
0 | 0.013282 | 0.0033289
1 | 0.0097334 | 0.0024394
2 | 0.037313 | 0.0093515
3 | 0.028307 | 0.0070943
4 | 0.0067393 | 0.001689
5 | 0.0095531 | 0.0023942
6 | 0.0095318 | 0.0023889
7 | 0.0039523 | 0.00099054
8 | 0.0048224 | 0.0012086
9 | 0.0095923 | 0.0024041
10 | 0.0073442 | 0.0018406
11 | 0.016321 | 0.0040904
12 | 0.0076758 | 0.0019237
13 | 0.0062478 | 0.0015659
14 | 0.012651 | 0.0031707
15 | 0.012918 | 0.0032376
16 | 0.012812 | 0.0032111
17 | 0.016851 | 0.0042232
18 | 0.007615 | 0.0019085
19 | 0.012305 | 0.0030838
20 | 0.034821 | 0.0087269
21 | 0.0063685 | 0.0015961
22 | 0.010854 | 0.0027202
23 | 0.012231 | 0.0030653
24 | 0.0098109 | 0.0024588
25 | 0.0086434 | 0.0021662
26 | 0.0086985 | 0.00218
27 | 0.0087313 | 0.0021883
28 | 0.0097591 | 0.0024459
29 | 0.012859 | 0.0032228
30 | 0.036596 | 0.0091718
31 | 0.053211 | 0.013336
32 | 0.053225 | 0.013339
33 | 0.036056 | 0.0090365
34 | 0.007213 | 0.0018078
35 | 0.0069305 | 0.001737
36 | 0.0070179 | 0.0017588
37 | 0.0061204 | 0.0015339
38 | 0.0058043 | 0.0014547
39 | 0.016318 | 0.0040897
40 | 0.0089633 | 0.0022464
41 | 0.0047762 | 0.001197

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1