## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-36_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-36_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_243-36_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_243-36_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_243-36_0_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_243-36_0_4_node_35 | 0.4 | n |  | TRUE
6 | bus_LV_243-36_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_243-36_0_4_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_243-36_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_243-36_0_4_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_243-36_0_4_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_243-36_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_243-36_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_243-36_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_243-36_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_243-36_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_243-36_0_4_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_243-36_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_243-36_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_243-36_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_243-36_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_243-36_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_243-36_0_4_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_243-36_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_243-36_0_4_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_243-36_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_243-36_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_243-36_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_243-36_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_243-36_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_243-36_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_243-36_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_243-36_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_243-36_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_243-36_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_243-36_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_243-36_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_243-36_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_243-36_0_4_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_243-36_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_243-36_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_MV_515_0_node_52 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-36_0_4_load_0 | 0 | 0.0060985 | 0.0015284 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-36_0_4_load_3 | 3 | 0.014349 | 0.0035961 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-36_0_4_load_8 | 4 | 0.032294 | 0.0080936 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-36_0_4_load_21 | 7 | 0.0080202 | 0.00201 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-36_0_4_load_14 | 8 | 0.0022986 | 0.00057609 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-36_0_4_load_4 | 10 | 0.008927 | 0.0022373 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-36_0_4_load_5 | 11 | 0.014727 | 0.0036909 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-36_0_4_load_7 | 12 | 0.02536 | 0.0063558 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-36_0_4_load_9 | 13 | 0.031242 | 0.0078301 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-36_0_4_load_26 | 15 | 0.017469 | 0.0043781 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-36_0_4_load_19 | 16 | 0.0069815 | 0.0017497 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-36_0_4_load_24 | 17 | 0.00641 | 0.0016065 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-36_0_4_load_10 | 18 | 0.0020742 | 0.00051985 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-36_0_4_load_11 | 19 | 0.0027541 | 0.00069025 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-36_0_4_load_13 | 21 | 0.0020009 | 0.00050147 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-36_0_4_load_36 | 22 | 0.0034638 | 0.00086811 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-36_0_4_load_22 | 23 | 0.0045314 | 0.0011357 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-36_0_4_load_38 | 24 | 0.0019816 | 0.00049664 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-36_0_4_load_20 | 25 | 0.0052739 | 0.0013218 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_243-36_0_4_load_17 | 26 | 0.0033966 | 0.00085128 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_243-36_0_4_load_16 | 27 | 0.0023016 | 0.00057684 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_243-36_0_4_load_18 | 28 | 0.0041969 | 0.0010518 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_243-36_0_4_load_23 | 29 | 0.017653 | 0.0044244 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_243-36_0_4_load_25 | 30 | 0.021302 | 0.0053389 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_243-36_0_4_load_27 | 31 | 0.0079003 | 0.00198 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_243-36_0_4_load_29 | 32 | 0.013688 | 0.0034305 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_243-36_0_4_load_30 | 33 | 0.0061111 | 0.0015316 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_243-36_0_4_load_28 | 34 | 0.016345 | 0.0040964 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_243-36_0_4_load_32 | 35 | 0.076337 | 0.019132 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_243-36_0_4_load_31 | 36 | 0.045223 | 0.011334 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_243-36_0_4_load_41 | 37 | 0.018761 | 0.004702 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_243-36_0_4_load_40 | 38 | 0.002841 | 0.00071201 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_243-36_0_4_load_39 | 40 | 0.0047089 | 0.0011802 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-36_0_4_line_0 |  | 0 | 1 | 0.030463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-36_0_4_line_1 |  | 1 | 2 | 0.032199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_243-36_0_4_line_2 |  | 1 | 3 | 0.025885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_243-36_0_4_line_3 |  | 2 | 4 | 0.0090871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_243-36_0_4_line_4 |  | 3 | 5 | 0.030849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_243-36_0_4_line_5 |  | 4 | 6 | 0.016615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_243-36_0_4_line_6 |  | 5 | 9 | 0.018908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_243-36_0_4_line_7 |  | 6 | 13 | 0.027758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_243-36_0_4_line_8 |  | 6 | 10 | 0.030518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_243-36_0_4_line_9 |  | 7 | 8 | 0.031135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_243-36_0_4_line_10 |  | 8 | 20 | 0.026095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-36_0_4_line_11 |  | 9 | 39 | 0.014963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_243-36_0_4_line_12 |  | 10 | 11 | 0.045097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_243-36_0_4_line_13 |  | 11 | 12 | 0.027689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_243-36_0_4_line_14 |  | 12 | 14 | 0.020955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_243-36_0_4_line_15 |  | 13 | 15 | 0.028441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_243-36_0_4_line_16 |  | 14 | 16 | 0.026565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_243-36_0_4_line_17 |  | 15 | 17 | 0.018604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_243-36_0_4_line_18 |  | 16 | 26 | 0.025115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-36_0_4_line_19 |  | 17 | 29 | 0.022236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-36_0_4_line_20 |  | 18 | 19 | 0.0040459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_243-36_0_4_line_21 |  | 18 | 20 | 0.027847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-36_0_4_line_22 |  | 19 | 21 | 0.0023581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_243-36_0_4_line_23 |  | 19 | 22 | 0.054907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_243-36_0_4_line_24 |  | 21 | 23 | 0.015524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_243-36_0_4_line_25 |  | 22 | 24 | 0.017994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_243-36_0_4_line_26 |  | 23 | 25 | 0.0016748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-36_0_4_line_27 |  | 25 | 28 | 0.015335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_243-36_0_4_line_28 |  | 26 | 27 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_243-36_0_4_line_29 |  | 27 | 28 | 0.0056411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_243-36_0_4_line_30 |  | 29 | 30 | 0.018078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_243-36_0_4_line_31 |  | 30 | 31 | 0.029183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_243-36_0_4_line_32 |  | 32 | 33 | 0.039563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_243-36_0_4_line_33 |  | 32 | 34 | 0.038312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_243-36_0_4_line_34 |  | 33 | 35 | 0.025102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_243-36_0_4_line_35 |  | 35 | 36 | 0.011557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_243-36_0_4_line_36 |  | 36 | 37 | 0.04404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_243-36_0_4_line_37 |  | 37 | 38 | 0.019666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_243-36_0_4_line_38 |  | 38 | 40 | 0.02768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_243-36_0_4_line_39 |  | 39 | 40 | 0.02732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-36_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 41 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2673601.5133 | 1250254.1065 | 2673577.0916 | 1250235.897
1 | 2673601.5133 | 1250254.1065 | 2673620.2677 | 1250227.8982
2 | 2673601.5133 | 1250254.1065 | 2673585.7574 | 1250274.6442
3 | 2673620.2677 | 1250227.8982 | 2673626.0906 | 1250220.9219
4 | 2673567.714 | 1250299.6532 | 2673570.232 | 1250296.2932 | 2673579.1975 | 1250283.195 | 2673585.7574 | 1250274.6442
5 | 2673636.7373 | 1250208.1663 | 2673626.0906 | 1250220.9219
6 | 2673567.714 | 1250299.6532 | 2673568.1629 | 1250305.4519 | 2673568.3533 | 1250310.1799 | 2673569.0604 | 1250316.471 | 2673569.292 | 1250318.4864
7 | 2673636.7373 | 1250208.1663 | 2673645.5126 | 1250212.2115 | 2673663.6052 | 1250211.9361 | 2673663.6052 | 1250211.9361
8 | 2673636.7373 | 1250208.1663 | 2673642.8657 | 1250200.4257 | 2673657.4193 | 1250185.7831
9 | 2673586.0861 | 1250155.8643 | 2673592.2172 | 1250172.8657 | 2673596.7494 | 1250185.1156
10 | 2673577.2335 | 1250131.3164 | 2673586.0861 | 1250155.8643
11 | 2673569.292 | 1250318.4864 | 2673569.3947 | 1250320.5559 | 2673568.244 | 1250323.844 | 2673566.7325 | 1250327.0164 | 2673564.2277 | 1250332.3558
12 | 2673657.4193 | 1250185.7831 | 2673689.2101 | 1250153.7976
13 | 2673707.2576 | 1250132.9413 | 2673701.3457 | 1250141.5877 | 2673689.2101 | 1250153.7976
14 | 2673711.8761 | 1250112.5865 | 2673709.8626 | 1250123.3248 | 2673707.8589 | 1250132.0618 | 2673707.2576 | 1250132.9413
15 | 2673663.6052 | 1250211.9361 | 2673669.2507 | 1250207.8255 | 2673690.6662 | 1250206.4841
16 | 2673711.8761 | 1250112.5865 | 2673693.9707 | 1250112.3638 | 2673685.3133 | 1250112.4467
17 | 2673709.2336 | 1250205.321 | 2673690.6662 | 1250206.4841
18 | 2673660.2517 | 1250114.0781 | 2673684.8795 | 1250112.4508 | 2673685.3133 | 1250112.4467
19 | 2673709.2336 | 1250205.321 | 2673731.4263 | 1250203.9309
20 | 2673604.0097 | 1250123.7498 | 2673607.9349 | 1250122.7686
21 | 2673577.2335 | 1250131.3164 | 2673587.3626 | 1250127.8952 | 2673596.2384 | 1250125.6927 | 2673604.0097 | 1250123.7498
22 | 2673607.9349 | 1250122.7686 | 2673610.2225 | 1250122.1967
23 | 2673607.9349 | 1250122.7686 | 2673593.3843 | 1250069.8248
24 | 2673625.4079 | 1250119.0217 | 2673617.2544 | 1250120.4387 | 2673610.2225 | 1250122.1967
25 | 2673610.8479 | 1250065.4861 | 2673593.3843 | 1250069.8248
26 | 2673625.4079 | 1250119.0217 | 2673627.058 | 1250118.7349
27 | 2673642.2018 | 1250116.3334 | 2673634.8685 | 1250117.3775 | 2673627.058 | 1250118.7349
28 | 2673660.2517 | 1250114.0781 | 2673656.1287 | 1250114.3505 | 2673647.7866 | 1250115.5382
29 | 2673642.2018 | 1250116.3334 | 2673647.7866 | 1250115.5382
30 | 2673749.4685 | 1250202.8007 | 2673731.4263 | 1250203.9309
31 | 2673749.4685 | 1250202.8007 | 2673778.5947 | 1250200.9763
32 | 2673755.1478 | 1250298.2514 | 2673746.3432 | 1250299.8283 | 2673716.057 | 1250304.3258
33 | 2673755.1478 | 1250298.2514 | 2673783.2601 | 1250293.2162 | 2673792.8281 | 1250291.3276
34 | 2673716.057 | 1250304.3258 | 2673707.7235 | 1250305.5633 | 2673691.1939 | 1250307.7779
35 | 2673679.7393 | 1250309.3126 | 2673691.1939 | 1250307.7779
36 | 2673638.5057 | 1250324.7819 | 2673679.7393 | 1250309.3126
37 | 2673638.5057 | 1250324.7819 | 2673618.9164 | 1250326.5166
38 | 2673591.3923 | 1250329.4439 | 2673617.0168 | 1250326.6848 | 2673618.9164 | 1250326.5166
39 | 2673564.2277 | 1250332.3558 | 2673585.1678 | 1250330.1141 | 2673591.3923 | 1250329.4439

## bus_geodata
| x | y | coords
0 | 2673577.0916 | 1250235.897
1 | 2673601.5133 | 1250254.1065
2 | 2673620.2677 | 1250227.8982
3 | 2673585.7574 | 1250274.6442
4 | 2673626.0906 | 1250220.9219
5 | 2673567.714 | 1250299.6532
6 | 2673636.7373 | 1250208.1663
7 | 2673596.7494 | 1250185.1156
8 | 2673586.0861 | 1250155.8643
9 | 2673569.292 | 1250318.4864
10 | 2673657.4193 | 1250185.7831
11 | 2673689.2101 | 1250153.7976
12 | 2673707.2576 | 1250132.9413
13 | 2673663.6052 | 1250211.9361
14 | 2673711.8761 | 1250112.5865
15 | 2673690.6662 | 1250206.4841
16 | 2673685.3133 | 1250112.4467
17 | 2673709.2336 | 1250205.321
18 | 2673604.0097 | 1250123.7498
19 | 2673607.9349 | 1250122.7686
20 | 2673577.2335 | 1250131.3164
21 | 2673610.2225 | 1250122.1967
22 | 2673593.3843 | 1250069.8248
23 | 2673625.4079 | 1250119.0217
24 | 2673610.8479 | 1250065.4861
25 | 2673627.058 | 1250118.7349
26 | 2673660.2517 | 1250114.0781
27 | 2673647.7866 | 1250115.5382
28 | 2673642.2018 | 1250116.3334
29 | 2673731.4263 | 1250203.9309
30 | 2673749.4685 | 1250202.8007
31 | 2673778.5947 | 1250200.9763
32 | 2673755.1478 | 1250298.2514
33 | 2673716.057 | 1250304.3258
34 | 2673792.8281 | 1250291.3276
35 | 2673691.1939 | 1250307.7779
36 | 2673679.7393 | 1250309.3126
37 | 2673638.5057 | 1250324.7819
38 | 2673618.9164 | 1250326.5166
39 | 2673564.2277 | 1250332.3558
40 | 2673591.3923 | 1250329.4439
41 | 2673636.7373 | 1250208.1663

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99316 | -0.13007 | 0.0060985 | 0.0015284
1 | 0.99333 | -0.12679 | 0 | 0
2 | 0.99536 | -0.0881 | 0 | 0
3 | 0.99174 | -0.15707 | 0.014349 | 0.0035961
4 | 0.99593 | -0.077209 | 0.032294 | 0.0080936
5 | 0.98999 | -0.19067 | 0 | 0
6 | 0.99714 | -0.054193 | 0 | 0
7 | 0.98335 | -0.32073 | 0.0080202 | 0.00201
8 | 0.98358 | -0.31623 | 0.0022986 | 0.00057609
9 | 0.98892 | -0.21132 | 0 | 0
10 | 0.99438 | -0.10693 | 0.008927 | 0.0022373
11 | 0.99068 | -0.17824 | 0.014727 | 0.0036909
12 | 0.98878 | -0.21501 | 0.02536 | 0.0063558
13 | 1 | 0 | -0.41248 | -0.10491
14 | 0.98783 | -0.23344 | 0 | 0
15 | 0.99817 | -0.03513 | 0.017469 | 0.0043781
16 | 0.98662 | -0.25685 | 0.0069815 | 0.0017497
17 | 0.99727 | -0.052481 | 0.00641 | 0.0016065
18 | 0.98409 | -0.30621 | 0.0020742 | 0.00051985
19 | 0.98414 | -0.30531 | 0.0027541 | 0.00069025
20 | 0.98383 | -0.31138 | 0 | 0
21 | 0.98418 | -0.30443 | 0.0020009 | 0.00050147
22 | 0.98386 | -0.31069 | 0.0034638 | 0.00086811
23 | 0.9845 | -0.29812 | 0.0045314 | 0.0011357
24 | 0.98383 | -0.31133 | 0.0019816 | 0.00049664
25 | 0.98455 | -0.2973 | 0.0052739 | 0.0013218
26 | 0.98564 | -0.2759 | 0.0033966 | 0.00085128
27 | 0.98519 | -0.28466 | 0.0023016 | 0.00057684
28 | 0.985 | -0.28837 | 0.0041969 | 0.0010518
29 | 0.99632 | -0.070759 | 0.017653 | 0.0044244
30 | 0.99584 | -0.080033 | 0.021302 | 0.0053389
31 | 0.99563 | -0.084086 | 0.0079003 | 0.00198
32 | 0.97755 | -0.4326 | 0.013688 | 0.0034305
33 | 0.97865 | -0.41095 | 0.0061111 | 0.0015316
34 | 0.97697 | -0.44403 | 0.016345 | 0.0040964
35 | 0.97949 | -0.39445 | 0.076337 | 0.019132
36 | 0.9807 | -0.37087 | 0.045223 | 0.011334
37 | 0.98391 | -0.30814 | 0.018761 | 0.004702
38 | 0.98498 | -0.28733 | 0.002841 | 0.00071201
39 | 0.98807 | -0.22769 | 0 | 0
40 | 0.98652 | -0.25766 | 0.0047089 | 0.0011802
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0060985 | -0.0015284 | 0.0060994 | 0.0015286 | 9.5372e-07 | 2.1611e-07 | 0.0091371 | 0.009137 | 0.0091371 | 0.99316 | -0.13007 | 0.99333 | -0.12679 | 2.5102
1 | -0.20676 | -0.052702 | 0.20714 | 0.052948 | 0.00038689 | 0.00024635 | 0.31004 | 0.31004 | 0.31004 | 0.99333 | -0.12679 | 0.99536 | -0.0881 | 28.3918
2 | 0.20066 | 0.051173 | -0.20036 | -0.050987 | 0.00029296 | 0.00018649 | 0.3009 | 0.3009 | 0.3009 | 0.99333 | -0.12679 | 0.99174 | -0.15707 | 27.5551
3 | -0.20714 | -0.052948 | 0.20725 | 0.053018 | 0.00010919 | 6.9524e-05 | 0.31004 | 0.31004 | 0.31004 | 0.99536 | -0.0881 | 0.99593 | -0.077209 | 28.3917
4 | 0.18602 | 0.047391 | -0.18571 | -0.047199 | 0.00030097 | 0.00019143 | 0.27937 | 0.27937 | 0.27937 | 0.99174 | -0.15707 | 0.98999 | -0.19067 | 25.5836
5 | -0.23955 | -0.061111 | 0.23981 | 0.061281 | 0.00026661 | 0.00016998 | 0.35829 | 0.35829 | 0.35829 | 0.99593 | -0.077209 | 0.99714 | -0.054193 | 32.8102
6 | 0.18571 | 0.047199 | -0.18553 | -0.047082 | 0.00018447 | 0.00011733 | 0.27937 | 0.27937 | 0.27937 | 0.98999 | -0.19067 | 0.98892 | -0.21132 | 25.5837
7 | -0.33898 | -0.086474 | 0.33987 | 0.087042 | 0.00088976 | 0.00056836 | 0.5064 | 0.5064 | 0.5064 | 0.99714 | -0.054193 | 1 | 0 | 46.3734
8 | 0.099171 | 0.025193 | -0.09892 | -0.025032 | 0.00025105 | 0.00016027 | 0.14811 | 0.14811 | 0.14811 | 0.99714 | -0.054193 | 0.99438 | -0.10693 | 40.6897
9 | -0.0080202 | -0.00201 | 0.0080219 | 0.0020107 | 1.7196e-06 | 7.0551e-07 | 0.012136 | 0.012136 | 0.012136 | 0.98335 | -0.32073 | 0.98358 | -0.31623 | 3.3341
10 | -0.010321 | -0.0025868 | 0.010323 | 0.002588 | 2.3856e-06 | 1.1955e-06 | 0.015614 | 0.015613 | 0.015614 | 0.98358 | -0.31623 | 0.98383 | -0.31138 | 4.2894
11 | 0.18553 | 0.047082 | -0.18538 | -0.046989 | 0.00014598 | 9.2853e-05 | 0.27937 | 0.27937 | 0.27937 | 0.98892 | -0.21132 | 0.98807 | -0.22769 | 25.5837
12 | 0.089993 | 0.022795 | -0.089685 | -0.022599 | 0.00030708 | 0.00019595 | 0.13475 | 0.13475 | 0.13475 | 0.99438 | -0.10693 | 0.99068 | -0.17824 | 37.0198
13 | 0.074958 | 0.018908 | -0.074827 | -0.018824 | 0.00013172 | 8.3948e-05 | 0.11263 | 0.11263 | 0.11263 | 0.99068 | -0.17824 | 0.98878 | -0.21501 | 30.9429
14 | 0.049467 | 0.012468 | -0.049423 | -0.012441 | 4.3576e-05 | 2.762e-05 | 0.074468 | 0.074468 | 0.074468 | 0.98878 | -0.21501 | 0.98783 | -0.23344 | 20.4582
15 | 0.070953 | 0.017866 | -0.070834 | -0.01779 | 0.00011895 | 7.5757e-05 | 0.10561 | 0.10561 | 0.10561 | 1 | 0 | 0.99817 | -0.03513 | 29.0134
16 | 0.049423 | 0.012441 | -0.049368 | -0.012406 | 5.5242e-05 | 3.5015e-05 | 0.074468 | 0.074468 | 0.074468 | 0.98783 | -0.23344 | 0.98662 | -0.25685 | 20.4582
17 | 0.053365 | 0.013412 | -0.053321 | -0.013384 | 4.4168e-05 | 2.8024e-05 | 0.079568 | 0.079568 | 0.079568 | 0.99817 | -0.03513 | 0.99727 | -0.052481 | 21.8592
18 | 0.042386 | 0.010656 | -0.042348 | -0.010632 | 3.8503e-05 | 2.4321e-05 | 0.063938 | 0.063939 | 0.063939 | 0.98662 | -0.25685 | 0.98564 | -0.2759 | 17.5655
19 | 0.046911 | 0.011778 | -0.04687 | -0.011752 | 4.0863e-05 | 2.5862e-05 | 0.070003 | 0.070003 | 0.070003 | 0.99727 | -0.052481 | 0.99632 | -0.070759 | 19.2317
20 | -0.0124 | -0.0031092 | 0.0124 | 0.0031094 | 5.3338e-07 | 2.8996e-07 | 0.01875 | 0.01875 | 0.01875 | 0.98409 | -0.30621 | 0.98414 | -0.30531 | 5.151
21 | 0.010325 | 0.0025893 | -0.010323 | -0.002588 | 2.5457e-06 | 1.2755e-06 | 0.015613 | 0.015613 | 0.015613 | 0.98409 | -0.30621 | 0.98383 | -0.31138 | 4.2894
22 | -0.020601 | -0.0051644 | 0.020602 | 0.005165 | 8.5801e-07 | 5.1916e-07 | 0.031149 | 0.031149 | 0.031149 | 0.98414 | -0.30531 | 0.98418 | -0.30443 | 8.5576
23 | 0.0054469 | 0.0013648 | -0.0054455 | -0.0013646 | 1.3965e-06 | 1.9632e-07 | 0.0082355 | 0.0082358 | 0.0082358 | 0.98414 | -0.30531 | 0.98386 | -0.31069 | 2.2626
24 | -0.022603 | -0.0056664 | 0.02261 | 0.0056706 | 6.799e-06 | 4.154e-06 | 0.034175 | 0.034175 | 0.034175 | 0.98418 | -0.30443 | 0.9845 | -0.29812 | 9.3886
25 | 0.0019817 | 0.00049645 | -0.0019816 | -0.00049664 | 6.0615e-08 | -1.8972e-07 | 0.0029971 | 0.0029972 | 0.0029972 | 0.98386 | -0.31069 | 0.98383 | -0.31133 | 0.8234
26 | -0.027141 | -0.0068063 | 0.027142 | 0.0068069 | 1.057e-06 | 6.5518e-07 | 0.041024 | 0.041024 | 0.041024 | 0.9845 | -0.29812 | 0.98455 | -0.2973 | 11.2702
27 | -0.032416 | -0.0081287 | 0.03243 | 0.0081373 | 1.3804e-05 | 8.6394e-06 | 0.048994 | 0.048994 | 0.048994 | 0.98455 | -0.2973 | 0.985 | -0.28837 | 13.46
28 | 0.038951 | 0.0097803 | -0.038935 | -0.0097701 | 1.6288e-05 | 1.0264e-05 | 0.058811 | 0.058811 | 0.058811 | 0.98564 | -0.2759 | 0.98519 | -0.28466 | 16.1568
29 | 0.036633 | 0.0091932 | -0.036627 | -0.0091892 | 6.4772e-06 | 4.0736e-06 | 0.055334 | 0.055334 | 0.055334 | 0.98519 | -0.28466 | 0.985 | -0.28837 | 15.2018
30 | 0.029217 | 0.0073275 | -0.029204 | -0.0073194 | 1.2909e-05 | 8.0265e-06 | 0.043638 | 0.043638 | 0.043638 | 0.99632 | -0.070759 | 0.99584 | -0.080033 | 11.9884
31 | 0.0079018 | 0.0019806 | -0.0079003 | -0.00198 | 1.5257e-06 | 5.9683e-07 | 0.011807 | 0.011807 | 0.011807 | 0.99584 | -0.080033 | 0.99563 | -0.084086 | 3.2438
32 | -0.030042 | -0.0075321 | 0.030073 | 0.0075515 | 3.1026e-05 | 1.936e-05 | 0.04573 | 0.04573 | 0.04573 | 0.97755 | -0.4326 | 0.97865 | -0.41095 | 12.5633
33 | 0.016354 | 0.0041017 | -0.016345 | -0.0040964 | 8.904e-06 | 5.2186e-06 | 0.024895 | 0.024895 | 0.024895 | 0.97755 | -0.4326 | 0.97697 | -0.44403 | 6.8393
34 | -0.036184 | -0.0090831 | 0.036212 | 0.009101 | 2.8498e-05 | 1.7923e-05 | 0.055022 | 0.055022 | 0.055022 | 0.97865 | -0.41095 | 0.97949 | -0.39445 | 15.1159
35 | -0.11255 | -0.028233 | 0.11268 | 0.028314 | 0.00012671 | 8.095e-05 | 0.17099 | 0.17099 | 0.17099 | 0.97949 | -0.39445 | 0.9807 | -0.37087 | 46.9753
36 | -0.1579 | -0.039648 | 0.15837 | 0.03995 | 0.00047408 | 0.00030229 | 0.23961 | 0.23961 | 0.23961 | 0.9807 | -0.37087 | 0.98391 | -0.30814 | 32.9131
37 | -0.17713 | -0.044652 | 0.17731 | 0.044764 | 0.00017654 | 0.00011223 | 0.26798 | 0.26798 | 0.26798 | 0.98391 | -0.30814 | 0.98498 | -0.28733 | 24.5403
38 | -0.18015 | -0.045476 | 0.18041 | 0.045639 | 0.00025649 | 0.0001631 | 0.27227 | 0.27227 | 0.27227 | 0.98498 | -0.28733 | 0.98652 | -0.25766 | 24.9333
39 | 0.18538 | 0.046989 | -0.18512 | -0.04682 | 0.00026654 | 0.00016954 | 0.27937 | 0.27937 | 0.27937 | 0.98807 | -0.22769 | 0.98652 | -0.25766 | 25.5837

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44372 | 0.11274

## res_load
| p_mw | q_mvar
0 | 0.0060985 | 0.0015284
1 | 0.014349 | 0.0035961
2 | 0.032294 | 0.0080936
3 | 0.0080202 | 0.00201
4 | 0.0022986 | 0.00057609
5 | 0.008927 | 0.0022373
6 | 0.014727 | 0.0036909
7 | 0.02536 | 0.0063558
8 | 0.031242 | 0.0078301
9 | 0.017469 | 0.0043781
10 | 0.0069815 | 0.0017497
11 | 0.00641 | 0.0016065
12 | 0.0020742 | 0.00051985
13 | 0.0027541 | 0.00069025
14 | 0.0020009 | 0.00050147
15 | 0.0034638 | 0.00086811
16 | 0.0045314 | 0.0011357
17 | 0.0019816 | 0.00049664
18 | 0.0052739 | 0.0013218
19 | 0.0033966 | 0.00085128
20 | 0.0023016 | 0.00057684
21 | 0.0041969 | 0.0010518
22 | 0.017653 | 0.0044244
23 | 0.021302 | 0.0053389
24 | 0.0079003 | 0.00198
25 | 0.013688 | 0.0034305
26 | 0.0061111 | 0.0015316
27 | 0.016345 | 0.0040964
28 | 0.076337 | 0.019132
29 | 0.045223 | 0.011334
30 | 0.018761 | 0.004702
31 | 0.002841 | 0.00071201
32 | 0.0047089 | 0.0011802

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1