## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_243-44_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_243-44_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_243-44_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_243-44_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_243-44_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_243-44_0_6_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_243-44_0_6_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_243-44_0_6_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_243-44_0_6_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_243-44_0_6_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_243-44_0_6_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_243-44_0_6_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_243-44_0_6_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_243-44_0_6_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_243-44_0_6_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_243-44_0_6_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_243-44_0_6_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_243-44_0_6_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_243-44_0_6_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_243-44_0_6_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_243-44_0_6_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_243-44_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_243-44_0_6_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_243-44_0_6_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_243-44_0_6_node_106 | 0.4 | n |  | TRUE
25 | bus_LV_243-44_0_6_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_243-44_0_6_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_243-44_0_6_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_243-44_0_6_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_243-44_0_6_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_243-44_0_6_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_243-44_0_6_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_243-44_0_6_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_243-44_0_6_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_243-44_0_6_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_243-44_0_6_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_243-44_0_6_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_243-44_0_6_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_243-44_0_6_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_243-44_0_6_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_243-44_0_6_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_243-44_0_6_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_243-44_0_6_node_103 | 0.4 | n |  | TRUE
43 | bus_LV_243-44_0_6_node_104 | 0.4 | n |  | TRUE
44 | bus_LV_243-44_0_6_node_105 | 0.4 | n |  | TRUE
45 | bus_LV_243-44_0_6_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_243-44_0_6_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_243-44_0_6_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_243-44_0_6_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_243-44_0_6_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_243-44_0_6_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_243-44_0_6_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_243-44_0_6_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_243-44_0_6_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_243-44_0_6_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_243-44_0_6_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_243-44_0_6_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_243-44_0_6_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_243-44_0_6_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_243-44_0_6_node_109 | 0.4 | n |  | TRUE
60 | bus_LV_243-44_0_6_node_118 | 0.4 | n |  | TRUE
61 | bus_LV_243-44_0_6_node_119 | 0.4 | n |  | TRUE
62 | bus_LV_243-44_0_6_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_243-44_0_6_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_243-44_0_6_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_243-44_0_6_node_99 | 0.4 | n |  | TRUE
66 | bus_LV_243-44_0_6_node_120 | 0.4 | n |  | TRUE
67 | bus_LV_243-44_0_6_node_123 | 0.4 | n |  | TRUE
68 | bus_LV_243-44_0_6_node_121 | 0.4 | n |  | TRUE
69 | bus_LV_243-44_0_6_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_243-44_0_6_node_132 | 0.4 | n |  | TRUE
71 | bus_LV_243-44_0_6_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_243-44_0_6_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_243-44_0_6_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_243-44_0_6_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_243-44_0_6_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_243-44_0_6_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_243-44_0_6_node_83 | 0.4 | n |  | TRUE
78 | bus_LV_243-44_0_6_node_87 | 0.4 | n |  | TRUE
79 | bus_LV_243-44_0_6_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_243-44_0_6_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_243-44_0_6_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_243-44_0_6_node_90 | 0.4 | n |  | TRUE
83 | bus_LV_243-44_0_6_node_91 | 0.4 | n |  | TRUE
84 | bus_LV_243-44_0_6_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_243-44_0_6_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_243-44_0_6_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_243-44_0_6_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_243-44_0_6_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_243-44_0_6_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_243-44_0_6_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_243-44_0_6_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_243-44_0_6_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_243-44_0_6_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_243-44_0_6_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_243-44_0_6_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_243-44_0_6_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_243-44_0_6_node_108 | 0.4 | n |  | TRUE
98 | bus_LV_243-44_0_6_node_100 | 0.4 | n |  | TRUE
99 | bus_LV_243-44_0_6_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_243-44_0_6_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_243-44_0_6_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_243-44_0_6_node_128 | 0.4 | n |  | TRUE
103 | bus_LV_243-44_0_6_node_127 | 0.4 | n |  | TRUE
104 | bus_LV_243-44_0_6_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_243-44_0_6_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_243-44_0_6_node_107 | 0.4 | n |  | TRUE
107 | bus_LV_243-44_0_6_node_101 | 0.4 | n |  | TRUE
108 | bus_LV_243-44_0_6_node_129 | 0.4 | n |  | TRUE
109 | bus_LV_243-44_0_6_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_243-44_0_6_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_243-44_0_6_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_243-44_0_6_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_243-44_0_6_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_243-44_0_6_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_243-44_0_6_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_243-44_0_6_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_243-44_0_6_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_243-44_0_6_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_243-44_0_6_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_243-44_0_6_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_243-44_0_6_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_243-44_0_6_node_124 | 0.4 | n |  | TRUE
123 | bus_LV_243-44_0_6_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_243-44_0_6_node_125 | 0.4 | n |  | TRUE
125 | bus_LV_243-44_0_6_node_126 | 0.4 | n |  | TRUE
126 | bus_LV_243-44_0_6_node_131 | 0.4 | n |  | TRUE
127 | bus_LV_243-44_0_6_node_130 | 0.4 | n |  | TRUE
128 | bus_MV_515_0_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_243-44_0_6_load_0 | 0 | 0.0016388 | 0.00041072 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_243-44_0_6_load_1 | 1 | 0.00061222 | 0.00015344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_243-44_0_6_load_4 | 3 | 0.001289 | 0.00032306 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_243-44_0_6_load_5 | 4 | 0.001302 | 0.00032631 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_243-44_0_6_load_7 | 6 | 0.00079861 | 0.00020015 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_243-44_0_6_load_11 | 8 | 0.00099391 | 0.0002491 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_243-44_0_6_load_8 | 9 | 0.00050326 | 0.00012613 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_243-44_0_6_load_10 | 10 | 0.0024766 | 0.00062068 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_243-44_0_6_load_13 | 12 | 0.0014274 | 0.00035773 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_243-44_0_6_load_14 | 13 | 0.00083742 | 0.00020988 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_243-44_0_6_load_15 | 14 | 0.0057223 | 0.0014341 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_243-44_0_6_load_16 | 15 | 0.00098355 | 0.0002465 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_243-44_0_6_load_17 | 16 | 0.0033771 | 0.00084639 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_243-44_0_6_load_23 | 17 | 0.0035148 | 0.00088088 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_243-44_0_6_load_18 | 19 | 0.0071283 | 0.0017865 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_243-44_0_6_load_21 | 21 | 0.0018482 | 0.00046321 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_243-44_0_6_load_106 | 24 | 0.0010117 | 0.00025356 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_243-44_0_6_load_25 | 26 | 0.0077256 | 0.0019362 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_243-44_0_6_load_26 | 27 | 0.0071087 | 0.0017816 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_243-44_0_6_load_28 | 28 | 0.0070661 | 0.0017709 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_243-44_0_6_load_27 | 29 | 0.0031574 | 0.00079133 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_243-44_0_6_load_32 | 32 | 0.0027521 | 0.00068973 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_243-44_0_6_load_33 | 33 | 0.002262 | 0.00056691 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_243-44_0_6_load_35 | 35 | 0.0025699 | 0.00064407 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_243-44_0_6_load_38 | 38 | 0.0067873 | 0.0017011 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_243-44_0_6_load_39 | 39 | 0.012214 | 0.0030611 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_243-44_0_6_load_40 | 40 | 0.0042513 | 0.0010655 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_243-44_0_6_load_42 | 41 | 0.014213 | 0.0035621 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_243-44_0_6_load_43 | 45 | 0.0050108 | 0.0012558 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_243-44_0_6_load_44 | 46 | 0.0074941 | 0.0018782 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_243-44_0_6_load_46 | 48 | 0.0043924 | 0.0011008 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_243-44_0_6_load_47 | 49 | 0.0032587 | 0.0008167 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_243-44_0_6_load_48 | 50 | 0.0044114 | 0.0011056 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_243-44_0_6_load_49 | 51 | 0.012863 | 0.0032238 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_243-44_0_6_load_50 | 52 | 0.0073411 | 0.0018399 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_243-44_0_6_load_51 | 53 | 0.0034409 | 0.00086236 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_243-44_0_6_load_54 | 56 | 0.0022322 | 0.00055944 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_243-44_0_6_load_60 | 58 | 0.0023416 | 0.00058685 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_243-44_0_6_load_109 | 59 | 0.0024106 | 0.00060415 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_243-44_0_6_load_56 | 62 | 0.0013917 | 0.0003488 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_243-44_0_6_load_61 | 64 | 0.0014985 | 0.00037555 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_243-44_0_6_load_99 | 65 | 0.0022438 | 0.00056234 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_243-44_0_6_load_120 | 66 | 0.0095018 | 0.0023814 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_243-44_0_6_load_121 | 68 | 0.0064452 | 0.0016153 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_243-44_0_6_load_58 | 69 | 0.0021684 | 0.00054345 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_243-44_0_6_load_132 | 70 | 0.0014619 | 0.00036639 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_243-44_0_6_load_59 | 71 | 0.0026579 | 0.00066614 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_243-44_0_6_load_62 | 72 | 0.0087712 | 0.0021983 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_243-44_0_6_load_87 | 78 | 0.0034201 | 0.00085715 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_243-44_0_6_load_67 | 79 | 0.0077419 | 0.0019403 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_243-44_0_6_load_89 | 80 | 0.0038897 | 0.00097485 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_243-44_0_6_load_72 | 81 | 0.0028384 | 0.00071137 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_243-44_0_6_load_68 | 84 | 0.0043074 | 0.0010795 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_243-44_0_6_load_69 | 85 | 0.010899 | 0.0027316 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_243-44_0_6_load_70 | 86 | 0.0042682 | 0.0010697 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_243-44_0_6_load_73 | 88 | 0.008123 | 0.0020358 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_243-44_0_6_load_81 | 90 | 0.0071666 | 0.0017961 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_243-44_0_6_load_74 | 92 | 0.0026822 | 0.00067221 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_243-44_0_6_load_75 | 93 | 0.0068865 | 0.0017259 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_243-44_0_6_load_77 | 94 | 0.014922 | 0.0037399 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_243-44_0_6_load_79 | 95 | 0.0077344 | 0.0019384 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_243-44_0_6_load_80 | 96 | 0.0069992 | 0.0017542 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_243-44_0_6_load_108 | 97 | 0.013418 | 0.0033629 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_243-44_0_6_load_100 | 98 | 0.0082207 | 0.0020603 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_243-44_0_6_load_84 | 99 | 0.00769 | 0.0019273 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_243-44_0_6_load_85 | 100 | 0.0030012 | 0.00075216 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_243-44_0_6_load_128 | 102 | 0.0085526 | 0.0021435 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_243-44_0_6_load_127 | 103 | 0.0084998 | 0.0021303 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_243-44_0_6_load_92 | 104 | 0.0071677 | 0.0017964 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_243-44_0_6_load_86 | 105 | 0.0161 | 0.004035 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_243-44_0_6_load_107 | 106 | 0.012455 | 0.0031216 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_243-44_0_6_load_101 | 107 | 0.0082125 | 0.0020582 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_243-44_0_6_load_129 | 108 | 0.0083044 | 0.0020813 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_243-44_0_6_load_94 | 109 | 0.02732 | 0.0068469 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_243-44_0_6_load_95 | 110 | 0.01066 | 0.0026716 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_243-44_0_6_load_96 | 111 | 0.015574 | 0.0039033 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_243-44_0_6_load_102 | 114 | 0.0088193 | 0.0022103 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_243-44_0_6_load_113 | 115 | 0.0058159 | 0.0014576 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_243-44_0_6_load_112 | 116 | 0.010362 | 0.0025968 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_243-44_0_6_load_117 | 117 | 0.022899 | 0.0057391 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_243-44_0_6_load_110 | 118 | 0.0055812 | 0.0013988 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_243-44_0_6_load_116 | 119 | 0.0025893 | 0.00064894 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_243-44_0_6_load_111 | 120 | 0.013714 | 0.003437 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_243-44_0_6_load_115 | 121 | 0.013328 | 0.0033402 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_243-44_0_6_load_124 | 122 | 0.010287 | 0.0025781 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_243-44_0_6_load_122 | 123 | 0.0064466 | 0.0016157 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_243-44_0_6_load_125 | 124 | 0.0097741 | 0.0024496 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_243-44_0_6_load_126 | 125 | 0.0085913 | 0.0021532 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_243-44_0_6_load_131 | 126 | 0.0086442 | 0.0021664 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_243-44_0_6_load_130 | 127 | 0.0085099 | 0.0021328 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 111 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_243-44_0_6_line_0 |  | 0 | 1 | 0.013692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_243-44_0_6_line_1 |  | 0 | 2 | 0.067991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_243-44_0_6_line_2 |  | 2 | 3 | 0.076567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_243-44_0_6_line_3 |  | 2 | 4 | 0.0088378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_243-44_0_6_line_4 |  | 3 | 5 | 0.011977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_243-44_0_6_line_5 |  | 4 | 6 | 0.022316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_243-44_0_6_line_6 |  | 5 | 7 | 0.037414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_243-44_0_6_line_7 |  | 6 | 8 | 0.020296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_243-44_0_6_line_8 |  | 7 | 9 | 0.011513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_243-44_0_6_line_9 |  | 8 | 10 | 0.015194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_243-44_0_6_line_10 |  | 10 | 11 | 0.0020853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_243-44_0_6_line_11 |  | 11 | 12 | 0.016194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_243-44_0_6_line_12 |  | 11 | 13 | 0.0088845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_243-44_0_6_line_13 |  | 12 | 14 | 0.018483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_243-44_0_6_line_14 |  | 13 | 15 | 0.011356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_243-44_0_6_line_15 |  | 14 | 16 | 0.023284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_243-44_0_6_line_16 |  | 15 | 17 | 0.015417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_243-44_0_6_line_17 |  | 17 | 18 | 0.022955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_243-44_0_6_line_18 |  | 18 | 26 | 0.024568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_243-44_0_6_line_19 |  | 18 | 27 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_243-44_0_6_line_20 |  | 19 | 20 | 0.033193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_243-44_0_6_line_21 |  | 20 | 21 | 0.010145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_243-44_0_6_line_22 |  | 21 | 22 | 0.023431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_243-44_0_6_line_23 |  | 22 | 23 | 0.016252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_243-44_0_6_line_24 |  | 23 | 24 | 0.042451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_243-44_0_6_line_25 |  | 23 | 25 | 0.007755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_243-44_0_6_line_26 |  | 24 | 31 | 0.016577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_243-44_0_6_line_27 |  | 25 | 30 | 0.010542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_243-44_0_6_line_28 |  | 25 | 29 | 0.021793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_243-44_0_6_line_29 |  | 27 | 28 | 0.027275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_243-44_0_6_line_30 |  | 28 | 30 | 0.018196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_243-44_0_6_line_31 |  | 31 | 37 | 0.01803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_243-44_0_6_line_32 |  | 32 | 33 | 0.035589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_243-44_0_6_line_33 |  | 32 | 34 | 0.021815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_243-44_0_6_line_34 |  | 33 | 35 | 0.00071648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_243-44_0_6_line_35 |  | 34 | 36 | 0.054326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_243-44_0_6_line_36 |  | 34 | 37 | 0.021497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_243-44_0_6_line_37 |  | 35 | 38 | 0.006978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_243-44_0_6_line_38 |  | 36 | 39 | 0.078119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_243-44_0_6_line_39 |  | 36 | 40 | 0.032214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_243-44_0_6_line_40 |  | 37 | 41 | 0.026493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_243-44_0_6_line_41 |  | 41 | 42 | 0.0072519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_243-44_0_6_line_42 |  | 42 | 43 | 0.067933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_243-44_0_6_line_43 |  | 42 | 44 | 0.053697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_243-44_0_6_line_44 |  | 43 | 117 | 0.072262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_243-44_0_6_line_45 |  | 44 | 118 | 0.030517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_243-44_0_6_line_46 |  | 45 | 46 | 0.0092803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_243-44_0_6_line_47 |  | 45 | 47 | 0.027687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_243-44_0_6_line_48 |  | 46 | 48 | 0.015542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_243-44_0_6_line_49 |  | 47 | 49 | 0.043077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_243-44_0_6_line_50 |  | 47 | 50 | 0.031339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_243-44_0_6_line_51 |  | 47 | 51 | 0.071232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_243-44_0_6_line_52 |  | 48 | 52 | 0.046353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_243-44_0_6_line_53 |  | 49 | 53 | 0.012405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_243-44_0_6_line_54 |  | 50 | 54 | 0.012867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_243-44_0_6_line_55 |  | 51 | 55 | 0.028737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_243-44_0_6_line_56 |  | 52 | 56 | 0.0077535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_243-44_0_6_line_57 |  | 52 | 57 | 0.05602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_243-44_0_6_line_58 |  | 53 | 58 | 0.052497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_243-44_0_6_line_59 |  | 54 | 59 | 0.016449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_243-44_0_6_line_60 |  | 55 | 60 | 0.064477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_243-44_0_6_line_61 |  | 55 | 61 | 0.032386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_243-44_0_6_line_62 |  | 56 | 62 | 0.01155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_243-44_0_6_line_63 |  | 57 | 63 | 0.008769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_243-44_0_6_line_64 |  | 58 | 64 | 0.01917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_243-44_0_6_line_65 |  | 59 | 65 | 0.017002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_243-44_0_6_line_66 |  | 60 | 66 | 0.025978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_243-44_0_6_line_67 |  | 61 | 67 | 0.039876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_243-44_0_6_line_68 |  | 61 | 68 | 0.037147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_243-44_0_6_line_69 |  | 62 | 69 | 0.0084362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_243-44_0_6_line_70 |  | 63 | 70 | 0.058584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_243-44_0_6_line_71 |  | 65 | 112 | 0.0096673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_243-44_0_6_line_72 |  | 67 | 122 | 0.029872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_243-44_0_6_line_73 |  | 67 | 103 | 0.019725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_243-44_0_6_line_74 |  | 68 | 123 | 0.02078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_243-44_0_6_line_75 |  | 69 | 71 | 0.012046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_243-44_0_6_line_76 |  | 72 | 73 | 0.020694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_243-44_0_6_line_77 |  | 72 | 74 | 0.003604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_243-44_0_6_line_78 |  | 73 | 75 | 0.023629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_243-44_0_6_line_79 |  | 74 | 76 | 0.03523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_243-44_0_6_line_80 |  | 75 | 77 | 0.021446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_243-44_0_6_line_81 |  | 75 | 78 | 0.001524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_243-44_0_6_line_82 |  | 76 | 79 | 0.0039274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_243-44_0_6_line_83 |  | 77 | 80 | 0.015151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_243-44_0_6_line_84 |  | 77 | 81 | 0.02226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_243-44_0_6_line_85 |  | 79 | 82 | 0.052653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_243-44_0_6_line_86 |  | 81 | 87 | 0.018453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_243-44_0_6_line_87 |  | 82 | 83 | 0.022392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_243-44_0_6_line_88 |  | 83 | 104 | 0.020894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_243-44_0_6_line_89 |  | 84 | 85 | 0.036213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_243-44_0_6_line_90 |  | 84 | 86 | 0.0031924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_243-44_0_6_line_91 |  | 85 | 87 | 0.046608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_243-44_0_6_line_92 |  | 87 | 88 | 0.002201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_243-44_0_6_line_93 |  | 88 | 89 | 0.029859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_243-44_0_6_line_94 |  | 89 | 90 | 0.035241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_243-44_0_6_line_95 |  | 89 | 91 | 0.009643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_243-44_0_6_line_96 |  | 91 | 95 | 0.026915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_243-44_0_6_line_97 |  | 91 | 92 | 0.012262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_243-44_0_6_line_98 |  | 92 | 93 | 0.027845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_243-44_0_6_line_99 |  | 93 | 94 | 0.0068706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_243-44_0_6_line_100 |  | 94 | 96 | 0.031857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_243-44_0_6_line_101 |  | 96 | 97 | 0.0064416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_243-44_0_6_line_102 |  | 97 | 98 | 0.018386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_243-44_0_6_line_103 |  | 98 | 112 | 0.024864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_243-44_0_6_line_104 |  | 99 | 100 | 0.0083446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_243-44_0_6_line_105 |  | 100 | 105 | 0.026036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_243-44_0_6_line_106 |  | 101 | 102 | 0.018502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_243-44_0_6_line_107 |  | 101 | 103 | 0.033271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_243-44_0_6_line_108 |  | 102 | 108 | 0.002718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_243-44_0_6_line_109 |  | 105 | 106 | 0.0032259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_243-44_0_6_line_110 |  | 106 | 107 | 0.0268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_243-44_0_6_line_111 |  | 107 | 113 | 0.03168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_243-44_0_6_line_112 |  | 108 | 126 | 0.031392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_243-44_0_6_line_113 |  | 109 | 110 | 0.018462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_243-44_0_6_line_114 |  | 109 | 111 | 0.022181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_243-44_0_6_line_115 |  | 110 | 112 | 0.020567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_243-44_0_6_line_116 |  | 111 | 113 | 0.022595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_243-44_0_6_line_117 |  | 113 | 114 | 0.015508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_243-44_0_6_line_118 |  | 114 | 115 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_243-44_0_6_line_119 |  | 115 | 116 | 0.0012075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_243-44_0_6_line_120 |  | 116 | 120 | 0.03964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_243-44_0_6_line_121 |  | 117 | 119 | 0.053915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_243-44_0_6_line_122 |  | 118 | 120 | 0.029253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_243-44_0_6_line_123 |  | 119 | 121 | 0.025818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_243-44_0_6_line_124 |  | 122 | 124 | 0.017078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_243-44_0_6_line_125 |  | 124 | 125 | 0.020019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_243-44_0_6_line_126 |  | 126 | 127 | 0.017151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_243-44_0_6_trafo_96 | 0.63 MVA 20/0.4 kV | 128 | 111 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2671978.2018 | 1250053.6465 | 2671967.0867 | 1250051.25 | 2671964.8392 | 1250050.6682
1 | 2672044.6882 | 1250060.2434 | 2672037.557 | 1250062.4472 | 2672031.4945 | 1250063.6855 | 2672023.5401 | 1250063.4221 | 2671978.2018 | 1250053.6465
2 | 2672044.6882 | 1250060.2434 | 2672036.0496 | 1250039.2567 | 2672015.494 | 1249997.4213 | 2672011.9525 | 1249991.0841
3 | 2672044.6882 | 1250060.2434 | 2672048.4531 | 1250068.2392
4 | 2672006.1096 | 1249980.6286 | 2672011.9525 | 1249991.0841
5 | 2672048.4531 | 1250068.2392 | 2672056.6257 | 1250085.5956 | 2672057.8755 | 1250088.4668
6 | 2672022.3733 | 1249949.4926 | 2672021.7505 | 1249959.1142 | 2672018.6477 | 1249967.7828 | 2672017.4753 | 1249971.0709 | 2672014.1206 | 1249975.6223 | 2672006.1096 | 1249980.6286
7 | 2672065.9756 | 1250107.0763 | 2672057.8755 | 1250088.4668
8 | 2672022.3733 | 1249949.4926 | 2672020.5608 | 1249938.1232
9 | 2672065.9756 | 1250107.0763 | 2672072.0396 | 1250121.0079
10 | 2672072.8719 | 1250122.9199 | 2672072.0396 | 1250121.0079
11 | 2672072.8719 | 1250122.9199 | 2672087.5616 | 1250116.1047
12 | 2672072.8719 | 1250122.9199 | 2672076.7008 | 1250130.937
13 | 2672101.5106 | 1250104.7328 | 2672098.7499 | 1250108.8689 | 2672094.7311 | 1250112.7784 | 2672087.5616 | 1250116.1047
14 | 2672081.5949 | 1250141.1844 | 2672076.7008 | 1250130.937
15 | 2672095.9365 | 1250082.5936 | 2672102.3186 | 1250101.6182 | 2672101.5106 | 1250104.7328
16 | 2672081.5949 | 1250141.1844 | 2672088.2389 | 1250155.0959
17 | 2672098.1315 | 1250175.8095 | 2672088.2389 | 1250155.0959
18 | 2672098.1315 | 1250175.8095 | 2672076.2804 | 1250187.1631
19 | 2672098.1315 | 1250175.8095 | 2672103.2922 | 1250172.9814 | 2672109.7224 | 1250173.1597
20 | 2672164.2637 | 1250197.1628 | 2672163.1108 | 1250196.3594 | 2672160.6805 | 1250193.2053 | 2672158.8446 | 1250190.8368 | 2672162.6943 | 1250182.2108 | 2672164.7824 | 1250176.8879 | 2672163.8877 | 1250175.9652 | 2672164.3137 | 1250173.8467 | 2672168.0121 | 1250168.8719
21 | 2672164.2637 | 1250197.1628 | 2672161.1003 | 1250204.6075 | 2672159.5749 | 1250205.9857
22 | 2672140.4368 | 1250219.4889 | 2672149.4145 | 1250213.1937 | 2672158.7567 | 1250206.7249 | 2672159.5749 | 1250205.9857
23 | 2672127.788 | 1250225.9397 | 2672139.1603 | 1250217.6721 | 2672140.4368 | 1250219.4889
24 | 2672127.788 | 1250225.9397 | 2672132.1013 | 1250231.9409 | 2672137.5532 | 1250239.913 | 2672152.5272 | 1250260.4331
25 | 2672127.788 | 1250225.9397 | 2672123.739 | 1250219.319
26 | 2672162.6537 | 1250273.5538 | 2672155.4492 | 1250264.4373 | 2672152.5272 | 1250260.4331
27 | 2672123.739 | 1250219.319 | 2672132.0326 | 1250212.7818
28 | 2672123.739 | 1250219.319 | 2672112.3671 | 1250200.7282
29 | 2672123.1047 | 1250196.9261 | 2672109.7224 | 1250173.1597
30 | 2672132.0326 | 1250212.7818 | 2672123.1047 | 1250196.9261
31 | 2672174.4001 | 1250287.2511 | 2672168.9559 | 1250280.5133 | 2672162.6537 | 1250273.5538
32 | 2672144.1661 | 1250282.8166 | 2672139.8416 | 1250277.0453 | 2672122.6493 | 1250254.4693
33 | 2672157.2473 | 1250300.2739 | 2672144.1661 | 1250282.8166
34 | 2672122.2152 | 1250253.8992 | 2672122.6493 | 1250254.4693
35 | 2672128.0956 | 1250338.3354 | 2672132.4245 | 1250334.363 | 2672149.4186 | 1250319.4813 | 2672145.1723 | 1250309.8449 | 2672157.2473 | 1250300.2739
36 | 2672174.4001 | 1250287.2511 | 2672157.2473 | 1250300.2739
37 | 2672117.9876 | 1250248.3477 | 2672122.2152 | 1250253.8992
38 | 2672128.0956 | 1250338.3354 | 2672127.8999 | 1250343.2477 | 2672071.0599 | 1250389.3766
39 | 2672128.0956 | 1250338.3354 | 2672127.1273 | 1250337.2562 | 2672106.5891 | 1250314.3515
40 | 2672174.4001 | 1250287.2511 | 2672192.7858 | 1250306.3258
41 | 2672198.016 | 1250311.3449 | 2672194.604 | 1250308.2122 | 2672192.7858 | 1250306.3258
42 | 2672198.016 | 1250311.3449 | 2672200.5542 | 1250313.6886 | 2672206.9671 | 1250318.9927 | 2672227.0739 | 1250335.5162 | 2672230.1975 | 1250330.7175 | 2672234.0275 | 1250325.5716 | 2672236.7493 | 1250322.1467 | 2672240.1268 | 1250320.6757 | 2672243.9409 | 1250321.167 | 2672248.4663 | 1250325.2362
43 | 2672195.2733 | 1250359.2237 | 2672204.0137 | 1250331.5102 | 2672206.9671 | 1250318.9927 | 2672200.5542 | 1250313.6886 | 2672198.016 | 1250311.3449
44 | 2672248.4663 | 1250325.2362 | 2672248.5837 | 1250330.4636 | 2672245.4238 | 1250341.3329 | 2672241.5191 | 1250355.0841 | 2672228.3794 | 1250376.4283 | 2672225.1742 | 1250392.4659
45 | 2672195.2733 | 1250359.2237 | 2672188.1803 | 1250358.9372 | 2672178.7092 | 1250363.603 | 2672169.1758 | 1250370.2917 | 2672168.199 | 1250371.0131
46 | 2671933.4228 | 1250417.5323 | 2671929.2282 | 1250416.5311 | 2671924.3294 | 1250415.7061
47 | 2671959.8665 | 1250425.6205 | 2671943.8543 | 1250420.0222 | 2671933.4228 | 1250417.5323
48 | 2671909.0104 | 1250413.0848 | 2671910.3705 | 1250413.3556 | 2671924.3294 | 1250415.7061
49 | 2671959.8665 | 1250425.6205 | 2671959.4192 | 1250409.6147 | 2671946.7821 | 1250394.0279 | 2671941.6473 | 1250389.2716
50 | 2671959.8665 | 1250425.6205 | 2671976.9539 | 1250433.4447 | 2671986.319 | 1250441.7925
51 | 2671959.8665 | 1250425.6205 | 2671948.382 | 1250438.2013 | 2671920.4179 | 1250484.6277
52 | 2671863.5327 | 1250404.1254 | 2671866.7196 | 1250404.6644 | 2671909.0104 | 1250413.0848
53 | 2671941.6473 | 1250389.2716 | 2671932.547 | 1250380.8421
54 | 2671995.9238 | 1250450.3539 | 2671986.319 | 1250441.7925
55 | 2671905.5905 | 1250509.2444 | 2671920.4179 | 1250484.6277
56 | 2671863.5327 | 1250404.1254 | 2671865.0962 | 1250399.0852 | 2671866.7133 | 1250397.2098
57 | 2671863.5327 | 1250404.1254 | 2671836.4611 | 1250399.0937 | 2671807.9508 | 1250396.2796
58 | 2671892.6143 | 1250347.016 | 2671894.7962 | 1250348.6534 | 2671903.736 | 1250354.1547 | 2671932.547 | 1250380.8421
59 | 2671995.9238 | 1250450.3539 | 2672007.6779 | 1250461.8603
60 | 2671905.5905 | 1250509.2444 | 2671850.151 | 1250476.0483
61 | 2671905.5905 | 1250509.2444 | 2671902.3255 | 1250514.5197 | 2671916.2295 | 1250524.6179 | 2671922.8977 | 1250530.6587
62 | 2671874.2559 | 1250388.4624 | 2671866.7133 | 1250397.2098
63 | 2671807.2112 | 1250387.5421 | 2671807.9508 | 1250396.2796
64 | 2671877.2823 | 1250335.5094 | 2671892.6143 | 1250347.016
65 | 2672019.8277 | 1250473.754 | 2672007.6779 | 1250461.8603
66 | 2671864.4037 | 1250454.3054 | 2671850.151 | 1250476.0483
67 | 2671922.8977 | 1250530.6587 | 2671930.0517 | 1250535.8492 | 2671953.4636 | 1250556.2258
68 | 2671922.8977 | 1250530.6587 | 2671946.153 | 1250501.6921
69 | 2671874.2559 | 1250388.4624 | 2671879.765 | 1250382.0734
70 | 2671807.2112 | 1250387.5421 | 2671809.1062 | 1250381.9277 | 2671824.939 | 1250360.6264 | 2671842.127 | 1250340.8871
71 | 2672026.736 | 1250480.5166 | 2672019.8277 | 1250473.754
72 | 2671953.4636 | 1250556.2258 | 2671968.2664 | 1250541.417 | 2671968.6918 | 1250532.4935
73 | 2671953.4636 | 1250556.2258 | 2671967.6808 | 1250569.8982
74 | 2671959.1619 | 1250485.4884 | 2671946.153 | 1250501.6921
75 | 2671887.6313 | 1250372.9507 | 2671879.765 | 1250382.0734
76 | 2672165.4486 | 1250661.3672 | 2672145.6067 | 1250667.2431
77 | 2672142.1511 | 1250668.2664 | 2672145.6067 | 1250667.2431
78 | 2672165.4486 | 1250661.3672 | 2672170.6688 | 1250659.8185 | 2672179.542 | 1250657.0913 | 2672184.1117 | 1250649.4525
79 | 2672142.1511 | 1250668.2664 | 2672124.9967 | 1250669.7365 | 2672106.9113 | 1250670.795
80 | 2672165.3964 | 1250639.006 | 2672167.5184 | 1250640.8109 | 2672184.1117 | 1250649.4525
81 | 2672184.1117 | 1250649.4525 | 2672185.492 | 1250650.0987
82 | 2672106.9113 | 1250670.795 | 2672102.9877 | 1250670.9661
83 | 2672165.3964 | 1250639.006 | 2672174.9653 | 1250627.2591
84 | 2672165.3964 | 1250639.006 | 2672149.6978 | 1250625.6942 | 2672148.5841 | 1250624.44
85 | 2672050.5175 | 1250672.2104 | 2672057.3871 | 1250673.4614 | 2672089.5619 | 1250671.5512 | 2672102.9877 | 1250670.9661
86 | 2672136.3304 | 1250610.6429 | 2672138.6018 | 1250613.1946 | 2672143.0402 | 1250618.1967 | 2672148.5841 | 1250624.44
87 | 2672050.5175 | 1250672.2104 | 2672058.4948 | 1250651.2811
88 | 2672058.4948 | 1250651.2811 | 2672064.9103 | 1250653.8721 | 2672077.572 | 1250659.7865
89 | 2672185.4562 | 1250545.9847 | 2672166.8504 | 1250577.0531
90 | 2672185.4562 | 1250545.9847 | 2672187.0964 | 1250543.2459
91 | 2672136.3304 | 1250610.6429 | 2672153.1444 | 1250599.9398 | 2672166.8504 | 1250577.0531
92 | 2672136.3304 | 1250610.6429 | 2672134.8692 | 1250608.9969
93 | 2672115.0467 | 1250586.6667 | 2672134.8692 | 1250608.9969
94 | 2672115.0467 | 1250586.6667 | 2672123.9739 | 1250576.4123 | 2672136.5124 | 1250558.7685
95 | 2672115.0467 | 1250586.6667 | 2672108.8102 | 1250579.2966
96 | 2672108.8102 | 1250579.2966 | 2672097.668 | 1250588.5678 | 2672089.413 | 1250597.8474
97 | 2672108.8102 | 1250579.2966 | 2672101.7635 | 1250569.6484 | 2672101.5736 | 1250569.3973
98 | 2672101.5736 | 1250569.3973 | 2672084.7796 | 1250547.1862
99 | 2672084.7796 | 1250547.1862 | 2672080.6358 | 1250541.7058
100 | 2672080.6358 | 1250541.7058 | 2672079.6082 | 1250540.3468 | 2672059.6414 | 1250517.7523
101 | 2672055.3758 | 1250512.9254 | 2672059.6414 | 1250517.7523
102 | 2672055.3758 | 1250512.9254 | 2672043.201 | 1250499.1484
103 | 2672026.736 | 1250480.5166 | 2672043.201 | 1250499.1484
104 | 2672136.7005 | 1250503.7622 | 2672140.4126 | 1250511.2357
105 | 2672125.1184 | 1250480.4441 | 2672136.7005 | 1250503.7622
106 | 2671991.6617 | 1250592.9604 | 2672004.6867 | 1250579.82
107 | 2671991.6617 | 1250592.9604 | 2671967.6808 | 1250569.8982
108 | 2672006.6001 | 1250577.8896 | 2672004.6867 | 1250579.82
109 | 2672125.1184 | 1250480.4441 | 2672123.6834 | 1250477.5549
110 | 2672123.6834 | 1250477.5549 | 2672111.7616 | 1250453.5529
111 | 2672092.4442 | 1250428.5 | 2672110.7949 | 1250451.6065 | 2672111.7616 | 1250453.5529
112 | 2672006.6001 | 1250577.8896 | 2672028.6994 | 1250555.5945
113 | 2672057.3372 | 1250456.2918 | 2672042.862 | 1250467.7507
114 | 2672057.3372 | 1250456.2918 | 2672074.7283 | 1250442.5244
115 | 2672026.736 | 1250480.5166 | 2672042.862 | 1250467.7507
116 | 2672092.4442 | 1250428.5 | 2672074.7283 | 1250442.5244
117 | 2672092.4442 | 1250428.5 | 2672104.4965 | 1250418.7406
118 | 2672114.0686 | 1250410.9895 | 2672104.4965 | 1250418.7406
119 | 2672114.0686 | 1250410.9895 | 2672115.007 | 1250410.2296
120 | 2672142.9942 | 1250382.6931 | 2672135.6527 | 1250393.5116 | 2672115.007 | 1250410.2296
121 | 2672225.1742 | 1250392.4659 | 2672215.781 | 1250439.4647 | 2672214.9459 | 1250445.3927
122 | 2672168.199 | 1250371.0131 | 2672151.6239 | 1250383.2541 | 2672142.9942 | 1250382.6931 | 2672142.9942 | 1250382.6931
123 | 2672211.721 | 1250470.9968 | 2672212.0454 | 1250465.9827 | 2672214.9459 | 1250445.3927
124 | 2671968.6918 | 1250532.4935 | 2671980.0166 | 1250519.7099
125 | 2671994.5457 | 1250524.6129 | 2671983.9238 | 1250515.2994 | 2671980.0166 | 1250519.7099
126 | 2672041.5095 | 1250566.999 | 2672028.6994 | 1250555.5945 | 2672028.6994 | 1250555.5945

## bus_geodata
| x | y | coords
0 | 2671978.2018 | 1250053.6465
1 | 2671964.8392 | 1250050.6682
2 | 2672044.6882 | 1250060.2434
3 | 2672011.9525 | 1249991.0841
4 | 2672048.4531 | 1250068.2392
5 | 2672006.1096 | 1249980.6286
6 | 2672057.8755 | 1250088.4668
7 | 2672022.3733 | 1249949.4926
8 | 2672065.9756 | 1250107.0763
9 | 2672020.5608 | 1249938.1232
10 | 2672072.0396 | 1250121.0079
11 | 2672072.8719 | 1250122.9199
12 | 2672087.5616 | 1250116.1047
13 | 2672076.7008 | 1250130.937
14 | 2672101.5106 | 1250104.7328
15 | 2672081.5949 | 1250141.1844
16 | 2672095.9365 | 1250082.5936
17 | 2672088.2389 | 1250155.0959
18 | 2672098.1315 | 1250175.8095
19 | 2672168.0121 | 1250168.8719
20 | 2672164.2637 | 1250197.1629
21 | 2672159.5749 | 1250205.9857
22 | 2672140.4368 | 1250219.4889
23 | 2672127.788 | 1250225.9397
24 | 2672152.5272 | 1250260.4331
25 | 2672123.739 | 1250219.319
26 | 2672076.2804 | 1250187.1631
27 | 2672109.7224 | 1250173.1597
28 | 2672123.1047 | 1250196.9261
29 | 2672112.3671 | 1250200.7282
30 | 2672132.0326 | 1250212.7818
31 | 2672162.6537 | 1250273.5538
32 | 2672144.1661 | 1250282.8166
33 | 2672122.6493 | 1250254.4693
34 | 2672157.2473 | 1250300.2739
35 | 2672122.2152 | 1250253.8992
36 | 2672128.0956 | 1250338.3354
37 | 2672174.4001 | 1250287.2511
38 | 2672117.9876 | 1250248.3477
39 | 2672071.0599 | 1250389.3766
40 | 2672106.5891 | 1250314.3515
41 | 2672192.7858 | 1250306.3258
42 | 2672198.016 | 1250311.3449
43 | 2672248.4663 | 1250325.2362
44 | 2672195.2733 | 1250359.2237
45 | 2671933.4228 | 1250417.5323
46 | 2671924.3294 | 1250415.7061
47 | 2671959.8665 | 1250425.6205
48 | 2671909.0104 | 1250413.0848
49 | 2671941.6473 | 1250389.2716
50 | 2671986.319 | 1250441.7925
51 | 2671920.4179 | 1250484.6277
52 | 2671863.5327 | 1250404.1254
53 | 2671932.547 | 1250380.8421
54 | 2671995.9238 | 1250450.3539
55 | 2671905.5905 | 1250509.2444
56 | 2671866.7133 | 1250397.2098
57 | 2671807.9508 | 1250396.2796
58 | 2671892.6143 | 1250347.016
59 | 2672007.6779 | 1250461.8603
60 | 2671850.151 | 1250476.0483
61 | 2671922.8977 | 1250530.6587
62 | 2671874.2559 | 1250388.4624
63 | 2671807.2112 | 1250387.5421
64 | 2671877.2823 | 1250335.5094
65 | 2672019.8277 | 1250473.754
66 | 2671864.4037 | 1250454.3054
67 | 2671953.4636 | 1250556.2258
68 | 2671946.153 | 1250501.6921
69 | 2671879.765 | 1250382.0734
70 | 2671842.127 | 1250340.8871
71 | 2671887.6313 | 1250372.9507
72 | 2672145.6067 | 1250667.2431
73 | 2672165.4486 | 1250661.3672
74 | 2672142.1511 | 1250668.2664
75 | 2672184.1117 | 1250649.4525
76 | 2672106.9113 | 1250670.795
77 | 2672165.3964 | 1250639.006
78 | 2672185.492 | 1250650.0987
79 | 2672102.9877 | 1250670.9661
80 | 2672174.9653 | 1250627.2591
81 | 2672148.5841 | 1250624.44
82 | 2672050.5175 | 1250672.2104
83 | 2672058.4948 | 1250651.2811
84 | 2672185.4562 | 1250545.9847
85 | 2672166.8504 | 1250577.0531
86 | 2672187.0964 | 1250543.2459
87 | 2672136.3304 | 1250610.6429
88 | 2672134.8692 | 1250608.9969
89 | 2672115.0467 | 1250586.6667
90 | 2672136.5124 | 1250558.7685
91 | 2672108.8102 | 1250579.2966
92 | 2672101.5736 | 1250569.3973
93 | 2672084.7796 | 1250547.1862
94 | 2672080.6358 | 1250541.7058
95 | 2672089.413 | 1250597.8474
96 | 2672059.6414 | 1250517.7523
97 | 2672055.3758 | 1250512.9254
98 | 2672043.201 | 1250499.1484
99 | 2672140.4126 | 1250511.2357
100 | 2672136.7005 | 1250503.7622
101 | 2671991.6617 | 1250592.9604
102 | 2672004.6867 | 1250579.82
103 | 2671967.6808 | 1250569.8982
104 | 2672077.572 | 1250659.7865
105 | 2672125.1184 | 1250480.4441
106 | 2672123.6834 | 1250477.5549
107 | 2672111.7616 | 1250453.5529
108 | 2672006.6001 | 1250577.8896
109 | 2672057.3372 | 1250456.2918
110 | 2672042.862 | 1250467.7507
111 | 2672074.7283 | 1250442.5244
112 | 2672026.736 | 1250480.5166
113 | 2672092.4442 | 1250428.5
114 | 2672104.4965 | 1250418.7406
115 | 2672114.0686 | 1250410.9895
116 | 2672115.007 | 1250410.2296
117 | 2672225.1742 | 1250392.4659
118 | 2672168.199 | 1250371.0131
119 | 2672214.9459 | 1250445.3927
120 | 2672142.9942 | 1250382.6931
121 | 2672211.721 | 1250470.9968
122 | 2671968.6918 | 1250532.4935
123 | 2671959.1619 | 1250485.4884
124 | 2671980.0166 | 1250519.7099
125 | 2671994.5457 | 1250524.6129
126 | 2672028.6994 | 1250555.5945
127 | 2672041.5095 | 1250566.999
128 | 2672092.4442 | 1250428.5

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97641 | -0.45539 | 0.0016388 | 0.00041072
1 | 0.9764 | -0.45555 | 0.00061222 | 0.00015344
2 | 0.97655 | -0.45259 | 0 | 0
3 | 0.97642 | -0.45511 | 0.001289 | 0.00032306
4 | 0.97658 | -0.45194 | 0.001302 | 0.00032631
5 | 0.97642 | -0.45522 | 0 | 0
6 | 0.97669 | -0.44976 | 0.00079861 | 0.00020015
7 | 0.9764 | -0.45556 | 0 | 0
8 | 0.97681 | -0.44748 | 0.00099391 | 0.0002491
9 | 0.97639 | -0.45567 | 0.00050326 | 0.00012613
10 | 0.97691 | -0.44549 | 0.0024766 | 0.00062068
11 | 0.97693 | -0.44513 | 0 | 0
12 | 0.97677 | -0.44824 | 0.0014274 | 0.00035773
13 | 0.97709 | -0.44186 | 0.00083742 | 0.00020988
14 | 0.97661 | -0.45131 | 0.0057223 | 0.0014341
15 | 0.97732 | -0.43751 | 0.00098355 | 0.0002465
16 | 0.97654 | -0.45275 | 0.0033771 | 0.00084639
17 | 0.97763 | -0.43133 | 0.0035148 | 0.00088088
18 | 0.97817 | -0.42066 | 0 | 0
19 | 0.98058 | -0.37346 | 0.0071283 | 0.0017865
20 | 0.9808 | -0.36917 | 0 | 0
21 | 0.98087 | -0.36786 | 0.0018482 | 0.00046321
22 | 0.98106 | -0.36405 | 0 | 0
23 | 0.9812 | -0.36141 | 0 | 0
24 | 0.98354 | -0.31576 | 0.0010117 | 0.00025356
25 | 0.98083 | -0.36851 | 0 | 0
26 | 0.978 | -0.42412 | 0.0077256 | 0.0019362
27 | 0.97855 | -0.41321 | 0.0071087 | 0.0017816
28 | 0.97957 | -0.39321 | 0.0070661 | 0.0017709
29 | 0.98077 | -0.36975 | 0.0031574 | 0.00079133
30 | 0.98037 | -0.37756 | 0 | 0
31 | 0.98447 | -0.2977 | 0 | 0
32 | 0.98458 | -0.29563 | 0.0027521 | 0.00068973
33 | 0.9842 | -0.30307 | 0.002262 | 0.00056691
34 | 0.98487 | -0.28999 | 0 | 0
35 | 0.9842 | -0.30319 | 0.0025699 | 0.00064407
36 | 0.98405 | -0.30609 | 0 | 0
37 | 0.98548 | -0.27809 | 0 | 0
38 | 0.98415 | -0.30404 | 0.0067873 | 0.0017011
39 | 0.98317 | -0.32328 | 0.012214 | 0.0030611
40 | 0.98392 | -0.30855 | 0.0042513 | 0.0010655
41 | 0.98772 | -0.23473 | 0.014213 | 0.0035621
42 | 0.98843 | -0.22106 | 0 | 0
43 | 0.986 | -0.26823 | 0 | 0
44 | 0.99201 | -0.15213 | 0 | 0
45 | 0.98843 | -0.22047 | 0.0050108 | 0.0012558
46 | 0.98818 | -0.22529 | 0.0074941 | 0.0018782
47 | 0.9893 | -0.20361 | 0 | 0
48 | 0.98787 | -0.2313 | 0.0043924 | 0.0011008
49 | 0.98888 | -0.2117 | 0.0032587 | 0.0008167
50 | 0.9915 | -0.16153 | 0.0044114 | 0.0011056
51 | 0.98224 | -0.33959 | 0.012863 | 0.0032238
52 | 0.98714 | -0.2456 | 0.0073411 | 0.0018399
53 | 0.9888 | -0.21331 | 0.0034409 | 0.00086236
54 | 0.99211 | -0.1497 | 0 | 0
55 | 0.97974 | -0.3883 | 0 | 0
56 | 0.98708 | -0.24677 | 0.0022322 | 0.00055944
57 | 0.98706 | -0.24707 | 0 | 0
58 | 0.98862 | -0.21691 | 0.0023416 | 0.00058685
59 | 0.9929 | -0.13461 | 0.0024106 | 0.00060415
60 | 0.97917 | -0.39943 | 0 | 0
61 | 0.9772 | -0.43786 | 0 | 0
62 | 0.98701 | -0.24806 | 0.0013917 | 0.0003488
63 | 0.98705 | -0.2473 | 0 | 0
64 | 0.98859 | -0.21742 | 0.0014985 | 0.00037555
65 | 0.99373 | -0.1188 | 0.0022438 | 0.00056234
66 | 0.97894 | -0.40392 | 0.0095018 | 0.0023814
67 | 0.97455 | -0.4898 | 0 | 0
68 | 0.97676 | -0.4466 | 0.0064452 | 0.0016153
69 | 0.98698 | -0.24879 | 0.0021684 | 0.00054345
70 | 0.98697 | -0.24883 | 0.0014619 | 0.00036639
71 | 0.98695 | -0.24936 | 0.0026579 | 0.00066614
72 | 0.97695 | -0.4442 | 0.0087712 | 0.0021983
73 | 0.97741 | -0.43525 | 0 | 0
74 | 0.9769 | -0.44518 | 0 | 0
75 | 0.97793 | -0.42504 | 0 | 0
76 | 0.97642 | -0.45478 | 0 | 0
77 | 0.97847 | -0.41446 | 0 | 0
78 | 0.97792 | -0.42514 | 0.0034201 | 0.00085715
79 | 0.97636 | -0.45585 | 0.0077419 | 0.0019403
80 | 0.97841 | -0.41553 | 0.0038897 | 0.00097485
81 | 0.97911 | -0.4019 | 0.0028384 | 0.00071137
82 | 0.97601 | -0.46275 | 0 | 0
83 | 0.97586 | -0.46569 | 0 | 0
84 | 0.97856 | -0.41271 | 0.0043074 | 0.0010795
85 | 0.97885 | -0.40706 | 0.010899 | 0.0027316
86 | 0.97855 | -0.41295 | 0.0042682 | 0.0010697
87 | 0.97969 | -0.39056 | 0 | 0
88 | 0.9798 | -0.38843 | 0.008123 | 0.0020358
89 | 0.9815 | -0.35518 | 0 | 0
90 | 0.98126 | -0.35975 | 0.0071666 | 0.0017961
91 | 0.98211 | -0.34321 | 0 | 0
92 | 0.98298 | -0.32631 | 0.0026822 | 0.00067221
93 | 0.98502 | -0.2867 | 0.0068865 | 0.0017259
94 | 0.98556 | -0.2761 | 0.014922 | 0.0037399
95 | 0.98192 | -0.34698 | 0.0077344 | 0.0019384
96 | 0.98854 | -0.21864 | 0.0069992 | 0.0017542
97 | 0.98918 | -0.20626 | 0.013418 | 0.0033629
98 | 0.99124 | -0.16663 | 0.0082207 | 0.0020603
99 | 0.99565 | -0.083387 | 0.00769 | 0.0019273
100 | 0.99571 | -0.082258 | 0.0030012 | 0.00075216
101 | 0.97272 | -0.52602 | 0 | 0
102 | 0.97213 | -0.53762 | 0.0085526 | 0.0021435
103 | 0.97377 | -0.5052 | 0.0084998 | 0.0021303
104 | 0.97572 | -0.46843 | 0.0071677 | 0.0017964
105 | 0.99596 | -0.077366 | 0.0161 | 0.004035
106 | 0.99604 | -0.075847 | 0.012455 | 0.0031216
107 | 0.997 | -0.057386 | 0.0082125 | 0.0020582
108 | 0.97206 | -0.5389 | 0.0083044 | 0.0020813
109 | 0.99776 | -0.042321 | 0.02732 | 0.0068469
110 | 0.99605 | -0.074736 | 0.01066 | 0.0026716
111 | 1 | 0 | -0.57351 | -0.14643
112 | 0.99421 | -0.10969 | 0 | 0
113 | 0.99836 | -0.031057 | 0 | 0
114 | 0.99747 | -0.048133 | 0.0088193 | 0.0022103
115 | 0.99678 | -0.061082 | 0.0058159 | 0.0014576
116 | 0.99672 | -0.062311 | 0.010362 | 0.0025968
117 | 0.98341 | -0.31865 | 0.022899 | 0.0057391
118 | 0.99337 | -0.12615 | 0.0055812 | 0.0013988
119 | 0.98262 | -0.33413 | 0.0025893 | 0.00064894
120 | 0.99472 | -0.10034 | 0.013714 | 0.003437
121 | 0.9823 | -0.34034 | 0.013328 | 0.0033402
122 | 0.97376 | -0.50552 | 0.010287 | 0.0025781
123 | 0.97663 | -0.44905 | 0.0064466 | 0.0016157
124 | 0.97347 | -0.51129 | 0.0097741 | 0.0024496
125 | 0.9733 | -0.51445 | 0.0085913 | 0.0021532
126 | 0.97156 | -0.54884 | 0.0086442 | 0.0021664
127 | 0.97143 | -0.55153 | 0.0085099 | 0.0021328
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00061222 | 0.00015327 | -0.00061222 | -0.00015344 | 4.4693e-09 | -1.6839e-07 | 0.00093294 | 0.00093301 | 0.00093301 | 0.97641 | -0.45539 | 0.9764 | -0.45555 | 0.25632
1 | -0.002251 | -0.00056398 | 0.0022513 | 0.00056332 | 3.0001e-07 | -6.5852e-07 | 0.0034304 | 0.0034301 | 0.0034304 | 0.97641 | -0.45539 | 0.97655 | -0.45259 | 0.94241
2 | 0.0017925 | 0.00044762 | -0.0017923 | -0.00044844 | 2.1414e-07 | -8.2077e-07 | 0.0027308 | 0.0027311 | 0.0027311 | 0.97655 | -0.45259 | 0.97642 | -0.45511 | 0.7503
3 | -0.0040438 | -0.0010109 | 0.0040439 | 0.0010109 | 1.2579e-07 | -3.0068e-08 | 0.0061609 | 0.0061608 | 0.0061609 | 0.97655 | -0.45259 | 0.97658 | -0.45194 | 1.6925
4 | 0.00050327 | 0.00012537 | -0.00050327 | -0.00012552 | 2.6403e-09 | -1.4812e-07 | 0.00076669 | 0.00076674 | 0.00076674 | 0.97642 | -0.45511 | 0.97642 | -0.45522 | 0.21064
5 | -0.0053459 | -0.0013372 | 0.0053465 | 0.0013373 | 5.5511e-07 | 7.6026e-08 | 0.0081446 | 0.0081445 | 0.0081446 | 0.97658 | -0.45194 | 0.97669 | -0.44976 | 2.2375
6 | 0.00050327 | 0.00012552 | -0.00050326 | -0.00012599 | 8.25e-09 | -4.6268e-07 | 0.00076674 | 0.00076691 | 0.00076691 | 0.97642 | -0.45522 | 0.9764 | -0.45556 | 0.21069
7 | -0.0061451 | -0.0015374 | 0.0061458 | 0.0015376 | 6.6696e-07 | 1.7283e-07 | 0.0093612 | 0.0093612 | 0.0093612 | 0.97669 | -0.44976 | 0.97681 | -0.44748 | 2.5718
8 | 0.00050326 | 0.00012599 | -0.00050326 | -0.00012613 | 2.5394e-09 | -1.4237e-07 | 0.00076691 | 0.00076696 | 0.00076696 | 0.9764 | -0.45556 | 0.97639 | -0.45567 | 0.2107
9 | -0.0071397 | -0.0017867 | 0.0071403 | 0.001787 | 6.7388e-07 | 2.4106e-07 | 0.010875 | 0.010875 | 0.010875 | 0.97681 | -0.44748 | 0.97691 | -0.44549 | 2.9877
10 | -0.0096169 | -0.0024076 | 0.0096171 | 0.0024077 | 1.6777e-07 | 8.1264e-08 | 0.014647 | 0.014647 | 0.014647 | 0.97691 | -0.44549 | 0.97693 | -0.44513 | 4.024
11 | 0.01053 | 0.0026395 | -0.010528 | -0.0026387 | 1.5622e-06 | 7.9706e-07 | 0.016039 | 0.016039 | 0.016039 | 0.97693 | -0.44513 | 0.97677 | -0.44824 | 4.4063
12 | -0.020147 | -0.0050473 | 0.02015 | 0.0050492 | 3.1373e-06 | 1.8966e-06 | 0.030686 | 0.030686 | 0.030686 | 0.97693 | -0.44513 | 0.97709 | -0.44186 | 8.4303
13 | 0.009101 | 0.002281 | -0.0090996 | -0.0022804 | 1.3323e-06 | 6.2139e-07 | 0.013865 | 0.013865 | 0.013865 | 0.97677 | -0.44824 | 0.97661 | -0.45131 | 3.809
14 | -0.020988 | -0.005259 | 0.020992 | 0.0052617 | 4.3503e-06 | 2.6419e-06 | 0.031962 | 0.031961 | 0.031962 | 0.97709 | -0.44186 | 0.97732 | -0.43751 | 8.7806
15 | 0.0033774 | 0.00084625 | -0.0033771 | -0.00084639 | 2.3122e-07 | -1.4335e-07 | 0.0051458 | 0.0051459 | 0.0051459 | 0.97661 | -0.45131 | 0.97654 | -0.45275 | 1.4137
16 | -0.021975 | -0.0055082 | 0.021982 | 0.0055121 | 6.4721e-06 | 3.9489e-06 | 0.033459 | 0.033459 | 0.033459 | 0.97732 | -0.43751 | 0.97763 | -0.43133 | 9.192
17 | -0.025497 | -0.006393 | 0.02551 | 0.006401 | 1.2965e-05 | 8.0093e-06 | 0.038809 | 0.038809 | 0.038809 | 0.97763 | -0.43133 | 0.97817 | -0.42066 | 10.6617
18 | 0.0077269 | 0.0019367 | -0.0077256 | -0.0019362 | 1.2729e-06 | 5.0633e-07 | 0.011754 | 0.011754 | 0.011754 | 0.97817 | -0.42066 | 0.978 | -0.42412 | 3.2292
19 | -0.033236 | -0.0083377 | 0.033248 | 0.0083451 | 1.1809e-05 | 7.4031e-06 | 0.050563 | 0.050563 | 0.050563 | 0.97817 | -0.42066 | 0.97855 | -0.41321 | 13.8909
20 | -0.0071283 | -0.0017865 | 0.0071297 | 0.001787 | 1.4564e-06 | 5.1329e-07 | 0.010817 | 0.010817 | 0.010817 | 0.98058 | -0.37346 | 0.9808 | -0.36917 | 2.9717
21 | -0.0071297 | -0.001787 | 0.0071302 | 0.0017872 | 4.4511e-07 | 1.5683e-07 | 0.010817 | 0.010817 | 0.010817 | 0.9808 | -0.36917 | 0.98087 | -0.36786 | 2.9717
22 | -0.0089784 | -0.0022504 | 0.00898 | 0.0022511 | 1.6301e-06 | 7.4745e-07 | 0.013621 | 0.013621 | 0.013621 | 0.98087 | -0.36786 | 0.98106 | -0.36405 | 3.7419
23 | -0.00898 | -0.0022511 | 0.0089812 | 0.0022517 | 1.1306e-06 | 5.1837e-07 | 0.013621 | 0.01362 | 0.013621 | 0.98106 | -0.36405 | 0.9812 | -0.36141 | 3.7419
24 | -0.059674 | -0.015011 | 0.059804 | 0.015094 | 0.00013043 | 8.2938e-05 | 0.090517 | 0.090517 | 0.090517 | 0.9812 | -0.36141 | 0.98354 | -0.31576 | 24.8673
25 | 0.050693 | 0.01276 | -0.050675 | -0.012749 | 1.7196e-05 | 1.0907e-05 | 0.076896 | 0.076896 | 0.076896 | 0.9812 | -0.36141 | 0.98083 | -0.36851 | 21.1254
26 | -0.060816 | -0.015348 | 0.060869 | 0.015381 | 5.2668e-05 | 3.3497e-05 | 0.092047 | 0.092047 | 0.092047 | 0.98354 | -0.31576 | 0.98447 | -0.2977 | 25.2877
27 | 0.047518 | 0.011958 | -0.047497 | -0.011944 | 2.0554e-05 | 1.3022e-05 | 0.072106 | 0.072106 | 0.072106 | 0.98083 | -0.36851 | 0.98037 | -0.37756 | 19.8094
28 | 0.0031576 | 0.00079118 | -0.0031574 | -0.00079133 | 1.8754e-07 | -1.5501e-07 | 0.0047903 | 0.0047904 | 0.0047904 | 0.98083 | -0.36851 | 0.98077 | -0.36975 | 1.3161
29 | -0.040357 | -0.010127 | 0.040396 | 0.010151 | 3.8525e-05 | 2.4313e-05 | 0.061373 | 0.061372 | 0.061373 | 0.97855 | -0.41321 | 0.97957 | -0.39321 | 16.8606
30 | -0.047462 | -0.011922 | 0.047497 | 0.011944 | 3.5478e-05 | 2.2477e-05 | 0.072106 | 0.072106 | 0.072106 | 0.97957 | -0.39321 | 0.98037 | -0.37756 | 19.8094
31 | -0.060869 | -0.015381 | 0.060926 | 0.015418 | 5.7286e-05 | 3.6434e-05 | 0.092047 | 0.092047 | 0.092047 | 0.98447 | -0.2977 | 0.98548 | -0.27809 | 25.2877
32 | 0.011624 | 0.0029143 | -0.01162 | -0.0029122 | 4.1187e-06 | 2.1836e-06 | 0.017567 | 0.017568 | 0.017568 | 0.98458 | -0.29563 | 0.9842 | -0.30307 | 4.8263
33 | -0.014376 | -0.0036041 | 0.01438 | 0.0036063 | 3.8616e-06 | 2.1939e-06 | 0.021727 | 0.021727 | 0.021727 | 0.98458 | -0.29563 | 0.98487 | -0.28999 | 5.9689
34 | 0.0093575 | 0.0023452 | -0.0093575 | -0.0023452 | 5.3778e-08 | 2.5313e-08 | 0.014148 | 0.014148 | 0.014148 | 0.9842 | -0.30307 | 0.9842 | -0.30319 | 3.8867
35 | 0.016489 | 0.0041393 | -0.016476 | -0.0041319 | 1.2646e-05 | 7.4027e-06 | 0.024915 | 0.024915 | 0.024915 | 0.98487 | -0.28999 | 0.98405 | -0.30609 | 6.8447
36 | -0.030868 | -0.0077456 | 0.030886 | 0.0077566 | 1.7537e-05 | 1.095e-05 | 0.046641 | 0.046641 | 0.046641 | 0.98487 | -0.28999 | 0.98548 | -0.27809 | 12.8135
37 | 0.0067876 | 0.0017011 | -0.0067873 | -0.0017011 | 2.7558e-07 | 8.77e-08 | 0.010262 | 0.010262 | 0.010262 | 0.9842 | -0.30319 | 0.98415 | -0.30404 | 2.8193
38 | 0.012224 | 0.0030666 | -0.012214 | -0.0030611 | 1.0011e-05 | 5.4153e-06 | 0.018486 | 0.018486 | 0.018486 | 0.98405 | -0.30609 | 0.98317 | -0.32328 | 5.0786
39 | 0.0042518 | 0.0010654 | -0.0042513 | -0.0010655 | 4.9935e-07 | -8.9615e-08 | 0.0064292 | 0.0064294 | 0.0064294 | 0.98405 | -0.30609 | 0.98392 | -0.30855 | 1.7663
40 | -0.091811 | -0.023174 | 0.092003 | 0.023296 | 0.00019109 | 0.00012196 | 0.13869 | 0.13869 | 0.13869 | 0.98548 | -0.27809 | 0.98772 | -0.23473 | 38.1011
41 | -0.10622 | -0.026858 | 0.10629 | 0.026903 | 6.9706e-05 | 4.4519e-05 | 0.1601 | 0.1601 | 0.1601 | 0.98772 | -0.23473 | 0.98843 | -0.22106 | 43.9835
42 | 0.039013 | 0.0098517 | -0.038926 | -0.0097963 | 8.7954e-05 | 5.5422e-05 | 0.058759 | 0.058759 | 0.058759 | 0.98843 | -0.22106 | 0.986 | -0.26823 | 16.1426
43 | -0.1453 | -0.036755 | 0.14578 | 0.037062 | 0.00048226 | 0.00030726 | 0.21886 | 0.21886 | 0.21886 | 0.98843 | -0.22106 | 0.99201 | -0.15213 | 30.063
44 | 0.038926 | 0.0097963 | -0.038832 | -0.0097373 | 9.356e-05 | 5.8959e-05 | 0.058759 | 0.058759 | 0.058759 | 0.986 | -0.26823 | 0.98341 | -0.31865 | 16.1426
45 | -0.14578 | -0.037062 | 0.14596 | 0.037178 | 0.00018272 | 0.00011575 | 0.21886 | 0.21886 | 0.21886 | 0.99201 | -0.15213 | 0.99337 | -0.12615 | 20.0419
46 | 0.029166 | 0.0073167 | -0.029159 | -0.0073126 | 6.7098e-06 | 4.1754e-06 | 0.04391 | 0.04391 | 0.04391 | 0.98843 | -0.22047 | 0.98818 | -0.22529 | 12.0631
47 | -0.034177 | -0.0085726 | 0.034204 | 0.0085898 | 2.7487e-05 | 1.7237e-05 | 0.051453 | 0.051453 | 0.051453 | 0.98843 | -0.22047 | 0.9893 | -0.20361 | 14.1355
48 | 0.021665 | 0.0054344 | -0.021659 | -0.0054306 | 6.2036e-06 | 3.7713e-06 | 0.032625 | 0.032625 | 0.032625 | 0.98818 | -0.22529 | 0.98787 | -0.2313 | 8.9629
49 | 0.010545 | 0.0026432 | -0.010541 | -0.0026412 | 4.0638e-06 | 2.048e-06 | 0.015861 | 0.015861 | 0.015861 | 0.9893 | -0.20361 | 0.98888 | -0.2117 | 4.3574
50 | -0.15261 | -0.038819 | 0.15292 | 0.039016 | 0.00031015 | 0.00019769 | 0.22974 | 0.22974 | 0.22974 | 0.9893 | -0.20361 | 0.9915 | -0.16153 | 31.558
51 | 0.10786 | 0.027586 | -0.10715 | -0.027135 | 0.00070475 | 0.00045013 | 0.16243 | 0.16243 | 0.16243 | 0.9893 | -0.20361 | 0.98224 | -0.33959 | 44.6234
52 | 0.017266 | 0.0043298 | -0.017255 | -0.0043228 | 1.1759e-05 | 6.9325e-06 | 0.026009 | 0.026009 | 0.026009 | 0.98787 | -0.2313 | 0.98714 | -0.2456 | 7.1454
53 | 0.0072821 | 0.0018245 | -0.0072816 | -0.0018243 | 5.5853e-07 | 1.9833e-07 | 0.010958 | 0.010958 | 0.010958 | 0.98888 | -0.2117 | 0.9888 | -0.21331 | 3.0103
54 | -0.15733 | -0.040122 | 0.15742 | 0.040179 | 8.9853e-05 | 5.7008e-05 | 0.23636 | 0.23636 | 0.23636 | 0.9915 | -0.16153 | 0.99211 | -0.1497 | 21.6449
55 | 0.09429 | 0.023912 | -0.09407 | -0.023771 | 0.00022019 | 0.00014056 | 0.14294 | 0.14294 | 0.14294 | 0.98224 | -0.33959 | 0.97974 | -0.3883 | 39.27
56 | 0.0084514 | 0.002118 | -0.0084509 | -0.0021178 | 4.7189e-07 | 2.0289e-07 | 0.01274 | 0.01274 | 0.01274 | 0.98714 | -0.2456 | 0.98708 | -0.24677 | 3.4999
57 | 0.0014621 | 0.00036496 | -0.001462 | -0.00036561 | 1.0201e-07 | -6.5082e-07 | 0.0022035 | 0.0022038 | 0.0022038 | 0.98714 | -0.2456 | 0.98706 | -0.24707 | 0.60543
58 | 0.0038407 | 0.00096193 | -0.0038401 | -0.00096218 | 6.5762e-07 | -2.5238e-07 | 0.0057796 | 0.0057798 | 0.0057798 | 0.9888 | -0.21331 | 0.98862 | -0.21691 | 1.5879
59 | -0.15742 | -0.040179 | 0.15753 | 0.040252 | 0.00011487 | 7.2877e-05 | 0.23636 | 0.23636 | 0.23636 | 0.99211 | -0.1497 | 0.9929 | -0.13461 | 21.6449
60 | 0.0095089 | 0.0023848 | -0.0095038 | -0.0023823 | 5.0435e-06 | 2.4164e-06 | 0.014443 | 0.014443 | 0.014443 | 0.97974 | -0.3883 | 0.97917 | -0.39943 | 3.9678
61 | 0.084561 | 0.021386 | -0.084361 | -0.021258 | 0.00020054 | 0.00012794 | 0.1285 | 0.1285 | 0.1285 | 0.97974 | -0.3883 | 0.9772 | -0.43786 | 35.3023
62 | 0.0062187 | 0.0015584 | -0.0062183 | -0.0015583 | 3.8065e-07 | 9.5987e-08 | 0.0093746 | 0.0093746 | 0.0093746 | 0.98708 | -0.24677 | 0.98701 | -0.24806 | 2.5755
63 | 0.001462 | 0.00036561 | -0.001462 | -0.00036571 | 1.5971e-08 | -1.0186e-07 | 0.0022038 | 0.0022038 | 0.0022038 | 0.98706 | -0.24707 | 0.98705 | -0.2473 | 0.60544
64 | 0.0014985 | 0.00037533 | -0.0014985 | -0.00037555 | 3.6568e-08 | -2.2239e-07 | 0.0022554 | 0.0022555 | 0.0022555 | 0.98862 | -0.21691 | 0.98859 | -0.21742 | 0.61964
65 | -0.15994 | -0.040856 | 0.16007 | 0.040934 | 0.00012239 | 7.767e-05 | 0.23997 | 0.23997 | 0.23997 | 0.9929 | -0.13461 | 0.99373 | -0.1188 | 21.9757
66 | 0.0095038 | 0.0023823 | -0.0095018 | -0.0023814 | 2.0321e-06 | 9.7386e-07 | 0.014443 | 0.014443 | 0.014443 | 0.97917 | -0.39943 | 0.97894 | -0.40392 | 3.9678
67 | 0.071463 | 0.018024 | -0.071285 | -0.017911 | 0.00017721 | 0.00011291 | 0.10886 | 0.10886 | 0.10886 | 0.9772 | -0.43786 | 0.97455 | -0.4898 | 29.9065
68 | 0.012898 | 0.0032342 | -0.012893 | -0.0032312 | 5.3736e-06 | 2.974e-06 | 0.019641 | 0.019641 | 0.019641 | 0.9772 | -0.43786 | 0.97676 | -0.4466 | 5.3958
69 | 0.0048266 | 0.0012095 | -0.0048264 | -0.0012095 | 1.675e-07 | -6.147e-10 | 0.0072765 | 0.0072765 | 0.0072765 | 0.98701 | -0.24806 | 0.98698 | -0.24879 | 1.999
70 | 0.001462 | 0.00036571 | -0.0014619 | -0.00036639 | 1.0671e-07 | -6.8045e-07 | 0.0022038 | 0.0022041 | 0.0022041 | 0.98705 | -0.2473 | 0.98697 | -0.24883 | 0.60551
71 | -0.16231 | -0.041496 | 0.16238 | 0.041541 | 7.1552e-05 | 4.5417e-05 | 0.24333 | 0.24333 | 0.24333 | 0.99373 | -0.1188 | 0.99421 | -0.10969 | 22.2834
72 | 0.02868 | 0.0071978 | -0.028658 | -0.0071845 | 2.1485e-05 | 1.3378e-05 | 0.043794 | 0.043794 | 0.043794 | 0.97455 | -0.4898 | 0.97376 | -0.50552 | 12.0313
73 | 0.042606 | 0.010713 | -0.042574 | -0.010694 | 3.1315e-05 | 1.9796e-05 | 0.065066 | 0.065066 | 0.065066 | 0.97455 | -0.4898 | 0.97377 | -0.5052 | 17.8753
74 | 0.0064474 | 0.0016159 | -0.0064466 | -0.0016157 | 7.5177e-07 | 2.2108e-07 | 0.0098221 | 0.0098222 | 0.0098222 | 0.97676 | -0.4466 | 0.97663 | -0.44905 | 2.6984
75 | 0.002658 | 0.00066604 | -0.0026579 | -0.00066614 | 7.2541e-08 | -1.0751e-07 | 0.0040073 | 0.0040074 | 0.0040074 | 0.98698 | -0.24879 | 0.98695 | -0.24936 | 1.1009
76 | -0.023693 | -0.0059413 | 0.023704 | 0.0059475 | 1.0107e-05 | 6.2092e-06 | 0.036089 | 0.036089 | 0.036089 | 0.97695 | -0.4442 | 0.97741 | -0.43525 | 9.9146
77 | 0.014922 | 0.003743 | -0.014922 | -0.0037426 | 6.9822e-07 | 4.0173e-07 | 0.022729 | 0.022729 | 0.022729 | 0.97695 | -0.4442 | 0.9769 | -0.44518 | 6.2444
78 | -0.023704 | -0.0059475 | 0.023715 | 0.0059546 | 1.1541e-05 | 7.0897e-06 | 0.036089 | 0.036089 | 0.036089 | 0.97741 | -0.43525 | 0.97793 | -0.42504 | 9.9145
79 | 0.014922 | 0.0037426 | -0.014915 | -0.0037387 | 6.8254e-06 | 3.9274e-06 | 0.022729 | 0.02273 | 0.02273 | 0.9769 | -0.44518 | 0.97642 | -0.45478 | 6.2444
80 | -0.027135 | -0.0068117 | 0.027149 | 0.0068202 | 1.3713e-05 | 8.507e-06 | 0.041293 | 0.041293 | 0.041293 | 0.97793 | -0.42504 | 0.97847 | -0.41446 | 11.3442
81 | 0.0034201 | 0.00085714 | -0.0034201 | -0.00085715 | 1.5477e-08 | -9.2153e-09 | 0.005204 | 0.005204 | 0.005204 | 0.97793 | -0.42504 | 0.97792 | -0.42514 | 1.4297
82 | 0.014915 | 0.0037387 | -0.014914 | -0.0037383 | 7.6088e-07 | 4.3785e-07 | 0.02273 | 0.02273 | 0.02273 | 0.97642 | -0.45478 | 0.97636 | -0.45585 | 6.2444
83 | 0.0038899 | 0.00097478 | -0.0038897 | -0.00097485 | 1.9882e-07 | -6.3045e-08 | 0.0059156 | 0.0059156 | 0.0059156 | 0.97847 | -0.41446 | 0.97841 | -0.41553 | 1.6252
84 | -0.031039 | -0.007795 | 0.031057 | 0.0078067 | 1.8603e-05 | 1.1626e-05 | 0.047208 | 0.047208 | 0.047208 | 0.97847 | -0.41446 | 0.97911 | -0.4019 | 12.9693
85 | 0.007172 | 0.001798 | -0.0071697 | -0.0017971 | 2.3591e-06 | 8.5159e-07 | 0.010931 | 0.010931 | 0.010931 | 0.97636 | -0.45585 | 0.97601 | -0.46275 | 3.003
86 | -0.033896 | -0.008518 | 0.033914 | 0.0085295 | 1.8369e-05 | 1.1524e-05 | 0.051522 | 0.051522 | 0.051522 | 0.97911 | -0.4019 | 0.97969 | -0.39056 | 14.1544
87 | 0.0071697 | 0.0017971 | -0.0071687 | -0.0017967 | 1.0033e-06 | 3.6233e-07 | 0.010931 | 0.010931 | 0.010931 | 0.97601 | -0.46275 | 0.97586 | -0.46569 | 3.003
88 | 0.0071687 | 0.0017967 | -0.0071677 | -0.0017964 | 9.3621e-07 | 3.3817e-07 | 0.010931 | 0.010931 | 0.010931 | 0.97586 | -0.46569 | 0.97572 | -0.46843 | 3.003
89 | -0.0085757 | -0.0021492 | 0.008578 | 0.0021503 | 2.3093e-06 | 1.0229e-06 | 0.01304 | 0.01304 | 0.01304 | 0.97856 | -0.41271 | 0.97885 | -0.40706 | 3.5825
90 | 0.0042683 | 0.0010697 | -0.0042682 | -0.0010697 | 5.0431e-08 | -7.8294e-09 | 0.0064904 | 0.0064904 | 0.0064904 | 0.97856 | -0.41271 | 0.97855 | -0.41295 | 1.7831
91 | -0.019477 | -0.0048819 | 0.019493 | 0.0048911 | 1.5323e-05 | 9.2202e-06 | 0.029609 | 0.029609 | 0.029609 | 0.97885 | -0.40706 | 0.97969 | -0.39056 | 8.1343
92 | -0.053407 | -0.013421 | 0.053412 | 0.013424 | 5.4326e-06 | 3.4492e-06 | 0.08113 | 0.08113 | 0.08113 | 0.97969 | -0.39056 | 0.9798 | -0.38843 | 22.2886
93 | -0.061535 | -0.01546 | 0.061633 | 0.015522 | 9.7819e-05 | 6.2228e-05 | 0.093467 | 0.093467 | 0.093467 | 0.9798 | -0.38843 | 0.9815 | -0.35518 | 25.6777
94 | 0.0071682 | 0.0017967 | -0.0071666 | -0.0017961 | 1.5608e-06 | 5.5363e-07 | 0.010867 | 0.010868 | 0.010868 | 0.9815 | -0.35518 | 0.98126 | -0.35975 | 2.9856
95 | -0.068801 | -0.017319 | 0.06884 | 0.017344 | 3.9364e-05 | 2.5071e-05 | 0.10433 | 0.10433 | 0.10433 | 0.9815 | -0.35518 | 0.98211 | -0.34321 | 28.6632
96 | 0.0077357 | 0.001939 | -0.0077344 | -0.0019384 | 1.3865e-06 | 5.4687e-07 | 0.011721 | 0.011721 | 0.011721 | 0.98211 | -0.34321 | 0.98192 | -0.34698 | 3.22
97 | -0.076576 | -0.019283 | 0.076638 | 0.019322 | 6.1935e-05 | 3.9483e-05 | 0.11605 | 0.11605 | 0.11605 | 0.98211 | -0.34321 | 0.98298 | -0.32631 | 31.8832
98 | -0.07932 | -0.019995 | 0.079471 | 0.020091 | 0.00015065 | 9.6065e-05 | 0.12011 | 0.12011 | 0.12011 | 0.98298 | -0.32631 | 0.98502 | -0.2867 | 32.9986
99 | -0.086357 | -0.021817 | 0.086401 | 0.021845 | 4.389e-05 | 2.8002e-05 | 0.13052 | 0.13052 | 0.13052 | 0.98502 | -0.2867 | 0.98556 | -0.2761 | 35.8566
100 | -0.10132 | -0.025584 | 0.1016 | 0.025763 | 0.00027982 | 0.00017868 | 0.15305 | 0.15305 | 0.15305 | 0.98556 | -0.2761 | 0.98854 | -0.21864 | 42.0461
101 | -0.1086 | -0.027517 | 0.10867 | 0.027559 | 6.464e-05 | 4.1287e-05 | 0.16358 | 0.16358 | 0.16358 | 0.98854 | -0.21864 | 0.98918 | -0.20626 | 44.9404
102 | -0.12209 | -0.030921 | 0.12232 | 0.03107 | 0.00023284 | 0.00014878 | 0.18377 | 0.18377 | 0.18377 | 0.98918 | -0.20626 | 0.99124 | -0.16663 | 50.4857
103 | -0.13054 | -0.033131 | 0.1309 | 0.03336 | 0.00035859 | 0.00022918 | 0.19611 | 0.19611 | 0.19611 | 0.99124 | -0.16663 | 0.99421 | -0.10969 | 53.876
104 | -0.00769 | -0.0019273 | 0.0076904 | 0.0019275 | 4.1333e-07 | 1.56e-07 | 0.011493 | 0.011493 | 0.011493 | 0.99565 | -0.083387 | 0.99571 | -0.082258 | 3.1574
105 | -0.010692 | -0.0026796 | 0.010694 | 0.0026809 | 2.4925e-06 | 1.2565e-06 | 0.015978 | 0.015978 | 0.015978 | 0.99571 | -0.082258 | 0.99596 | -0.077366 | 4.3895
106 | 0.034041 | 0.008542 | -0.034022 | -0.0085302 | 1.8817e-05 | 1.1813e-05 | 0.052078 | 0.052078 | 0.052078 | 0.97272 | -0.52602 | 0.97213 | -0.53762 | 14.307
107 | -0.034041 | -0.008542 | 0.034074 | 0.0085633 | 3.3837e-05 | 2.1242e-05 | 0.052078 | 0.052077 | 0.052078 | 0.97272 | -0.52602 | 0.97377 | -0.5052 | 14.307
108 | 0.025469 | 0.0063867 | -0.025468 | -0.0063858 | 1.5492e-06 | 9.5779e-07 | 0.038986 | 0.038986 | 0.038986 | 0.97213 | -0.53762 | 0.97206 | -0.5389 | 10.7106
109 | -0.026794 | -0.0067159 | 0.026796 | 0.0067171 | 1.9387e-06 | 1.1988e-06 | 0.040032 | 0.040032 | 0.040032 | 0.99596 | -0.077366 | 0.99604 | -0.075847 | 10.9978
110 | -0.039251 | -0.0098387 | 0.039286 | 0.0098605 | 3.4557e-05 | 2.1768e-05 | 0.058639 | 0.058639 | 0.058639 | 0.99604 | -0.075847 | 0.997 | -0.057386 | 16.1097
111 | -0.047498 | -0.011919 | 0.047558 | 0.011957 | 5.9713e-05 | 3.7802e-05 | 0.070896 | 0.070896 | 0.070896 | 0.997 | -0.057386 | 0.99836 | -0.031057 | 19.477
112 | 0.017163 | 0.0043045 | -0.017155 | -0.0042997 | 8.1267e-06 | 4.8121e-06 | 0.026274 | 0.026274 | 0.026274 | 0.97206 | -0.5389 | 0.97156 | -0.54884 | 7.2182
113 | 0.30491 | 0.078195 | -0.30444 | -0.07789 | 0.00047853 | 0.00030554 | 0.45537 | 0.45537 | 0.45537 | 0.99776 | -0.042321 | 0.99605 | -0.074736 | 41.7003
114 | -0.33223 | -0.085042 | 0.33292 | 0.085478 | 0.00068241 | 0.00043587 | 0.49611 | 0.49611 | 0.49611 | 0.99776 | -0.042321 | 1 | 0 | 45.4313
115 | 0.29378 | 0.075218 | -0.29328 | -0.074901 | 0.00049647 | 0.00031694 | 0.43944 | 0.43944 | 0.43944 | 0.99605 | -0.074736 | 0.99421 | -0.10969 | 40.242
116 | 0.23895 | 0.060955 | -0.23859 | -0.060727 | 0.00035782 | 0.00022812 | 0.35593 | 0.35593 | 0.35593 | 1 | 0 | 0.99836 | -0.031057 | 32.5947
117 | 0.19103 | 0.04877 | -0.19087 | -0.04867 | 0.0001575 | 0.00010019 | 0.28504 | 0.28504 | 0.28504 | 0.99836 | -0.031057 | 0.99747 | -0.048133 | 26.1024
118 | 0.18205 | 0.046459 | -0.18194 | -0.046387 | 0.00011381 | 7.2354e-05 | 0.27188 | 0.27188 | 0.27188 | 0.99747 | -0.048133 | 0.99678 | -0.061082 | 24.8976
119 | 0.17612 | 0.04493 | -0.17611 | -0.044923 | 1.0456e-05 | 6.6448e-06 | 0.2632 | 0.2632 | 0.2632 | 0.99678 | -0.061082 | 0.99672 | -0.062311 | 24.1026
120 | 0.16575 | 0.042326 | -0.16545 | -0.042133 | 0.00030409 | 0.00019307 | 0.24773 | 0.24773 | 0.24773 | 0.99672 | -0.062311 | 0.99472 | -0.10034 | 22.6861
121 | 0.015932 | 0.0039982 | -0.015921 | -0.0039913 | 1.1752e-05 | 6.838e-06 | 0.02411 | 0.02411 | 0.02411 | 0.98341 | -0.31865 | 0.98262 | -0.33413 | 6.6236
122 | -0.15154 | -0.038576 | 0.15173 | 0.038696 | 0.00018879 | 0.00011968 | 0.22722 | 0.22722 | 0.22722 | 0.99337 | -0.12615 | 0.99472 | -0.10034 | 20.8075
123 | 0.013331 | 0.0033424 | -0.013328 | -0.0033402 | 3.9461e-06 | 2.1986e-06 | 0.020189 | 0.020189 | 0.020189 | 0.98262 | -0.33413 | 0.9823 | -0.34034 | 5.5464
124 | 0.018372 | 0.0046064 | -0.018367 | -0.0046034 | 5.048e-06 | 3.0183e-06 | 0.028075 | 0.028075 | 0.028075 | 0.97376 | -0.50552 | 0.97347 | -0.51129 | 7.7129
125 | 0.0085926 | 0.0021538 | -0.0085913 | -0.0021532 | 1.2951e-06 | 5.8004e-07 | 0.013135 | 0.013135 | 0.013135 | 0.97347 | -0.51129 | 0.9733 | -0.51445 | 3.6084
126 | 0.008511 | 0.0021333 | -0.0085099 | -0.0021328 | 1.0929e-06 | 4.8706e-07 | 0.013035 | 0.013035 | 0.013035 | 0.97156 | -0.54884 | 0.97143 | -0.55153 | 3.5811

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58909 | 0.15034

## res_load
| p_mw | q_mvar
0 | 0.0016388 | 0.00041072
1 | 0.00061222 | 0.00015344
2 | 0.001289 | 0.00032306
3 | 0.001302 | 0.00032631
4 | 0.00079861 | 0.00020015
5 | 0.00099391 | 0.0002491
6 | 0.00050326 | 0.00012613
7 | 0.0024766 | 0.00062068
8 | 0.0014274 | 0.00035773
9 | 0.00083742 | 0.00020988
10 | 0.0057223 | 0.0014341
11 | 0.00098355 | 0.0002465
12 | 0.0033771 | 0.00084639
13 | 0.0035148 | 0.00088088
14 | 0.0071283 | 0.0017865
15 | 0.0018482 | 0.00046321
16 | 0.0010117 | 0.00025356
17 | 0.0077256 | 0.0019362
18 | 0.0071087 | 0.0017816
19 | 0.0070661 | 0.0017709
20 | 0.0031574 | 0.00079133
21 | 0.0027521 | 0.00068973
22 | 0.002262 | 0.00056691
23 | 0.0025699 | 0.00064407
24 | 0.0067873 | 0.0017011
25 | 0.012214 | 0.0030611
26 | 0.0042513 | 0.0010655
27 | 0.014213 | 0.0035621
28 | 0.0050108 | 0.0012558
29 | 0.0074941 | 0.0018782
30 | 0.0043924 | 0.0011008
31 | 0.0032587 | 0.0008167
32 | 0.0044114 | 0.0011056
33 | 0.012863 | 0.0032238
34 | 0.0073411 | 0.0018399
35 | 0.0034409 | 0.00086236
36 | 0.0022322 | 0.00055944
37 | 0.0023416 | 0.00058685
38 | 0.0024106 | 0.00060415
39 | 0.0013917 | 0.0003488
40 | 0.0014985 | 0.00037555
41 | 0.0022438 | 0.00056234
42 | 0.0095018 | 0.0023814
43 | 0.0064452 | 0.0016153
44 | 0.0021684 | 0.00054345
45 | 0.0014619 | 0.00036639
46 | 0.0026579 | 0.00066614
47 | 0.0087712 | 0.0021983
48 | 0.0034201 | 0.00085715
49 | 0.0077419 | 0.0019403
50 | 0.0038897 | 0.00097485
51 | 0.0028384 | 0.00071137
52 | 0.0043074 | 0.0010795
53 | 0.010899 | 0.0027316
54 | 0.0042682 | 0.0010697
55 | 0.008123 | 0.0020358
56 | 0.0071666 | 0.0017961
57 | 0.0026822 | 0.00067221
58 | 0.0068865 | 0.0017259
59 | 0.014922 | 0.0037399
60 | 0.0077344 | 0.0019384
61 | 0.0069992 | 0.0017542
62 | 0.013418 | 0.0033629
63 | 0.0082207 | 0.0020603
64 | 0.00769 | 0.0019273
65 | 0.0030012 | 0.00075216
66 | 0.0085526 | 0.0021435
67 | 0.0084998 | 0.0021303
68 | 0.0071677 | 0.0017964
69 | 0.0161 | 0.004035
70 | 0.012455 | 0.0031216
71 | 0.0082125 | 0.0020582
72 | 0.0083044 | 0.0020813
73 | 0.02732 | 0.0068469
74 | 0.01066 | 0.0026716
75 | 0.015574 | 0.0039033
76 | 0.0088193 | 0.0022103
77 | 0.0058159 | 0.0014576
78 | 0.010362 | 0.0025968
79 | 0.022899 | 0.0057391
80 | 0.0055812 | 0.0013988
81 | 0.0025893 | 0.00064894
82 | 0.013714 | 0.003437
83 | 0.013328 | 0.0033402
84 | 0.010287 | 0.0025781
85 | 0.0064466 | 0.0016157
86 | 0.0097741 | 0.0024496
87 | 0.0085913 | 0.0021532
88 | 0.0086442 | 0.0021664
89 | 0.0085099 | 0.0021328

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1