## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_244-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_244-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_244-8_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_244-8_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_244-8_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_244-8_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_244-8_0_4_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_244-8_0_4_node_66 | 0.4 | n |  | TRUE
8 | bus_LV_244-8_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_244-8_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_244-8_0_4_node_64 | 0.4 | n |  | TRUE
11 | bus_LV_244-8_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_244-8_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_244-8_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_244-8_0_4_node_70 | 0.4 | n |  | TRUE
15 | bus_LV_244-8_0_4_node_69 | 0.4 | n |  | TRUE
16 | bus_LV_244-8_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_244-8_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_244-8_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_244-8_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_244-8_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_244-8_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_244-8_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_244-8_0_4_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_244-8_0_4_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_244-8_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_244-8_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_244-8_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_244-8_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_244-8_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_244-8_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_244-8_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_244-8_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_244-8_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_244-8_0_4_node_124 | 0.4 | n |  | TRUE
35 | bus_LV_244-8_0_4_node_54 | 0.4 | n |  | TRUE
36 | bus_LV_244-8_0_4_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_244-8_0_4_node_52 | 0.4 | n |  | TRUE
38 | bus_LV_244-8_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_244-8_0_4_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_244-8_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_244-8_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_244-8_0_4_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_244-8_0_4_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_244-8_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_244-8_0_4_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_244-8_0_4_node_62 | 0.4 | n |  | TRUE
47 | bus_LV_244-8_0_4_node_53 | 0.4 | n |  | TRUE
48 | bus_LV_244-8_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_244-8_0_4_node_50 | 0.4 | n |  | TRUE
50 | bus_LV_244-8_0_4_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_244-8_0_4_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_244-8_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_244-8_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_244-8_0_4_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_244-8_0_4_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_244-8_0_4_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_244-8_0_4_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_244-8_0_4_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_244-8_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_244-8_0_4_node_98 | 0.4 | n |  | TRUE
61 | bus_LV_244-8_0_4_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_244-8_0_4_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_244-8_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_244-8_0_4_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_244-8_0_4_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_244-8_0_4_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_244-8_0_4_node_67 | 0.4 | n |  | TRUE
68 | bus_LV_244-8_0_4_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_244-8_0_4_node_115 | 0.4 | n |  | TRUE
70 | bus_LV_244-8_0_4_node_116 | 0.4 | n |  | TRUE
71 | bus_LV_244-8_0_4_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_244-8_0_4_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_244-8_0_4_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_244-8_0_4_node_118 | 0.4 | n |  | TRUE
75 | bus_LV_244-8_0_4_node_109 | 0.4 | n |  | TRUE
76 | bus_LV_244-8_0_4_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_244-8_0_4_node_83 | 0.4 | n |  | TRUE
78 | bus_LV_244-8_0_4_node_84 | 0.4 | n |  | TRUE
79 | bus_LV_244-8_0_4_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_244-8_0_4_node_107 | 0.4 | n |  | TRUE
81 | bus_LV_244-8_0_4_node_105 | 0.4 | n |  | TRUE
82 | bus_LV_244-8_0_4_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_244-8_0_4_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_244-8_0_4_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_244-8_0_4_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_244-8_0_4_node_126 | 0.4 | n |  | TRUE
87 | bus_LV_244-8_0_4_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_244-8_0_4_node_127 | 0.4 | n |  | TRUE
89 | bus_LV_244-8_0_4_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_244-8_0_4_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_244-8_0_4_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_244-8_0_4_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_244-8_0_4_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_244-8_0_4_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_244-8_0_4_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_244-8_0_4_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_244-8_0_4_node_132 | 0.4 | n |  | TRUE
98 | bus_LV_244-8_0_4_node_130 | 0.4 | n |  | TRUE
99 | bus_LV_244-8_0_4_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_244-8_0_4_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_244-8_0_4_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_244-8_0_4_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_244-8_0_4_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_244-8_0_4_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_244-8_0_4_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_244-8_0_4_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_244-8_0_4_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_244-8_0_4_node_112 | 0.4 | n |  | TRUE
109 | bus_LV_244-8_0_4_node_108 | 0.4 | n |  | TRUE
110 | bus_LV_244-8_0_4_node_120 | 0.4 | n |  | TRUE
111 | bus_LV_244-8_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_244-8_0_4_node_121 | 0.4 | n |  | TRUE
113 | bus_LV_244-8_0_4_node_99 | 0.4 | n |  | TRUE
114 | bus_LV_244-8_0_4_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_244-8_0_4_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_244-8_0_4_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_244-8_0_4_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_244-8_0_4_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_244-8_0_4_node_104 | 0.4 | n |  | TRUE
120 | bus_LV_244-8_0_4_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_244-8_0_4_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_244-8_0_4_node_122 | 0.4 | n |  | TRUE
123 | bus_LV_244-8_0_4_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_244-8_0_4_node_138 | 0.4 | n |  | TRUE
125 | bus_LV_244-8_0_4_node_147 | 0.4 | n |  | TRUE
126 | bus_LV_244-8_0_4_node_145 | 0.4 | n |  | TRUE
127 | bus_LV_244-8_0_4_node_128 | 0.4 | n |  | TRUE
128 | bus_LV_244-8_0_4_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_244-8_0_4_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_244-8_0_4_node_134 | 0.4 | n |  | TRUE
131 | bus_LV_244-8_0_4_node_133 | 0.4 | n |  | TRUE
132 | bus_LV_244-8_0_4_node_135 | 0.4 | n |  | TRUE
133 | bus_LV_244-8_0_4_node_136 | 0.4 | n |  | TRUE
134 | bus_LV_244-8_0_4_node_137 | 0.4 | n |  | TRUE
135 | bus_LV_244-8_0_4_node_141 | 0.4 | n |  | TRUE
136 | bus_LV_244-8_0_4_node_140 | 0.4 | n |  | TRUE
137 | bus_LV_244-8_0_4_node_143 | 0.4 | n |  | TRUE
138 | bus_LV_244-8_0_4_node_144 | 0.4 | n |  | TRUE
139 | bus_LV_244-8_0_4_node_146 | 0.4 | n |  | TRUE
140 | bus_MV_516_1_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_244-8_0_4_load_0 | 0 | 0.0013258 | 0.00033229 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_244-8_0_4_load_3 | 2 | 0.002237 | 0.00056065 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_244-8_0_4_load_4 | 3 | 0.0019171 | 0.00048048 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_244-8_0_4_load_14 | 6 | 0.0027671 | 0.0006935 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_244-8_0_4_load_66 | 7 | 0.0023252 | 0.00058274 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_244-8_0_4_load_6 | 8 | 0.0015019 | 0.00037642 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_244-8_0_4_load_30 | 9 | 0.0049903 | 0.0012507 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_244-8_0_4_load_64 | 10 | 0.021891 | 0.0054864 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_244-8_0_4_load_5 | 11 | 0.0015736 | 0.00039439 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_244-8_0_4_load_7 | 12 | 0.0022425 | 0.00056201 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_244-8_0_4_load_8 | 13 | 0.001175 | 0.00029447 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_244-8_0_4_load_69 | 15 | 0.0032069 | 0.00080371 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_244-8_0_4_load_9 | 16 | 0.005151 | 0.001291 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_244-8_0_4_load_10 | 17 | 0.0079202 | 0.001985 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_244-8_0_4_load_11 | 18 | 0.0059042 | 0.0014797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_244-8_0_4_load_13 | 20 | 0.0054288 | 0.0013606 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_244-8_0_4_load_29 | 21 | 0.0080283 | 0.0020121 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_244-8_0_4_load_28 | 22 | 0.0083038 | 0.0020811 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_244-8_0_4_load_26 | 23 | 0.0063421 | 0.0015895 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_244-8_0_4_load_27 | 24 | 0.0056857 | 0.001425 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_244-8_0_4_load_16 | 25 | 0.0073949 | 0.0018533 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_244-8_0_4_load_17 | 26 | 0.0013875 | 0.00034773 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_244-8_0_4_load_21 | 30 | 0.0051708 | 0.0012959 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_244-8_0_4_load_22 | 32 | 0.007416 | 0.0018586 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_244-8_0_4_load_51 | 33 | 0.0026322 | 0.0006597 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_244-8_0_4_load_124 | 34 | 0.005497 | 0.0013777 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_244-8_0_4_load_54 | 35 | 0.0028072 | 0.00070355 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_244-8_0_4_load_60 | 36 | 0.0034581 | 0.00086668 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_244-8_0_4_load_52 | 37 | 0.005395 | 0.0013521 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_244-8_0_4_load_31 | 38 | 0.0022338 | 0.00055983 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_244-8_0_4_load_32 | 39 | 0.0023757 | 0.00059541 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_244-8_0_4_load_34 | 41 | 0.0044034 | 0.0011036 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_244-8_0_4_load_36 | 42 | 0.0081486 | 0.0020422 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_244-8_0_4_load_44 | 43 | 0.0023114 | 0.0005793 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_244-8_0_4_load_62 | 46 | 0.0036858 | 0.00092374 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_244-8_0_4_load_43 | 48 | 0.0045714 | 0.0011457 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_244-8_0_4_load_50 | 49 | 0.0051927 | 0.0013014 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_244-8_0_4_load_47 | 50 | 0.0051952 | 0.001302 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_244-8_0_4_load_63 | 51 | 0.0043532 | 0.001091 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_244-8_0_4_load_37 | 52 | 0.002803 | 0.00070249 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_244-8_0_4_load_38 | 53 | 0.0045014 | 0.0011282 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_244-8_0_4_load_40 | 55 | 0.0033464 | 0.00083869 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_244-8_0_4_load_41 | 56 | 0.0028971 | 0.00072608 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_244-8_0_4_load_42 | 57 | 0.004645 | 0.0011641 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_244-8_0_4_load_48 | 58 | 0.0034426 | 0.00086279 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_244-8_0_4_load_98 | 60 | 0.004435 | 0.0011115 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_244-8_0_4_load_56 | 61 | 0.0062654 | 0.0015702 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_244-8_0_4_load_57 | 62 | 0.0068323 | 0.0017123 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_244-8_0_4_load_58 | 63 | 0.0087776 | 0.0021999 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_244-8_0_4_load_93 | 64 | 0.0022539 | 0.00056488 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_244-8_0_4_load_45 | 65 | 0.0023169 | 0.00058068 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_244-8_0_4_load_46 | 66 | 0.0044217 | 0.0011082 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_244-8_0_4_load_65 | 68 | 0.0021145 | 0.00052996 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_244-8_0_4_load_115 | 69 | 0.0018308 | 0.00045884 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_244-8_0_4_load_59 | 71 | 0.0037133 | 0.00093065 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_244-8_0_4_load_61 | 72 | 0.0017311 | 0.00043387 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_244-8_0_4_load_111 | 73 | 0.0066719 | 0.0016721 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_244-8_0_4_load_118 | 74 | 0.0057213 | 0.0014339 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_244-8_0_4_load_84 | 78 | 0.001927 | 0.00048295 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_244-8_0_4_load_78 | 79 | 0.0028619 | 0.00071725 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_244-8_0_4_load_107 | 80 | 0.0014522 | 0.00036396 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_244-8_0_4_load_105 | 81 | 0.0021458 | 0.00053778 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_244-8_0_4_load_72 | 83 | 0.0023791 | 0.00059626 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_244-8_0_4_load_73 | 84 | 0.002853 | 0.00071502 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_244-8_0_4_load_85 | 85 | 0.0026088 | 0.00065382 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_244-8_0_4_load_86 | 87 | 0.0027498 | 0.00068916 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_244-8_0_4_load_127 | 88 | 0.0027635 | 0.00069259 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_244-8_0_4_load_74 | 89 | 0.0023364 | 0.00058556 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_244-8_0_4_load_75 | 90 | 0.0012831 | 0.00032157 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_244-8_0_4_load_76 | 91 | 0.0021954 | 0.00055023 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_244-8_0_4_load_77 | 92 | 0.002312 | 0.00057943 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_244-8_0_4_load_80 | 93 | 0.0032068 | 0.0008037 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_244-8_0_4_load_79 | 94 | 0.0032604 | 0.00081714 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_244-8_0_4_load_81 | 95 | 0.0019882 | 0.00049828 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_244-8_0_4_load_82 | 96 | 0.0021681 | 0.00054338 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_244-8_0_4_load_132 | 97 | 0.004388 | 0.0010997 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_244-8_0_4_load_87 | 99 | 0.0021089 | 0.00052854 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_244-8_0_4_load_88 | 100 | 0.0019982 | 0.00050079 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_244-8_0_4_load_89 | 101 | 0.0035703 | 0.00089481 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_244-8_0_4_load_92 | 103 | 0.0089982 | 0.0022552 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_244-8_0_4_load_94 | 104 | 0.0025357 | 0.00063551 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_244-8_0_4_load_97 | 106 | 0.0020283 | 0.00050834 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_244-8_0_4_load_112 | 108 | 0.001876 | 0.00047018 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_244-8_0_4_load_108 | 109 | 0.0018758 | 0.00047012 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_244-8_0_4_load_120 | 110 | 0.001772 | 0.0004441 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_244-8_0_4_load_113 | 111 | 0.006572 | 0.0016471 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_244-8_0_4_load_121 | 112 | 0.0036433 | 0.0009131 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_244-8_0_4_load_99 | 113 | 0.0037105 | 0.00092993 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_244-8_0_4_load_100 | 114 | 0.0035338 | 0.00088566 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_244-8_0_4_load_101 | 115 | 0.0057209 | 0.0014338 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_244-8_0_4_load_102 | 116 | 0.0030112 | 0.00075467 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_244-8_0_4_load_117 | 117 | 0.0035992 | 0.00090205 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_244-8_0_4_load_103 | 118 | 0.0024778 | 0.00062099 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_244-8_0_4_load_104 | 119 | 0.0019141 | 0.00047971 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_244-8_0_4_load_106 | 120 | 0.0029545 | 0.00074047 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_244-8_0_4_load_122 | 122 | 0.0040936 | 0.001026 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_244-8_0_4_load_114 | 123 | 0.0029044 | 0.0007279 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_244-8_0_4_load_138 | 124 | 0.0012817 | 0.00032122 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_244-8_0_4_load_147 | 125 | 0.0029617 | 0.00074228 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_244-8_0_4_load_128 | 127 | 0.00088635 | 0.00022214 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_244-8_0_4_load_129 | 128 | 0.001021 | 0.00025587 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_244-8_0_4_load_131 | 129 | 0.0014304 | 0.00035848 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_244-8_0_4_load_134 | 130 | 0.0010052 | 0.00025193 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_244-8_0_4_load_133 | 131 | 0.0023064 | 0.00057805 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_244-8_0_4_load_136 | 133 | 0.0017845 | 0.00044723 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_244-8_0_4_load_137 | 134 | 0.0018649 | 0.00046738 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_244-8_0_4_load_141 | 135 | 0.0011893 | 0.00029807 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_244-8_0_4_load_140 | 136 | 0.001273 | 0.00031906 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_244-8_0_4_load_143 | 137 | 0.0035533 | 0.00089054 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_244-8_0_4_load_146 | 139 | 0.0041547 | 0.0010413 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_244-8_0_4_line_0 |  | 0 | 1 | 0.025038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_244-8_0_4_line_1 |  | 1 | 2 | 0.016232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_244-8_0_4_line_2 |  | 1 | 3 | 0.035308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_244-8_0_4_line_3 |  | 2 | 7 | 0.02197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_244-8_0_4_line_4 |  | 3 | 8 | 0.013029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_244-8_0_4_line_5 |  | 4 | 5 | 0.026069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_244-8_0_4_line_6 |  | 4 | 6 | 0.023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_244-8_0_4_line_7 |  | 5 | 9 | 0.026471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_244-8_0_4_line_8 |  | 7 | 10 | 0.019449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_244-8_0_4_line_9 |  | 8 | 11 | 0.014956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_244-8_0_4_line_10 |  | 9 | 21 | 0.0025851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_244-8_0_4_line_11 |  | 10 | 68 | 0.022794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_244-8_0_4_line_12 |  | 11 | 12 | 0.010161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_244-8_0_4_line_13 |  | 12 | 13 | 0.027093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_244-8_0_4_line_14 |  | 13 | 14 | 0.028343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_244-8_0_4_line_15 |  | 14 | 15 | 0.045153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_244-8_0_4_line_16 |  | 15 | 82 | 0.017729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_244-8_0_4_line_17 |  | 16 | 17 | 0.010927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_244-8_0_4_line_18 |  | 16 | 18 | 0.010947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_244-8_0_4_line_19 |  | 17 | 19 | 0.018526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_244-8_0_4_line_20 |  | 18 | 20 | 0.014399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_244-8_0_4_line_21 |  | 19 | 21 | 0.013046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_244-8_0_4_line_22 |  | 19 | 22 | 0.017717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_244-8_0_4_line_23 |  | 20 | 23 | 0.015435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_244-8_0_4_line_24 |  | 23 | 24 | 0.0064911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_244-8_0_4_line_25 |  | 24 | 30 | 0.014624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_244-8_0_4_line_26 |  | 25 | 26 | 0.010585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_244-8_0_4_line_27 |  | 25 | 27 | 0.058388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_244-8_0_4_line_28 |  | 26 | 28 | 0.017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_244-8_0_4_line_29 |  | 27 | 29 | 0.033887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_244-8_0_4_line_30 |  | 27 | 30 | 0.0057339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_244-8_0_4_line_31 |  | 28 | 31 | 0.004914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_244-8_0_4_line_32 |  | 28 | 32 | 0.050375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_244-8_0_4_line_33 |  | 29 | 33 | 0.017388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_244-8_0_4_line_34 |  | 31 | 34 | 0.03764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_244-8_0_4_line_35 |  | 33 | 37 | 0.0093642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_244-8_0_4_line_36 |  | 35 | 36 | 0.021293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_244-8_0_4_line_37 |  | 36 | 71 | 0.023951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_244-8_0_4_line_38 |  | 37 | 47 | 0.02461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_244-8_0_4_line_39 |  | 38 | 39 | 0.017972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_244-8_0_4_line_40 |  | 38 | 40 | 0.0176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_244-8_0_4_line_41 |  | 39 | 41 | 0.013304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_244-8_0_4_line_42 |  | 40 | 42 | 0.018004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_244-8_0_4_line_43 |  | 41 | 43 | 0.015136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_244-8_0_4_line_44 |  | 42 | 47 | 0.017633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_244-8_0_4_line_45 |  | 43 | 48 | 0.014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_244-8_0_4_line_46 |  | 44 | 45 | 0.004237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_244-8_0_4_line_47 |  | 44 | 46 | 0.031177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_244-8_0_4_line_48 |  | 45 | 49 | 0.015063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_244-8_0_4_line_49 |  | 45 | 50 | 0.011877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_244-8_0_4_line_50 |  | 46 | 51 | 0.022327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_244-8_0_4_line_51 |  | 47 | 51 | 0.015064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_244-8_0_4_line_52 |  | 48 | 65 | 0.013007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_244-8_0_4_line_53 |  | 49 | 69 | 0.021088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_244-8_0_4_line_54 |  | 50 | 58 | 0.0023441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_244-8_0_4_line_55 |  | 52 | 53 | 0.030443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_244-8_0_4_line_56 |  | 52 | 54 | 0.0077598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_244-8_0_4_line_57 |  | 53 | 55 | 0.0027392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_244-8_0_4_line_58 |  | 54 | 56 | 0.027272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_244-8_0_4_line_59 |  | 54 | 57 | 0.023191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_244-8_0_4_line_60 |  | 55 | 58 | 0.030291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_244-8_0_4_line_61 |  | 56 | 59 | 0.027574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_244-8_0_4_line_62 |  | 57 | 60 | 0.00099621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_244-8_0_4_line_63 |  | 59 | 61 | 0.018746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_244-8_0_4_line_64 |  | 59 | 62 | 0.016328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_244-8_0_4_line_65 |  | 59 | 63 | 0.040392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_244-8_0_4_line_66 |  | 60 | 64 | 0.022997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_244-8_0_4_line_67 |  | 61 | 72 | 0.032597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_244-8_0_4_line_68 |  | 62 | 73 | 0.051498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_244-8_0_4_line_69 |  | 63 | 74 | 0.011655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_244-8_0_4_line_70 |  | 64 | 102 | 0.035556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_244-8_0_4_line_71 |  | 65 | 66 | 0.016149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_244-8_0_4_line_72 |  | 66 | 67 | 0.011203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_244-8_0_4_line_73 |  | 67 | 68 | 0.01244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_244-8_0_4_line_74 |  | 69 | 70 | 0.014488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_244-8_0_4_line_75 |  | 70 | 117 | 0.021037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_244-8_0_4_line_76 |  | 70 | 116 | 0.0020473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_244-8_0_4_line_77 |  | 71 | 72 | 0.022284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_244-8_0_4_line_78 |  | 73 | 75 | 0.002584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_244-8_0_4_line_79 |  | 74 | 76 | 0.030306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_244-8_0_4_line_80 |  | 75 | 109 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_244-8_0_4_line_81 |  | 76 | 121 | 0.067859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_244-8_0_4_line_82 |  | 77 | 78 | 0.054309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_244-8_0_4_line_83 |  | 77 | 79 | 0.0072807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_244-8_0_4_line_84 |  | 78 | 97 | 0.028832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_244-8_0_4_line_85 |  | 79 | 91 | 0.011474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_244-8_0_4_line_86 |  | 80 | 81 | 0.023985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_244-8_0_4_line_87 |  | 81 | 118 | 0.020085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_244-8_0_4_line_88 |  | 82 | 83 | 0.045608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_244-8_0_4_line_89 |  | 82 | 84 | 0.038656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_244-8_0_4_line_90 |  | 83 | 85 | 0.026889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_244-8_0_4_line_91 |  | 84 | 86 | 0.0064777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_244-8_0_4_line_92 |  | 85 | 87 | 0.018106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_244-8_0_4_line_93 |  | 86 | 88 | 0.028885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_244-8_0_4_line_94 |  | 87 | 96 | 0.0085193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_244-8_0_4_line_95 |  | 88 | 125 | 0.02515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_244-8_0_4_line_96 |  | 89 | 90 | 0.0061234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_244-8_0_4_line_97 |  | 89 | 91 | 0.016767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_244-8_0_4_line_98 |  | 90 | 92 | 0.022264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_244-8_0_4_line_99 |  | 92 | 93 | 0.0016607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_244-8_0_4_line_100 |  | 93 | 94 | 0.021111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_244-8_0_4_line_101 |  | 94 | 95 | 0.0040091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_244-8_0_4_line_102 |  | 95 | 96 | 0.021404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_244-8_0_4_line_103 |  | 97 | 98 | 0.029741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_244-8_0_4_line_104 |  | 98 | 127 | 0.021144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_244-8_0_4_line_105 |  | 99 | 100 | 0.0097566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_244-8_0_4_line_106 |  | 99 | 101 | 0.071746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_244-8_0_4_line_107 |  | 100 | 102 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_244-8_0_4_line_108 |  | 102 | 103 | 0.0036248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_244-8_0_4_line_109 |  | 103 | 104 | 0.035514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_244-8_0_4_line_110 |  | 104 | 105 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_244-8_0_4_line_111 |  | 105 | 106 | 0.010988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_244-8_0_4_line_112 |  | 106 | 110 | 0.014558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_244-8_0_4_line_113 |  | 107 | 108 | 0.010088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_244-8_0_4_line_114 |  | 107 | 109 | 0.0090362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_244-8_0_4_line_115 |  | 108 | 111 | 0.017989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_244-8_0_4_line_116 |  | 110 | 112 | 0.014586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_244-8_0_4_line_117 |  | 111 | 123 | 0.010207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_244-8_0_4_line_118 |  | 112 | 124 | 0.010961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_244-8_0_4_line_119 |  | 113 | 114 | 0.0055992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_244-8_0_4_line_120 |  | 113 | 115 | 0.010149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_244-8_0_4_line_121 |  | 114 | 116 | 0.029067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_244-8_0_4_line_122 |  | 117 | 120 | 0.0019507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_244-8_0_4_line_123 |  | 118 | 119 | 0.0037859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_244-8_0_4_line_124 |  | 119 | 120 | 0.022367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_244-8_0_4_line_125 |  | 121 | 122 | 0.017814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_244-8_0_4_line_126 |  | 125 | 126 | 0.030851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_244-8_0_4_line_127 |  | 126 | 137 | 0.011016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_244-8_0_4_line_128 |  | 127 | 128 | 0.010324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_244-8_0_4_line_129 |  | 128 | 129 | 0.0066773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_244-8_0_4_line_130 |  | 129 | 130 | 0.0018869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_244-8_0_4_line_131 |  | 130 | 131 | 0.023651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_244-8_0_4_line_132 |  | 131 | 132 | 0.016281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_244-8_0_4_line_133 |  | 132 | 133 | 0.013159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_244-8_0_4_line_134 |  | 132 | 134 | 0.01851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_244-8_0_4_line_135 |  | 134 | 135 | 0.022074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_244-8_0_4_line_136 |  | 135 | 136 | 0.019553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_244-8_0_4_line_137 |  | 137 | 138 | 0.056001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_244-8_0_4_line_138 |  | 138 | 139 | 0.0086305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_244-8_0_4_trafo_36 | 0.63 MVA 20/0.4 kV | 140 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2673396.4035 | 1253200.1486 | 2673401.3124 | 1253196.1621 | 2673406.4152 | 1253192.9785 | 2673418.3555 | 1253188.6514
1 | 2673396.4035 | 1253200.1486 | 2673389.9849 | 1253205.9956 | 2673383.0069 | 1253208.878 | 2673383.0069 | 1253208.878
2 | 2673396.4035 | 1253200.1486 | 2673408.3137 | 1253212.7053 | 2673419.5258 | 1253226.7879
3 | 2673383.0069 | 1253208.878 | 2673375.1762 | 1253208.1138 | 2673363.8943 | 1253203.9154 | 2673361.8678 | 1253203.5219
4 | 2673431.7032 | 1253230.9602 | 2673429.0279 | 1253230.8975 | 2673419.5258 | 1253226.7879
5 | 2673355.6408 | 1253139.822 | 2673358.7986 | 1253151.7142 | 2673361.4407 | 1253158.3295 | 2673365.1225 | 1253163.8681
6 | 2673365.1225 | 1253163.8681 | 2673387.1128 | 1253158.8812 | 2673387.9985 | 1253157.8879
7 | 2673355.6408 | 1253139.822 | 2673343.029 | 1253138.198 | 2673330.8767 | 1253131.754 | 2673330.8767 | 1253131.754
8 | 2673342.7599 | 1253199.9368 | 2673343.7123 | 1253199.9961 | 2673361.8678 | 1253203.5219
9 | 2673446.6263 | 1253230.7731 | 2673443.1572 | 1253231.2284 | 2673431.7032 | 1253230.9602
10 | 2673328.4737 | 1253130.8011 | 2673330.8767 | 1253131.754
11 | 2673342.7599 | 1253199.9368 | 2673325.2014 | 1253198.8439 | 2673320.0305 | 1253199.4061
12 | 2673446.6263 | 1253230.7731 | 2673449.5817 | 1253230.3852 | 2673456.3319 | 1253227.9374
13 | 2673481.8175 | 1253218.7473 | 2673480.3564 | 1253219.2253 | 2673456.3319 | 1253227.9374
14 | 2673506.7381 | 1253226.4133 | 2673503.3597 | 1253221.9904 | 2673494.6116 | 1253217.9233 | 2673487.1678 | 1253216.997 | 2673481.8175 | 1253218.7473
15 | 2673506.7381 | 1253226.4133 | 2673509.3936 | 1253237.4098 | 2673507.902 | 1253260.3081 | 2673506.8397 | 1253271.1501
16 | 2673505.111 | 1253288.7943 | 2673506.8397 | 1253271.1501
17 | 2673287.1467 | 1253125.3076 | 2673292.4916 | 1253124.9408 | 2673298.0368 | 1253124.4178
18 | 2673287.1467 | 1253125.3076 | 2673276.2258 | 1253126.057
19 | 2673316.3466 | 1253125.9922 | 2673304.1638 | 1253123.8399 | 2673298.0368 | 1253124.4178
20 | 2673276.2258 | 1253126.057 | 2673268.3314 | 1253126.5988 | 2673261.8697 | 1253127.1577
21 | 2673316.3466 | 1253125.9922 | 2673328.4737 | 1253130.8011
22 | 2673316.3466 | 1253125.9922 | 2673323.2054 | 1253109.6565
23 | 2673246.4925 | 1253128.4877 | 2673261.8697 | 1253127.1577
24 | 2673246.4925 | 1253128.4877 | 2673240.0255 | 1253129.047
25 | 2673225.4562 | 1253130.3072 | 2673240.0255 | 1253129.047
26 | 2673208.2276 | 1253062.8611 | 2673210.5684 | 1253073.1843
27 | 2673219.7436 | 1253130.8013 | 2673214.0412 | 1253088.4999 | 2673210.5684 | 1253073.1843
28 | 2673204.4309 | 1253046.1169 | 2673208.2276 | 1253062.8611
29 | 2673219.7436 | 1253130.8013 | 2673185.9597 | 1253134.5088
30 | 2673219.7436 | 1253130.8013 | 2673225.4562 | 1253130.3072
31 | 2673204.4309 | 1253046.1169 | 2673199.763 | 1253047.6937
32 | 2673204.4309 | 1253046.1169 | 2673247.5894 | 1253034.9421 | 2673253.3822 | 1253034.9112
33 | 2673185.9597 | 1253134.5088 | 2673187.749 | 1253150.3091 | 2673187.8322 | 1253151.7937
34 | 2673199.763 | 1253047.6937 | 2673162.637 | 1253053.8924
35 | 2673187.8322 | 1253151.7937 | 2673188.3563 | 1253161.1432
36 | 2673131.8489 | 1253141.8467 | 2673152.9486 | 1253138.9854
37 | 2673108.1325 | 1253145.1908 | 2673128.8466 | 1253142.2538 | 2673131.8489 | 1253141.8467
38 | 2673189.7336 | 1253185.7151 | 2673188.3563 | 1253161.1432
39 | 2673208.6556 | 1253219.8242 | 2673225.2932 | 1253218.4005 | 2673226.5386 | 1253218.1341
40 | 2673191.1196 | 1253221.3249 | 2673208.6556 | 1253219.8242
41 | 2673239.5482 | 1253215.3514 | 2673226.5386 | 1253218.1341
42 | 2673191.1196 | 1253221.3249 | 2673190.4194 | 1253203.3343
43 | 2673239.5482 | 1253215.3514 | 2673254.3494 | 1253212.1854
44 | 2673189.7336 | 1253185.7151 | 2673190.4194 | 1253203.3343
45 | 2673268.1541 | 1253208.7403 | 2673255.8595 | 1253211.8624 | 2673254.3494 | 1253212.1854
46 | 2673157.2428 | 1253222.2072 | 2673153.0149 | 1253221.7769
47 | 2673157.2428 | 1253222.2072 | 2673156.413 | 1253191.0408
48 | 2673153.0149 | 1253221.7769 | 2673154.6008 | 1253236.7564
49 | 2673153.0149 | 1253221.7769 | 2673141.1653 | 1253220.9712
50 | 2673156.413 | 1253191.0408 | 2673156.413 | 1253191.0408 | 2673160.3697 | 1253190.8228 | 2673160.2063 | 1253186.9513 | 2673174.683 | 1253186.3452
51 | 2673189.7336 | 1253185.7151 | 2673174.683 | 1253186.3452
52 | 2673268.1541 | 1253208.7403 | 2673280.7613 | 1253205.5387
53 | 2673156.821 | 1253257.7273 | 2673154.6008 | 1253236.7564
54 | 2673141.1653 | 1253220.9712 | 2673138.8266 | 1253220.8122
55 | 2673077.543 | 1253206.6087 | 2673085.4935 | 1253210.8468 | 2673102.3616 | 1253216.1031 | 2673106.0825 | 1253216.6769
56 | 2673070.6953 | 1253202.9585 | 2673077.543 | 1253206.6087
57 | 2673106.0825 | 1253216.6769 | 2673108.7898 | 1253217.0943
58 | 2673070.6953 | 1253202.9585 | 2673062.8351 | 1253195.4116 | 2673052.8326 | 1253182.4467
59 | 2673070.6953 | 1253202.9585 | 2673061.8324 | 1253222.2411 | 2673061.0194 | 1253224.035
60 | 2673138.8266 | 1253220.8122 | 2673128.2324 | 1253220.092 | 2673108.7898 | 1253217.0943
61 | 2673036.2676 | 1253160.403 | 2673049.6965 | 1253178.3817 | 2673052.8326 | 1253182.4467
62 | 2673060.6081 | 1253224.9424 | 2673061.0194 | 1253224.035
63 | 2673036.2676 | 1253160.403 | 2673054.3013 | 1253155.2853
64 | 2673036.2676 | 1253160.403 | 2673029.4419 | 1253162.576 | 2673021.9813 | 1253167.8991 | 2673021.9813 | 1253167.8991
65 | 2673036.2676 | 1253160.403 | 2673028.6454 | 1253151.2913 | 2673016.8579 | 1253142.1727 | 2673007.0741 | 1253137.0039 | 2673004.5661 | 1253136.5752
66 | 2673044.75 | 1253239.8656 | 2673053.34 | 1253236.5802 | 2673058.3495 | 1253229.926 | 2673060.6081 | 1253224.9424
67 | 2673086.0689 | 1253148.3191 | 2673071.6386 | 1253150.3651 | 2673054.3013 | 1253155.2853
68 | 2673021.9813 | 1253167.8991 | 2673011.3935 | 1253169.8033 | 2673000.827 | 1253169.3728 | 2672985.1046 | 1253170.3243 | 2672970.9549 | 1253173.0729
69 | 2672993.0775 | 1253134.611 | 2673004.5661 | 1253136.5752
70 | 2673009.3995 | 1253236.0493 | 2673034.3666 | 1253238.67 | 2673044.75 | 1253239.8656
71 | 2673296.5853 | 1253202.4169 | 2673287.9246 | 1253203.7196 | 2673280.7613 | 1253205.5387
72 | 2673307.6637 | 1253200.7505 | 2673296.5853 | 1253202.4169
73 | 2673307.6637 | 1253200.7505 | 2673320.0305 | 1253199.4061
74 | 2673158.3464 | 1253272.135 | 2673156.821 | 1253257.7273
75 | 2673158.3464 | 1253272.135 | 2673176.8765 | 1253269.2729 | 2673179.1179 | 1253268.8167
76 | 2673158.3464 | 1253272.135 | 2673156.3077 | 1253272.3236
77 | 2673108.1325 | 1253145.1908 | 2673086.0689 | 1253148.3191
78 | 2672968.4183 | 1253173.5656 | 2672970.9549 | 1253173.0729
79 | 2672969.1473 | 1253119.9243 | 2672970.906 | 1253124.1713 | 2672972.9938 | 1253127.4327 | 2672976.8031 | 1253130.6042 | 2672980.9296 | 1253132.5342 | 2672993.0775 | 1253134.611
80 | 2672968.4183 | 1253173.5656 | 2672952.2784 | 1253178.0694
81 | 2672969.1473 | 1253119.9243 | 2672969.7319 | 1253115.962 | 2672971.7689 | 1253110.483 | 2672975.1583 | 1253107.3225 | 2672981.8518 | 1253103.6356 | 2673023.6516 | 1253085.0814
82 | 2673307.6126 | 1253248.7628 | 2673305.6636 | 1253255.0321 | 2673298.509 | 1253284.3873 | 2673280.9835 | 1253284.7419
83 | 2673307.6126 | 1253248.7628 | 2673314.1586 | 1253251.9502
84 | 2673273.2447 | 1253309.1217 | 2673276.6886 | 1253284.8288 | 2673280.9835 | 1253284.7419
85 | 2673324.4568 | 1253257.0074 | 2673323.4989 | 1253256.4983 | 2673314.1586 | 1253251.9502
86 | 2673249.0717 | 1253251.1443 | 2673225.8982 | 1253257.3318
87 | 2673206.4926 | 1253262.5132 | 2673225.8982 | 1253257.3318
88 | 2673505.111 | 1253288.7943 | 2673500.3062 | 1253289.8577 | 2673494.8955 | 1253292.9261 | 2673488.7857 | 1253295.1742 | 2673482.5162 | 1253298.132 | 2673471.5339 | 1253300.82 | 2673461.8555 | 1253301.6974
89 | 2673505.111 | 1253288.7943 | 2673504.256 | 1253299.9252 | 2673502.5176 | 1253311.1006 | 2673496.5207 | 1253320.6666 | 2673494.0751 | 1253324.904
90 | 2673435.0272 | 1253302.0124 | 2673438.3339 | 1253302.5319 | 2673458.9107 | 1253301.9643 | 2673461.8555 | 1253301.6974
91 | 2673490.8372 | 1253330.5144 | 2673494.0751 | 1253324.904
92 | 2673417.3944 | 1253298.141 | 2673423.9646 | 1253300.2744 | 2673435.0272 | 1253302.0124
93 | 2673490.8372 | 1253330.5144 | 2673467.0656 | 1253343.4847 | 2673465.4319 | 1253344.2535
94 | 2673417.3944 | 1253298.141 | 2673410.0082 | 1253295.7426 | 2673409.299 | 1253295.4882
95 | 2673465.4319 | 1253344.2535 | 2673447.453 | 1253352.7149 | 2673442.728 | 1253355.0694
96 | 2673344.6695 | 1253267.7503 | 2673339.2624 | 1253264.8764
97 | 2673324.4568 | 1253257.0074 | 2673339.2624 | 1253264.8764
98 | 2673344.6695 | 1253267.7503 | 2673351.8805 | 1253271.5828 | 2673364.4352 | 1253277.9963
99 | 2673364.4352 | 1253277.9963 | 2673365.9141 | 1253278.7517
100 | 2673385.3777 | 1253286.9101 | 2673381.7767 | 1253285.6188 | 2673366.1574 | 1253278.876 | 2673365.9141 | 1253278.7517
101 | 2673385.3777 | 1253286.9101 | 2673389.1514 | 1253288.2634
102 | 2673409.299 | 1253295.4882 | 2673389.1514 | 1253288.2634
103 | 2673268.6296 | 1253338.5017 | 2673272.5218 | 1253314.221 | 2673273.2447 | 1253309.1217
104 | 2673268.6296 | 1253338.5017 | 2673260.0479 | 1253339.2851 | 2673247.5696 | 1253340.3878
105 | 2673011.0247 | 1253260.915 | 2673010.6408 | 1253258.3809 | 2673010.2416 | 1253251.1984
106 | 2673011.0247 | 1253260.915 | 2673014.4647 | 1253283.6243 | 2673056.4724 | 1253281.1514 | 2673063.1613 | 1253281.4896
107 | 2673009.3995 | 1253236.0493 | 2673010.2416 | 1253251.1984
108 | 2673009.3995 | 1253236.0493 | 2673005.7942 | 1253235.6736
109 | 2672970.6672 | 1253239.1186 | 2672979.4527 | 1253237.0589 | 2672989.9535 | 1253235.4649 | 2673001.17 | 1253235.1918 | 2673005.7942 | 1253235.6736
110 | 2672957.7788 | 1253242.1402 | 2672970.6672 | 1253239.1186
111 | 2672957.7788 | 1253242.1402 | 2672958.368 | 1253245.1497 | 2672957.3321 | 1253253.0029
112 | 2672946.4947 | 1253259.5145 | 2672954.1875 | 1253258.6302 | 2672956.9447 | 1253255.94 | 2672957.3321 | 1253253.0029
113 | 2672943.5747 | 1253180.4981 | 2672933.9116 | 1253183.3943
114 | 2672943.5747 | 1253180.4981 | 2672952.2784 | 1253178.0694
115 | 2672933.9116 | 1253183.3943 | 2672916.6801 | 1253188.5588
116 | 2672946.4947 | 1253259.5145 | 2672935.8403 | 1253260.7393 | 2672935.8523 | 1253258.5378 | 2672934.1984 | 1253258.6794
117 | 2672906.903 | 1253191.4891 | 2672916.6801 | 1253188.5588
118 | 2672923.277 | 1253259.6145 | 2672934.1984 | 1253258.6794
119 | 2673121.7884 | 1253275.5164 | 2673127.3638 | 1253275.0007
120 | 2673111.6826 | 1253276.4511 | 2673121.7884 | 1253275.5164
121 | 2673156.3077 | 1253272.3236 | 2673127.3638 | 1253275.0007
122 | 2673179.1179 | 1253268.8167 | 2673181.0295 | 1253268.4277
123 | 2673206.4926 | 1253262.5132 | 2673202.8349 | 1253263.4899
124 | 2673181.0295 | 1253268.4277 | 2673194.9565 | 1253265.5935 | 2673202.8349 | 1253263.4899
125 | 2673023.6516 | 1253085.0814 | 2673040.0171 | 1253078.0449
126 | 2673413.9502 | 1253364.8753 | 2673418.1208 | 1253365.0493 | 2673428.2057 | 1253362.3056 | 2673442.728 | 1253355.0694
127 | 2673413.9502 | 1253364.8753 | 2673407.8487 | 1253364.6329 | 2673403.2712 | 1253362.8572
128 | 2673237.2862 | 1253341.2966 | 2673247.5696 | 1253340.3878
129 | 2673230.6348 | 1253341.8844 | 2673237.2862 | 1253341.2966
130 | 2673230.6348 | 1253341.8844 | 2673228.7552 | 1253342.0505
131 | 2673205.1851 | 1253343.9994 | 2673205.1851 | 1253343.9994 | 2673221.4169 | 1253342.699 | 2673228.7552 | 1253342.0505
132 | 2673189.0344 | 1253346.0569 | 2673205.1851 | 1253343.9994
133 | 2673189.0344 | 1253346.0569 | 2673176.4171 | 1253349.7927
134 | 2673189.0344 | 1253346.0569 | 2673185.713 | 1253327.847 | 2673185.713 | 1253327.847
135 | 2673185.713 | 1253327.847 | 2673166.7368 | 1253324.0766 | 2673164.0484 | 1253324.5338
136 | 2673144.7722 | 1253327.8123 | 2673164.0484 | 1253324.5338
137 | 2673351.7056 | 1253342.3546 | 2673356.6071 | 1253343.2159 | 2673376.0426 | 1253348.2714 | 2673386.8309 | 1253353.3087 | 2673401.6007 | 1253362.2092 | 2673403.2712 | 1253362.8572
138 | 2673351.7056 | 1253342.3546 | 2673343.2049 | 1253340.863

## bus_geodata
| x | y | coords
0 | 2673418.3555 | 1253188.6514
1 | 2673396.4035 | 1253200.1486
2 | 2673383.0069 | 1253208.878
3 | 2673419.5258 | 1253226.7879
4 | 2673365.1225 | 1253163.8681
5 | 2673355.6408 | 1253139.822
6 | 2673387.9985 | 1253157.8879
7 | 2673361.8678 | 1253203.5219
8 | 2673431.7032 | 1253230.9602
9 | 2673330.8767 | 1253131.754
10 | 2673342.7599 | 1253199.9368
11 | 2673446.6263 | 1253230.7731
12 | 2673456.3319 | 1253227.9374
13 | 2673481.8175 | 1253218.7473
14 | 2673506.7381 | 1253226.4133
15 | 2673506.8397 | 1253271.1501
16 | 2673287.1467 | 1253125.3076
17 | 2673298.0368 | 1253124.4178
18 | 2673276.2258 | 1253126.057
19 | 2673316.3466 | 1253125.9922
20 | 2673261.8697 | 1253127.1577
21 | 2673328.4737 | 1253130.8011
22 | 2673323.2054 | 1253109.6565
23 | 2673246.4925 | 1253128.4877
24 | 2673240.0255 | 1253129.047
25 | 2673210.5684 | 1253073.1843
26 | 2673208.2276 | 1253062.8611
27 | 2673219.7436 | 1253130.8013
28 | 2673204.4309 | 1253046.1169
29 | 2673185.9597 | 1253134.5088
30 | 2673225.4562 | 1253130.3072
31 | 2673199.763 | 1253047.6937
32 | 2673253.3822 | 1253034.9112
33 | 2673187.8322 | 1253151.7937
34 | 2673162.637 | 1253053.8924
35 | 2673152.9486 | 1253138.9854
36 | 2673131.8489 | 1253141.8467
37 | 2673188.3563 | 1253161.1432
38 | 2673208.6556 | 1253219.8242
39 | 2673226.5386 | 1253218.1341
40 | 2673191.1196 | 1253221.3249
41 | 2673239.5482 | 1253215.3514
42 | 2673190.4194 | 1253203.3343
43 | 2673254.3494 | 1253212.1854
44 | 2673157.2428 | 1253222.2072
45 | 2673153.0149 | 1253221.7769
46 | 2673156.413 | 1253191.0408
47 | 2673189.7336 | 1253185.7151
48 | 2673268.1541 | 1253208.7403
49 | 2673154.6008 | 1253236.7564
50 | 2673141.1653 | 1253220.9712
51 | 2673174.683 | 1253186.3452
52 | 2673077.543 | 1253206.6087
53 | 2673106.0825 | 1253216.6769
54 | 2673070.6953 | 1253202.9585
55 | 2673108.7898 | 1253217.0943
56 | 2673052.8326 | 1253182.4467
57 | 2673061.0194 | 1253224.035
58 | 2673138.8266 | 1253220.8122
59 | 2673036.2676 | 1253160.403
60 | 2673060.6081 | 1253224.9424
61 | 2673054.3013 | 1253155.2853
62 | 2673021.9813 | 1253167.8991
63 | 2673004.5661 | 1253136.5752
64 | 2673044.75 | 1253239.8656
65 | 2673280.7613 | 1253205.5387
66 | 2673296.5853 | 1253202.4169
67 | 2673307.6637 | 1253200.7505
68 | 2673320.0305 | 1253199.4061
69 | 2673156.821 | 1253257.7273
70 | 2673158.3464 | 1253272.135
71 | 2673108.1325 | 1253145.1908
72 | 2673086.0689 | 1253148.3191
73 | 2672970.9549 | 1253173.0729
74 | 2672993.0775 | 1253134.611
75 | 2672968.4183 | 1253173.5656
76 | 2672969.1473 | 1253119.9243
77 | 2673307.6126 | 1253248.7628
78 | 2673280.9835 | 1253284.7419
79 | 2673314.1586 | 1253251.9502
80 | 2673249.0717 | 1253251.1443
81 | 2673225.8982 | 1253257.3318
82 | 2673505.111 | 1253288.7943
83 | 2673461.8555 | 1253301.6974
84 | 2673494.0751 | 1253324.904
85 | 2673435.0272 | 1253302.0124
86 | 2673490.8372 | 1253330.5144
87 | 2673417.3944 | 1253298.141
88 | 2673465.4319 | 1253344.2535
89 | 2673339.2624 | 1253264.8764
90 | 2673344.6695 | 1253267.7503
91 | 2673324.4568 | 1253257.0074
92 | 2673364.4352 | 1253277.9963
93 | 2673365.9141 | 1253278.7517
94 | 2673385.3777 | 1253286.9101
95 | 2673389.1514 | 1253288.2634
96 | 2673409.299 | 1253295.4882
97 | 2673273.2447 | 1253309.1217
98 | 2673268.6296 | 1253338.5017
99 | 2673011.0247 | 1253260.915
100 | 2673010.2416 | 1253251.1984
101 | 2673063.1613 | 1253281.4896
102 | 2673009.3995 | 1253236.0493
103 | 2673005.7942 | 1253235.6736
104 | 2672970.6672 | 1253239.1186
105 | 2672957.7788 | 1253242.1402
106 | 2672957.3321 | 1253253.0029
107 | 2672943.5747 | 1253180.4981
108 | 2672933.9116 | 1253183.3943
109 | 2672952.2784 | 1253178.0694
110 | 2672946.4947 | 1253259.5145
111 | 2672916.6801 | 1253188.5588
112 | 2672934.1984 | 1253258.6794
113 | 2673121.7884 | 1253275.5164
114 | 2673127.3638 | 1253275.0007
115 | 2673111.6826 | 1253276.4511
116 | 2673156.3077 | 1253272.3236
117 | 2673179.1179 | 1253268.8167
118 | 2673206.4926 | 1253262.5132
119 | 2673202.8349 | 1253263.4899
120 | 2673181.0295 | 1253268.4277
121 | 2673023.6516 | 1253085.0814
122 | 2673040.0171 | 1253078.0449
123 | 2672906.903 | 1253191.4891
124 | 2672923.277 | 1253259.6145
125 | 2673442.728 | 1253355.0694
126 | 2673413.9502 | 1253364.8753
127 | 2673247.5696 | 1253340.3878
128 | 2673237.2862 | 1253341.2966
129 | 2673230.6348 | 1253341.8844
130 | 2673228.7552 | 1253342.0505
131 | 2673205.1851 | 1253343.9994
132 | 2673189.0344 | 1253346.0569
133 | 2673176.4171 | 1253349.7927
134 | 2673185.713 | 1253327.847
135 | 2673164.0484 | 1253324.5338
136 | 2673144.7722 | 1253327.8123
137 | 2673403.2712 | 1253362.8572
138 | 2673351.7056 | 1253342.3546
139 | 2673343.2049 | 1253340.863
140 | 2673189.7336 | 1253185.7151

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98851 | -0.21893 | 0.0013258 | 0.00033229
1 | 0.98854 | -0.21834 | 0 | 0
2 | 0.98913 | -0.2071 | 0.002237 | 0.00056065
3 | 0.98729 | -0.24241 | 0.0019171 | 0.00048048
4 | 0.98661 | -0.25753 | 0 | 0
5 | 0.98668 | -0.25624 | 0 | 0
6 | 0.98655 | -0.25871 | 0.0027671 | 0.0006935
7 | 0.98994 | -0.19147 | 0.0023252 | 0.00058274
8 | 0.98684 | -0.25109 | 0.0015019 | 0.00037642
9 | 0.98675 | -0.25492 | 0.0049903 | 0.0012507
10 | 0.99069 | -0.17726 | 0.021891 | 0.0054864
11 | 0.98633 | -0.26086 | 0.0015736 | 0.00039439
12 | 0.98599 | -0.26735 | 0.0022425 | 0.00056201
13 | 0.98512 | -0.28416 | 0.001175 | 0.00029447
14 | 0.98423 | -0.30146 | 0 | 0
15 | 0.98137 | -0.35682 | 0.0032069 | 0.00080371
16 | 0.98769 | -0.23664 | 0.005151 | 0.001291
17 | 0.98736 | -0.2429 | 0.0079202 | 0.001985
18 | 0.98806 | -0.22938 | 0.0059042 | 0.0014797
19 | 0.98695 | -0.25088 | 0 | 0
20 | 0.98863 | -0.21831 | 0.0054288 | 0.0013606
21 | 0.98677 | -0.25457 | 0.0080283 | 0.0020121
22 | 0.98682 | -0.25351 | 0.0083038 | 0.0020811
23 | 0.98932 | -0.20497 | 0.0063421 | 0.0015895
24 | 0.98964 | -0.19864 | 0.0056857 | 0.001425
25 | 0.98964 | -0.19873 | 0.0073949 | 0.0018533
26 | 0.9895 | -0.20142 | 0.0013875 | 0.00034773
27 | 0.9908 | -0.17621 | 0 | 0
28 | 0.9893 | -0.20537 | 0 | 0
29 | 0.99352 | -0.12376 | 0 | 0
30 | 0.99046 | -0.1829 | 0.0051708 | 0.0012959
31 | 0.98927 | -0.20585 | 0 | 0
32 | 0.98896 | -0.21203 | 0.007416 | 0.0018586
33 | 0.99491 | -0.096967 | 0.0026322 | 0.0006597
34 | 0.98908 | -0.20954 | 0.005497 | 0.0013777
35 | 0.97896 | -0.40525 | 0.0028072 | 0.00070355
36 | 0.97902 | -0.40416 | 0.0034581 | 0.00086668
37 | 0.99569 | -0.082134 | 0.005395 | 0.0013521
38 | 0.99788 | -0.040081 | 0.0022338 | 0.00055983
39 | 0.99683 | -0.060026 | 0.0023757 | 0.00059541
40 | 0.99893 | -0.020247 | 0 | 0
41 | 0.99607 | -0.074539 | 0.0044034 | 0.0011036
42 | 1 | 0 | -0.40185 | -0.10243
43 | 0.99523 | -0.090491 | 0.0023114 | 0.0005793
44 | 0.99261 | -0.14066 | 0 | 0
45 | 0.9923 | -0.14675 | 0 | 0
46 | 0.99495 | -0.096 | 0.0036858 | 0.00092374
47 | 0.99784 | -0.040933 | 0 | 0
48 | 0.99445 | -0.10522 | 0.0045714 | 0.0011457
49 | 0.99178 | -0.15676 | 0.0051927 | 0.0013014
50 | 0.99092 | -0.17302 | 0.0051952 | 0.001302
51 | 0.99666 | -0.063423 | 0.0043532 | 0.001091
52 | 0.98407 | -0.30536 | 0.002803 | 0.00070249
53 | 0.98712 | -0.2462 | 0.0045014 | 0.0011282
54 | 0.98332 | -0.3201 | 0 | 0
55 | 0.98741 | -0.24068 | 0.0033464 | 0.00083869
56 | 0.98164 | -0.35271 | 0.0028971 | 0.00072608
57 | 0.98247 | -0.33654 | 0.004645 | 0.0011641
58 | 0.99067 | -0.17799 | 0.0034426 | 0.00086279
59 | 0.98003 | -0.38434 | 0 | 0
60 | 0.98244 | -0.33716 | 0.004435 | 0.0011115
61 | 0.97972 | -0.39045 | 0.0062654 | 0.0015702
62 | 0.97962 | -0.39226 | 0.0068323 | 0.0017123
63 | 0.97933 | -0.39798 | 0.0087776 | 0.0021999
64 | 0.9818 | -0.34971 | 0.0022539 | 0.00056488
65 | 0.99377 | -0.11818 | 0.0023169 | 0.00058068
66 | 0.99295 | -0.13397 | 0.0044217 | 0.0011082
67 | 0.9924 | -0.1445 | 0 | 0
68 | 0.99178 | -0.1562 | 0.0021145 | 0.00052996
69 | 0.99115 | -0.16886 | 0.0018308 | 0.00045884
70 | 0.99075 | -0.17671 | 0 | 0
71 | 0.97916 | -0.40143 | 0.0037133 | 0.00093065
72 | 0.97936 | -0.39739 | 0.0017311 | 0.00043387
73 | 0.97867 | -0.4109 | 0.0066719 | 0.0016721
74 | 0.97923 | -0.40006 | 0.0057213 | 0.0014339
75 | 0.97864 | -0.41152 | 0 | 0
76 | 0.97911 | -0.40231 | 0 | 0
77 | 0.97296 | -0.52163 | 0 | 0
78 | 0.97199 | -0.54073 | 0.001927 | 0.00048295
79 | 0.97309 | -0.51907 | 0.0028619 | 0.00071725
80 | 0.99017 | -0.18801 | 0.0014522 | 0.00036396
81 | 0.9902 | -0.1874 | 0.0021458 | 0.00053778
82 | 0.98031 | -0.37761 | 0 | 0
83 | 0.97825 | -0.41777 | 0.0023791 | 0.00059626
84 | 0.97972 | -0.38904 | 0.002853 | 0.00071502
85 | 0.97709 | -0.44035 | 0.0026088 | 0.00065382
86 | 0.97964 | -0.39062 | 0 | 0
87 | 0.97636 | -0.45473 | 0.0027498 | 0.00068916
88 | 0.97928 | -0.39768 | 0.0027635 | 0.00069259
89 | 0.9737 | -0.50699 | 0.0023364 | 0.00058556
90 | 0.97385 | -0.50401 | 0.0012831 | 0.00032157
91 | 0.97333 | -0.51444 | 0.0021954 | 0.00055023
92 | 0.97443 | -0.49266 | 0.002312 | 0.00057943
93 | 0.97448 | -0.49174 | 0.0032068 | 0.0008037
94 | 0.97513 | -0.47885 | 0.0032604 | 0.00081714
95 | 0.97527 | -0.47617 | 0.0019882 | 0.00049828
96 | 0.97604 | -0.46107 | 0.0021681 | 0.00054338
97 | 0.97153 | -0.54986 | 0.004388 | 0.0010997
98 | 0.97118 | -0.55687 | 0 | 0
99 | 0.98072 | -0.37081 | 0.0021089 | 0.00052854
100 | 0.98077 | -0.3698 | 0.0019982 | 0.00050079
101 | 0.98049 | -0.37545 | 0.0035703 | 0.00089481
102 | 0.98088 | -0.36769 | 0 | 0
103 | 0.98081 | -0.36902 | 0.0089982 | 0.0022552
104 | 0.98044 | -0.37627 | 0.0025357 | 0.00063551
105 | 0.98034 | -0.37837 | 0 | 0
106 | 0.98025 | -0.38011 | 0.0020283 | 0.00050834
107 | 0.97834 | -0.41742 | 0 | 0
108 | 0.97823 | -0.41951 | 0.001876 | 0.00047018
109 | 0.97844 | -0.41555 | 0.0018758 | 0.00047012
110 | 0.98016 | -0.38187 | 0.001772 | 0.0004441
111 | 0.97808 | -0.42261 | 0.006572 | 0.0016471
112 | 0.98009 | -0.38318 | 0.0036433 | 0.0009131
113 | 0.99033 | -0.18492 | 0.0037105 | 0.00092993
114 | 0.99037 | -0.18399 | 0.0035338 | 0.00088566
115 | 0.99027 | -0.18596 | 0.0057209 | 0.0014338
116 | 0.99072 | -0.17729 | 0.0030112 | 0.00075467
117 | 0.99047 | -0.18215 | 0.0035992 | 0.00090205
118 | 0.99026 | -0.18611 | 0.0024778 | 0.00062099
119 | 0.99029 | -0.1857 | 0.0019141 | 0.00047971
120 | 0.99045 | -0.18253 | 0.0029545 | 0.00074047
121 | 0.97885 | -0.40737 | 0 | 0
122 | 0.97879 | -0.4087 | 0.0040936 | 0.001026
123 | 0.97805 | -0.42315 | 0.0029044 | 0.0007279
124 | 0.98008 | -0.38343 | 0.0012817 | 0.00032122
125 | 0.97903 | -0.40256 | 0.0029617 | 0.00074228
126 | 0.97881 | -0.40688 | 0 | 0
127 | 0.97092 | -0.56186 | 0.00088635 | 0.00022214
128 | 0.97081 | -0.56413 | 0.001021 | 0.00025587
129 | 0.97074 | -0.56547 | 0.0014304 | 0.00035848
130 | 0.97073 | -0.5658 | 0.0010052 | 0.00025193
131 | 0.97054 | -0.56948 | 0.0023064 | 0.00057805
132 | 0.97045 | -0.57132 | 0 | 0
133 | 0.97043 | -0.57176 | 0.0017845 | 0.00044723
134 | 0.97037 | -0.57281 | 0.0018649 | 0.00046738
135 | 0.97032 | -0.57381 | 0.0011893 | 0.00029807
136 | 0.9703 | -0.57427 | 0.001273 | 0.00031906
137 | 0.97874 | -0.40843 | 0.0035533 | 0.00089054
138 | 0.97852 | -0.41266 | 0 | 0
139 | 0.97849 | -0.41332 | 0.0041547 | 0.0010413
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0013258 | -0.00033229 | 0.0013259 | 0.00033199 | 3.7398e-08 | -2.9706e-07 | 0.0019958 | 0.0019957 | 0.0019958 | 0.98851 | -0.21893 | 0.98854 | -0.21834 | 0.54829
1 | -0.078525 | -0.020006 | 0.078568 | 0.020033 | 4.2607e-05 | 2.6852e-05 | 0.11832 | 0.11832 | 0.11832 | 0.98854 | -0.21834 | 0.98913 | -0.2071 | 16.2525
2 | 0.077199 | 0.019674 | -0.07711 | -0.019618 | 8.9577e-05 | 5.6425e-05 | 0.11632 | 0.11632 | 0.11632 | 0.98854 | -0.21834 | 0.98729 | -0.24241 | 15.9784
3 | -0.080805 | -0.020594 | 0.080866 | 0.020632 | 6.0995e-05 | 3.8472e-05 | 0.12168 | 0.12168 | 0.12168 | 0.98913 | -0.2071 | 0.98994 | -0.19147 | 16.7147
4 | 0.075193 | 0.019137 | -0.075161 | -0.019118 | 3.1433e-05 | 1.9784e-05 | 0.11343 | 0.11343 | 0.11343 | 0.98729 | -0.24241 | 0.98684 | -0.25109 | 15.5815
5 | -0.0027672 | -0.00069329 | 0.0027674 | 0.00069307 | 1.7027e-07 | -2.2396e-07 | 0.0041735 | 0.0041734 | 0.0041735 | 0.98661 | -0.25753 | 0.98668 | -0.25624 | 1.1466
6 | 0.0027672 | 0.00069329 | -0.0027671 | -0.0006935 | 1.5598e-07 | -2.051e-07 | 0.0041735 | 0.0041736 | 0.0041736 | 0.98661 | -0.25753 | 0.98655 | -0.25871 | 1.1466
7 | -0.0027674 | -0.00069307 | 0.0027676 | 0.00069284 | 1.7289e-07 | -2.2747e-07 | 0.0041734 | 0.0041733 | 0.0041734 | 0.98668 | -0.25624 | 0.98675 | -0.25492 | 1.1465
8 | -0.083191 | -0.021215 | 0.083248 | 0.021251 | 5.7141e-05 | 3.607e-05 | 0.12518 | 0.12518 | 0.12518 | 0.98994 | -0.19147 | 0.99069 | -0.17726 | 17.1948
9 | 0.073659 | 0.018741 | -0.073625 | -0.018719 | 3.4656e-05 | 2.1798e-05 | 0.11117 | 0.11117 | 0.11117 | 0.98684 | -0.25109 | 0.98633 | -0.26086 | 15.2704
10 | -0.0077579 | -0.0019435 | 0.0077581 | 0.0019436 | 1.3267e-07 | 5.1888e-08 | 0.011699 | 0.011699 | 0.011699 | 0.98675 | -0.25492 | 0.98677 | -0.25457 | 3.2139
11 | -0.10514 | -0.026737 | 0.10525 | 0.026805 | 0.00010677 | 6.7745e-05 | 0.15806 | 0.15806 | 0.15806 | 0.99069 | -0.17726 | 0.99178 | -0.1562 | 21.7112
12 | 0.072051 | 0.018325 | -0.072028 | -0.018311 | 2.2551e-05 | 1.4173e-05 | 0.10879 | 0.10879 | 0.10879 | 0.98633 | -0.26086 | 0.98599 | -0.26735 | 14.9443
13 | 0.069786 | 0.017749 | -0.06973 | -0.017713 | 5.6445e-05 | 3.5434e-05 | 0.10541 | 0.10541 | 0.10541 | 0.98599 | -0.26735 | 0.98512 | -0.28416 | 14.4795
14 | 0.068555 | 0.017419 | -0.068498 | -0.017383 | 5.7079e-05 | 3.5809e-05 | 0.10364 | 0.10364 | 0.10364 | 0.98512 | -0.28416 | 0.98423 | -0.30146 | 14.2358
15 | 0.068498 | 0.017383 | -0.068316 | -0.017267 | 0.00018186 | 0.00011582 | 0.10364 | 0.10364 | 0.10364 | 0.98423 | -0.30146 | 0.98137 | -0.35682 | 28.4716
16 | 0.065109 | 0.016464 | -0.065044 | -0.016422 | 6.4863e-05 | 4.1288e-05 | 0.098774 | 0.098774 | 0.098774 | 0.98137 | -0.35682 | 0.98031 | -0.37761 | 27.1358
17 | 0.032033 | 0.0080354 | -0.032023 | -0.0080295 | 9.5446e-06 | 5.9687e-06 | 0.048262 | 0.048262 | 0.048262 | 0.98769 | -0.23664 | 0.98736 | -0.2429 | 13.2589
18 | -0.037184 | -0.0093264 | 0.037197 | 0.0093345 | 1.2884e-05 | 8.1054e-06 | 0.056023 | 0.056023 | 0.056023 | 0.98769 | -0.23664 | 0.98806 | -0.22938 | 15.3908
19 | 0.024103 | 0.0060445 | -0.024094 | -0.0060388 | 9.1674e-06 | 5.6303e-06 | 0.036326 | 0.036326 | 0.036326 | 0.98736 | -0.2429 | 0.98695 | -0.25088 | 9.9797
20 | -0.043101 | -0.010814 | 0.043124 | 0.010829 | 2.2753e-05 | 1.4377e-05 | 0.064914 | 0.064914 | 0.064914 | 0.98806 | -0.22938 | 0.98863 | -0.21831 | 17.8336
21 | 0.015789 | 0.0039573 | -0.015786 | -0.0039557 | 2.7723e-06 | 1.6076e-06 | 0.023805 | 0.023805 | 0.023805 | 0.98695 | -0.25088 | 0.98677 | -0.25457 | 6.5399
22 | 0.0083048 | 0.0020816 | -0.0083038 | -0.0020811 | 1.0416e-06 | 4.4026e-07 | 0.012521 | 0.012521 | 0.012521 | 0.98695 | -0.25088 | 0.98682 | -0.25351 | 3.4399
23 | -0.048552 | -0.012189 | 0.048583 | 0.012209 | 3.0916e-05 | 1.9588e-05 | 0.073085 | 0.073085 | 0.073085 | 0.98863 | -0.21831 | 0.98932 | -0.20497 | 20.0784
24 | -0.054925 | -0.013798 | 0.054942 | 0.013809 | 1.6617e-05 | 1.0552e-05 | 0.082624 | 0.082624 | 0.082624 | 0.98932 | -0.20497 | 0.98964 | -0.19864 | 22.6989
25 | -0.060628 | -0.015234 | 0.060673 | 0.015263 | 4.5585e-05 | 2.8986e-05 | 0.091173 | 0.091173 | 0.091173 | 0.98964 | -0.19864 | 0.99046 | -0.1829 | 25.0476
26 | 0.014308 | 0.0035874 | -0.014306 | -0.0035864 | 1.8373e-06 | 1.0399e-06 | 0.021514 | 0.021514 | 0.021514 | 0.98964 | -0.19873 | 0.9895 | -0.20142 | 5.9105
27 | -0.021703 | -0.0054408 | 0.021726 | 0.0054549 | 2.3317e-05 | 1.4172e-05 | 0.032633 | 0.032633 | 0.032633 | 0.98964 | -0.19873 | 0.9908 | -0.17621 | 8.9651
28 | 0.012919 | 0.0032387 | -0.012916 | -0.0032373 | 2.4301e-06 | 1.3348e-06 | 0.019428 | 0.019428 | 0.019428 | 0.9895 | -0.20142 | 0.9893 | -0.20537 | 5.3373
29 | -0.087592 | -0.022027 | 0.087812 | 0.022167 | 0.00021999 | 0.00014036 | 0.13157 | 0.13157 | 0.13157 | 0.9908 | -0.17621 | 0.99352 | -0.12376 | 36.1468
30 | 0.065865 | 0.016572 | -0.065844 | -0.016559 | 2.1049e-05 | 1.3398e-05 | 0.098941 | 0.098941 | 0.098941 | 0.9908 | -0.17621 | 0.99046 | -0.1829 | 27.1817
31 | 0.0054981 | 0.0013778 | -0.005498 | -0.0013778 | 1.2602e-07 | 1.756e-08 | 0.0082697 | 0.0082697 | 0.0082697 | 0.9893 | -0.20537 | 0.98927 | -0.20585 | 2.2719
32 | 0.0074184 | 0.0018595 | -0.007416 | -0.0018586 | 2.352e-06 | 8.5868e-07 | 0.011158 | 0.011158 | 0.011158 | 0.9893 | -0.20537 | 0.98896 | -0.21203 | 3.0655
33 | -0.087812 | -0.022167 | 0.087924 | 0.022239 | 0.00011288 | 7.2019e-05 | 0.13157 | 0.13157 | 0.13157 | 0.99352 | -0.12376 | 0.99491 | -0.096967 | 36.1467
34 | 0.005498 | 0.0013778 | -0.005497 | -0.0013777 | 9.6532e-07 | 1.3463e-07 | 0.0082697 | 0.0082699 | 0.0082699 | 0.98927 | -0.20585 | 0.98908 | -0.20954 | 2.272
35 | -0.090557 | -0.022899 | 0.090621 | 0.02294 | 6.4483e-05 | 4.1148e-05 | 0.13551 | 0.13551 | 0.13551 | 0.99491 | -0.096967 | 0.99569 | -0.082134 | 37.2282
36 | -0.0028072 | -0.00070355 | 0.0028073 | 0.00070337 | 1.4537e-07 | -1.7469e-07 | 0.0042669 | 0.0042668 | 0.0042669 | 0.97896 | -0.40525 | 0.97902 | -0.40416 | 1.1722
37 | -0.0062654 | -0.0015701 | 0.0062662 | 0.0015703 | 8.1448e-07 | 2.2005e-07 | 0.0095228 | 0.0095227 | 0.0095228 | 0.97902 | -0.40416 | 0.97916 | -0.40143 | 2.6162
38 | -0.096016 | -0.024292 | 0.096206 | 0.024414 | 0.00019024 | 0.00012143 | 0.14357 | 0.14357 | 0.14357 | 0.99569 | -0.082134 | 0.99784 | -0.040933 | 39.4432
39 | 0.12842 | 0.032869 | -0.1283 | -0.03279 | 0.00012389 | 7.8822e-05 | 0.19174 | 0.19175 | 0.19175 | 0.99788 | -0.040081 | 0.99683 | -0.060026 | 26.3386
40 | -0.13066 | -0.033429 | 0.13078 | 0.033509 | 0.00012558 | 7.9911e-05 | 0.19508 | 0.19508 | 0.19508 | 0.99788 | -0.040081 | 0.99893 | -0.020247 | 26.7961
41 | 0.12592 | 0.032195 | -0.12584 | -0.032139 | 8.8352e-05 | 5.6199e-05 | 0.1882 | 0.1882 | 0.1882 | 0.99683 | -0.060026 | 0.99607 | -0.074539 | 25.8515
42 | -0.13078 | -0.033509 | 0.13091 | 0.033591 | 0.00012846 | 8.1745e-05 | 0.19508 | 0.19508 | 0.19508 | 0.99893 | -0.020247 | 1 | 0 | 26.7961
43 | 0.12143 | 0.031035 | -0.12134 | -0.030976 | 9.3615e-05 | 5.952e-05 | 0.18162 | 0.18162 | 0.18162 | 0.99607 | -0.074539 | 0.99523 | -0.090491 | 24.9479
44 | 0.26929 | 0.068844 | -0.26875 | -0.068503 | 0.00053211 | 0.00034009 | 0.40118 | 0.40118 | 0.40118 | 1 | 0 | 0.99784 | -0.040933 | 55.1074
45 | 0.11903 | 0.030396 | -0.11894 | -0.030342 | 8.4688e-05 | 5.3831e-05 | 0.17817 | 0.17817 | 0.17817 | 0.99523 | -0.090491 | 0.99445 | -0.10522 | 24.4732
46 | 0.1637 | 0.041562 | -0.16366 | -0.041532 | 4.7919e-05 | 3.0559e-05 | 0.2456 | 0.2456 | 0.2456 | 0.99261 | -0.14066 | 0.9923 | -0.14675 | 33.736
47 | -0.1637 | -0.041562 | 0.16406 | 0.041787 | 0.00035261 | 0.00022486 | 0.2456 | 0.2456 | 0.2456 | 0.99261 | -0.14066 | 0.99495 | -0.096 | 33.736
48 | 0.037602 | 0.0094445 | -0.037584 | -0.0094332 | 1.7965e-05 | 1.1303e-05 | 0.056395 | 0.056395 | 0.056395 | 0.9923 | -0.14675 | 0.99178 | -0.15676 | 15.493
49 | 0.12605 | 0.032087 | -0.12589 | -0.031985 | 0.00015944 | 0.00010189 | 0.1892 | 0.1892 | 0.1892 | 0.9923 | -0.14675 | 0.99092 | -0.17302 | 51.979
50 | -0.16774 | -0.042711 | 0.16801 | 0.042879 | 0.00026397 | 0.00016836 | 0.25111 | 0.25111 | 0.25111 | 0.99495 | -0.096 | 0.99666 | -0.063423 | 34.4931
51 | 0.17255 | 0.04409 | -0.17236 | -0.04397 | 0.00018744 | 0.00011957 | 0.25761 | 0.25761 | 0.25761 | 0.99784 | -0.040933 | 0.99666 | -0.063423 | 35.3858
52 | 0.11437 | 0.029197 | -0.1143 | -0.029151 | 7.1586e-05 | 4.5478e-05 | 0.17132 | 0.17132 | 0.17132 | 0.99445 | -0.10522 | 0.99377 | -0.11818 | 23.5337
53 | 0.032392 | 0.0081318 | -0.032373 | -0.0081201 | 1.8681e-05 | 1.1684e-05 | 0.048604 | 0.048604 | 0.048604 | 0.99178 | -0.15676 | 0.99115 | -0.16886 | 13.3527
54 | 0.1207 | 0.030683 | -0.12067 | -0.030665 | 2.8926e-05 | 1.8483e-05 | 0.1814 | 0.1814 | 0.1814 | 0.99092 | -0.17302 | 0.99067 | -0.17799 | 49.8358
55 | -0.10869 | -0.027393 | 0.109 | 0.02759 | 0.00030856 | 0.00019709 | 0.1644 | 0.1644 | 0.1644 | 0.98407 | -0.30536 | 0.98712 | -0.2462 | 45.1657
56 | 0.10589 | 0.026691 | -0.10581 | -0.026643 | 7.4647e-05 | 4.7676e-05 | 0.16016 | 0.16016 | 0.16016 | 0.98407 | -0.30536 | 0.98332 | -0.3201 | 44.0013
57 | -0.1135 | -0.028719 | 0.11353 | 0.028738 | 3.0103e-05 | 1.9231e-05 | 0.17119 | 0.17119 | 0.17119 | 0.98712 | -0.2462 | 0.98741 | -0.24068 | 47.0298
58 | 0.066457 | 0.016751 | -0.066354 | -0.016685 | 0.0001035 | 6.5897e-05 | 0.1006 | 0.1006 | 0.1006 | 0.98332 | -0.3201 | 0.98164 | -0.35271 | 27.6379
59 | 0.039354 | 0.0098919 | -0.039323 | -0.0098725 | 3.0854e-05 | 1.9453e-05 | 0.059563 | 0.059563 | 0.059563 | 0.98332 | -0.3201 | 0.98247 | -0.33654 | 16.3635
60 | -0.11688 | -0.029576 | 0.11723 | 0.029802 | 0.00035279 | 0.00022539 | 0.17623 | 0.17623 | 0.17623 | 0.98741 | -0.24068 | 0.99067 | -0.17799 | 48.4153
61 | 0.063457 | 0.015959 | -0.063361 | -0.015898 | 9.5716e-05 | 6.091e-05 | 0.09621 | 0.09621 | 0.09621 | 0.98164 | -0.35271 | 0.98003 | -0.38434 | 26.4314
62 | 0.034678 | 0.0087083 | -0.034677 | -0.0087077 | 1.0308e-06 | 6.4709e-07 | 0.052528 | 0.052528 | 0.052528 | 0.98247 | -0.33654 | 0.98244 | -0.33716 | 14.4308
63 | 0.017987 | 0.0045112 | -0.017982 | -0.0045081 | 5.2437e-06 | 3.1198e-06 | 0.027312 | 0.027312 | 0.027312 | 0.98003 | -0.38434 | 0.97972 | -0.39045 | 7.5033
64 | 0.026767 | 0.00672 | -0.026757 | -0.0067138 | 1.0116e-05 | 6.2683e-06 | 0.040645 | 0.040645 | 0.040645 | 0.98003 | -0.38434 | 0.97962 | -0.39226 | 11.1663
65 | 0.018607 | 0.0046671 | -0.018595 | -0.0046598 | 1.2091e-05 | 7.2299e-06 | 0.028254 | 0.028254 | 0.028254 | 0.98003 | -0.38434 | 0.97933 | -0.39798 | 7.762
66 | 0.030242 | 0.0075962 | -0.030224 | -0.0075849 | 1.8099e-05 | 1.1292e-05 | 0.045811 | 0.045811 | 0.045811 | 0.98244 | -0.33716 | 0.9818 | -0.34971 | 12.5854
67 | 0.011717 | 0.0029378 | -0.011713 | -0.0029357 | 3.8712e-06 | 2.0672e-06 | 0.017796 | 0.017796 | 0.017796 | 0.97972 | -0.39045 | 0.97936 | -0.39739 | 4.889
68 | 0.019924 | 0.0050015 | -0.019907 | -0.0049908 | 1.7692e-05 | 1.0675e-05 | 0.030267 | 0.030267 | 0.030267 | 0.97962 | -0.39226 | 0.97867 | -0.4109 | 8.3152
69 | 0.0098176 | 0.00246 | -0.0098167 | -0.0024595 | 9.7255e-07 | 4.7579e-07 | 0.014917 | 0.014917 | 0.014917 | 0.97933 | -0.39798 | 0.97923 | -0.40006 | 4.0981
70 | 0.02797 | 0.00702 | -0.027946 | -0.0070051 | 2.3965e-05 | 1.4888e-05 | 0.042395 | 0.042395 | 0.042395 | 0.9818 | -0.34971 | 0.98088 | -0.36769 | 11.647
71 | 0.11198 | 0.028571 | -0.1119 | -0.028516 | 8.5313e-05 | 5.4182e-05 | 0.16786 | 0.16786 | 0.16786 | 0.99377 | -0.11818 | 0.99295 | -0.13397 | 23.0571
72 | 0.10748 | 0.027408 | -0.10742 | -0.027374 | 5.4604e-05 | 3.4657e-05 | 0.16123 | 0.16123 | 0.16123 | 0.99295 | -0.13397 | 0.9924 | -0.1445 | 22.147
73 | 0.10742 | 0.027374 | -0.10736 | -0.027335 | 6.0632e-05 | 3.8483e-05 | 0.16123 | 0.16123 | 0.16123 | 0.9924 | -0.1445 | 0.99178 | -0.1562 | 22.147
74 | 0.030542 | 0.0076613 | -0.030531 | -0.0076542 | 1.1424e-05 | 7.1249e-06 | 0.045855 | 0.045855 | 0.045855 | 0.99115 | -0.16886 | 0.99075 | -0.17671 | 12.5976
75 | 0.014549 | 0.0036473 | -0.014545 | -0.0036452 | 3.767e-06 | 2.1401e-06 | 0.021852 | 0.021852 | 0.021852 | 0.99075 | -0.17671 | 0.99047 | -0.18215 | 6.0033
76 | 0.015982 | 0.0040068 | -0.015981 | -0.0040066 | 4.4235e-07 | 2.5674e-07 | 0.024003 | 0.024003 | 0.024003 | 0.99075 | -0.17671 | 0.99072 | -0.17729 | 6.5944
77 | -0.0099796 | -0.0025009 | 0.0099815 | 0.0025019 | 1.922e-06 | 9.4974e-07 | 0.015166 | 0.015166 | 0.015166 | 0.97916 | -0.40143 | 0.97936 | -0.39739 | 4.1664
78 | 0.013235 | 0.0033186 | -0.013234 | -0.0033184 | 3.9239e-07 | 2.1866e-07 | 0.020123 | 0.020123 | 0.020123 | 0.97867 | -0.4109 | 0.97864 | -0.41152 | 5.5284
79 | 0.0040953 | 0.0010256 | -0.0040949 | -0.0010257 | 4.401e-07 | -9.9531e-08 | 0.0062229 | 0.0062231 | 0.0062231 | 0.97923 | -0.40006 | 0.97911 | -0.40231 | 1.7096
80 | 0.013234 | 0.0033184 | -0.013232 | -0.003317 | 2.5446e-06 | 1.418e-06 | 0.020123 | 0.020123 | 0.020123 | 0.97864 | -0.41152 | 0.97844 | -0.41555 | 5.5284
81 | 0.0040949 | 0.0010257 | -0.0040939 | -0.0010259 | 9.8553e-07 | -2.225e-07 | 0.0062231 | 0.0062234 | 0.0062234 | 0.97911 | -0.40231 | 0.97885 | -0.40737 | 1.7097
82 | 0.019113 | 0.0048012 | -0.019095 | -0.0047907 | 1.7406e-05 | 1.0466e-05 | 0.029234 | 0.029235 | 0.029235 | 0.97296 | -0.52163 | 0.97199 | -0.54073 | 8.0315
83 | -0.019113 | -0.0048012 | 0.019115 | 0.0048026 | 2.3334e-06 | 1.403e-06 | 0.029234 | 0.029234 | 0.029234 | 0.97296 | -0.52163 | 0.97309 | -0.51907 | 8.0315
84 | 0.017168 | 0.0043077 | -0.017161 | -0.0043033 | 7.4698e-06 | 4.4235e-06 | 0.026285 | 0.026285 | 0.026285 | 0.97199 | -0.54073 | 0.97153 | -0.54986 | 7.2211
85 | -0.021977 | -0.0055198 | 0.021982 | 0.0055228 | 4.8606e-06 | 2.9682e-06 | 0.033611 | 0.033611 | 0.033611 | 0.97309 | -0.51907 | 0.97333 | -0.51444 | 9.2337
86 | -0.0014522 | -0.00036396 | 0.0014523 | 0.00036368 | 4.2837e-08 | -2.8111e-07 | 0.0021824 | 0.0021823 | 0.0021824 | 0.99017 | -0.18801 | 0.9902 | -0.1874 | 0.59956
87 | -0.003598 | -0.00090146 | 0.0035982 | 0.00090134 | 2.2019e-07 | -1.1746e-07 | 0.0054068 | 0.0054067 | 0.0054068 | 0.9902 | -0.1874 | 0.99026 | -0.18611 | 1.4854
88 | 0.048738 | 0.01233 | -0.048644 | -0.012271 | 9.371e-05 | 5.9401e-05 | 0.074021 | 0.074021 | 0.074021 | 0.98031 | -0.37761 | 0.97825 | -0.41777 | 20.3355
89 | 0.016306 | 0.0040919 | -0.016297 | -0.0040867 | 8.8821e-06 | 5.1975e-06 | 0.024753 | 0.024753 | 0.024753 | 0.98031 | -0.37761 | 0.97972 | -0.38904 | 6.8004
90 | 0.046265 | 0.011675 | -0.046215 | -0.011643 | 4.9978e-05 | 3.1649e-05 | 0.070402 | 0.070403 | 0.070403 | 0.97825 | -0.41777 | 0.97709 | -0.44035 | 19.3414
91 | 0.013444 | 0.0033717 | -0.013443 | -0.0033711 | 1.0129e-06 | 5.667e-07 | 0.02042 | 0.02042 | 0.02042 | 0.97972 | -0.38904 | 0.97964 | -0.39062 | 5.6099
92 | 0.043606 | 0.010989 | -0.043576 | -0.01097 | 2.9963e-05 | 1.895e-05 | 0.06643 | 0.06643 | 0.06643 | 0.97709 | -0.44035 | 0.97636 | -0.45473 | 18.2499
93 | 0.013443 | 0.0033711 | -0.013439 | -0.0033686 | 4.5168e-06 | 2.5272e-06 | 0.02042 | 0.02042 | 0.02042 | 0.97964 | -0.39062 | 0.97928 | -0.39768 | 5.61
94 | 0.040827 | 0.010281 | -0.040814 | -0.010273 | 1.2375e-05 | 7.8137e-06 | 0.062239 | 0.062239 | 0.062239 | 0.97636 | -0.45473 | 0.97604 | -0.46107 | 17.0986
95 | 0.010675 | 0.002676 | -0.010673 | -0.0026747 | 2.4816e-06 | 1.2719e-06 | 0.016221 | 0.016221 | 0.016221 | 0.97928 | -0.39768 | 0.97903 | -0.40256 | 4.4564
96 | -0.026522 | -0.0066639 | 0.026526 | 0.0066662 | 3.7734e-06 | 2.3388e-06 | 0.040537 | 0.040537 | 0.040537 | 0.9737 | -0.50699 | 0.97385 | -0.50401 | 11.1367
97 | 0.024186 | 0.0060783 | -0.024177 | -0.006073 | 8.5923e-06 | 5.2906e-06 | 0.036967 | 0.036967 | 0.036967 | 0.9737 | -0.50699 | 0.97333 | -0.51444 | 10.1558
98 | -0.027809 | -0.0069878 | 0.027824 | 0.0069971 | 1.5079e-05 | 9.3734e-06 | 0.042498 | 0.042498 | 0.042498 | 0.97385 | -0.50401 | 0.97443 | -0.49266 | 11.6753
99 | -0.030136 | -0.0075766 | 0.030138 | 0.0075774 | 1.3194e-06 | 8.237e-07 | 0.046028 | 0.046028 | 0.046028 | 0.97443 | -0.49266 | 0.97448 | -0.49174 | 12.6452
100 | -0.033344 | -0.0083811 | 0.033365 | 0.008394 | 2.0531e-05 | 1.2877e-05 | 0.050925 | 0.050925 | 0.050925 | 0.97448 | -0.49174 | 0.97513 | -0.47885 | 13.9904
101 | -0.036625 | -0.0092111 | 0.03663 | 0.0092141 | 4.6979e-06 | 2.9566e-06 | 0.0559 | 0.0559 | 0.0559 | 0.97513 | -0.47885 | 0.97527 | -0.47617 | 15.3572
102 | -0.038618 | -0.0097124 | 0.038646 | 0.0097299 | 2.7877e-05 | 1.7574e-05 | 0.058934 | 0.058934 | 0.058934 | 0.97527 | -0.47617 | 0.97604 | -0.46107 | 16.1906
103 | 0.012773 | 0.0032036 | -0.012769 | -0.0032012 | 4.2688e-06 | 2.3639e-06 | 0.019564 | 0.019564 | 0.019564 | 0.97153 | -0.54986 | 0.97118 | -0.55687 | 5.3748
104 | 0.012769 | 0.0032012 | -0.012766 | -0.0031995 | 3.0349e-06 | 1.6808e-06 | 0.019564 | 0.019564 | 0.019564 | 0.97118 | -0.55687 | 0.97092 | -0.56186 | 5.3748
105 | -0.00568 | -0.0014229 | 0.0056803 | 0.001423 | 2.7172e-07 | 5.0784e-08 | 0.0086179 | 0.0086178 | 0.0086179 | 0.98072 | -0.37081 | 0.98077 | -0.3698 | 2.3675
106 | 0.0035711 | 0.00089441 | -0.0035703 | -0.00089481 | 7.8987e-07 | -3.9959e-07 | 0.0054181 | 0.0054184 | 0.0054184 | 0.98072 | -0.37081 | 0.98049 | -0.37545 | 1.4886
107 | -0.0076784 | -0.0019238 | 0.0076792 | 0.0019241 | 7.7213e-07 | 3.0267e-07 | 0.011649 | 0.011649 | 0.011649 | 0.98077 | -0.3698 | 0.98088 | -0.36769 | 3.2004
108 | 0.020267 | 0.005081 | -0.020266 | -0.0050802 | 1.2849e-06 | 7.7662e-07 | 0.030746 | 0.030746 | 0.030746 | 0.98088 | -0.36769 | 0.98081 | -0.36902 | 8.4466
109 | 0.011267 | 0.0028251 | -0.011263 | -0.002823 | 3.8917e-06 | 2.0426e-06 | 0.017094 | 0.017095 | 0.017095 | 0.98081 | -0.36902 | 0.98044 | -0.37627 | 4.6963
110 | 0.0087277 | 0.0021875 | -0.0087269 | -0.0021871 | 8.7102e-07 | 3.9052e-07 | 0.013246 | 0.013246 | 0.013246 | 0.98044 | -0.37627 | 0.98034 | -0.37837 | 3.6391
111 | 0.0087269 | 0.0021871 | -0.0087261 | -0.0021868 | 7.2298e-07 | 3.2418e-07 | 0.013246 | 0.013246 | 0.013246 | 0.98034 | -0.37837 | 0.98025 | -0.38011 | 3.6391
112 | 0.0066978 | 0.0016785 | -0.0066973 | -0.0016783 | 5.6435e-07 | 1.7768e-07 | 0.010167 | 0.010167 | 0.010167 | 0.98025 | -0.38011 | 0.98016 | -0.38187 | 2.7932
113 | 0.011355 | 0.0028464 | -0.011354 | -0.0028458 | 1.1284e-06 | 5.9549e-07 | 0.017271 | 0.017271 | 0.017271 | 0.97834 | -0.41742 | 0.97823 | -0.41951 | 4.7447
114 | -0.011355 | -0.0028464 | 0.011356 | 0.0028469 | 1.0107e-06 | 5.3338e-07 | 0.017271 | 0.017271 | 0.017271 | 0.97834 | -0.41742 | 0.97844 | -0.41555 | 4.7447
115 | 0.0094778 | 0.0023756 | -0.0094764 | -0.0023749 | 1.4021e-06 | 6.7155e-07 | 0.014417 | 0.014417 | 0.014417 | 0.97823 | -0.41951 | 0.97808 | -0.42261 | 3.9607
116 | 0.0049253 | 0.0012342 | -0.004925 | -0.0012342 | 3.0581e-07 | 1.1892e-08 | 0.0074772 | 0.0074773 | 0.0074773 | 0.98016 | -0.38187 | 0.98009 | -0.38318 | 2.0542
117 | 0.0029044 | 0.00072782 | -0.0029044 | -0.0007279 | 7.4733e-08 | -8.0266e-08 | 0.0044187 | 0.0044187 | 0.0044187 | 0.97808 | -0.42261 | 0.97805 | -0.42315 | 1.2139
118 | 0.0012817 | 0.00032109 | -0.0012817 | -0.00032122 | 1.5565e-08 | -1.2817e-07 | 0.0019459 | 0.0019459 | 0.0019459 | 0.98009 | -0.38318 | 0.98008 | -0.38343 | 0.5346
119 | -0.0094316 | -0.0023638 | 0.0094321 | 0.002364 | 4.2169e-07 | 1.9783e-07 | 0.014172 | 0.014172 | 0.014172 | 0.99033 | -0.18492 | 0.99037 | -0.18399 | 3.8933
120 | 0.0057212 | 0.0014338 | -0.0057209 | -0.0014338 | 2.8124e-07 | 4.942e-08 | 0.0085964 | 0.0085964 | 0.0085964 | 0.99033 | -0.18492 | 0.99027 | -0.18596 | 2.3616
121 | -0.012966 | -0.0032496 | 0.01297 | 0.0032519 | 4.1367e-06 | 2.2733e-06 | 0.019481 | 0.019481 | 0.019481 | 0.99037 | -0.18399 | 0.99072 | -0.17729 | 5.3519
122 | 0.010946 | 0.0027431 | -0.010946 | -0.002743 | 1.9783e-07 | 1.015e-07 | 0.016445 | 0.016445 | 0.016445 | 0.99047 | -0.18215 | 0.99045 | -0.18253 | 4.5178
123 | -0.006076 | -0.0015223 | 0.0060762 | 0.0015224 | 1.1834e-07 | 2.7031e-08 | 0.00913 | 0.00913 | 0.00913 | 0.99026 | -0.18611 | 0.99029 | -0.1857 | 2.5082
124 | -0.0079902 | -0.0020021 | 0.0079914 | 0.0020026 | 1.209e-06 | 4.8596e-07 | 0.012006 | 0.012006 | 0.012006 | 0.99029 | -0.1857 | 0.99045 | -0.18253 | 3.2984
125 | 0.0040939 | 0.0010259 | -0.0040936 | -0.001026 | 2.5873e-07 | -5.8325e-08 | 0.0062234 | 0.0062234 | 0.0062234 | 0.97885 | -0.40737 | 0.97879 | -0.4087 | 1.7097
126 | 0.0077111 | 0.0019325 | -0.0077095 | -0.0019318 | 1.5891e-06 | 6.2916e-07 | 0.01172 | 0.01172 | 0.01172 | 0.97903 | -0.40256 | 0.97881 | -0.40688 | 3.2198
127 | 0.0077095 | 0.0019318 | -0.0077089 | -0.0019316 | 5.6744e-07 | 2.2471e-07 | 0.01172 | 0.01172 | 0.01172 | 0.97881 | -0.40688 | 0.97874 | -0.40843 | 3.2198
128 | 0.011879 | 0.0029774 | -0.011878 | -0.0029767 | 1.2832e-06 | 6.9357e-07 | 0.018206 | 0.018206 | 0.018206 | 0.97092 | -0.56186 | 0.97081 | -0.56413 | 5.0016
129 | 0.010857 | 0.0027208 | -0.010856 | -0.0027205 | 6.9342e-07 | 3.6123e-07 | 0.016641 | 0.016641 | 0.016641 | 0.97081 | -0.56413 | 0.97074 | -0.56547 | 4.5717
130 | 0.0094259 | 0.002362 | -0.0094258 | -0.0023619 | 1.4772e-07 | 7.1211e-08 | 0.014449 | 0.014449 | 0.014449 | 0.97074 | -0.56547 | 0.97073 | -0.5658 | 3.9694
131 | 0.0084206 | 0.00211 | -0.0084191 | -0.0021093 | 1.4777e-06 | 6.5338e-07 | 0.012908 | 0.012908 | 0.012908 | 0.97073 | -0.5658 | 0.97054 | -0.56948 | 3.5461
132 | 0.0061127 | 0.0015313 | -0.0061121 | -0.0015311 | 5.3623e-07 | 1.4201e-07 | 0.0093716 | 0.0093717 | 0.0093717 | 0.97054 | -0.56948 | 0.97045 | -0.57132 | 2.5746
133 | 0.0017845 | 0.00044709 | -0.0017845 | -0.00044723 | 3.6944e-08 | -1.3893e-07 | 0.0027362 | 0.0027362 | 0.0027362 | 0.97045 | -0.57132 | 0.97043 | -0.57176 | 0.75171
134 | 0.0043277 | 0.001084 | -0.0043274 | -0.0010841 | 3.0563e-07 | -3.3078e-08 | 0.0066355 | 0.0066356 | 0.0066356 | 0.97045 | -0.57132 | 0.97037 | -0.57281 | 1.823
135 | 0.0024625 | 0.0006167 | -0.0024624 | -0.0006169 | 1.1803e-07 | -1.9714e-07 | 0.0037759 | 0.003776 | 0.003776 | 0.97037 | -0.57281 | 0.97032 | -0.57381 | 1.0374
136 | 0.0012731 | 0.00031883 | -0.001273 | -0.00031906 | 2.7946e-08 | -2.2363e-07 | 0.0019522 | 0.0019523 | 0.0019523 | 0.97032 | -0.57381 | 0.9703 | -0.57427 | 0.53635
137 | 0.0041556 | 0.0010411 | -0.0041548 | -0.0010412 | 8.3827e-07 | -1.6714e-07 | 0.0063178 | 0.0063181 | 0.0063181 | 0.97874 | -0.40843 | 0.97852 | -0.41266 | 1.7357
138 | 0.0041548 | 0.0010412 | -0.0041547 | -0.0010413 | 1.2919e-07 | -2.5727e-08 | 0.0063181 | 0.0063181 | 0.0063181 | 0.97852 | -0.41266 | 0.97849 | -0.41332 | 1.7357

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41 | 0.10448

## res_load
| p_mw | q_mvar
0 | 0.0013258 | 0.00033229
1 | 0.002237 | 0.00056065
2 | 0.0019171 | 0.00048048
3 | 0.0027671 | 0.0006935
4 | 0.0023252 | 0.00058274
5 | 0.0015019 | 0.00037642
6 | 0.0049903 | 0.0012507
7 | 0.021891 | 0.0054864
8 | 0.0015736 | 0.00039439
9 | 0.0022425 | 0.00056201
10 | 0.001175 | 0.00029447
11 | 0.0032069 | 0.00080371
12 | 0.005151 | 0.001291
13 | 0.0079202 | 0.001985
14 | 0.0059042 | 0.0014797
15 | 0.0054288 | 0.0013606
16 | 0.0080283 | 0.0020121
17 | 0.0083038 | 0.0020811
18 | 0.0063421 | 0.0015895
19 | 0.0056857 | 0.001425
20 | 0.0073949 | 0.0018533
21 | 0.0013875 | 0.00034773
22 | 0.0051708 | 0.0012959
23 | 0.007416 | 0.0018586
24 | 0.0026322 | 0.0006597
25 | 0.005497 | 0.0013777
26 | 0.0028072 | 0.00070355
27 | 0.0034581 | 0.00086668
28 | 0.005395 | 0.0013521
29 | 0.0022338 | 0.00055983
30 | 0.0023757 | 0.00059541
31 | 0.0044034 | 0.0011036
32 | 0.0081486 | 0.0020422
33 | 0.0023114 | 0.0005793
34 | 0.0036858 | 0.00092374
35 | 0.0045714 | 0.0011457
36 | 0.0051927 | 0.0013014
37 | 0.0051952 | 0.001302
38 | 0.0043532 | 0.001091
39 | 0.002803 | 0.00070249
40 | 0.0045014 | 0.0011282
41 | 0.0033464 | 0.00083869
42 | 0.0028971 | 0.00072608
43 | 0.004645 | 0.0011641
44 | 0.0034426 | 0.00086279
45 | 0.004435 | 0.0011115
46 | 0.0062654 | 0.0015702
47 | 0.0068323 | 0.0017123
48 | 0.0087776 | 0.0021999
49 | 0.0022539 | 0.00056488
50 | 0.0023169 | 0.00058068
51 | 0.0044217 | 0.0011082
52 | 0.0021145 | 0.00052996
53 | 0.0018308 | 0.00045884
54 | 0.0037133 | 0.00093065
55 | 0.0017311 | 0.00043387
56 | 0.0066719 | 0.0016721
57 | 0.0057213 | 0.0014339
58 | 0.001927 | 0.00048295
59 | 0.0028619 | 0.00071725
60 | 0.0014522 | 0.00036396
61 | 0.0021458 | 0.00053778
62 | 0.0023791 | 0.00059626
63 | 0.002853 | 0.00071502
64 | 0.0026088 | 0.00065382
65 | 0.0027498 | 0.00068916
66 | 0.0027635 | 0.00069259
67 | 0.0023364 | 0.00058556
68 | 0.0012831 | 0.00032157
69 | 0.0021954 | 0.00055023
70 | 0.002312 | 0.00057943
71 | 0.0032068 | 0.0008037
72 | 0.0032604 | 0.00081714
73 | 0.0019882 | 0.00049828
74 | 0.0021681 | 0.00054338
75 | 0.004388 | 0.0010997
76 | 0.0021089 | 0.00052854
77 | 0.0019982 | 0.00050079
78 | 0.0035703 | 0.00089481
79 | 0.0089982 | 0.0022552
80 | 0.0025357 | 0.00063551
81 | 0.0020283 | 0.00050834
82 | 0.001876 | 0.00047018
83 | 0.0018758 | 0.00047012
84 | 0.001772 | 0.0004441
85 | 0.006572 | 0.0016471
86 | 0.0036433 | 0.0009131
87 | 0.0037105 | 0.00092993
88 | 0.0035338 | 0.00088566
89 | 0.0057209 | 0.0014338
90 | 0.0030112 | 0.00075467
91 | 0.0035992 | 0.00090205
92 | 0.0024778 | 0.00062099
93 | 0.0019141 | 0.00047971
94 | 0.0029545 | 0.00074047
95 | 0.0040936 | 0.001026
96 | 0.0029044 | 0.0007279
97 | 0.0012817 | 0.00032122
98 | 0.0029617 | 0.00074228
99 | 0.00088635 | 0.00022214
100 | 0.001021 | 0.00025587
101 | 0.0014304 | 0.00035848
102 | 0.0010052 | 0.00025193
103 | 0.0023064 | 0.00057805
104 | 0.0017845 | 0.00044723
105 | 0.0018649 | 0.00046738
106 | 0.0011893 | 0.00029807
107 | 0.001273 | 0.00031906
108 | 0.0035533 | 0.00089054
109 | 0.0041547 | 0.0010413

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1