## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_247-15_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_247-15_0_6_node_53 | 0.4 | n |  | TRUE
2 | bus_LV_247-15_0_6_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_247-15_0_6_node_74 | 0.4 | n |  | TRUE
4 | bus_LV_247-15_0_6_node_75 | 0.4 | n |  | TRUE
5 | bus_LV_247-15_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_247-15_0_6_node_73 | 0.4 | n |  | TRUE
7 | bus_LV_247-15_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_247-15_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_247-15_0_6_node_72 | 0.4 | n |  | TRUE
10 | bus_LV_247-15_0_6_node_76 | 0.4 | n |  | TRUE
11 | bus_LV_247-15_0_6_node_77 | 0.4 | n |  | TRUE
12 | bus_LV_247-15_0_6_node_71 | 0.4 | n |  | TRUE
13 | bus_LV_247-15_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_247-15_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_247-15_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_247-15_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_247-15_0_6_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_247-15_0_6_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_247-15_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_247-15_0_6_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_247-15_0_6_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_247-15_0_6_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_247-15_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_247-15_0_6_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_247-15_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_247-15_0_6_node_80 | 0.4 | n |  | TRUE
27 | bus_LV_247-15_0_6_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_247-15_0_6_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_247-15_0_6_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_247-15_0_6_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_247-15_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_247-15_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_247-15_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_247-15_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_247-15_0_6_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_247-15_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_247-15_0_6_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_247-15_0_6_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_247-15_0_6_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_247-15_0_6_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_247-15_0_6_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_247-15_0_6_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_247-15_0_6_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_247-15_0_6_node_59 | 0.4 | n |  | TRUE
45 | bus_LV_247-15_0_6_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_247-15_0_6_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_247-15_0_6_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_247-15_0_6_node_66 | 0.4 | n |  | TRUE
49 | bus_LV_247-15_0_6_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_247-15_0_6_node_67 | 0.4 | n |  | TRUE
51 | bus_LV_247-15_0_6_node_65 | 0.4 | n |  | TRUE
52 | bus_LV_247-15_0_6_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_247-15_0_6_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_247-15_0_6_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_247-15_0_6_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_247-15_0_6_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_247-15_0_6_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_247-15_0_6_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_247-15_0_6_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_247-15_0_6_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_247-15_0_6_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_247-15_0_6_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_247-15_0_6_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_247-15_0_6_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_247-15_0_6_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_247-15_0_6_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_247-15_0_6_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_247-15_0_6_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_247-15_0_6_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_247-15_0_6_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_247-15_0_6_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_247-15_0_6_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_247-15_0_6_node_81 | 0.4 | n |  | TRUE
74 | bus_MV_517_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_247-15_0_6_load_0 | 0 | 0.043417 | 0.010881 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_247-15_0_6_load_1 | 2 | 0.015883 | 0.0039808 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_247-15_0_6_load_74 | 3 | 0.00060952 | 0.00015276 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_247-15_0_6_load_75 | 4 | 0.00058993 | 0.00014785 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_247-15_0_6_load_5 | 5 | 0.01187 | 0.0029749 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_247-15_0_6_load_73 | 6 | 0.00093725 | 0.0002349 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_247-15_0_6_load_72 | 9 | 0.00095469 | 0.00023927 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_247-15_0_6_load_76 | 10 | 0.00090544 | 0.00022693 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_247-15_0_6_load_77 | 11 | 0.0090114 | 0.0022585 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_247-15_0_6_load_71 | 12 | 0.003816 | 0.00095639 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_247-15_0_6_load_8 | 13 | 0.0071412 | 0.0017897 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_247-15_0_6_load_11 | 15 | 0.0066613 | 0.0016695 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_247-15_0_6_load_37 | 18 | 0.012144 | 0.0030435 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_247-15_0_6_load_29 | 20 | 0.0019601 | 0.00049126 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_247-15_0_6_load_20 | 21 | 0.0043611 | 0.001093 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_247-15_0_6_load_80 | 26 | 0.025444 | 0.0063769 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_247-15_0_6_load_28 | 27 | 0.0015302 | 0.0003835 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_247-15_0_6_load_27 | 28 | 0.013565 | 0.0033996 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_247-15_0_6_load_38 | 29 | 0.023716 | 0.0059438 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_247-15_0_6_load_21 | 31 | 0.00085007 | 0.00021305 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_247-15_0_6_load_22 | 32 | 0.0019601 | 0.00049126 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_247-15_0_6_load_24 | 34 | 0.0019591 | 0.00049099 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_247-15_0_6_load_25 | 35 | 0.0041765 | 0.0010467 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_247-15_0_6_load_26 | 36 | 0.014843 | 0.0037199 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_247-15_0_6_load_30 | 37 | 0.0020486 | 0.00051342 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_247-15_0_6_load_31 | 39 | 0.0084369 | 0.0021145 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_247-15_0_6_load_34 | 40 | 0.022385 | 0.0056103 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_247-15_0_6_load_46 | 43 | 0.0047816 | 0.0011984 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_247-15_0_6_load_59 | 44 | 0.0047805 | 0.0011981 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_247-15_0_6_load_57 | 46 | 0.014437 | 0.0036182 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_247-15_0_6_load_66 | 48 | 0.014043 | 0.0035195 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_247-15_0_6_load_44 | 49 | 0.011549 | 0.0028944 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_247-15_0_6_load_65 | 51 | 0.012226 | 0.0030641 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_247-15_0_6_load_39 | 52 | 0.036378 | 0.0091172 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_247-15_0_6_load_45 | 56 | 0.01155 | 0.0028947 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_247-15_0_6_load_50 | 57 | 0.039767 | 0.0099664 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_247-15_0_6_load_54 | 59 | 0.015769 | 0.003952 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_247-15_0_6_load_58 | 61 | 0.0047803 | 0.0011981 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_247-15_0_6_load_56 | 62 | 0.015427 | 0.0038663 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_247-15_0_6_load_64 | 65 | 0.014973 | 0.0037527 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_247-15_0_6_load_60 | 68 | 0.013885 | 0.0034799 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_247-15_0_6_load_70 | 70 | 0.023462 | 0.0058801 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_247-15_0_6_load_81 | 73 | 0.010395 | 0.0026052 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_247-15_0_6_line_0 |  | 0 | 1 | 0.030629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_247-15_0_6_line_1 |  | 1 | 3 | 0.034983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_247-15_0_6_line_2 |  | 2 | 3 | 0.024528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_247-15_0_6_line_3 |  | 3 | 4 | 0.037818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_247-15_0_6_line_4 |  | 4 | 10 | 0.037863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_247-15_0_6_line_5 |  | 5 | 6 | 0.025559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_247-15_0_6_line_6 |  | 6 | 10 | 0.037824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_247-15_0_6_line_7 |  | 6 | 9 | 0.037043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_247-15_0_6_line_8 |  | 7 | 8 | 0.097676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_247-15_0_6_line_9 |  | 7 | 9 | 0.10138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_247-15_0_6_line_10 |  | 8 | 11 | 0.063121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_247-15_0_6_line_11 |  | 9 | 12 | 0.032983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_247-15_0_6_line_12 |  | 12 | 25 | 0.053935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_247-15_0_6_line_13 |  | 13 | 14 | 0.0032567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_247-15_0_6_line_14 |  | 14 | 15 | 0.017616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_247-15_0_6_line_15 |  | 14 | 16 | 0.012193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_247-15_0_6_line_16 |  | 15 | 17 | 0.032049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_247-15_0_6_line_17 |  | 16 | 18 | 0.018792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_247-15_0_6_line_18 |  | 17 | 21 | 0.014658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_247-15_0_6_line_19 |  | 17 | 22 | 0.058133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_247-15_0_6_line_20 |  | 17 | 19 | 0.018767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_247-15_0_6_line_21 |  | 18 | 23 | 0.016926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_247-15_0_6_line_22 |  | 19 | 20 | 0.023336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_247-15_0_6_line_23 |  | 20 | 28 | 0.0097829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_247-15_0_6_line_24 |  | 22 | 27 | 0.056642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_247-15_0_6_line_25 |  | 23 | 24 | 0.058772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_247-15_0_6_line_26 |  | 24 | 26 | 0.057447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_247-15_0_6_line_27 |  | 24 | 25 | 0.025646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_247-15_0_6_line_28 |  | 28 | 34 | 0.0044118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_247-15_0_6_line_29 |  | 29 | 30 | 0.027792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_247-15_0_6_line_30 |  | 30 | 46 | 0.031244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_247-15_0_6_line_31 |  | 31 | 32 | 0.016536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_247-15_0_6_line_32 |  | 31 | 33 | 0.03132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_247-15_0_6_line_33 |  | 32 | 34 | 0.014891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_247-15_0_6_line_34 |  | 33 | 35 | 0.017538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_247-15_0_6_line_35 |  | 33 | 36 | 0.036554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_247-15_0_6_line_36 |  | 35 | 37 | 0.0077253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_247-15_0_6_line_37 |  | 36 | 38 | 0.0043914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_247-15_0_6_line_38 |  | 37 | 39 | 0.046878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_247-15_0_6_line_39 |  | 38 | 40 | 0.030992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_247-15_0_6_line_40 |  | 38 | 41 | 0.034573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_247-15_0_6_line_41 |  | 39 | 42 | 0.014712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_247-15_0_6_line_42 |  | 40 | 45 | 0.022642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_247-15_0_6_line_43 |  | 41 | 47 | 0.029181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_247-15_0_6_line_44 |  | 41 | 48 | 0.019943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_247-15_0_6_line_45 |  | 42 | 43 | 0.023428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_247-15_0_6_line_46 |  | 43 | 44 | 0.026677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_247-15_0_6_line_47 |  | 44 | 61 | 0.022885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_247-15_0_6_line_48 |  | 45 | 49 | 0.014335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_247-15_0_6_line_49 |  | 46 | 50 | 0.028427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_247-15_0_6_line_50 |  | 47 | 51 | 0.028594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_247-15_0_6_line_51 |  | 48 | 50 | 0.0049526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_247-15_0_6_line_52 |  | 51 | 65 | 0.029741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_247-15_0_6_line_53 |  | 52 | 53 | 0.045503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_247-15_0_6_line_54 |  | 52 | 54 | 0.032635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_247-15_0_6_line_55 |  | 53 | 55 | 0.034806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_247-15_0_6_line_56 |  | 54 | 56 | 0.013651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_247-15_0_6_line_57 |  | 55 | 57 | 0.0075659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_247-15_0_6_line_58 |  | 56 | 58 | 0.019974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_247-15_0_6_line_59 |  | 57 | 60 | 0.034749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_247-15_0_6_line_60 |  | 58 | 62 | 0.0081296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_247-15_0_6_line_61 |  | 58 | 59 | 0.023138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_247-15_0_6_line_62 |  | 60 | 67 | 0.046487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_247-15_0_6_line_63 |  | 62 | 63 | 0.019154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_247-15_0_6_line_64 |  | 63 | 64 | 0.026887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_247-15_0_6_line_65 |  | 64 | 65 | 0.0058544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_247-15_0_6_line_66 |  | 64 | 66 | 0.011507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_247-15_0_6_line_67 |  | 66 | 69 | 0.029084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_247-15_0_6_line_68 |  | 67 | 68 | 0.026709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_247-15_0_6_line_69 |  | 69 | 70 | 0.029216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_247-15_0_6_line_70 |  | 70 | 71 | 0.03721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_247-15_0_6_line_71 |  | 71 | 72 | 0.022874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_247-15_0_6_line_72 |  | 72 | 73 | 0.043881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_247-15_0_6_trafo_64 | 0.63 MVA 20/0.4 kV | 74 | 65 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2675896.8316 | 1250659.7656 | 2675872.4753 | 1250641.1933
1 | 2675896.8316 | 1250659.7656 | 2675911.0908 | 1250659.8594 | 2675931.8145 | 1250659.9397
2 | 2675931.8145 | 1250659.9397 | 2675948.7567 | 1250642.2025
3 | 2675931.8145 | 1250659.9397 | 2675965.7898 | 1250660.0714 | 2675969.6324 | 1250660.0647
4 | 2675969.6324 | 1250660.0647 | 2676007.4957 | 1250659.9985
5 | 2676045.3201 | 1250659.9492 | 2676032.0329 | 1250638.1156
6 | 2676045.3201 | 1250659.9492 | 2676033.674 | 1250659.9527 | 2676007.4957 | 1250659.9985
7 | 2676082.3616 | 1250659.879 | 2676081.0381 | 1250659.9382 | 2676045.3201 | 1250659.9492
8 | 2676069.2136 | 1250479.6439 | 2676063.6508 | 1250557.1624 | 2676083.5638 | 1250558.5078
9 | 2676082.3616 | 1250659.879 | 2676083.5638 | 1250558.5078
10 | 2676069.2136 | 1250479.6439 | 2676051.1612 | 1250477.4218 | 2676031.2874 | 1250478.879 | 2676006.3552 | 1250480.7883
11 | 2676115.312 | 1250658.4037 | 2676082.3616 | 1250659.879
12 | 2676168.5746 | 1250660.2737 | 2676166.2203 | 1250658.431 | 2676162.7456 | 1250658.0083 | 2676126.1933 | 1250657.9165 | 2676115.312 | 1250658.4037
13 | 2676189.1323 | 1250778.7466 | 2676189.3091 | 1250775.4947
14 | 2676189.1323 | 1250778.7466 | 2676188.266 | 1250796.3413
15 | 2676176.9457 | 1250778.3452 | 2676183.1333 | 1250778.5471 | 2676189.1323 | 1250778.7466
16 | 2676186.69 | 1250828.3514 | 2676188.266 | 1250796.3413
17 | 2676176.9457 | 1250778.3452 | 2676177.8576 | 1250759.5757
18 | 2676186.69 | 1250828.3514 | 2676201.325 | 1250829.1771
19 | 2676179.9002 | 1250880.8469 | 2676180.1359 | 1250850.1942 | 2676185.6071 | 1250850.3313 | 2676186.69 | 1250828.3514
20 | 2676167.941 | 1250827.5543 | 2676180.3006 | 1250827.9912 | 2676186.69 | 1250828.3514
21 | 2676176.5717 | 1250742.859 | 2676177.8409 | 1250747.4786 | 2676178.2803 | 1250750.8757 | 2676177.8576 | 1250759.5757
22 | 2676167.941 | 1250827.5543 | 2676144.6069 | 1250827.2309
23 | 2676134.825 | 1250827.0954 | 2676144.6069 | 1250827.2309
24 | 2676179.9002 | 1250880.8469 | 2676126.4351 | 1250879.3478 | 2676124.0832 | 1250881.4518
25 | 2676173.2089 | 1250684.4175 | 2676174.4589 | 1250734.5591 | 2676174.7684 | 1250737.4985 | 2676176.5717 | 1250742.859
26 | 2676123.2612 | 1250703.3898 | 2676153.4526 | 1250702.6214 | 2676160.7444 | 1250699.157 | 2676173.2089 | 1250684.4175
27 | 2676168.5746 | 1250660.2737 | 2676169.9124 | 1250661.325 | 2676172.1112 | 1250664.7002 | 2676173.3044 | 1250668.1847 | 2676173.2089 | 1250684.4175
28 | 2676134.825 | 1250827.0954 | 2676130.4136 | 1250827.0343
29 | 2676101.0323 | 1250750.7166 | 2676119.5729 | 1250745.4286 | 2676128.0527 | 1250744.687
30 | 2676101.0323 | 1250750.7166 | 2676100.3789 | 1250734.5854 | 2676085.2791 | 1250734.5303
31 | 2676099.0097 | 1250827.5432 | 2676112.5184 | 1250826.7863 | 2676115.5244 | 1250826.8279
32 | 2676067.8615 | 1250830.6603 | 2676087.9815 | 1250828.1612 | 2676099.0097 | 1250827.5432
33 | 2676115.5244 | 1250826.8279 | 2676130.4136 | 1250827.0343
34 | 2676067.8615 | 1250830.6603 | 2676050.5124 | 1250833.2295
35 | 2676067.8615 | 1250830.6603 | 2676064.2783 | 1250794.2826
36 | 2676050.5124 | 1250833.2295 | 2676042.8704 | 1250834.3612
37 | 2676063.8478 | 1250789.9124 | 2676064.2783 | 1250794.2826
38 | 2676042.8704 | 1250834.3612 | 2676022.466 | 1250837.3828 | 2675996.292 | 1250839.3914
39 | 2676063.8478 | 1250789.9124 | 2676032.8564 | 1250789.7909
40 | 2676063.8478 | 1250789.9124 | 2676061.7024 | 1250765.9229 | 2676062.2683 | 1250761.2379 | 2676056.8274 | 1250759.3222
41 | 2675981.6235 | 1250840.517 | 2675996.292 | 1250839.3914
42 | 2676010.2144 | 1250789.7021 | 2676032.8564 | 1250789.7909
43 | 2676056.8274 | 1250759.3222 | 2676054.5326 | 1250759.315 | 2676027.5591 | 1250759.3579
44 | 2676056.8274 | 1250759.3222 | 2676056.8476 | 1250739.3793
45 | 2675981.6235 | 1250840.517 | 2675958.1978 | 1250840.8555
46 | 2675958.1978 | 1250840.8555 | 2675931.5235 | 1250841.241
47 | 2675908.6414 | 1250841.5716 | 2675908.6414 | 1250841.5716 | 2675931.5235 | 1250841.241
48 | 2676010.2144 | 1250789.7021 | 2675995.8795 | 1250789.6404
49 | 2676056.8526 | 1250734.4266 | 2676085.2791 | 1250734.5303
50 | 2676027.5591 | 1250759.3579 | 2676027.3161 | 1250731.8236 | 2676026.2574 | 1250731.8392
51 | 2676056.8526 | 1250734.4266 | 2676056.8476 | 1250739.3793
52 | 2675996.5194 | 1250732.2787 | 2676026.2574 | 1250731.8392
53 | 2675884.9218 | 1250793.2994 | 2675930.4245 | 1250793.1056
54 | 2675963.0588 | 1250792.9666 | 2675930.4245 | 1250793.1056
55 | 2675884.9218 | 1250793.2994 | 2675893.6274 | 1250759.5974
56 | 2675963.0588 | 1250792.9666 | 2675963.05 | 1250779.3154
57 | 2675893.6274 | 1250759.5974 | 2675895.5584 | 1250752.282
58 | 2675963.0371 | 1250759.3418 | 2675963.05 | 1250779.3154
59 | 2675899.071 | 1250718.3036 | 2675900.7444 | 1250732.6355 | 2675895.5584 | 1250752.282
60 | 2675963.0371 | 1250759.3418 | 2675971.1666 | 1250759.3136
61 | 2675963.0371 | 1250759.3418 | 2675939.8991 | 1250759.427
62 | 2675899.071 | 1250718.3036 | 2675902.1795 | 1250716.6756 | 2675901.0386 | 1250703.1956 | 2675930.4882 | 1250703.1727
63 | 2675990.3208 | 1250759.247 | 2675971.1666 | 1250759.3136
64 | 2675990.6656 | 1250732.3652 | 2675990.3208 | 1250759.247
65 | 2675990.6656 | 1250732.3652 | 2675996.5194 | 1250732.2787
66 | 2675990.6656 | 1250732.3652 | 2675979.1249 | 1250732.2171
67 | 2675979.1249 | 1250732.2171 | 2675978.8864 | 1250703.1373
68 | 2675930.4882 | 1250703.1727 | 2675930.536 | 1250729.8818
69 | 2675978.8864 | 1250703.1373 | 2676008.1023 | 1250703.1161
70 | 2676045.3122 | 1250703.089 | 2676008.1023 | 1250703.1161
71 | 2676045.3122 | 1250703.089 | 2676057.0362 | 1250703.0839 | 2676068.1865 | 1250703.0714
72 | 2676112.1985 | 1250703.0475 | 2676068.1865 | 1250703.0714

## bus_geodata
| x | y | coords
0 | 2675872.4753 | 1250641.1933
1 | 2675896.8316 | 1250659.7656
2 | 2675948.7567 | 1250642.2025
3 | 2675931.8145 | 1250659.9397
4 | 2675969.6324 | 1250660.0647
5 | 2676032.0329 | 1250638.1156
6 | 2676045.3201 | 1250659.9492
7 | 2676083.5638 | 1250558.5078
8 | 2676069.2136 | 1250479.6439
9 | 2676082.3616 | 1250659.879
10 | 2676007.4957 | 1250659.9985
11 | 2676006.3552 | 1250480.7883
12 | 2676115.312 | 1250658.4037
13 | 2676189.3091 | 1250775.4947
14 | 2676189.1323 | 1250778.7466
15 | 2676188.266 | 1250796.3413
16 | 2676176.9457 | 1250778.3452
17 | 2676186.69 | 1250828.3514
18 | 2676177.8576 | 1250759.5757
19 | 2676167.941 | 1250827.5543
20 | 2676144.6069 | 1250827.2309
21 | 2676201.325 | 1250829.1771
22 | 2676179.9002 | 1250880.8469
23 | 2676176.5717 | 1250742.859
24 | 2676173.2089 | 1250684.4175
25 | 2676168.5746 | 1250660.2737
26 | 2676123.2612 | 1250703.3898
27 | 2676124.0832 | 1250881.4518
28 | 2676134.825 | 1250827.0954
29 | 2676128.0527 | 1250744.687
30 | 2676101.0323 | 1250750.7166
31 | 2676099.0097 | 1250827.5432
32 | 2676115.5244 | 1250826.8279
33 | 2676067.8615 | 1250830.6603
34 | 2676130.4136 | 1250827.0343
35 | 2676050.5124 | 1250833.2295
36 | 2676064.2783 | 1250794.2826
37 | 2676042.8704 | 1250834.3612
38 | 2676063.8478 | 1250789.9124
39 | 2675996.292 | 1250839.3914
40 | 2676032.8564 | 1250789.7909
41 | 2676056.8274 | 1250759.3222
42 | 2675981.6235 | 1250840.517
43 | 2675958.1978 | 1250840.8555
44 | 2675931.5235 | 1250841.241
45 | 2676010.2144 | 1250789.7021
46 | 2676085.2791 | 1250734.5303
47 | 2676027.5591 | 1250759.3579
48 | 2676056.8476 | 1250739.3793
49 | 2675995.8795 | 1250789.6404
50 | 2676056.8526 | 1250734.4266
51 | 2676026.2574 | 1250731.8392
52 | 2675930.4245 | 1250793.1056
53 | 2675884.9218 | 1250793.2994
54 | 2675963.0588 | 1250792.9666
55 | 2675893.6274 | 1250759.5974
56 | 2675963.05 | 1250779.3154
57 | 2675895.5584 | 1250752.282
58 | 2675963.0371 | 1250759.3418
59 | 2675939.8991 | 1250759.427
60 | 2675899.071 | 1250718.3036
61 | 2675908.6414 | 1250841.5716
62 | 2675971.1666 | 1250759.3136
63 | 2675990.3208 | 1250759.247
64 | 2675990.6656 | 1250732.3652
65 | 2675996.5194 | 1250732.2787
66 | 2675979.1249 | 1250732.2171
67 | 2675930.4882 | 1250703.1727
68 | 2675930.536 | 1250729.8818
69 | 2675978.8864 | 1250703.1373
70 | 2676008.1023 | 1250703.1161
71 | 2676045.3122 | 1250703.089
72 | 2676068.1865 | 1250703.0714
73 | 2676112.1985 | 1250703.0475
74 | 2675990.6656 | 1250732.3652

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97042 | -0.57195 | 0.043417 | 0.010881
1 | 0.97166 | -0.54737 | 0 | 0
2 | 0.97272 | -0.52654 | 0.015883 | 0.0039808
3 | 0.97308 | -0.51937 | 0.00060952 | 0.00015276
4 | 0.9752 | -0.47775 | 0.00058993 | 0.00014785
5 | 0.97814 | -0.42021 | 0.01187 | 0.0029749
6 | 0.97842 | -0.41469 | 0.00093725 | 0.0002349
7 | 0.97822 | -0.41882 | 0 | 0
8 | 0.9774 | -0.43487 | 0 | 0
9 | 0.97906 | -0.40218 | 0.00095469 | 0.00023927
10 | 0.97734 | -0.43586 | 0.00090544 | 0.00022693
11 | 0.97687 | -0.44526 | 0.0090114 | 0.0022585
12 | 0.97971 | -0.38957 | 0.003816 | 0.00095639
13 | 0.98423 | -0.30192 | 0.0071412 | 0.0017897
14 | 0.98425 | -0.3015 | 0 | 0
15 | 0.98479 | -0.29099 | 0.0066613 | 0.0016695
16 | 0.98389 | -0.3084 | 0 | 0
17 | 0.98583 | -0.27093 | 0 | 0
18 | 0.98334 | -0.31903 | 0.012144 | 0.0030435
19 | 0.98646 | -0.25871 | 0 | 0
20 | 0.98725 | -0.24353 | 0.0019601 | 0.00049126
21 | 0.98577 | -0.27208 | 0.0043611 | 0.001093
22 | 0.98575 | -0.27253 | 0 | 0
23 | 0.9829 | -0.32769 | 0 | 0
24 | 0.98134 | -0.35782 | 0 | 0
25 | 0.98082 | -0.36804 | 0 | 0
26 | 0.97999 | -0.38431 | 0.025444 | 0.0063769
27 | 0.98567 | -0.27409 | 0.0015302 | 0.0003835
28 | 0.98758 | -0.23709 | 0.013565 | 0.0033996
29 | 0.99055 | -0.18079 | 0.023716 | 0.0059438
30 | 0.99115 | -0.16908 | 0 | 0
31 | 0.98894 | -0.21095 | 0.00085007 | 0.00021305
32 | 0.98831 | -0.2231 | 0.0019601 | 0.00049126
33 | 0.99015 | -0.18787 | 0 | 0
34 | 0.98775 | -0.23392 | 0.0019591 | 0.00049099
35 | 0.98968 | -0.19692 | 0.0041765 | 0.0010467
36 | 0.99179 | -0.15629 | 0.014843 | 0.0037199
37 | 0.9895 | -0.20033 | 0.0020486 | 0.00051342
38 | 0.99201 | -0.15222 | 0 | 0
39 | 0.98852 | -0.21936 | 0.0084369 | 0.0021145
40 | 0.99104 | -0.17086 | 0.022385 | 0.0056103
41 | 0.99395 | -0.11502 | 0 | 0
42 | 0.98833 | -0.22313 | 0 | 0
43 | 0.98802 | -0.22912 | 0.0047816 | 0.0011984
44 | 0.98779 | -0.23368 | 0.0047805 | 0.0011981
45 | 0.9908 | -0.17551 | 0 | 0
46 | 0.99183 | -0.15595 | 0.014437 | 0.0036182
47 | 0.99594 | -0.077049 | 0 | 0
48 | 0.993 | -0.13341 | 0.014043 | 0.0035195
49 | 0.99065 | -0.17845 | 0.011549 | 0.0028944
50 | 0.99282 | -0.13675 | 0 | 0
51 | 0.99789 | -0.039984 | 0.012226 | 0.0030641
52 | 0.98735 | -0.24276 | 0.036378 | 0.0091172
53 | 0.98509 | -0.28651 | 0 | 0
54 | 0.99005 | -0.19037 | 0 | 0
55 | 0.98337 | -0.32011 | 0 | 0
56 | 0.99119 | -0.16854 | 0.01155 | 0.0028947
57 | 0.983 | -0.32743 | 0.039767 | 0.0099664
58 | 0.99305 | -0.13261 | 0 | 0
59 | 0.99272 | -0.13906 | 0.015769 | 0.003952
60 | 0.98255 | -0.33614 | 0 | 0
61 | 0.98769 | -0.23563 | 0.0047803 | 0.0011981
62 | 0.99393 | -0.11576 | 0.015427 | 0.0038663
63 | 0.99627 | -0.070994 | 0 | 0
64 | 0.99955 | -0.0085062 | 0 | 0
65 | 1 | 0 | -0.48225 | -0.12281
66 | 0.9992 | -0.015306 | 0 | 0
67 | 0.98196 | -0.3478 | 0 | 0
68 | 0.98161 | -0.35451 | 0.013885 | 0.0034799
69 | 0.9983 | -0.032514 | 0 | 0
70 | 0.9974 | -0.049831 | 0.023462 | 0.0058801
71 | 0.99705 | -0.056612 | 0 | 0
72 | 0.99684 | -0.060783 | 0 | 0
73 | 0.99642 | -0.068787 | 0.010395 | 0.0026052
74 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.043417 | -0.010881 | 0.043468 | 0.010913 | 5.0907e-05 | 3.2201e-05 | 0.066574 | 0.066574 | 0.066574 | 0.97042 | -0.57195 | 0.97166 | -0.54737 | 18.2895
1 | -0.043468 | -0.010913 | 0.043526 | 0.01095 | 5.8143e-05 | 3.6777e-05 | 0.066574 | 0.066573 | 0.066574 | 0.97166 | -0.54737 | 0.97308 | -0.51937 | 18.2895
2 | -0.015883 | -0.0039808 | 0.015889 | 0.0039839 | 5.4303e-06 | 3.1708e-06 | 0.024298 | 0.024298 | 0.024298 | 0.97272 | -0.52654 | 0.97308 | -0.51937 | 6.6752
3 | -0.060024 | -0.015087 | 0.060144 | 0.015163 | 0.00011952 | 7.6023e-05 | 0.091803 | 0.091803 | 0.091803 | 0.97308 | -0.51937 | 0.9752 | -0.47775 | 25.2206
4 | -0.060734 | -0.015311 | 0.060856 | 0.015388 | 0.00012202 | 7.762e-05 | 0.092703 | 0.092703 | 0.092703 | 0.9752 | -0.47775 | 0.97734 | -0.43586 | 25.4679
5 | -0.01187 | -0.0029749 | 0.011873 | 0.0029765 | 3.1251e-06 | 1.6792e-06 | 0.018057 | 0.018057 | 0.018057 | 0.97814 | -0.42021 | 0.97842 | -0.41469 | 4.9608
6 | 0.061824 | 0.015655 | -0.061761 | -0.015615 | 6.2774e-05 | 3.9226e-05 | 0.094081 | 0.094081 | 0.094081 | 0.97842 | -0.41469 | 0.97734 | -0.43586 | 12.9233
7 | -0.074634 | -0.018866 | 0.074679 | 0.018893 | 4.4787e-05 | 2.6801e-05 | 0.11356 | 0.11356 | 0.11356 | 0.97842 | -0.41469 | 0.97906 | -0.40218 | 7.7997
8 | 0.0090228 | 0.0022637 | -0.0090159 | -0.0022605 | 6.901e-06 | 3.1915e-06 | 0.013726 | 0.013726 | 0.013726 | 0.97822 | -0.41882 | 0.9774 | -0.43487 | 3.771
9 | -0.0090228 | -0.0022637 | 0.0090299 | 0.002267 | 7.1621e-06 | 3.3099e-06 | 0.013726 | 0.013725 | 0.013726 | 0.97822 | -0.41882 | 0.97906 | -0.40218 | 3.7708
10 | 0.0090159 | 0.0022605 | -0.0090114 | -0.0022585 | 4.4599e-06 | 2.0636e-06 | 0.013726 | 0.013727 | 0.013727 | 0.9774 | -0.43487 | 0.97687 | -0.44526 | 3.771
11 | -0.084663 | -0.021399 | 0.084715 | 0.02143 | 5.1249e-05 | 3.1139e-05 | 0.12874 | 0.12874 | 0.12874 | 0.97906 | -0.40218 | 0.97971 | -0.38957 | 8.842
12 | -0.088531 | -0.022387 | 0.088622 | 0.022442 | 9.1517e-05 | 5.5851e-05 | 0.13453 | 0.13453 | 0.13453 | 0.97971 | -0.38957 | 0.98082 | -0.36804 | 9.24
13 | -0.0071412 | -0.0017897 | 0.0071413 | 0.0017898 | 1.4235e-07 | 4.9718e-08 | 0.010796 | 0.010796 | 0.010796 | 0.98423 | -0.30192 | 0.98425 | -0.3015 | 2.9661
14 | -0.13375 | -0.033898 | 0.13381 | 0.03394 | 6.7613e-05 | 4.2377e-05 | 0.20234 | 0.20234 | 0.20234 | 0.98425 | -0.3015 | 0.98479 | -0.29099 | 13.8968
15 | 0.12661 | 0.032108 | -0.12656 | -0.032082 | 4.1939e-05 | 2.6221e-05 | 0.19154 | 0.19154 | 0.19154 | 0.98425 | -0.3015 | 0.98389 | -0.3084 | 13.1553
16 | -0.14048 | -0.03561 | 0.14061 | 0.035695 | 0.00013555 | 8.512e-05 | 0.2124 | 0.2124 | 0.2124 | 0.98479 | -0.29099 | 0.98583 | -0.27093 | 14.5881
17 | 0.12656 | 0.032082 | -0.1265 | -0.032042 | 6.4634e-05 | 4.0412e-05 | 0.19154 | 0.19154 | 0.19154 | 0.98389 | -0.3084 | 0.98334 | -0.31903 | 13.1553
18 | 0.0043613 | 0.001093 | -0.0043611 | -0.001093 | 2.3821e-07 | -3.4428e-08 | 0.006583 | 0.006583 | 0.006583 | 0.98583 | -0.27093 | 0.98577 | -0.27208 | 1.8085
19 | 0.0015304 | 0.00038219 | -0.0015303 | -0.00038285 | 1.1629e-07 | -6.6671e-07 | 0.0023096 | 0.0023098 | 0.0023098 | 0.98583 | -0.27093 | 0.98575 | -0.27253 | 0.63456
20 | -0.1465 | -0.03717 | 0.14659 | 0.037224 | 8.616e-05 | 5.4184e-05 | 0.22129 | 0.22129 | 0.22129 | 0.98583 | -0.27093 | 0.98646 | -0.25871 | 15.1988
21 | 0.11435 | 0.028998 | -0.11431 | -0.028969 | 4.7584e-05 | 2.9595e-05 | 0.17317 | 0.17317 | 0.17317 | 0.98334 | -0.31903 | 0.9829 | -0.32769 | 11.8933
22 | -0.14659 | -0.037224 | 0.1467 | 0.037292 | 0.00010714 | 6.7375e-05 | 0.22129 | 0.22129 | 0.22129 | 0.98646 | -0.25871 | 0.98725 | -0.24353 | 15.1988
23 | -0.14866 | -0.037783 | 0.1487 | 0.037812 | 4.612e-05 | 2.9017e-05 | 0.22425 | 0.22425 | 0.22425 | 0.98725 | -0.24353 | 0.98758 | -0.23709 | 15.4016
24 | 0.0015303 | 0.00038285 | -0.0015302 | -0.0003835 | 1.1334e-07 | -6.4947e-07 | 0.0023098 | 0.0023101 | 0.0023101 | 0.98575 | -0.27253 | 0.98567 | -0.27409 | 0.63463
25 | 0.11431 | 0.028969 | -0.11414 | -0.028866 | 0.00016522 | 0.00010277 | 0.17317 | 0.17317 | 0.17317 | 0.9829 | -0.32769 | 0.98134 | -0.35782 | 11.8933
26 | 0.025476 | 0.0063968 | -0.025444 | -0.0063769 | 3.2155e-05 | 1.9854e-05 | 0.038634 | 0.038635 | 0.038635 | 0.98134 | -0.35782 | 0.97999 | -0.38431 | 10.6139
27 | 0.088666 | 0.022469 | -0.088622 | -0.022442 | 4.3516e-05 | 2.6555e-05 | 0.13453 | 0.13453 | 0.13453 | 0.98134 | -0.35782 | 0.98082 | -0.36804 | 9.2399
28 | -0.16227 | -0.041212 | 0.16229 | 0.041227 | 2.4763e-05 | 1.5623e-05 | 0.24469 | 0.24469 | 0.24469 | 0.98758 | -0.23709 | 0.98775 | -0.23392 | 16.8053
29 | -0.023716 | -0.0059438 | 0.023729 | 0.0059519 | 1.3228e-05 | 8.1079e-06 | 0.035626 | 0.035626 | 0.035626 | 0.99055 | -0.18079 | 0.99115 | -0.16908 | 9.7874
30 | -0.023729 | -0.0059519 | 0.023744 | 0.005961 | 1.4871e-05 | 9.1144e-06 | 0.035626 | 0.035626 | 0.035626 | 0.99115 | -0.16908 | 0.99183 | -0.15595 | 9.7874
31 | 0.16639 | 0.042325 | -0.1663 | -0.042264 | 9.7348e-05 | 6.1454e-05 | 0.25059 | 0.25059 | 0.25059 | 0.98894 | -0.21095 | 0.98831 | -0.2231 | 17.2107
32 | -0.16724 | -0.042538 | 0.16743 | 0.042656 | 0.00018627 | 0.0001176 | 0.25187 | 0.25187 | 0.25187 | 0.98894 | -0.21095 | 0.99015 | -0.18787 | 17.2985
33 | 0.16434 | 0.041772 | -0.16425 | -0.041718 | 8.5608e-05 | 5.4026e-05 | 0.24764 | 0.24764 | 0.24764 | 0.98831 | -0.2231 | 0.98775 | -0.23392 | 17.008
34 | 0.029051 | 0.0072969 | -0.029038 | -0.0072891 | 1.2539e-05 | 7.7996e-06 | 0.043664 | 0.043664 | 0.043664 | 0.99015 | -0.18787 | 0.98968 | -0.19692 | 11.9956
35 | -0.19648 | -0.049952 | 0.19678 | 0.050142 | 0.0002993 | 0.00018967 | 0.29553 | 0.29553 | 0.29553 | 0.99015 | -0.18787 | 0.99179 | -0.15629 | 20.2974
36 | 0.024862 | 0.0062423 | -0.024858 | -0.0062398 | 4.0488e-06 | 2.492e-06 | 0.037385 | 0.037385 | 0.037385 | 0.98968 | -0.19692 | 0.9895 | -0.20033 | 10.2705
37 | -0.21162 | -0.053862 | 0.21166 | 0.053888 | 4.1579e-05 | 2.6384e-05 | 0.3178 | 0.3178 | 0.3178 | 0.99179 | -0.15629 | 0.99201 | -0.15222 | 21.8268
38 | 0.022809 | 0.0057264 | -0.022788 | -0.0057138 | 2.0687e-05 | 1.2638e-05 | 0.034304 | 0.034304 | 0.034304 | 0.9895 | -0.20033 | 0.98852 | -0.21936 | 9.4242
39 | 0.033969 | 0.0085259 | -0.033939 | -0.0085069 | 3.0179e-05 | 1.8915e-05 | 0.050958 | 0.050958 | 0.050958 | 0.99201 | -0.15222 | 0.99104 | -0.17086 | 13.9994
40 | -0.24563 | -0.062414 | 0.24607 | 0.062695 | 0.00044074 | 0.00028028 | 0.36876 | 0.36875 | 0.36876 | 0.99201 | -0.15222 | 0.99395 | -0.11502 | 25.3266
41 | 0.014352 | 0.0035993 | -0.014349 | -0.0035978 | 2.575e-06 | 1.4594e-06 | 0.021604 | 0.021604 | 0.021604 | 0.98852 | -0.21936 | 0.98833 | -0.22313 | 5.9352
42 | 0.011553 | 0.0028966 | -0.011551 | -0.0028953 | 2.5551e-06 | 1.3436e-06 | 0.017347 | 0.017347 | 0.017347 | 0.99104 | -0.17086 | 0.9908 | -0.17551 | 4.7657
43 | -0.29838 | -0.075848 | 0.29893 | 0.076197 | 0.00054682 | 0.00034845 | 0.44708 | 0.44708 | 0.44708 | 0.99395 | -0.11502 | 0.99594 | -0.077049 | 30.7062
44 | 0.052311 | 0.013154 | -0.052265 | -0.013125 | 4.5884e-05 | 2.9107e-05 | 0.078328 | 0.078328 | 0.078328 | 0.99395 | -0.11502 | 0.993 | -0.13341 | 21.5188
45 | 0.014349 | 0.0035978 | -0.014345 | -0.0035955 | 4.1006e-06 | 2.3243e-06 | 0.021604 | 0.021604 | 0.021604 | 0.98833 | -0.22313 | 0.98802 | -0.22912 | 5.9353
46 | 0.0095633 | 0.0023971 | -0.0095613 | -0.0023962 | 2.0753e-06 | 9.8663e-07 | 0.014403 | 0.014403 | 0.014403 | 0.98802 | -0.22912 | 0.98779 | -0.23368 | 3.9569
47 | 0.0047808 | 0.0011981 | -0.0047803 | -0.0011981 | 4.451e-07 | -8.0442e-09 | 0.0072018 | 0.0072019 | 0.0072019 | 0.98779 | -0.23368 | 0.98769 | -0.23563 | 1.9785
48 | 0.011551 | 0.0028953 | -0.011549 | -0.0028944 | 1.6177e-06 | 8.5071e-07 | 0.017347 | 0.017347 | 0.017347 | 0.9908 | -0.17551 | 0.99065 | -0.17845 | 4.7657
49 | -0.038181 | -0.0095792 | 0.038216 | 0.0096012 | 3.4981e-05 | 2.2021e-05 | 0.057285 | 0.057285 | 0.057285 | 0.99183 | -0.15595 | 0.99282 | -0.13675 | 15.7376
50 | -0.29893 | -0.076197 | 0.29947 | 0.076538 | 0.00053583 | 0.00034144 | 0.44708 | 0.44708 | 0.44708 | 0.99594 | -0.077049 | 0.99789 | -0.039984 | 30.7062
51 | 0.038222 | 0.009605 | -0.038216 | -0.0096012 | 6.0946e-06 | 3.8365e-06 | 0.057285 | 0.057285 | 0.057285 | 0.993 | -0.13341 | 0.99282 | -0.13675 | 15.7376
52 | -0.31169 | -0.079602 | 0.3123 | 0.079987 | 0.0006037 | 0.00038481 | 0.46531 | 0.46531 | 0.46531 | 0.99789 | -0.039984 | 1 | 0 | 31.9583
53 | 0.053887 | 0.013594 | -0.053774 | -0.013523 | 0.00011263 | 7.1502e-05 | 0.081244 | 0.081244 | 0.081244 | 0.98735 | -0.24276 | 0.98509 | -0.28651 | 22.3198
54 | -0.090265 | -0.022712 | 0.090492 | 0.022856 | 0.00022658 | 0.00014459 | 0.13607 | 0.13607 | 0.13607 | 0.98735 | -0.24276 | 0.99005 | -0.19037 | 37.3815
55 | 0.053774 | 0.013523 | -0.053688 | -0.013468 | 8.6153e-05 | 5.4695e-05 | 0.081244 | 0.081244 | 0.081244 | 0.98509 | -0.28651 | 0.98337 | -0.32011 | 22.3198
56 | -0.090492 | -0.022856 | 0.090586 | 0.022917 | 9.478e-05 | 6.0484e-05 | 0.13607 | 0.13607 | 0.13607 | 0.99005 | -0.19037 | 0.99119 | -0.16854 | 37.3815
57 | 0.053688 | 0.013468 | -0.053669 | -0.013456 | 1.8727e-05 | 1.189e-05 | 0.081244 | 0.081244 | 0.081244 | 0.98337 | -0.32011 | 0.983 | -0.32743 | 22.3198
58 | -0.10214 | -0.025812 | 0.10231 | 0.025924 | 0.00017627 | 0.00011256 | 0.15341 | 0.15341 | 0.15341 | 0.99119 | -0.16854 | 0.99305 | -0.13261 | 42.1451
59 | 0.013903 | 0.00349 | -0.013897 | -0.0034867 | 5.7726e-06 | 3.2541e-06 | 0.021047 | 0.021048 | 0.021048 | 0.983 | -0.32743 | 0.98255 | -0.33614 | 5.7823
60 | -0.11809 | -0.029879 | 0.11818 | 0.02994 | 9.5557e-05 | 6.1051e-05 | 0.17704 | 0.17704 | 0.17704 | 0.99305 | -0.13261 | 0.99393 | -0.11576 | 48.6385
61 | 0.015774 | 0.0039548 | -0.015769 | -0.003952 | 4.8475e-06 | 2.8031e-06 | 0.023636 | 0.023636 | 0.023636 | 0.99305 | -0.13261 | 0.99272 | -0.13906 | 6.4935
62 | 0.013897 | 0.0034867 | -0.013889 | -0.0034824 | 7.7227e-06 | 4.3541e-06 | 0.021048 | 0.021048 | 0.021048 | 0.98255 | -0.33614 | 0.98196 | -0.3478 | 5.7823
63 | -0.13361 | -0.033806 | 0.1339 | 0.03399 | 0.00028771 | 0.00018389 | 0.20014 | 0.20014 | 0.20014 | 0.99393 | -0.11576 | 0.99627 | -0.070994 | 54.9833
64 | -0.1339 | -0.03399 | 0.1343 | 0.034248 | 0.00040387 | 0.00025812 | 0.20014 | 0.20014 | 0.20014 | 0.99627 | -0.070994 | 0.99955 | -0.0085062 | 54.9833
65 | -0.16823 | -0.04278 | 0.1683 | 0.042824 | 6.8972e-05 | 4.3989e-05 | 0.25066 | 0.25066 | 0.25066 | 0.99955 | -0.0085062 | 1 | 0 | 34.4319
66 | 0.033933 | 0.0085319 | -0.033922 | -0.008525 | 1.1016e-05 | 6.8993e-06 | 0.050525 | 0.050526 | 0.050526 | 0.99955 | -0.0085062 | 0.9992 | -0.015306 | 13.8806
67 | 0.033922 | 0.008525 | -0.033894 | -0.0085075 | 2.7842e-05 | 1.7439e-05 | 0.050526 | 0.050526 | 0.050526 | 0.9992 | -0.015306 | 0.9983 | -0.032514 | 13.8807
68 | 0.013889 | 0.0034824 | -0.013885 | -0.0034799 | 4.4371e-06 | 2.502e-06 | 0.021048 | 0.021048 | 0.021048 | 0.98196 | -0.3478 | 0.98161 | -0.35451 | 5.7824
69 | 0.033894 | 0.0085075 | -0.033866 | -0.00849 | 2.7969e-05 | 1.7518e-05 | 0.050526 | 0.050526 | 0.050526 | 0.9983 | -0.032514 | 0.9974 | -0.049831 | 13.8807
70 | 0.010404 | 0.0026099 | -0.010401 | -0.0026082 | 3.3624e-06 | 1.6664e-06 | 0.015523 | 0.015523 | 0.015523 | 0.9974 | -0.049831 | 0.99705 | -0.056612 | 4.2646
71 | 0.010401 | 0.0026082 | -0.010399 | -0.0026072 | 2.067e-06 | 1.0246e-06 | 0.015523 | 0.015523 | 0.015523 | 0.99705 | -0.056612 | 0.99684 | -0.060783 | 4.2646
72 | 0.010399 | 0.0026072 | -0.010395 | -0.0026052 | 3.9653e-06 | 1.966e-06 | 0.015523 | 0.015523 | 0.015523 | 0.99684 | -0.060783 | 0.99642 | -0.068787 | 4.2647

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49722 | 0.12656

## res_load
| p_mw | q_mvar
0 | 0.043417 | 0.010881
1 | 0.015883 | 0.0039808
2 | 0.00060952 | 0.00015276
3 | 0.00058993 | 0.00014785
4 | 0.01187 | 0.0029749
5 | 0.00093725 | 0.0002349
6 | 0.00095469 | 0.00023927
7 | 0.00090544 | 0.00022693
8 | 0.0090114 | 0.0022585
9 | 0.003816 | 0.00095639
10 | 0.0071412 | 0.0017897
11 | 0.0066613 | 0.0016695
12 | 0.012144 | 0.0030435
13 | 0.0019601 | 0.00049126
14 | 0.0043611 | 0.001093
15 | 0.025444 | 0.0063769
16 | 0.0015302 | 0.0003835
17 | 0.013565 | 0.0033996
18 | 0.023716 | 0.0059438
19 | 0.00085007 | 0.00021305
20 | 0.0019601 | 0.00049126
21 | 0.0019591 | 0.00049099
22 | 0.0041765 | 0.0010467
23 | 0.014843 | 0.0037199
24 | 0.0020486 | 0.00051342
25 | 0.0084369 | 0.0021145
26 | 0.022385 | 0.0056103
27 | 0.0047816 | 0.0011984
28 | 0.0047805 | 0.0011981
29 | 0.014437 | 0.0036182
30 | 0.014043 | 0.0035195
31 | 0.011549 | 0.0028944
32 | 0.012226 | 0.0030641
33 | 0.036378 | 0.0091172
34 | 0.01155 | 0.0028947
35 | 0.039767 | 0.0099664
36 | 0.015769 | 0.003952
37 | 0.0047803 | 0.0011981
38 | 0.015427 | 0.0038663
39 | 0.014973 | 0.0037527
40 | 0.013885 | 0.0034799
41 | 0.023462 | 0.0058801
42 | 0.010395 | 0.0026052

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1