## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_247-26_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_247-26_0_8_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_247-26_0_8_node_12 | 0.4 | n |  | TRUE
3 | bus_LV_247-26_0_8_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_247-26_0_8_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_247-26_0_8_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_247-26_0_8_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_247-26_0_8_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_247-26_0_8_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_247-26_0_8_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_247-26_0_8_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_247-26_0_8_node_63 | 0.4 | n |  | TRUE
12 | bus_LV_247-26_0_8_node_126 | 0.4 | n |  | TRUE
13 | bus_LV_247-26_0_8_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_247-26_0_8_node_153 | 0.4 | n |  | TRUE
15 | bus_LV_247-26_0_8_node_91 | 0.4 | n |  | TRUE
16 | bus_LV_247-26_0_8_node_137 | 0.4 | n |  | TRUE
17 | bus_LV_247-26_0_8_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_247-26_0_8_node_89 | 0.4 | n |  | TRUE
19 | bus_LV_247-26_0_8_node_90 | 0.4 | n |  | TRUE
20 | bus_LV_247-26_0_8_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_247-26_0_8_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_247-26_0_8_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_247-26_0_8_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_247-26_0_8_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_247-26_0_8_node_99 | 0.4 | n |  | TRUE
26 | bus_LV_247-26_0_8_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_247-26_0_8_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_247-26_0_8_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_247-26_0_8_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_247-26_0_8_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_247-26_0_8_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_247-26_0_8_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_247-26_0_8_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_247-26_0_8_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_247-26_0_8_node_78 | 0.4 | n |  | TRUE
36 | bus_LV_247-26_0_8_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_247-26_0_8_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_247-26_0_8_node_131 | 0.4 | n |  | TRUE
39 | bus_LV_247-26_0_8_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_247-26_0_8_node_111 | 0.4 | n |  | TRUE
41 | bus_LV_247-26_0_8_node_125 | 0.4 | n |  | TRUE
42 | bus_LV_247-26_0_8_node_155 | 0.4 | n |  | TRUE
43 | bus_LV_247-26_0_8_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_247-26_0_8_node_154 | 0.4 | n |  | TRUE
45 | bus_LV_247-26_0_8_node_138 | 0.4 | n |  | TRUE
46 | bus_LV_247-26_0_8_node_14 | 0.4 | n |  | TRUE
47 | bus_LV_247-26_0_8_node_16 | 0.4 | n |  | TRUE
48 | bus_LV_247-26_0_8_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_247-26_0_8_node_64 | 0.4 | n |  | TRUE
50 | bus_LV_247-26_0_8_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_247-26_0_8_node_100 | 0.4 | n |  | TRUE
52 | bus_LV_247-26_0_8_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_247-26_0_8_node_88 | 0.4 | n |  | TRUE
54 | bus_LV_247-26_0_8_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_247-26_0_8_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_247-26_0_8_node_87 | 0.4 | n |  | TRUE
57 | bus_LV_247-26_0_8_node_98 | 0.4 | n |  | TRUE
58 | bus_LV_247-26_0_8_node_156 | 0.4 | n |  | TRUE
59 | bus_LV_247-26_0_8_node_93 | 0.4 | n |  | TRUE
60 | bus_LV_247-26_0_8_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_247-26_0_8_node_77 | 0.4 | n |  | TRUE
62 | bus_LV_247-26_0_8_node_70 | 0.4 | n |  | TRUE
63 | bus_LV_247-26_0_8_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_247-26_0_8_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_247-26_0_8_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_247-26_0_8_node_94 | 0.4 | n |  | TRUE
67 | bus_LV_247-26_0_8_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_247-26_0_8_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_247-26_0_8_node_82 | 0.4 | n |  | TRUE
70 | bus_LV_247-26_0_8_node_152 | 0.4 | n |  | TRUE
71 | bus_LV_247-26_0_8_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_247-26_0_8_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_247-26_0_8_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_247-26_0_8_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_247-26_0_8_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_247-26_0_8_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_247-26_0_8_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_247-26_0_8_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_247-26_0_8_node_105 | 0.4 | n |  | TRUE
80 | bus_LV_247-26_0_8_node_124 | 0.4 | n |  | TRUE
81 | bus_LV_247-26_0_8_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_247-26_0_8_node_103 | 0.4 | n |  | TRUE
83 | bus_LV_247-26_0_8_node_122 | 0.4 | n |  | TRUE
84 | bus_LV_247-26_0_8_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_247-26_0_8_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_247-26_0_8_node_56 | 0.4 | n |  | TRUE
87 | bus_LV_247-26_0_8_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_247-26_0_8_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_247-26_0_8_node_60 | 0.4 | n |  | TRUE
90 | bus_LV_247-26_0_8_node_110 | 0.4 | n |  | TRUE
91 | bus_LV_247-26_0_8_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_247-26_0_8_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_247-26_0_8_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_247-26_0_8_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_247-26_0_8_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_247-26_0_8_node_71 | 0.4 | n |  | TRUE
97 | bus_LV_247-26_0_8_node_74 | 0.4 | n |  | TRUE
98 | bus_LV_247-26_0_8_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_247-26_0_8_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_247-26_0_8_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_247-26_0_8_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_247-26_0_8_node_136 | 0.4 | n |  | TRUE
103 | bus_LV_247-26_0_8_node_130 | 0.4 | n |  | TRUE
104 | bus_LV_247-26_0_8_node_96 | 0.4 | n |  | TRUE
105 | bus_LV_247-26_0_8_node_148 | 0.4 | n |  | TRUE
106 | bus_LV_247-26_0_8_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_247-26_0_8_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_247-26_0_8_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_247-26_0_8_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_247-26_0_8_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_247-26_0_8_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_247-26_0_8_node_157 | 0.4 | n |  | TRUE
113 | bus_LV_247-26_0_8_node_135 | 0.4 | n |  | TRUE
114 | bus_LV_247-26_0_8_node_149 | 0.4 | n |  | TRUE
115 | bus_LV_247-26_0_8_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_247-26_0_8_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_247-26_0_8_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_247-26_0_8_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_247-26_0_8_node_129 | 0.4 | n |  | TRUE
120 | bus_LV_247-26_0_8_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_247-26_0_8_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_247-26_0_8_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_247-26_0_8_node_112 | 0.4 | n |  | TRUE
124 | bus_LV_247-26_0_8_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_247-26_0_8_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_247-26_0_8_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_247-26_0_8_node_128 | 0.4 | n |  | TRUE
128 | bus_LV_247-26_0_8_node_134 | 0.4 | n |  | TRUE
129 | bus_LV_247-26_0_8_node_140 | 0.4 | n |  | TRUE
130 | bus_LV_247-26_0_8_node_115 | 0.4 | n |  | TRUE
131 | bus_LV_247-26_0_8_node_117 | 0.4 | n |  | TRUE
132 | bus_LV_247-26_0_8_node_118 | 0.4 | n |  | TRUE
133 | bus_LV_247-26_0_8_node_132 | 0.4 | n |  | TRUE
134 | bus_LV_247-26_0_8_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_247-26_0_8_node_123 | 0.4 | n |  | TRUE
136 | bus_LV_247-26_0_8_node_141 | 0.4 | n |  | TRUE
137 | bus_LV_247-26_0_8_node_142 | 0.4 | n |  | TRUE
138 | bus_LV_247-26_0_8_node_139 | 0.4 | n |  | TRUE
139 | bus_LV_247-26_0_8_node_143 | 0.4 | n |  | TRUE
140 | bus_LV_247-26_0_8_node_146 | 0.4 | n |  | TRUE
141 | bus_LV_247-26_0_8_node_147 | 0.4 | n |  | TRUE
142 | bus_LV_247-26_0_8_node_144 | 0.4 | n |  | TRUE
143 | bus_LV_247-26_0_8_node_145 | 0.4 | n |  | TRUE
144 | bus_LV_247-26_0_8_node_151 | 0.4 | n |  | TRUE
145 | bus_LV_247-26_0_8_node_150 | 0.4 | n |  | TRUE
146 | bus_MV_514_0_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_247-26_0_8_load_0 | 0 | 0.036442 | 0.0091333 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_247-26_0_8_load_44 | 5 | 0.015171 | 0.0038021 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_247-26_0_8_load_33 | 8 | 0.014811 | 0.0037119 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_247-26_0_8_load_41 | 9 | 0.021124 | 0.0052942 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_247-26_0_8_load_126 | 12 | 0.0022029 | 0.00055209 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_247-26_0_8_load_11 | 13 | 0.017288 | 0.0043328 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_247-26_0_8_load_153 | 14 | 0.0019269 | 0.00048294 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_247-26_0_8_load_137 | 16 | 0.0020553 | 0.00051511 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_247-26_0_8_load_62 | 17 | 0.0021331 | 0.00053462 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_247-26_0_8_load_89 | 18 | 0.0097405 | 0.0024412 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_247-26_0_8_load_90 | 19 | 0.0097432 | 0.0024419 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_247-26_0_8_load_45 | 23 | 0.030641 | 0.0076794 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_247-26_0_8_load_99 | 25 | 0.061665 | 0.015455 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_247-26_0_8_load_13 | 28 | 0.0057029 | 0.0014293 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_247-26_0_8_load_28 | 30 | 0.018582 | 0.004657 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_247-26_0_8_load_43 | 32 | 0.0051562 | 0.0012923 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_247-26_0_8_load_42 | 33 | 0.012448 | 0.0031198 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_247-26_0_8_load_34 | 34 | 0.044353 | 0.011116 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_247-26_0_8_load_78 | 35 | 0.016939 | 0.0042453 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_247-26_0_8_load_131 | 38 | 0.0023661 | 0.000593 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_247-26_0_8_load_46 | 39 | 0.0057273 | 0.0014354 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_247-26_0_8_load_111 | 40 | 0.0023145 | 0.00058006 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_247-26_0_8_load_125 | 41 | 0.0021316 | 0.00053422 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_247-26_0_8_load_155 | 42 | 0.0021787 | 0.00054604 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_247-26_0_8_load_154 | 44 | 0.0020012 | 0.00050156 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_247-26_0_8_load_138 | 45 | 0.0020313 | 0.00050909 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_247-26_0_8_load_16 | 47 | 0.0070364 | 0.0017635 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_247-26_0_8_load_29 | 50 | 0.0050666 | 0.0012698 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_247-26_0_8_load_100 | 51 | 0.0052226 | 0.0013089 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_247-26_0_8_load_88 | 53 | 0.00086809 | 0.00021756 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_247-26_0_8_load_87 | 56 | 0.00080525 | 0.00020181 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_247-26_0_8_load_156 | 58 | 0.002017 | 0.0005055 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_247-26_0_8_load_93 | 59 | 0.017375 | 0.0043545 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_247-26_0_8_load_77 | 61 | 0.0017208 | 0.00043126 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_247-26_0_8_load_70 | 62 | 0.0011545 | 0.00028933 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_247-26_0_8_load_68 | 64 | 0.0012383 | 0.00031036 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_247-26_0_8_load_65 | 65 | 0.001824 | 0.00045714 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_247-26_0_8_load_86 | 67 | 0.00080962 | 0.00020291 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_247-26_0_8_load_85 | 68 | 0.00085211 | 0.00021356 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_247-26_0_8_load_82 | 69 | 0.00086265 | 0.0002162 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_247-26_0_8_load_47 | 71 | 0.0036313 | 0.00091008 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_247-26_0_8_load_48 | 72 | 0.013729 | 0.0034409 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_247-26_0_8_load_49 | 73 | 0.0024001 | 0.00060151 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_247-26_0_8_load_51 | 75 | 0.0022808 | 0.00057161 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_247-26_0_8_load_52 | 76 | 0.0022622 | 0.00056697 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_247-26_0_8_load_53 | 77 | 0.0021877 | 0.00054829 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_247-26_0_8_load_58 | 78 | 0.002335 | 0.0005852 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_247-26_0_8_load_105 | 79 | 0.0022497 | 0.00056383 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_247-26_0_8_load_124 | 80 | 0.0022903 | 0.00057401 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_247-26_0_8_load_59 | 81 | 0.013995 | 0.0035075 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_247-26_0_8_load_122 | 83 | 0.0021842 | 0.00054742 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_247-26_0_8_load_54 | 84 | 0.0022611 | 0.00056668 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_247-26_0_8_load_55 | 85 | 0.0022509 | 0.00056413 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_247-26_0_8_load_56 | 86 | 0.0021878 | 0.00054831 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_247-26_0_8_load_57 | 87 | 0.0022891 | 0.00057371 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_247-26_0_8_load_61 | 88 | 0.0021856 | 0.00054775 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_247-26_0_8_load_60 | 89 | 0.0022907 | 0.0005741 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_247-26_0_8_load_110 | 90 | 0.0023482 | 0.00058851 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_247-26_0_8_load_69 | 91 | 0.0017901 | 0.00044864 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_247-26_0_8_load_66 | 92 | 0.0018125 | 0.00045426 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_247-26_0_8_load_72 | 94 | 0.0013214 | 0.00033117 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_247-26_0_8_load_73 | 95 | 0.0013568 | 0.00034005 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_247-26_0_8_load_71 | 96 | 0.0014887 | 0.00037312 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_247-26_0_8_load_74 | 97 | 0.0011767 | 0.00029491 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_247-26_0_8_load_79 | 98 | 0.00089431 | 0.00022414 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_247-26_0_8_load_80 | 99 | 0.00089625 | 0.00022462 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_247-26_0_8_load_81 | 100 | 0.00086556 | 0.00021693 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_247-26_0_8_load_130 | 103 | 0.0019622 | 0.00049177 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_247-26_0_8_load_148 | 105 | 0.0018971 | 0.00047545 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_247-26_0_8_load_95 | 106 | 0.022833 | 0.0057225 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_247-26_0_8_load_84 | 107 | 0.00088686 | 0.00022227 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_247-26_0_8_load_106 | 108 | 0.0018712 | 0.00046898 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_247-26_0_8_load_101 | 109 | 0.0019613 | 0.00049155 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_247-26_0_8_load_107 | 110 | 0.0020553 | 0.00051511 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_247-26_0_8_load_108 | 111 | 0.0020313 | 0.00050908 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_247-26_0_8_load_157 | 112 | 0.034963 | 0.0087625 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_247-26_0_8_load_135 | 113 | 0.0018012 | 0.00045143 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_247-26_0_8_load_149 | 114 | 0.0019629 | 0.00049194 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_247-26_0_8_load_121 | 115 | 0.0020301 | 0.00050879 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_247-26_0_8_load_102 | 116 | 0.00203 | 0.00050876 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_247-26_0_8_load_104 | 117 | 0.0019607 | 0.00049141 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_247-26_0_8_load_119 | 118 | 0.0018965 | 0.00047532 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_247-26_0_8_load_129 | 119 | 0.0017936 | 0.00044953 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_247-26_0_8_load_120 | 121 | 0.0055129 | 0.0013817 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_247-26_0_8_load_109 | 122 | 0.0019623 | 0.00049179 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_247-26_0_8_load_112 | 123 | 0.0018965 | 0.00047532 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_247-26_0_8_load_113 | 124 | 0.0018032 | 0.00045192 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_247-26_0_8_load_127 | 126 | 0.0019643 | 0.00049229 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_247-26_0_8_load_128 | 127 | 0.0020303 | 0.00050884 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_247-26_0_8_load_134 | 128 | 0.0018954 | 0.00047503 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_247-26_0_8_load_115 | 130 | 0.0019613 | 0.00049155 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_247-26_0_8_load_132 | 133 | 0.0018029 | 0.00045186 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_247-26_0_8_load_133 | 134 | 0.0018032 | 0.00045192 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_247-26_0_8_load_123 | 135 | 0.0022918 | 0.00057439 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_247-26_0_8_load_141 | 136 | 0.001959 | 0.00049096 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_247-26_0_8_load_142 | 137 | 0.0019364 | 0.0004853 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_247-26_0_8_load_139 | 138 | 0.0019623 | 0.0004918 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_247-26_0_8_load_143 | 139 | 0.0018965 | 0.00047532 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_247-26_0_8_load_146 | 140 | 0.0018032 | 0.00045192 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_247-26_0_8_load_144 | 142 | 0.0019622 | 0.00049178 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_247-26_0_8_load_145 | 143 | 0.0018017 | 0.00045156 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_247-26_0_8_load_151 | 144 | 0.001995 | 0.0005 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_247-26_0_8_load_150 | 145 | 0.0020303 | 0.00050884 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_247-26_0_8_line_0 |  | 0 | 1 | 0.021003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_247-26_0_8_line_1 |  | 1 | 2 | 0.030111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_247-26_0_8_line_2 |  | 2 | 15 | 0.005128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_247-26_0_8_line_3 |  | 2 | 16 | 0.011685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_247-26_0_8_line_4 |  | 3 | 4 | 0.043721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_247-26_0_8_line_5 |  | 3 | 5 | 0.031237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_247-26_0_8_line_6 |  | 4 | 8 | 0.00085394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_247-26_0_8_line_7 |  | 6 | 7 | 0.033161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_247-26_0_8_line_8 |  | 6 | 8 | 0.024886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_247-26_0_8_line_9 |  | 7 | 9 | 0.0022142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_247-26_0_8_line_10 |  | 9 | 37 | 0.036343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_247-26_0_8_line_11 |  | 10 | 11 | 0.024933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_247-26_0_8_line_12 |  | 10 | 12 | 0.0082248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_247-26_0_8_line_13 |  | 11 | 17 | 0.014639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_247-26_0_8_line_14 |  | 12 | 41 | 0.0067223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_247-26_0_8_line_15 |  | 13 | 14 | 0.011326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_247-26_0_8_line_16 |  | 14 | 44 | 0.0067667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_247-26_0_8_line_17 |  | 15 | 19 | 0.01587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_247-26_0_8_line_18 |  | 16 | 45 | 0.0071358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_247-26_0_8_line_19 |  | 17 | 89 | 0.006862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_247-26_0_8_line_20 |  | 18 | 19 | 0.025547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_247-26_0_8_line_21 |  | 20 | 21 | 0.052025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_247-26_0_8_line_22 |  | 20 | 22 | 0.032399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_247-26_0_8_line_23 |  | 20 | 23 | 0.024414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_247-26_0_8_line_24 |  | 21 | 24 | 0.022905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_247-26_0_8_line_25 |  | 21 | 25 | 0.038825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_247-26_0_8_line_26 |  | 22 | 50 | 0.024588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_247-26_0_8_line_27 |  | 23 | 27 | 0.0018342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_247-26_0_8_line_28 |  | 24 | 34 | 0.0092542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_247-26_0_8_line_29 |  | 24 | 29 | 0.0288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_247-26_0_8_line_30 |  | 25 | 51 | 0.062262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_247-26_0_8_line_31 |  | 26 | 27 | 0.010474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_247-26_0_8_line_32 |  | 26 | 28 | 0.021462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_247-26_0_8_line_33 |  | 28 | 46 | 0.010158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_247-26_0_8_line_34 |  | 29 | 30 | 0.031344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_247-26_0_8_line_35 |  | 31 | 32 | 0.055343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_247-26_0_8_line_36 |  | 31 | 33 | 0.042438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_247-26_0_8_line_37 |  | 32 | 60 | 0.012021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_247-26_0_8_line_38 |  | 34 | 37 | 0.028381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_247-26_0_8_line_39 |  | 35 | 36 | 0.018003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_247-26_0_8_line_40 |  | 36 | 37 | 0.038912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_247-26_0_8_line_41 |  | 36 | 43 | 0.034656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_247-26_0_8_line_42 |  | 38 | 39 | 0.11364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_247-26_0_8_line_43 |  | 38 | 40 | 0.0068573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_247-26_0_8_line_44 |  | 39 | 71 | 0.042231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_247-26_0_8_line_45 |  | 40 | 90 | 0.006831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_247-26_0_8_line_46 |  | 41 | 135 | 0.0068647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_247-26_0_8_line_47 |  | 42 | 43 | 0.0095206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_247-26_0_8_line_48 |  | 43 | 58 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_247-26_0_8_line_49 |  | 43 | 55 | 0.046449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_247-26_0_8_line_50 |  | 44 | 144 | 0.006884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_247-26_0_8_line_51 |  | 45 | 138 | 0.0071411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_247-26_0_8_line_52 |  | 46 | 47 | 0.024798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_247-26_0_8_line_53 |  | 47 | 48 | 0.033269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_247-26_0_8_line_54 |  | 48 | 49 | 0.006232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_247-26_0_8_line_55 |  | 49 | 61 | 0.022768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_247-26_0_8_line_56 |  | 49 | 62 | 0.023595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_247-26_0_8_line_57 |  | 49 | 60 | 0.033785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_247-26_0_8_line_58 |  | 52 | 53 | 0.008484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_247-26_0_8_line_59 |  | 52 | 54 | 0.057256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_247-26_0_8_line_60 |  | 53 | 67 | 0.0067612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_247-26_0_8_line_61 |  | 54 | 59 | 0.029695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_247-26_0_8_line_62 |  | 55 | 56 | 0.0072501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_247-26_0_8_line_63 |  | 55 | 57 | 0.021608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_247-26_0_8_line_64 |  | 56 | 68 | 0.0066807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_247-26_0_8_line_65 |  | 57 | 69 | 0.0074564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_247-26_0_8_line_66 |  | 58 | 70 | 0.014937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_247-26_0_8_line_67 |  | 59 | 66 | 0.029551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_247-26_0_8_line_68 |  | 62 | 91 | 0.0017248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_247-26_0_8_line_69 |  | 63 | 64 | 0.0020688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_247-26_0_8_line_70 |  | 63 | 65 | 0.013528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_247-26_0_8_line_71 |  | 64 | 93 | 0.018364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_247-26_0_8_line_72 |  | 65 | 92 | 0.01459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_247-26_0_8_line_73 |  | 66 | 106 | 0.070482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_247-26_0_8_line_74 |  | 67 | 107 | 0.0068369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_247-26_0_8_line_75 |  | 68 | 107 | 0.0070081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_247-26_0_8_line_76 |  | 69 | 99 | 0.0067882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_247-26_0_8_line_77 |  | 70 | 145 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_247-26_0_8_line_78 |  | 70 | 143 | 0.011128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_247-26_0_8_line_79 |  | 72 | 73 | 0.0073308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_247-26_0_8_line_80 |  | 72 | 74 | 0.023534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_247-26_0_8_line_81 |  | 73 | 75 | 0.0067732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_247-26_0_8_line_82 |  | 74 | 76 | 0.0067078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_247-26_0_8_line_83 |  | 74 | 77 | 0.00010984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_247-26_0_8_line_84 |  | 75 | 78 | 0.0067623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_247-26_0_8_line_85 |  | 76 | 79 | 0.0067541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_247-26_0_8_line_86 |  | 77 | 80 | 0.0072162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_247-26_0_8_line_87 |  | 78 | 81 | 0.001647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_247-26_0_8_line_88 |  | 79 | 82 | 0.012412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_247-26_0_8_line_89 |  | 80 | 83 | 0.013764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_247-26_0_8_line_90 |  | 81 | 90 | 0.005214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_247-26_0_8_line_91 |  | 82 | 108 | 0.013686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_247-26_0_8_line_92 |  | 82 | 109 | 0.013391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_247-26_0_8_line_93 |  | 83 | 135 | 0.0069465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_247-26_0_8_line_94 |  | 84 | 85 | 0.0067524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_247-26_0_8_line_95 |  | 84 | 86 | 0.0067807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_247-26_0_8_line_96 |  | 86 | 87 | 0.0072183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_247-26_0_8_line_97 |  | 87 | 88 | 0.014138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_247-26_0_8_line_98 |  | 88 | 89 | 0.0069477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_247-26_0_8_line_99 |  | 91 | 96 | 0.044328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_247-26_0_8_line_100 |  | 93 | 94 | 0.014064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_247-26_0_8_line_101 |  | 93 | 95 | 0.0011528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_247-26_0_8_line_102 |  | 94 | 96 | 0.001457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_247-26_0_8_line_103 |  | 95 | 97 | 0.029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_247-26_0_8_line_104 |  | 98 | 99 | 0.0069053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_247-26_0_8_line_105 |  | 98 | 100 | 0.006792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_247-26_0_8_line_106 |  | 101 | 102 | 0.023108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_247-26_0_8_line_107 |  | 101 | 103 | 0.019785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_247-26_0_8_line_108 |  | 102 | 113 | 0.0076443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_247-26_0_8_line_109 |  | 102 | 104 | 0.003545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_247-26_0_8_line_110 |  | 103 | 115 | 0.0071406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_247-26_0_8_line_111 |  | 104 | 105 | 0.013396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_247-26_0_8_line_112 |  | 105 | 114 | 0.0068797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_247-26_0_8_line_113 |  | 106 | 112 | 0.013742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_247-26_0_8_line_114 |  | 108 | 119 | 0.023951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_247-26_0_8_line_115 |  | 109 | 116 | 0.0071387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_247-26_0_8_line_116 |  | 110 | 111 | 0.0071358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_247-26_0_8_line_117 |  | 111 | 122 | 0.0071412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_247-26_0_8_line_118 |  | 114 | 145 | 0.0071199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_247-26_0_8_line_119 |  | 115 | 131 | 0.014143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_247-26_0_8_line_120 |  | 116 | 117 | 0.0071396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_247-26_0_8_line_121 |  | 117 | 118 | 0.0068994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_247-26_0_8_line_122 |  | 118 | 120 | 0.011778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_247-26_0_8_line_123 |  | 119 | 121 | 0.0052823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_247-26_0_8_line_124 |  | 120 | 132 | 0.001845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_247-26_0_8_line_125 |  | 120 | 130 | 0.013113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_247-26_0_8_line_126 |  | 122 | 123 | 0.0068971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_247-26_0_8_line_127 |  | 123 | 124 | 0.0066158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_247-26_0_8_line_128 |  | 124 | 125 | 0.0077708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_247-26_0_8_line_129 |  | 125 | 126 | 0.006236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_247-26_0_8_line_130 |  | 125 | 127 | 0.00088507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_247-26_0_8_line_131 |  | 126 | 128 | 0.0068821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_247-26_0_8_line_132 |  | 127 | 129 | 0.01291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_247-26_0_8_line_133 |  | 128 | 134 | 0.0045178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_247-26_0_8_line_134 |  | 129 | 136 | 0.006347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_247-26_0_8_line_135 |  | 129 | 137 | 0.0065851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_247-26_0_8_line_136 |  | 130 | 131 | 0.0099846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_247-26_0_8_line_137 |  | 132 | 133 | 0.0071083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_247-26_0_8_line_138 |  | 133 | 134 | 0.0020743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_247-26_0_8_line_139 |  | 137 | 141 | 0.0050727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_247-26_0_8_line_140 |  | 138 | 139 | 0.0068971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_247-26_0_8_line_141 |  | 139 | 140 | 0.0066158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_247-26_0_8_line_142 |  | 140 | 141 | 0.0066294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_247-26_0_8_line_143 |  | 141 | 144 | 0.0016969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_247-26_0_8_line_144 |  | 142 | 143 | 0.00014257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_247-26_0_8_trafo_39 | 0.63 MVA 20/0.4 kV | 146 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2675518.6171 | 1250097.6598 | 2675530.9217 | 1250099.5735 | 2675539.4147 | 1250100.5603
1 | 2675518.6171 | 1250097.6598 | 2675516.0754 | 1250127.6603
2 | 2675516.0754 | 1250127.6603 | 2675515.6403 | 1250132.7696
3 | 2675516.0754 | 1250127.6603 | 2675504.472 | 1250126.2781
4 | 2675500.4978 | 1250015.2692 | 2675505.9399 | 1250014.7937 | 2675515.7675 | 1250014.9968 | 2675534.2152 | 1250015.9436 | 2675544.1502 | 1250016.604
5 | 2675544.1502 | 1250016.604 | 2675556.0898 | 1250017.5569 | 2675573.4655 | 1250020.2692 | 2675575.1026 | 1250020.6176
6 | 2675499.6614 | 1250015.4412 | 2675500.4978 | 1250015.2692
7 | 2675442.7156 | 1250026.6752 | 2675464.6272 | 1250022.4177 | 2675468.9016 | 1250021.7382 | 2675475.2828 | 1250020.4408
8 | 2675475.2828 | 1250020.4408 | 2675484.2605 | 1250018.6093 | 2675499.6614 | 1250015.4412
9 | 2675442.7156 | 1250026.6752 | 2675440.5426 | 1250027.1
10 | 2675406.1517 | 1250038.4741 | 2675428.378 | 1250029.6505 | 2675439.7789 | 1250027.2494 | 2675440.5426 | 1250027.1
11 | 2675589.8656 | 1250162.1703 | 2675587.043 | 1250186.9412
12 | 2675587.043 | 1250186.9412 | 2675578.8564 | 1250186.1488
13 | 2675589.8656 | 1250162.1703 | 2675575.3333 | 1250160.408
14 | 2675572.1654 | 1250185.5011 | 2675578.8564 | 1250186.1488
15 | 2675473.6138 | 1250095.7409 | 2675472.2043 | 1250106.9784
16 | 2675472.2043 | 1250106.9784 | 2675471.3622 | 1250113.6925
17 | 2675515.6403 | 1250132.7696 | 2675531.451 | 1250134.1408
18 | 2675504.472 | 1250126.2781 | 2675497.3863 | 1250125.434
19 | 2675568.5211 | 1250159.582 | 2675575.3333 | 1250160.408
20 | 2675556.9028 | 1250136.3482 | 2675531.451 | 1250134.1408
21 | 2675314.8586 | 1250031.2306 | 2675329.5158 | 1250029.8381 | 2675337.8583 | 1250028.0761 | 2675342.9877 | 1250028.4416 | 2675346.5565 | 1250029.8101 | 2675349.0311 | 1250032.9216 | 2675350.5373 | 1250039.1564 | 2675351.233 | 1250042.034 | 2675352.7538 | 1250048.3134
22 | 2675282.4283 | 1250033.2535 | 2675307.7617 | 1250031.8187 | 2675314.8586 | 1250031.2306
23 | 2675314.8586 | 1250031.2306 | 2675314.5811 | 1250018.0175 | 2675314.2239 | 1250006.8249
24 | 2675352.7538 | 1250048.3134 | 2675368.4547 | 1250044.9884 | 2675370.8191 | 1250051.4231
25 | 2675352.7538 | 1250048.3134 | 2675343.099 | 1250054.1172 | 2675332.363 | 1250055.8931 | 2675315.7243 | 1250057.0384
26 | 2675282.4283 | 1250033.2535 | 2675281.0315 | 1250008.705
27 | 2675314.1654 | 1250004.9917 | 2675314.2239 | 1250006.8249
28 | 2675370.8191 | 1250051.4231 | 2675379.5684 | 1250048.4084
29 | 2675362.7143 | 1250023.8112 | 2675363.8811 | 1250028.2403 | 2675365.5548 | 1250034.9554 | 2675366.3857 | 1250037.8903 | 2675368.4547 | 1250044.9884 | 2675370.8191 | 1250051.4231
30 | 2675253.5914 | 1250060.7953 | 2675261.18 | 1250060.7926 | 2675315.7243 | 1250057.0384
31 | 2675314.1654 | 1250004.9917 | 2675324.6268 | 1250004.035
32 | 2675324.6268 | 1250004.035 | 2675323.349 | 1249998.8372 | 2675321.4144 | 1249987.6934 | 2675320.7772 | 1249982.9369
33 | 2675319.4285 | 1249972.8685 | 2675320.7772 | 1249982.9369
34 | 2675362.7143 | 1250023.8112 | 2675373.3708 | 1250020.5776 | 2675392.5562 | 1250014.2324
35 | 2675412.7573 | 1249922.2738 | 2675379.6371 | 1249917.349 | 2675357.8275 | 1249915.8879
36 | 2675412.7573 | 1249922.2738 | 2675410.9493 | 1249945.0896 | 2675430.4712 | 1249946.1468
37 | 2675345.8337 | 1249915.0844 | 2675357.8275 | 1249915.8879
38 | 2675406.1517 | 1250038.4741 | 2675383.703 | 1250046.9837 | 2675379.5684 | 1250048.4084
39 | 2675421.8176 | 1250071.7087 | 2675426.0616 | 1250063.9348 | 2675434.4296 | 1250060.2423
40 | 2675421.8176 | 1250071.7087 | 2675414.2199 | 1250067.7536 | 2675406.1517 | 1250038.4741
41 | 2675421.8176 | 1250071.7087 | 2675421.4551 | 1250090.6956 | 2675422.0176 | 1250098.1082 | 2675424.7919 | 1250097.8321 | 2675430.2308 | 1250097.6012
42 | 2675576.2477 | 1250210.4938 | 2675564.9288 | 1250323.5711
43 | 2675569.4393 | 1250209.6769 | 2675576.2477 | 1250210.4938
44 | 2675564.9288 | 1250323.5711 | 2675522.9088 | 1250319.3517
45 | 2675562.6569 | 1250208.863 | 2675569.4393 | 1250209.6769
46 | 2675565.3326 | 1250184.8397 | 2675572.1654 | 1250185.5011
47 | 2675430.2308 | 1250097.6012 | 2675439.7426 | 1250097.1919
48 | 2675430.2308 | 1250097.6012 | 2675428.1897 | 1250114.3148
49 | 2675401.5181 | 1250121.3532 | 2675406.7244 | 1250099.0587 | 2675422.0176 | 1250098.1082 | 2675424.7919 | 1250097.8321 | 2675430.2308 | 1250097.6012
50 | 2675471.3622 | 1250113.6925 | 2675470.5055 | 1250120.523
51 | 2675497.3863 | 1250125.434 | 2675490.2953 | 1250124.5893
52 | 2675319.4285 | 1249972.8685 | 2675317.5023 | 1249948.1454
53 | 2675311.4001 | 1249918.4382 | 2675315.2159 | 1249918.798 | 2675317.5023 | 1249948.1454
54 | 2675312.0677 | 1249912.2422 | 2675311.4001 | 1249918.4382
55 | 2675312.0677 | 1249912.2422 | 2675289.5758 | 1249908.7062
56 | 2675312.0677 | 1249912.2422 | 2675312.8975 | 1249904.5805 | 2675318.2724 | 1249904.6488 | 2675318.478 | 1249894.1373
57 | 2675345.8337 | 1249915.0844 | 2675312.0677 | 1249912.2422
58 | 2675358.7635 | 1250116.5727 | 2675367.195 | 1250117.5155
59 | 2675318.3807 | 1250098.035 | 2675357.2525 | 1250098.2513 | 2675357.5499 | 1250101.5797 | 2675358.7635 | 1250116.5727
60 | 2675367.195 | 1250117.5155 | 2675373.9143 | 1250118.2668
61 | 2675318.3807 | 1250098.035 | 2675320.5509 | 1250127.6501
62 | 2675401.5181 | 1250121.3532 | 2675394.3129 | 1250120.5475
63 | 2675401.5181 | 1250121.3532 | 2675396.5996 | 1250142.3948
64 | 2675394.3129 | 1250120.5475 | 2675387.6736 | 1250119.8052
65 | 2675396.5996 | 1250142.3948 | 2675389.1912 | 1250141.5495
66 | 2675426.3789 | 1250129.1417 | 2675428.1897 | 1250114.3148
67 | 2675322.7105 | 1250157.1218 | 2675320.5509 | 1250127.6501
68 | 2675318.5117 | 1249892.4129 | 2675318.478 | 1249894.1373
69 | 2675306.1709 | 1249829.0958 | 2675308.196 | 1249829.519
70 | 2675306.1709 | 1249829.0958 | 2675302.2393 | 1249842.0404
71 | 2675326.1713 | 1249833.2752 | 2675308.196 | 1249829.519
72 | 2675297.9994 | 1249856.0004 | 2675302.2393 | 1249842.0404
73 | 2675322.7105 | 1250157.1218 | 2675291.4577 | 1250153.878 | 2675252.6706 | 1250149.2596
74 | 2675380.7089 | 1250119.0265 | 2675373.9143 | 1250118.2668
75 | 2675380.7089 | 1250119.0265 | 2675387.6736 | 1250119.8052
76 | 2675389.1912 | 1250141.5495 | 2675382.4467 | 1250140.7801
77 | 2675426.3789 | 1250129.1417 | 2675424.8327 | 1250141.8153
78 | 2675426.3789 | 1250129.1417 | 2675437.441 | 1250130.3484
79 | 2675535.1271 | 1250205.5596 | 2675542.4057 | 1250206.433
80 | 2675537.4264 | 1250182.1386 | 2675537.1152 | 1250185.2258 | 2675535.1271 | 1250205.5596 | 2675535.1271 | 1250205.5596
81 | 2675549.1306 | 1250207.24 | 2675542.4057 | 1250206.433
82 | 2675537.4264 | 1250182.1386 | 2675530.7528 | 1250181.4626
83 | 2675537.5357 | 1250182.1492 | 2675537.4264 | 1250182.1386
84 | 2675549.1306 | 1250207.24 | 2675555.8447 | 1250208.0456
85 | 2675524.0331 | 1250180.7819 | 2675530.7528 | 1250181.4626
86 | 2675537.5357 | 1250182.1492 | 2675544.7183 | 1250182.8444
87 | 2675557.48 | 1250208.2418 | 2675555.8447 | 1250208.0456
88 | 2675511.6845 | 1250179.531 | 2675524.0331 | 1250180.7819
89 | 2675558.4185 | 1250184.1705 | 2675544.7183 | 1250182.8444
90 | 2675557.48 | 1250208.2418 | 2675562.6569 | 1250208.863
91 | 2675511.6845 | 1250179.531 | 2675510.5437 | 1250193.1697
92 | 2675511.6845 | 1250179.531 | 2675498.3799 | 1250178.0121
93 | 2675558.4185 | 1250184.1705 | 2675565.3326 | 1250184.8397
94 | 2675533.6912 | 1250155.3584 | 2675526.988 | 1250154.5455
95 | 2675533.6912 | 1250155.3584 | 2675540.4227 | 1250156.1747
96 | 2675540.4227 | 1250156.1747 | 2675547.5885 | 1250157.0436
97 | 2675561.6239 | 1250158.7456 | 2675547.5885 | 1250157.0436
98 | 2675568.5211 | 1250159.582 | 2675561.6239 | 1250158.7456
99 | 2675318.5117 | 1249892.4129 | 2675318.8762 | 1249873.7785 | 2675318.9232 | 1249870.0876 | 2675323.173 | 1249848.5033
100 | 2675326.1713 | 1249833.2752 | 2675323.4544 | 1249847.0738
101 | 2675326.1713 | 1249833.2752 | 2675327.2934 | 1249833.5394
102 | 2675323.173 | 1249848.5033 | 2675323.4544 | 1249847.0738
103 | 2675327.2934 | 1249833.5394 | 2675355.5427 | 1249840.1909
104 | 2675375.5859 | 1250139.9973 | 2675382.4467 | 1250140.7801
105 | 2675375.5859 | 1250139.9973 | 2675368.8377 | 1250139.2274
106 | 2675425.0427 | 1250169.454 | 2675422.2442 | 1250192.3906
107 | 2675422.2442 | 1250192.3906 | 2675441.8914 | 1250194.7192
108 | 2675425.0427 | 1250169.454 | 2675432.6247 | 1250170.4277
109 | 2675421.5151 | 1250169.0088 | 2675425.0427 | 1250169.454
110 | 2675448.9824 | 1250195.5597 | 2675441.8914 | 1250194.7192
111 | 2675421.5151 | 1250169.0088 | 2675423.1373 | 1250155.7118
112 | 2675423.1373 | 1250155.7118 | 2675423.9705 | 1250148.8827
113 | 2675239.0255 | 1250147.6349 | 2675252.6706 | 1250149.2596
114 | 2675510.5437 | 1250193.1697 | 2675509.7428 | 1250202.7453 | 2675495.5 | 1250201.062
115 | 2675498.3799 | 1250178.0121 | 2675491.2873 | 1250177.2024
116 | 2675502.4486 | 1250151.638 | 2675495.3622 | 1250150.8002
117 | 2675495.3622 | 1250150.8002 | 2675488.2704 | 1250149.9617
118 | 2675423.9705 | 1250148.8827 | 2675424.8327 | 1250141.8153
119 | 2675463.027 | 1250197.2242 | 2675448.9824 | 1250195.5597
120 | 2675491.2873 | 1250177.2024 | 2675484.1938 | 1250176.3926
121 | 2675484.1938 | 1250176.3926 | 2675477.3389 | 1250175.61
122 | 2675465.6372 | 1250174.2741 | 2675477.3389 | 1250175.61
123 | 2675490.2541 | 1250200.4421 | 2675495.5 | 1250201.062
124 | 2675463.7976 | 1250174.0728 | 2675465.6372 | 1250174.2741
125 | 2675465.6372 | 1250174.2741 | 2675464.1553 | 1250187.3036
126 | 2675488.2704 | 1250149.9617 | 2675481.421 | 1250149.1518
127 | 2675481.421 | 1250149.1518 | 2675474.8509 | 1250148.375
128 | 2675467.1339 | 1250147.4626 | 2675474.8509 | 1250148.375
129 | 2675467.1339 | 1250147.4626 | 2675466.3581 | 1250153.6502
130 | 2675467.2439 | 1250146.5844 | 2675467.1339 | 1250147.4626
131 | 2675465.502 | 1250160.4787 | 2675466.3581 | 1250153.6502
132 | 2675468.8484 | 1250133.7745 | 2675467.2439 | 1250146.5844
133 | 2675465.502 | 1250160.4787 | 2675464.9399 | 1250164.9615
134 | 2675468.8484 | 1250133.7745 | 2675462.5388 | 1250133.0862
135 | 2675468.8484 | 1250133.7745 | 2675469.6652 | 1250127.2403
136 | 2675463.027 | 1250197.2242 | 2675464.1553 | 1250187.3036
137 | 2675463.7976 | 1250174.0728 | 2675464.6819 | 1250167.0197
138 | 2675464.6819 | 1250167.0197 | 2675464.9399 | 1250164.9615
139 | 2675470.2944 | 1250122.2067 | 2675469.6652 | 1250127.2403
140 | 2675490.2953 | 1250124.5893 | 2675483.4466 | 1250123.7735
141 | 2675483.4466 | 1250123.7735 | 2675476.8772 | 1250122.9909
142 | 2675470.2944 | 1250122.2067 | 2675476.8772 | 1250122.9909
143 | 2675470.2944 | 1250122.2067 | 2675470.5055 | 1250120.523
144 | 2675437.5827 | 1250130.3639 | 2675437.441 | 1250130.3484

## bus_geodata
| x | y | coords
0 | 2675539.4147 | 1250100.5603
1 | 2675518.6171 | 1250097.6598
2 | 2675516.0754 | 1250127.6603
3 | 2675544.1502 | 1250016.604
4 | 2675500.4978 | 1250015.2692
5 | 2675575.1026 | 1250020.6176
6 | 2675475.2828 | 1250020.4408
7 | 2675442.7156 | 1250026.6752
8 | 2675499.6614 | 1250015.4412
9 | 2675440.5426 | 1250027.1
10 | 2675587.043 | 1250186.9412
11 | 2675589.8656 | 1250162.1703
12 | 2675578.8565 | 1250186.1488
13 | 2675473.6138 | 1250095.7409
14 | 2675472.2043 | 1250106.9784
15 | 2675515.6403 | 1250132.7696
16 | 2675504.472 | 1250126.2781
17 | 2675575.3333 | 1250160.408
18 | 2675556.9028 | 1250136.3482
19 | 2675531.451 | 1250134.1408
20 | 2675314.8586 | 1250031.2306
21 | 2675352.7538 | 1250048.3134
22 | 2675282.4283 | 1250033.2535
23 | 2675314.2239 | 1250006.8249
24 | 2675370.8191 | 1250051.4231
25 | 2675315.7243 | 1250057.0384
26 | 2675324.6268 | 1250004.035
27 | 2675314.1654 | 1250004.9917
28 | 2675320.7772 | 1249982.9369
29 | 2675362.7143 | 1250023.8112
30 | 2675392.5562 | 1250014.2324
31 | 2675412.7573 | 1249922.2738
32 | 2675357.8275 | 1249915.8879
33 | 2675430.4712 | 1249946.1468
34 | 2675379.5684 | 1250048.4084
35 | 2675434.4296 | 1250060.2423
36 | 2675421.8176 | 1250071.7087
37 | 2675406.1517 | 1250038.4741
38 | 2675576.2477 | 1250210.4938
39 | 2675564.9288 | 1250323.5711
40 | 2675569.4393 | 1250209.6769
41 | 2675572.1654 | 1250185.5011
42 | 2675439.7426 | 1250097.1919
43 | 2675430.2308 | 1250097.6012
44 | 2675471.3622 | 1250113.6925
45 | 2675497.3863 | 1250125.434
46 | 2675319.4285 | 1249972.8685
47 | 2675317.5023 | 1249948.1454
48 | 2675311.4001 | 1249918.4382
49 | 2675312.0677 | 1249912.2422
50 | 2675281.0315 | 1250008.705
51 | 2675253.5914 | 1250060.7953
52 | 2675358.7635 | 1250116.5727
53 | 2675367.195 | 1250117.5155
54 | 2675318.3807 | 1250098.035
55 | 2675401.5181 | 1250121.3532
56 | 2675394.3129 | 1250120.5475
57 | 2675396.5996 | 1250142.3948
58 | 2675428.1897 | 1250114.3148
59 | 2675320.5509 | 1250127.6501
60 | 2675345.8337 | 1249915.0844
61 | 2675289.5758 | 1249908.7062
62 | 2675318.478 | 1249894.1373
63 | 2675306.1709 | 1249829.0958
64 | 2675308.196 | 1249829.519
65 | 2675302.2393 | 1249842.0404
66 | 2675322.7105 | 1250157.1218
67 | 2675373.9143 | 1250118.2668
68 | 2675387.6736 | 1250119.8052
69 | 2675389.1912 | 1250141.5495
70 | 2675426.3789 | 1250129.1417
71 | 2675522.9088 | 1250319.3517
72 | 2675535.1271 | 1250205.5596
73 | 2675542.4057 | 1250206.433
74 | 2675537.4264 | 1250182.1386
75 | 2675549.1306 | 1250207.24
76 | 2675530.7528 | 1250181.4626
77 | 2675537.5357 | 1250182.1492
78 | 2675555.8447 | 1250208.0456
79 | 2675524.0331 | 1250180.7819
80 | 2675544.7183 | 1250182.8444
81 | 2675557.48 | 1250208.2418
82 | 2675511.6845 | 1250179.531
83 | 2675558.4185 | 1250184.1705
84 | 2675533.6912 | 1250155.3584
85 | 2675526.988 | 1250154.5455
86 | 2675540.4227 | 1250156.1747
87 | 2675547.5885 | 1250157.0436
88 | 2675561.6239 | 1250158.7456
89 | 2675568.5211 | 1250159.582
90 | 2675562.6569 | 1250208.863
91 | 2675318.5117 | 1249892.4129
92 | 2675297.9994 | 1249856.0004
93 | 2675326.1713 | 1249833.2752
94 | 2675323.4544 | 1249847.0738
95 | 2675327.2934 | 1249833.5394
96 | 2675323.173 | 1249848.5033
97 | 2675355.5427 | 1249840.1909
98 | 2675375.5859 | 1250139.9973
99 | 2675382.4467 | 1250140.7801
100 | 2675368.8377 | 1250139.2274
101 | 2675422.2442 | 1250192.3906
102 | 2675425.0427 | 1250169.454
103 | 2675441.8914 | 1250194.7192
104 | 2675421.5151 | 1250169.0088
105 | 2675423.1373 | 1250155.7118
106 | 2675252.6706 | 1250149.2596
107 | 2675380.7089 | 1250119.0265
108 | 2675510.5437 | 1250193.1697
109 | 2675498.3799 | 1250178.0121
110 | 2675502.4486 | 1250151.638
111 | 2675495.3622 | 1250150.8002
112 | 2675239.0255 | 1250147.6349
113 | 2675432.6247 | 1250170.4277
114 | 2675423.9705 | 1250148.8827
115 | 2675448.9824 | 1250195.5597
116 | 2675491.2873 | 1250177.2024
117 | 2675484.1938 | 1250176.3926
118 | 2675477.3389 | 1250175.61
119 | 2675495.5 | 1250201.062
120 | 2675465.6372 | 1250174.2741
121 | 2675490.2541 | 1250200.4421
122 | 2675488.2704 | 1250149.9617
123 | 2675481.421 | 1250149.1518
124 | 2675474.8509 | 1250148.375
125 | 2675467.1339 | 1250147.4626
126 | 2675466.3581 | 1250153.6502
127 | 2675467.2439 | 1250146.5844
128 | 2675465.502 | 1250160.4787
129 | 2675468.8484 | 1250133.7745
130 | 2675464.1553 | 1250187.3036
131 | 2675463.027 | 1250197.2242
132 | 2675463.7976 | 1250174.0728
133 | 2675464.6819 | 1250167.0197
134 | 2675464.9399 | 1250164.9615
135 | 2675565.3326 | 1250184.8397
136 | 2675462.5388 | 1250133.0862
137 | 2675469.6652 | 1250127.2402
138 | 2675490.2953 | 1250124.5893
139 | 2675483.4466 | 1250123.7735
140 | 2675476.8772 | 1250122.9909
141 | 2675470.2944 | 1250122.2067
142 | 2675437.5827 | 1250130.3639
143 | 2675437.441 | 1250130.3484
144 | 2675470.5055 | 1250120.523
145 | 2675424.8327 | 1250141.8153
146 | 2675422.0176 | 1250098.1082

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97911 | -0.40222 | 0.036442 | 0.0091333
1 | 0.97982 | -0.38832 | 0 | 0
2 | 0.98083 | -0.36841 | 0 | 0
3 | 0.98995 | -0.19295 | 0 | 0
4 | 0.99055 | -0.18116 | 0 | 0
5 | 0.98951 | -0.20138 | 0.015171 | 0.0038021
6 | 0.99125 | -0.16768 | 0 | 0
7 | 0.99216 | -0.15006 | 0 | 0
8 | 0.99057 | -0.18093 | 0.014811 | 0.0037119
9 | 0.99222 | -0.14889 | 0.021124 | 0.0052942
10 | 0.98129 | -0.3596 | 0 | 0
11 | 0.98093 | -0.36665 | 0 | 0
12 | 0.98141 | -0.35728 | 0.0022029 | 0.00055209
13 | 0.98294 | -0.32737 | 0.017288 | 0.0043328
14 | 0.98312 | -0.32384 | 0.0019269 | 0.00048294
15 | 0.98074 | -0.37022 | 0 | 0
16 | 0.98144 | -0.35658 | 0.0020553 | 0.00051511
17 | 0.98072 | -0.37078 | 0.0021331 | 0.00053462
18 | 0.98023 | -0.38034 | 0.0097405 | 0.0024412
19 | 0.98046 | -0.37583 | 0.0097432 | 0.0024419
20 | 0.98617 | -0.26564 | 0 | 0
21 | 0.99006 | -0.19046 | 0 | 0
22 | 0.98602 | -0.26859 | 0 | 0
23 | 0.98446 | -0.2989 | 0.030641 | 0.0076794
24 | 0.99162 | -0.1604 | 0 | 0
25 | 0.98767 | -0.23675 | 0.061665 | 0.015455
26 | 0.98394 | -0.30892 | 0 | 0
27 | 0.98438 | -0.3004 | 0 | 0
28 | 0.98304 | -0.32642 | 0.0057029 | 0.0014293
29 | 0.99113 | -0.16989 | 0 | 0
30 | 0.99059 | -0.18023 | 0.018582 | 0.004657
31 | 0.97919 | -0.40177 | 0 | 0
32 | 0.97983 | -0.38925 | 0.0051562 | 0.0012923
33 | 0.9787 | -0.41138 | 0.012448 | 0.0031198
34 | 0.99209 | -0.1513 | 0.044353 | 0.011116
35 | 0.99676 | -0.061659 | 0.016939 | 0.0042453
36 | 0.99704 | -0.05631 | 0 | 0
37 | 0.99392 | -0.11606 | 0 | 0
38 | 0.9802 | -0.38093 | 0.0023661 | 0.000593
39 | 0.97921 | -0.40025 | 0.0057273 | 0.0014354
40 | 0.98027 | -0.37947 | 0.0023145 | 0.00058006
41 | 0.98152 | -0.35512 | 0.0021316 | 0.00053422
42 | 0.99998 | -0.00036157 | 0.0021787 | 0.00054604
43 | 1 | 0 | -0.60658 | -0.1547
44 | 0.98324 | -0.3215 | 0.0020012 | 0.00050156
45 | 0.98182 | -0.3491 | 0.0020313 | 0.00050909
46 | 0.98267 | -0.33366 | 0 | 0
47 | 0.98176 | -0.35138 | 0.0070364 | 0.0017635
48 | 0.98076 | -0.37095 | 0 | 0
49 | 0.98058 | -0.37462 | 0 | 0
50 | 0.9859 | -0.27082 | 0.0050666 | 0.0012698
51 | 0.98737 | -0.24256 | 0.0052226 | 0.0013089
52 | 0.99338 | -0.12588 | 0 | 0
53 | 0.99397 | -0.11462 | 0.00086809 | 0.00021756
54 | 0.98941 | -0.20221 | 0 | 0
55 | 0.99645 | -0.06737 | 0 | 0
56 | 0.99592 | -0.077481 | 0.00080525 | 0.00020181
57 | 0.99638 | -0.068706 | 0 | 0
58 | 0.99879 | -0.022825 | 0.002017 | 0.0005055
59 | 0.98735 | -0.24204 | 0.017375 | 0.0043545
60 | 0.98003 | -0.38541 | 0 | 0
61 | 0.98054 | -0.37533 | 0.0017208 | 0.00043126
62 | 0.98029 | -0.38025 | 0.0011545 | 0.00028933
63 | 0.97965 | -0.39274 | 0 | 0
64 | 0.97966 | -0.3926 | 0.0012383 | 0.00031036
65 | 0.97961 | -0.39363 | 0.001824 | 0.00045714
66 | 0.98577 | -0.27262 | 0 | 0
67 | 0.99444 | -0.10556 | 0.00080962 | 0.00020291
68 | 0.99543 | -0.086712 | 0.00085211 | 0.00021356
69 | 0.99635 | -0.069166 | 0.00086265 | 0.0002162
70 | 0.99773 | -0.042944 | 0 | 0
71 | 0.97907 | -0.40303 | 0.0036313 | 0.00091008
72 | 0.98116 | -0.362 | 0.013729 | 0.0034409
73 | 0.98091 | -0.36696 | 0.0024001 | 0.00060151
74 | 0.98228 | -0.34023 | 0 | 0
75 | 0.98069 | -0.37126 | 0.0022808 | 0.00057161
76 | 0.98277 | -0.33054 | 0.0022622 | 0.00056697
77 | 0.98227 | -0.34029 | 0.0021877 | 0.00054829
78 | 0.98049 | -0.37527 | 0.002335 | 0.0005852
79 | 0.98329 | -0.32052 | 0.0022497 | 0.00056383
80 | 0.9821 | -0.34377 | 0.0022903 | 0.00057401
81 | 0.98044 | -0.37618 | 0.013995 | 0.0035075
82 | 0.98426 | -0.30162 | 0 | 0
83 | 0.98179 | -0.34985 | 0.0021842 | 0.00054742
84 | 0.98037 | -0.3776 | 0.0022611 | 0.00056668
85 | 0.98036 | -0.37788 | 0.0022509 | 0.00056413
86 | 0.9804 | -0.37705 | 0.0021878 | 0.00054831
87 | 0.98044 | -0.37617 | 0.0022891 | 0.00057371
88 | 0.98056 | -0.37387 | 0.0021856 | 0.00054775
89 | 0.98063 | -0.37246 | 0.0022907 | 0.0005741
90 | 0.98036 | -0.37773 | 0.0023482 | 0.00058851
91 | 0.98027 | -0.38063 | 0.0017901 | 0.00044864
92 | 0.97958 | -0.39411 | 0.0018125 | 0.00045426
93 | 0.97974 | -0.39098 | 0 | 0
94 | 0.97984 | -0.38908 | 0.0013214 | 0.00033117
95 | 0.97974 | -0.39103 | 0.0013568 | 0.00034005
96 | 0.97985 | -0.38885 | 0.0014887 | 0.00037312
97 | 0.97971 | -0.39165 | 0.0011767 | 0.00029491
98 | 0.99633 | -0.069696 | 0.00089431 | 0.00022414
99 | 0.99634 | -0.069483 | 0.00089625 | 0.00022462
100 | 0.99632 | -0.0698 | 0.00086556 | 0.00021693
101 | 0.99315 | -0.1301 | 0 | 0
102 | 0.99471 | -0.10026 | 0 | 0
103 | 0.99181 | -0.15572 | 0.0019622 | 0.00049177
104 | 0.99495 | -0.095655 | 0 | 0
105 | 0.99587 | -0.078267 | 0.0018971 | 0.00047545
106 | 0.98201 | -0.34597 | 0.022833 | 0.0057225
107 | 0.99493 | -0.0963 | 0.00088686 | 0.00022227
108 | 0.98414 | -0.30388 | 0.0018712 | 0.00046898
109 | 0.98542 | -0.27907 | 0.0019613 | 0.00049155
110 | 0.98537 | -0.28008 | 0.0020553 | 0.00051511
111 | 0.98538 | -0.27982 | 0.0020313 | 0.00050908
112 | 0.98156 | -0.35466 | 0.034963 | 0.0087625
113 | 0.9947 | -0.1005 | 0.0018012 | 0.00045143
114 | 0.99634 | -0.069274 | 0.0019629 | 0.00049194
115 | 0.99133 | -0.1649 | 0.0020301 | 0.00050879
116 | 0.98605 | -0.26682 | 0.00203 | 0.00050876
117 | 0.98669 | -0.25432 | 0.0019607 | 0.00049141
118 | 0.98733 | -0.24202 | 0.0018965 | 0.00047532
119 | 0.98398 | -0.30703 | 0.0017936 | 0.00044953
120 | 0.98843 | -0.22065 | 0 | 0
121 | 0.98395 | -0.30756 | 0.0055129 | 0.0013817
122 | 0.98541 | -0.27929 | 0.0019623 | 0.00049179
123 | 0.98545 | -0.27854 | 0.0018965 | 0.00047532
124 | 0.98549 | -0.2776 | 0.0018032 | 0.00045192
125 | 0.98556 | -0.27624 | 0 | 0
126 | 0.98617 | -0.26455 | 0.0019643 | 0.00049229
127 | 0.98549 | -0.27775 | 0.0020303 | 0.00050884
128 | 0.98684 | -0.25142 | 0.0018954 | 0.00047503
129 | 0.98438 | -0.29927 | 0 | 0
130 | 0.98973 | -0.1957 | 0.0019613 | 0.00049155
131 | 0.99039 | -0.18294 | 0 | 0
132 | 0.98824 | -0.22434 | 0 | 0
133 | 0.98751 | -0.23856 | 0.0018029 | 0.00045186
134 | 0.9873 | -0.24265 | 0.0018032 | 0.00045192
135 | 0.98164 | -0.35264 | 0.0022918 | 0.00057439
136 | 0.98437 | -0.29949 | 0.001959 | 0.00049096
137 | 0.98383 | -0.31003 | 0.0019364 | 0.0004853
138 | 0.98222 | -0.34135 | 0.0019623 | 0.0004918
139 | 0.98261 | -0.33363 | 0.0018965 | 0.00047532
140 | 0.98301 | -0.32601 | 0.0018032 | 0.00045192
141 | 0.98341 | -0.31815 | 0 | 0
142 | 0.99769 | -0.043682 | 0.0019622 | 0.00049178
143 | 0.99769 | -0.043677 | 0.0018017 | 0.00045156
144 | 0.98337 | -0.31886 | 0.001995 | 0.0005
145 | 0.99683 | -0.059893 | 0.0020303 | 0.00050884
146 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.036442 | -0.0091333 | 0.036466 | 0.0091485 | 2.4158e-05 | 1.5197e-05 | 0.055384 | 0.055384 | 0.055384 | 0.97911 | -0.40222 | 0.97982 | -0.38832 | 15.2153
1 | -0.036466 | -0.0091485 | 0.036501 | 0.0091703 | 3.4635e-05 | 2.1787e-05 | 0.055384 | 0.055383 | 0.055384 | 0.97982 | -0.38832 | 0.98083 | -0.36841 | 15.2153
2 | 0.019493 | 0.0048882 | -0.019491 | -0.0048872 | 1.6818e-06 | 1.0116e-06 | 0.029573 | 0.029573 | 0.029573 | 0.98083 | -0.36841 | 0.98074 | -0.37022 | 8.1245
3 | -0.055994 | -0.014059 | 0.056025 | 0.014079 | 3.1628e-05 | 2.0094e-05 | 0.084957 | 0.084957 | 0.084957 | 0.98083 | -0.36841 | 0.98144 | -0.35658 | 23.3398
4 | -0.015177 | -0.0038056 | 0.015185 | 0.0038105 | 8.5329e-06 | 4.8986e-06 | 0.022813 | 0.022813 | 0.022813 | 0.98995 | -0.19295 | 0.99055 | -0.18116 | 6.2674
5 | 0.015177 | 0.0038056 | -0.015171 | -0.0038021 | 6.0965e-06 | 3.5003e-06 | 0.022813 | 0.022813 | 0.022813 | 0.98995 | -0.19295 | 0.98951 | -0.20138 | 6.2674
6 | -0.015185 | -0.0038105 | 0.015185 | 0.0038106 | 1.6666e-07 | 9.5668e-08 | 0.022813 | 0.022813 | 0.022813 | 0.99055 | -0.18116 | 0.99057 | -0.18093 | 6.2673
7 | -0.030015 | -0.0075344 | 0.03004 | 0.0075501 | 2.5251e-05 | 1.5732e-05 | 0.045061 | 0.045061 | 0.045061 | 0.99125 | -0.16768 | 0.99216 | -0.15006 | 12.3795
8 | 0.030015 | 0.0075344 | -0.029996 | -0.0075225 | 1.895e-05 | 1.1807e-05 | 0.045061 | 0.045062 | 0.045062 | 0.99125 | -0.16768 | 0.99057 | -0.18093 | 12.3796
9 | -0.03004 | -0.0075501 | 0.030042 | 0.0075511 | 1.686e-06 | 1.0504e-06 | 0.045061 | 0.045061 | 0.045061 | 0.99216 | -0.15006 | 0.99222 | -0.14889 | 12.3795
10 | -0.051166 | -0.012845 | 0.051247 | 0.012896 | 8.0261e-05 | 5.0897e-05 | 0.076741 | 0.076741 | 0.076741 | 0.99222 | -0.14889 | 0.99392 | -0.11606 | 21.0826
11 | 0.01561 | 0.0039156 | -0.015605 | -0.0039126 | 5.2393e-06 | 3.0383e-06 | 0.023672 | 0.023672 | 0.023672 | 0.98129 | -0.3596 | 0.98093 | -0.36665 | 6.5033
12 | -0.01561 | -0.0039156 | 0.015612 | 0.0039166 | 1.7283e-06 | 1.0022e-06 | 0.023672 | 0.023672 | 0.023672 | 0.98129 | -0.3596 | 0.98141 | -0.35728 | 6.5033
13 | 0.015605 | 0.0039126 | -0.015602 | -0.0039108 | 3.0761e-06 | 1.784e-06 | 0.023672 | 0.023672 | 0.023672 | 0.98093 | -0.36665 | 0.98072 | -0.37078 | 6.5033
14 | -0.017814 | -0.0044687 | 0.017816 | 0.0044698 | 1.8393e-06 | 1.0922e-06 | 0.027012 | 0.027012 | 0.027012 | 0.98141 | -0.35728 | 0.98152 | -0.35512 | 7.4208
15 | -0.017288 | -0.0043328 | 0.017291 | 0.0043345 | 2.909e-06 | 1.7182e-06 | 0.026172 | 0.026171 | 0.026172 | 0.98294 | -0.32737 | 0.98312 | -0.32384 | 7.19
16 | -0.019218 | -0.0048175 | 0.01922 | 0.0048187 | 2.147e-06 | 1.2883e-06 | 0.029088 | 0.029088 | 0.029088 | 0.98312 | -0.32384 | 0.98324 | -0.3215 | 7.9912
17 | 0.019491 | 0.0048872 | -0.019486 | -0.0048841 | 5.2049e-06 | 3.1309e-06 | 0.029573 | 0.029573 | 0.029573 | 0.98074 | -0.37022 | 0.98046 | -0.37583 | 8.1246
18 | -0.058081 | -0.014594 | 0.058102 | 0.014607 | 2.0757e-05 | 1.3194e-05 | 0.088073 | 0.088073 | 0.088073 | 0.98144 | -0.35658 | 0.98182 | -0.3491 | 24.1959
19 | 0.013468 | 0.0033762 | -0.013467 | -0.0033755 | 1.0746e-06 | 6.0118e-07 | 0.020436 | 0.020436 | 0.020436 | 0.98072 | -0.37078 | 0.98063 | -0.37246 | 5.6142
20 | -0.0097405 | -0.0024412 | 0.0097426 | 0.0024422 | 2.0946e-06 | 1.0184e-06 | 0.014786 | 0.014786 | 0.014786 | 0.98023 | -0.38034 | 0.98046 | -0.37583 | 4.0622
21 | -0.081235 | -0.02047 | 0.081528 | 0.020657 | 0.00029331 | 0.00018705 | 0.12261 | 0.12261 | 0.12261 | 0.98617 | -0.26564 | 0.99006 | -0.19046 | 33.6851
22 | 0.0050678 | 0.0012699 | -0.0050671 | -0.0012698 | 7.1042e-07 | 4.1359e-08 | 0.0076467 | 0.0076468 | 0.0076468 | 0.98617 | -0.26564 | 0.98602 | -0.26859 | 2.1008
23 | 0.076167 | 0.0192 | -0.076046 | -0.019123 | 0.00012101 | 7.7136e-05 | 0.11497 | 0.11497 | 0.11497 | 0.98617 | -0.26564 | 0.98446 | -0.2989 | 31.5844
24 | -0.14857 | -0.037515 | 0.14878 | 0.037651 | 0.00021431 | 0.00013657 | 0.22339 | 0.22339 | 0.22339 | 0.99006 | -0.19046 | 0.99162 | -0.1604 | 30.6852
25 | 0.067037 | 0.016858 | -0.066889 | -0.016764 | 0.00014786 | 9.413e-05 | 0.10077 | 0.10077 | 0.10077 | 0.99006 | -0.19046 | 0.98767 | -0.23675 | 27.6853
26 | 0.0050671 | 0.0012698 | -0.0050666 | -0.0012698 | 5.3917e-07 | 3.1484e-08 | 0.0076468 | 0.0076469 | 0.0076469 | 0.98602 | -0.26859 | 0.9859 | -0.27082 | 2.1008
27 | 0.045405 | 0.011443 | -0.045402 | -0.011441 | 3.2418e-06 | 2.0515e-06 | 0.068653 | 0.068653 | 0.068653 | 0.98446 | -0.2989 | 0.98438 | -0.3004 | 18.8607
28 | -0.16738 | -0.042319 | 0.16745 | 0.042365 | 7.3052e-05 | 4.6395e-05 | 0.2513 | 0.2513 | 0.2513 | 0.99162 | -0.1604 | 0.99209 | -0.1513 | 23.0128
29 | 0.018599 | 0.0046675 | -0.018591 | -0.0046625 | 8.4143e-06 | 5.0138e-06 | 0.027912 | 0.027913 | 0.027913 | 0.99162 | -0.1604 | 0.99113 | -0.16989 | 7.6683
30 | 0.0052241 | 0.001309 | -0.0052226 | -0.0013089 | 1.4463e-06 | 1.2908e-07 | 0.0078705 | 0.0078707 | 0.0078707 | 0.98767 | -0.23675 | 0.98737 | -0.24256 | 2.1623
31 | -0.045383 | -0.011429 | 0.045402 | 0.011441 | 1.8512e-05 | 1.1715e-05 | 0.068653 | 0.068653 | 0.068653 | 0.98394 | -0.30892 | 0.98438 | -0.3004 | 18.8607
32 | 0.045383 | 0.011429 | -0.045345 | -0.011405 | 3.7933e-05 | 2.4005e-05 | 0.068653 | 0.068653 | 0.068653 | 0.98394 | -0.30892 | 0.98304 | -0.32642 | 18.8607
33 | 0.039642 | 0.0099762 | -0.039629 | -0.0099675 | 1.3723e-05 | 8.6541e-06 | 0.060021 | 0.060021 | 0.060021 | 0.98304 | -0.32642 | 0.98267 | -0.33366 | 16.4892
34 | 0.018591 | 0.0046625 | -0.018582 | -0.004657 | 9.1576e-06 | 5.4571e-06 | 0.027913 | 0.027913 | 0.027913 | 0.99113 | -0.16989 | 0.99059 | -0.18023 | 7.6683
35 | -0.012454 | -0.0031229 | 0.012461 | 0.003127 | 7.4336e-06 | 4.0609e-06 | 0.018926 | 0.018926 | 0.018926 | 0.97919 | -0.40177 | 0.97983 | -0.38925 | 5.1994
36 | 0.012454 | 0.0031229 | -0.012448 | -0.0031198 | 5.7003e-06 | 3.1146e-06 | 0.018926 | 0.018926 | 0.018926 | 0.97919 | -0.40177 | 0.9787 | -0.41138 | 5.1995
37 | -0.017617 | -0.0044192 | 0.017621 | 0.0044211 | 3.227e-06 | 1.9139e-06 | 0.026756 | 0.026756 | 0.026756 | 0.97983 | -0.38925 | 0.98003 | -0.38541 | 7.3505
38 | -0.21181 | -0.053481 | 0.21216 | 0.053709 | 0.00035835 | 0.00022824 | 0.31782 | 0.31782 | 0.31782 | 0.99209 | -0.1513 | 0.99392 | -0.11606 | 29.1048
39 | -0.016939 | -0.0042453 | 0.016943 | 0.0042478 | 4.317e-06 | 2.5282e-06 | 0.025287 | 0.025287 | 0.025287 | 0.99676 | -0.061659 | 0.99704 | -0.05631 | 6.947
40 | 0.26417 | 0.067089 | -0.26341 | -0.066606 | 0.00075723 | 0.00048311 | 0.39456 | 0.39456 | 0.39456 | 0.99704 | -0.05631 | 0.99392 | -0.11606 | 36.1323
41 | -0.28111 | -0.071337 | 0.28187 | 0.071824 | 0.00076363 | 0.00048736 | 0.41985 | 0.41985 | 0.41985 | 0.99704 | -0.05631 | 1 | 0 | 38.4479
42 | 0.0093677 | 0.0023493 | -0.0093591 | -0.0023453 | 8.6193e-06 | 4.0854e-06 | 0.014221 | 0.014222 | 0.014222 | 0.9802 | -0.38093 | 0.97921 | -0.40025 | 3.9071
43 | -0.011734 | -0.0029424 | 0.011735 | 0.0029428 | 8.1597e-07 | 4.3578e-07 | 0.017813 | 0.017813 | 0.017813 | 0.9802 | -0.38093 | 0.98027 | -0.37947 | 4.8938
44 | 0.0036317 | 0.00090986 | -0.0036313 | -0.00091008 | 4.8234e-07 | -2.2248e-07 | 0.0055187 | 0.0055189 | 0.0055189 | 0.97921 | -0.40025 | 0.97907 | -0.40303 | 1.5162
45 | -0.014049 | -0.0035228 | 0.01405 | 0.0035235 | 1.1651e-06 | 6.5953e-07 | 0.021327 | 0.021327 | 0.021327 | 0.98027 | -0.37947 | 0.98036 | -0.37773 | 5.859
46 | -0.019948 | -0.005004 | 0.01995 | 0.0050054 | 2.3546e-06 | 1.4202e-06 | 0.030243 | 0.030243 | 0.030243 | 0.98152 | -0.35512 | 0.98164 | -0.35264 | 8.3086
47 | -0.0021787 | -0.00054604 | 0.0021788 | 0.00054594 | 3.7525e-08 | -1.0088e-07 | 0.003242 | 0.003242 | 0.003242 | 0.99998 | -0.00036157 | 1 | 0 | 0.89067
48 | 0.23675 | 0.060777 | -0.23649 | -0.06061 | 0.00026197 | 0.000167 | 0.3528 | 0.3528 | 0.3528 | 1 | 0 | 0.99879 | -0.022825 | 32.3076
49 | 0.08413 | 0.021555 | -0.083856 | -0.021381 | 0.0002737 | 0.00017456 | 0.12535 | 0.12535 | 0.12535 | 1 | 0 | 0.99645 | -0.06737 | 34.4379
50 | -0.021221 | -0.0053203 | 0.021224 | 0.0053219 | 2.6628e-06 | 1.6168e-06 | 0.032117 | 0.032117 | 0.032117 | 0.98324 | -0.3215 | 0.98337 | -0.31886 | 8.8232
51 | -0.060133 | -0.015116 | 0.060155 | 0.01513 | 2.225e-05 | 1.415e-05 | 0.091151 | 0.091151 | 0.091151 | 0.98182 | -0.3491 | 0.98222 | -0.34135 | 25.0416
52 | 0.039629 | 0.0099675 | -0.039595 | -0.0099464 | 3.3501e-05 | 2.1126e-05 | 0.060021 | 0.060021 | 0.060021 | 0.98267 | -0.33366 | 0.98176 | -0.35138 | 16.4892
53 | 0.032559 | 0.0081829 | -0.032528 | -0.0081639 | 3.0392e-05 | 1.903e-05 | 0.049356 | 0.049356 | 0.049356 | 0.98176 | -0.35138 | 0.98076 | -0.37095 | 13.5594
54 | 0.032528 | 0.0081639 | -0.032523 | -0.0081603 | 5.693e-06 | 3.5649e-06 | 0.049356 | 0.049356 | 0.049356 | 0.98076 | -0.37095 | 0.98058 | -0.37462 | 13.5594
55 | 0.0017208 | 0.00043101 | -0.0017208 | -0.00043126 | 5.8219e-08 | -2.4994e-07 | 0.0026112 | 0.0026113 | 0.0026113 | 0.98058 | -0.37462 | 0.98054 | -0.37533 | 0.7174
56 | 0.013172 | 0.0033028 | -0.013169 | -0.0033008 | 3.5355e-06 | 1.9652e-06 | 0.019989 | 0.019989 | 0.019989 | 0.98058 | -0.37462 | 0.98029 | -0.38025 | 5.4916
57 | 0.01763 | 0.0044265 | -0.017621 | -0.0044211 | 9.0697e-06 | 5.3787e-06 | 0.026756 | 0.026756 | 0.026756 | 0.98058 | -0.37462 | 0.98003 | -0.38541 | 7.3505
58 | -0.075895 | -0.019301 | 0.075936 | 0.019327 | 4.1191e-05 | 2.6252e-05 | 0.11378 | 0.11378 | 0.11378 | 0.99338 | -0.12588 | 0.99397 | -0.11462 | 31.2595
59 | 0.075895 | 0.019301 | -0.075617 | -0.019123 | 0.00027799 | 0.00017717 | 0.11378 | 0.11378 | 0.11378 | 0.99338 | -0.12588 | 0.98941 | -0.20221 | 31.2596
60 | -0.076804 | -0.019544 | 0.076838 | 0.019566 | 3.3581e-05 | 2.1404e-05 | 0.11508 | 0.11508 | 0.11508 | 0.99397 | -0.11462 | 0.99444 | -0.10556 | 31.6166
61 | 0.075617 | 0.019123 | -0.075473 | -0.019032 | 0.00014417 | 9.1889e-05 | 0.11378 | 0.11379 | 0.11379 | 0.98941 | -0.20221 | 0.98735 | -0.24204 | 31.2597
62 | 0.080337 | 0.020499 | -0.080298 | -0.020474 | 3.9215e-05 | 2.5003e-05 | 0.1201 | 0.1201 | 0.1201 | 0.99645 | -0.06737 | 0.99592 | -0.077481 | 32.9942
63 | 0.0035191 | 0.00088148 | -0.0035189 | -0.00088161 | 2.2377e-07 | -1.3824e-07 | 0.005255 | 0.0052551 | 0.0052551 | 0.99645 | -0.06737 | 0.99638 | -0.068706 | 1.4437
64 | 0.079493 | 0.020272 | -0.079457 | -0.02025 | 3.5415e-05 | 2.2579e-05 | 0.1189 | 0.1189 | 0.1189 | 0.99592 | -0.077481 | 0.99543 | -0.086712 | 32.6637
65 | 0.0035189 | 0.00088161 | -0.0035188 | -0.00088166 | 7.7221e-08 | -4.7692e-08 | 0.0052551 | 0.0052552 | 0.0052552 | 0.99638 | -0.068706 | 0.99635 | -0.069166 | 1.4437
66 | 0.23447 | 0.060105 | -0.23424 | -0.059959 | 0.00022846 | 0.00014563 | 0.34979 | 0.34979 | 0.34979 | 0.99879 | -0.022825 | 0.99773 | -0.042944 | 32.0325
67 | 0.058098 | 0.014677 | -0.058013 | -0.014623 | 8.5037e-05 | 5.4046e-05 | 0.0876 | 0.0876 | 0.0876 | 0.98735 | -0.24204 | 0.98577 | -0.27262 | 24.066
68 | 0.012014 | 0.0030115 | -0.012014 | -0.0030114 | 2.1511e-07 | 1.1593e-07 | 0.018237 | 0.018237 | 0.018237 | 0.98029 | -0.38025 | 0.98027 | -0.38063 | 5.0102
69 | -0.0036367 | -0.00091117 | 0.0036367 | 0.00091116 | 2.3671e-08 | -1.0898e-08 | 0.0055238 | 0.0055238 | 0.0055238 | 0.97965 | -0.39274 | 0.97966 | -0.3926 | 1.5175
70 | 0.0036367 | 0.00091117 | -0.0036366 | -0.00091124 | 1.548e-07 | -7.1258e-08 | 0.0055238 | 0.0055239 | 0.0055239 | 0.97965 | -0.39274 | 0.97961 | -0.39363 | 1.5175
71 | -0.0048751 | -0.0012215 | 0.0048755 | 0.0012215 | 3.7757e-07 | 1.041e-08 | 0.0074047 | 0.0074046 | 0.0074047 | 0.97966 | -0.3926 | 0.97974 | -0.39098 | 2.0343
72 | 0.0018126 | 0.0004541 | -0.0018125 | -0.00045426 | 4.1473e-08 | -1.5713e-07 | 0.0027532 | 0.0027533 | 0.0027533 | 0.97961 | -0.39363 | 0.97958 | -0.39411 | 0.75639
73 | 0.058013 | 0.014623 | -0.05781 | -0.014494 | 0.00020282 | 0.00012891 | 0.0876 | 0.0876 | 0.0876 | 0.98577 | -0.27262 | 0.98201 | -0.34597 | 24.0661
74 | -0.077647 | -0.019769 | 0.077682 | 0.019791 | 3.4675e-05 | 2.2103e-05 | 0.1163 | 0.1163 | 0.1163 | 0.99444 | -0.10556 | 0.99493 | -0.0963 | 31.9494
75 | 0.078605 | 0.020036 | -0.078569 | -0.020013 | 3.6359e-05 | 2.3179e-05 | 0.11762 | 0.11762 | 0.11762 | 0.99543 | -0.086712 | 0.99493 | -0.0963 | 32.3137
76 | 0.0026562 | 0.00066546 | -0.0026561 | -0.00066552 | 4.0057e-08 | -6.2771e-08 | 0.0039668 | 0.0039669 | 0.0039669 | 0.99635 | -0.069166 | 0.99634 | -0.069483 | 1.0898
77 | 0.23048 | 0.059016 | -0.23029 | -0.058895 | 0.00018906 | 0.0001205 | 0.34418 | 0.34418 | 0.34418 | 0.99773 | -0.042944 | 0.99683 | -0.059893 | 31.5184
78 | 0.0037641 | 0.00094328 | -0.003764 | -0.00094334 | 1.3151e-07 | -6.1155e-08 | 0.0056138 | 0.0056138 | 0.0056138 | 0.99773 | -0.042944 | 0.99769 | -0.043677 | 1.5423
79 | 0.037434 | 0.0093934 | -0.037425 | -0.0093878 | 8.8617e-06 | 5.5789e-06 | 0.056776 | 0.056776 | 0.056776 | 0.98116 | -0.362 | 0.98091 | -0.36696 | 15.5979
80 | -0.051164 | -0.012834 | 0.051217 | 0.012868 | 5.314e-05 | 3.3712e-05 | 0.077598 | 0.077598 | 0.077598 | 0.98116 | -0.362 | 0.98228 | -0.34023 | 21.3182
81 | 0.035025 | 0.0087863 | -0.035018 | -0.0087818 | 7.1712e-06 | 4.5041e-06 | 0.053135 | 0.053135 | 0.053135 | 0.98091 | -0.36696 | 0.98069 | -0.37126 | 14.5976
82 | -0.080136 | -0.020127 | 0.080173 | 0.02015 | 3.7078e-05 | 2.3645e-05 | 0.12141 | 0.12141 | 0.12141 | 0.98228 | -0.34023 | 0.98277 | -0.33054 | 33.3544
83 | 0.028919 | 0.0072585 | -0.028919 | -0.0072584 | 7.9061e-08 | 4.9209e-08 | 0.043812 | 0.043812 | 0.043812 | 0.98228 | -0.34023 | 0.98227 | -0.34029 | 12.0363
84 | 0.032737 | 0.0082102 | -0.032731 | -0.0082063 | 6.2574e-06 | 3.9195e-06 | 0.049675 | 0.049675 | 0.049675 | 0.98069 | -0.37126 | 0.98049 | -0.37527 | 13.6469
85 | -0.082435 | -0.020717 | 0.082475 | 0.020742 | 3.947e-05 | 2.5175e-05 | 0.12484 | 0.12484 | 0.12484 | 0.98277 | -0.33054 | 0.98329 | -0.32052 | 34.2954
86 | 0.026731 | 0.0067101 | -0.026727 | -0.0067074 | 4.4382e-06 | 2.7491e-06 | 0.040498 | 0.040498 | 0.040498 | 0.98227 | -0.34029 | 0.9821 | -0.34377 | 11.1258
87 | 0.030396 | 0.0076211 | -0.030395 | -0.0076203 | 1.3144e-06 | 8.2044e-07 | 0.046131 | 0.046131 | 0.046131 | 0.98049 | -0.37527 | 0.98044 | -0.37618 | 12.6734
88 | -0.084724 | -0.021306 | 0.084801 | 0.021355 | 7.6544e-05 | 4.883e-05 | 0.12824 | 0.12824 | 0.12824 | 0.98329 | -0.32052 | 0.98426 | -0.30162 | 35.2307
89 | 0.024436 | 0.0061334 | -0.024429 | -0.006129 | 7.0768e-06 | 4.355e-06 | 0.037028 | 0.037028 | 0.037028 | 0.9821 | -0.34377 | 0.98179 | -0.34985 | 10.1725
90 | 0.0164 | 0.0041127 | -0.016398 | -0.004112 | 1.2114e-06 | 7.0952e-07 | 0.024891 | 0.024891 | 0.024891 | 0.98044 | -0.37618 | 0.98036 | -0.37773 | 6.8381
91 | 0.00918 | 0.002301 | -0.009179 | -0.0023006 | 9.8858e-07 | 4.5877e-07 | 0.013879 | 0.013879 | 0.013879 | 0.98426 | -0.30162 | 0.98414 | -0.30388 | 3.8128
92 | -0.093981 | -0.023656 | 0.094082 | 0.023721 | 0.00010142 | 6.4742e-05 | 0.14212 | 0.14212 | 0.14212 | 0.98426 | -0.30162 | 0.98542 | -0.27907 | 39.0435
93 | 0.022245 | 0.0055816 | -0.022242 | -0.0055798 | 2.9615e-06 | 1.8075e-06 | 0.033717 | 0.033717 | 0.033717 | 0.98179 | -0.34985 | 0.98164 | -0.35264 | 9.263
94 | 0.0022509 | 0.00056406 | -0.0022509 | -0.00056413 | 2.9556e-08 | -6.6226e-08 | 0.0034165 | 0.0034165 | 0.0034165 | 0.98037 | -0.3776 | 0.98036 | -0.37788 | 0.93859
95 | -0.004512 | -0.0011307 | 0.0045121 | 0.0011307 | 1.1926e-07 | -9.1793e-09 | 0.0068483 | 0.0068483 | 0.0068483 | 0.98037 | -0.3776 | 0.9804 | -0.37705 | 1.8814
96 | -0.0066999 | -0.001679 | 0.0067002 | 0.0016791 | 2.7991e-07 | 8.8113e-08 | 0.010169 | 0.010169 | 0.010169 | 0.9804 | -0.37705 | 0.98044 | -0.37617 | 2.7936
97 | -0.0089893 | -0.0022528 | 0.0089903 | 0.0022533 | 9.8685e-07 | 4.5326e-07 | 0.013643 | 0.013643 | 0.013643 | 0.98044 | -0.37617 | 0.98056 | -0.37387 | 3.7481
98 | -0.011176 | -0.0028011 | 0.011177 | 0.0028014 | 7.4939e-07 | 3.9196e-07 | 0.01696 | 0.01696 | 0.01696 | 0.98056 | -0.37387 | 0.98063 | -0.37246 | 4.6592
99 | 0.010224 | 0.0025627 | -0.01022 | -0.0025607 | 4.0039e-06 | 2.0039e-06 | 0.01552 | 0.01552 | 0.01552 | 0.98027 | -0.38063 | 0.97985 | -0.38885 | 4.2637
100 | -0.007409 | -0.0018561 | 0.0074097 | 0.0018564 | 6.6775e-07 | 2.5024e-07 | 0.011252 | 0.011252 | 0.011252 | 0.97974 | -0.39098 | 0.97984 | -0.38908 | 3.0913
101 | 0.0025336 | 0.00063461 | -0.0025336 | -0.00063462 | 6.4003e-09 | -1.0421e-08 | 0.0038478 | 0.0038478 | 0.0038478 | 0.97974 | -0.39098 | 0.97974 | -0.39103 | 1.0571
102 | -0.0087311 | -0.0021876 | 0.0087312 | 0.0021876 | 9.6052e-08 | 4.3122e-08 | 0.013259 | 0.013259 | 0.013259 | 0.97984 | -0.38908 | 0.97985 | -0.38885 | 3.6426
103 | 0.0011768 | 0.00029457 | -0.0011767 | -0.00029491 | 3.4761e-08 | -3.4322e-07 | 0.0017871 | 0.0017872 | 0.0017872 | 0.97974 | -0.39103 | 0.97971 | -0.39165 | 0.491
104 | -0.0017599 | -0.00044098 | 0.0017599 | 0.0004409 | 1.7889e-08 | -7.8481e-08 | 0.0026284 | 0.0026283 | 0.0026284 | 0.99633 | -0.069696 | 0.99634 | -0.069483 | 0.72207
105 | 0.00086557 | 0.00021684 | -0.00086556 | -0.00021693 | 4.2563e-09 | -8.5728e-08 | 0.0012927 | 0.0012927 | 0.0012927 | 0.99633 | -0.069696 | 0.99632 | -0.0698 | 0.35514
106 | -0.22184 | -0.056484 | 0.22216 | 0.056687 | 0.00031971 | 0.00020371 | 0.33269 | 0.33269 | 0.33269 | 0.99315 | -0.1301 | 0.99471 | -0.10026 | 30.4662
107 | 0.22184 | 0.056484 | -0.22156 | -0.056309 | 0.00027373 | 0.00017442 | 0.33269 | 0.33269 | 0.33269 | 0.99315 | -0.1301 | 0.99181 | -0.15572 | 30.4662
108 | 0.0018013 | 0.00045135 | -0.0018012 | -0.00045143 | 2.0813e-08 | -8.5908e-08 | 0.0026945 | 0.0026946 | 0.0026946 | 0.99471 | -0.10026 | 0.9947 | -0.1005 | 0.74026
109 | -0.22396 | -0.057139 | 0.22401 | 0.05717 | 4.9844e-05 | 3.1762e-05 | 0.33538 | 0.33538 | 0.33538 | 0.99471 | -0.10026 | 0.99495 | -0.095655 | 30.7129
110 | 0.2196 | 0.055817 | -0.2195 | -0.055755 | 9.7052e-05 | 6.1837e-05 | 0.32975 | 0.32975 | 0.32975 | 0.99181 | -0.15572 | 0.99133 | -0.1649 | 30.1966
111 | -0.22401 | -0.05717 | 0.2242 | 0.05729 | 0.00018835 | 0.00012002 | 0.33538 | 0.33538 | 0.33538 | 0.99495 | -0.095655 | 0.99587 | -0.078267 | 30.7129
112 | -0.22609 | -0.057766 | 0.22619 | 0.057829 | 9.8372e-05 | 6.2689e-05 | 0.33822 | 0.33822 | 0.33822 | 0.99587 | -0.078267 | 0.99634 | -0.069274 | 30.9724
113 | 0.034977 | 0.0087716 | -0.034963 | -0.0087625 | 1.4476e-05 | 9.091e-06 | 0.053002 | 0.053002 | 0.053002 | 0.98201 | -0.34597 | 0.98156 | -0.35466 | 14.5611
114 | 0.0073078 | 0.0018316 | -0.0073067 | -0.0018312 | 1.0966e-06 | 3.9751e-07 | 0.011049 | 0.011049 | 0.011049 | 0.98414 | -0.30388 | 0.98398 | -0.30703 | 3.0356
115 | -0.096044 | -0.024212 | 0.0961 | 0.024248 | 5.6346e-05 | 3.597e-05 | 0.14508 | 0.14508 | 0.14508 | 0.98542 | -0.27907 | 0.98605 | -0.26682 | 39.8571
116 | -0.0020553 | -0.00051511 | 0.0020553 | 0.00051504 | 2.5778e-08 | -7.44e-08 | 0.0031038 | 0.0031037 | 0.0031038 | 0.98537 | -0.28008 | 0.98538 | -0.27982 | 0.85268
117 | -0.0040866 | -0.0010241 | 0.0040867 | 0.0010241 | 1.0198e-07 | -2.5701e-08 | 0.0061712 | 0.0061711 | 0.0061712 | 0.98538 | -0.27982 | 0.98541 | -0.27929 | 1.6954
118 | -0.22815 | -0.05832 | 0.22826 | 0.058386 | 0.00010358 | 6.6013e-05 | 0.34115 | 0.34115 | 0.34115 | 0.99634 | -0.069274 | 0.99683 | -0.059893 | 31.2409
119 | 0.21747 | 0.055247 | -0.21729 | -0.055126 | 0.00018869 | 0.00012022 | 0.3267 | 0.3267 | 0.3267 | 0.99133 | -0.1649 | 0.99039 | -0.18294 | 29.9176
120 | -0.09813 | -0.024757 | 0.098189 | 0.024795 | 5.8758e-05 | 3.7514e-05 | 0.14814 | 0.14814 | 0.14814 | 0.98605 | -0.26682 | 0.98669 | -0.25432 | 40.6987
121 | -0.10015 | -0.025286 | 0.10021 | 0.025324 | 5.907e-05 | 3.7717e-05 | 0.1511 | 0.1511 | 0.1511 | 0.98669 | -0.25432 | 0.98733 | -0.24202 | 41.511
122 | -0.10211 | -0.025799 | 0.10221 | 0.025866 | 0.00010469 | 6.685e-05 | 0.15396 | 0.15396 | 0.15396 | 0.98733 | -0.24202 | 0.98843 | -0.22065 | 42.2962
123 | 0.0055131 | 0.0013817 | -0.0055129 | -0.0013817 | 1.3768e-07 | 2.1022e-08 | 0.0083371 | 0.0083371 | 0.0083371 | 0.98398 | -0.30703 | 0.98395 | -0.30756 | 2.2904
124 | 0.11272 | 0.02852 | -0.1127 | -0.028507 | 1.9947e-05 | 1.2742e-05 | 0.16979 | 0.16979 | 0.16979 | 0.98843 | -0.22065 | 0.98824 | -0.22434 | 46.6465
125 | -0.21493 | -0.054385 | 0.21519 | 0.05455 | 0.00025772 | 0.0001646 | 0.32375 | 0.32375 | 0.32375 | 0.98843 | -0.22065 | 0.98973 | -0.1957 | 44.4713
126 | -0.006049 | -0.0015159 | 0.0060492 | 0.0015159 | 2.158e-07 | 5.0243e-08 | 0.0091343 | 0.0091342 | 0.0091343 | 0.98541 | -0.27929 | 0.98545 | -0.27854 | 2.5094
127 | -0.0079458 | -0.0019913 | 0.0079461 | 0.0019914 | 3.5713e-07 | 1.4428e-07 | 0.011998 | 0.011998 | 0.011998 | 0.98545 | -0.27854 | 0.98549 | -0.2776 | 3.2962
128 | -0.0097493 | -0.0024433 | 0.0097499 | 0.0024436 | 6.3146e-07 | 3.0512e-07 | 0.014721 | 0.014721 | 0.014721 | 0.98549 | -0.2776 | 0.98556 | -0.27624 | 4.0441
129 | -0.10497 | -0.026463 | 0.10503 | 0.026501 | 5.8776e-05 | 3.7537e-05 | 0.15854 | 0.15854 | 0.15854 | 0.98556 | -0.27624 | 0.98617 | -0.26455 | 43.5541
130 | 0.095218 | 0.024019 | -0.095211 | -0.024015 | 6.8647e-06 | 4.3822e-06 | 0.14382 | 0.14382 | 0.14382 | 0.98556 | -0.27624 | 0.98549 | -0.27775 | 39.51
131 | -0.10699 | -0.026993 | 0.10706 | 0.027036 | 6.7313e-05 | 4.2992e-05 | 0.1615 | 0.1615 | 0.1615 | 0.98617 | -0.26455 | 0.98684 | -0.25142 | 44.3684
132 | 0.093181 | 0.023506 | -0.093085 | -0.023445 | 9.5909e-05 | 6.1218e-05 | 0.14075 | 0.14075 | 0.14075 | 0.98549 | -0.27775 | 0.98438 | -0.29927 | 38.6678
133 | -0.10895 | -0.027511 | 0.109 | 0.02754 | 4.5766e-05 | 2.9233e-05 | 0.16436 | 0.16436 | 0.16436 | 0.98684 | -0.25142 | 0.9873 | -0.24265 | 45.1535
134 | 0.001959 | 0.0004909 | -0.001959 | -0.00049096 | 2.0872e-08 | -6.7329e-08 | 0.0029612 | 0.0029613 | 0.0029613 | 0.98438 | -0.29927 | 0.98437 | -0.29949 | 0.81354
135 | 0.091126 | 0.022954 | -0.091079 | -0.022924 | 4.6884e-05 | 2.9922e-05 | 0.13779 | 0.13779 | 0.13779 | 0.98438 | -0.29927 | 0.98383 | -0.31003 | 37.8543
136 | -0.21715 | -0.055042 | 0.21729 | 0.055126 | 0.00013321 | 8.4869e-05 | 0.3267 | 0.3267 | 0.3267 | 0.98973 | -0.1957 | 0.99039 | -0.18294 | 29.9176
137 | 0.1127 | 0.028507 | -0.11263 | -0.028458 | 7.6849e-05 | 4.9092e-05 | 0.16979 | 0.16979 | 0.16979 | 0.98824 | -0.22434 | 0.98751 | -0.23856 | 46.6465
138 | 0.11082 | 0.028006 | -0.1108 | -0.027992 | 2.1714e-05 | 1.387e-05 | 0.16708 | 0.16708 | 0.16708 | 0.98751 | -0.23856 | 0.9873 | -0.24265 | 45.9001
139 | 0.089142 | 0.022439 | -0.089108 | -0.022417 | 3.4597e-05 | 2.2078e-05 | 0.13486 | 0.13486 | 0.13486 | 0.98383 | -0.31003 | 0.98341 | -0.31815 | 37.0497
140 | -0.062117 | -0.015622 | 0.06214 | 0.015637 | 2.2914e-05 | 1.4578e-05 | 0.094124 | 0.094124 | 0.094124 | 0.98222 | -0.34135 | 0.98261 | -0.33363 | 25.8583
141 | -0.064037 | -0.016112 | 0.06406 | 0.016127 | 2.3341e-05 | 1.4855e-05 | 0.096996 | 0.096996 | 0.096996 | 0.98261 | -0.33363 | 0.98301 | -0.32601 | 26.6473
142 | -0.065863 | -0.016579 | 0.065888 | 0.016594 | 2.4724e-05 | 1.5739e-05 | 0.099726 | 0.099726 | 0.099726 | 0.98301 | -0.32601 | 0.98341 | -0.31815 | 27.3972
143 | 0.02322 | 0.0058224 | -0.023219 | -0.0058219 | 7.8556e-07 | 4.8123e-07 | 0.035135 | 0.035135 | 0.035135 | 0.98341 | -0.31815 | 0.98337 | -0.31886 | 9.6526
144 | -0.0019622 | -0.00049178 | 0.0019622 | 0.00049178 | 4.574e-10 | -1.5689e-09 | 0.0029266 | 0.0029266 | 0.0029266 | 0.99769 | -0.043682 | 0.99769 | -0.043677 | 0.80401

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60658 | 0.1547

## res_load
| p_mw | q_mvar
0 | 0.036442 | 0.0091333
1 | 0.015171 | 0.0038021
2 | 0.014811 | 0.0037119
3 | 0.021124 | 0.0052942
4 | 0.0022029 | 0.00055209
5 | 0.017288 | 0.0043328
6 | 0.0019269 | 0.00048294
7 | 0.0020553 | 0.00051511
8 | 0.0021331 | 0.00053462
9 | 0.0097405 | 0.0024412
10 | 0.0097432 | 0.0024419
11 | 0.030641 | 0.0076794
12 | 0.061665 | 0.015455
13 | 0.0057029 | 0.0014293
14 | 0.018582 | 0.004657
15 | 0.0051562 | 0.0012923
16 | 0.012448 | 0.0031198
17 | 0.044353 | 0.011116
18 | 0.016939 | 0.0042453
19 | 0.0023661 | 0.000593
20 | 0.0057273 | 0.0014354
21 | 0.0023145 | 0.00058006
22 | 0.0021316 | 0.00053422
23 | 0.0021787 | 0.00054604
24 | 0.0020012 | 0.00050156
25 | 0.0020313 | 0.00050909
26 | 0.0070364 | 0.0017635
27 | 0.0050666 | 0.0012698
28 | 0.0052226 | 0.0013089
29 | 0.00086809 | 0.00021756
30 | 0.00080525 | 0.00020181
31 | 0.002017 | 0.0005055
32 | 0.017375 | 0.0043545
33 | 0.0017208 | 0.00043126
34 | 0.0011545 | 0.00028933
35 | 0.0012383 | 0.00031036
36 | 0.001824 | 0.00045714
37 | 0.00080962 | 0.00020291
38 | 0.00085211 | 0.00021356
39 | 0.00086265 | 0.0002162
40 | 0.0036313 | 0.00091008
41 | 0.013729 | 0.0034409
42 | 0.0024001 | 0.00060151
43 | 0.0022808 | 0.00057161
44 | 0.0022622 | 0.00056697
45 | 0.0021877 | 0.00054829
46 | 0.002335 | 0.0005852
47 | 0.0022497 | 0.00056383
48 | 0.0022903 | 0.00057401
49 | 0.013995 | 0.0035075
50 | 0.0021842 | 0.00054742
51 | 0.0022611 | 0.00056668
52 | 0.0022509 | 0.00056413
53 | 0.0021878 | 0.00054831
54 | 0.0022891 | 0.00057371
55 | 0.0021856 | 0.00054775
56 | 0.0022907 | 0.0005741
57 | 0.0023482 | 0.00058851
58 | 0.0017901 | 0.00044864
59 | 0.0018125 | 0.00045426
60 | 0.0013214 | 0.00033117
61 | 0.0013568 | 0.00034005
62 | 0.0014887 | 0.00037312
63 | 0.0011767 | 0.00029491
64 | 0.00089431 | 0.00022414
65 | 0.00089625 | 0.00022462
66 | 0.00086556 | 0.00021693
67 | 0.0019622 | 0.00049177
68 | 0.0018971 | 0.00047545
69 | 0.022833 | 0.0057225
70 | 0.00088686 | 0.00022227
71 | 0.0018712 | 0.00046898
72 | 0.0019613 | 0.00049155
73 | 0.0020553 | 0.00051511
74 | 0.0020313 | 0.00050908
75 | 0.034963 | 0.0087625
76 | 0.0018012 | 0.00045143
77 | 0.0019629 | 0.00049194
78 | 0.0020301 | 0.00050879
79 | 0.00203 | 0.00050876
80 | 0.0019607 | 0.00049141
81 | 0.0018965 | 0.00047532
82 | 0.0017936 | 0.00044953
83 | 0.0055129 | 0.0013817
84 | 0.0019623 | 0.00049179
85 | 0.0018965 | 0.00047532
86 | 0.0018032 | 0.00045192
87 | 0.0019643 | 0.00049229
88 | 0.0020303 | 0.00050884
89 | 0.0018954 | 0.00047503
90 | 0.0019613 | 0.00049155
91 | 0.0018029 | 0.00045186
92 | 0.0018032 | 0.00045192
93 | 0.0022918 | 0.00057439
94 | 0.001959 | 0.00049096
95 | 0.0019364 | 0.0004853
96 | 0.0019623 | 0.0004918
97 | 0.0018965 | 0.00047532
98 | 0.0018032 | 0.00045192
99 | 0.0019622 | 0.00049178
100 | 0.0018017 | 0.00045156
101 | 0.001995 | 0.0005
102 | 0.0020303 | 0.00050884

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1