## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_247-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_247-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_247-2_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_247-2_0_5_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_247-2_0_5_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_247-2_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_247-2_0_5_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_247-2_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_247-2_0_5_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_247-2_0_5_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_247-2_0_5_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_247-2_0_5_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_247-2_0_5_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_247-2_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_247-2_0_5_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_247-2_0_5_node_50 | 0.4 | n |  | TRUE
16 | bus_LV_247-2_0_5_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_247-2_0_5_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_247-2_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_247-2_0_5_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_247-2_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_247-2_0_5_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_247-2_0_5_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_247-2_0_5_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_247-2_0_5_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_247-2_0_5_node_41 | 0.4 | n |  | TRUE
26 | bus_LV_247-2_0_5_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_247-2_0_5_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_247-2_0_5_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_247-2_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_247-2_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_247-2_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_247-2_0_5_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_247-2_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_247-2_0_5_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_247-2_0_5_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_247-2_0_5_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_247-2_0_5_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_247-2_0_5_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_247-2_0_5_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_247-2_0_5_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_247-2_0_5_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_247-2_0_5_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_247-2_0_5_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_247-2_0_5_node_45 | 0.4 | n |  | TRUE
45 | bus_MV_514_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_247-2_0_5_load_0 | 0 | 0.094639 | 0.023719 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_247-2_0_5_load_49 | 8 | 0.003529 | 0.00088444 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_247-2_0_5_load_48 | 9 | 0.00128 | 0.0003208 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_247-2_0_5_load_47 | 10 | 0.0021546 | 0.00053999 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_247-2_0_5_load_24 | 11 | 0.0089964 | 0.0022547 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_247-2_0_5_load_13 | 14 | 0.01915 | 0.0047994 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_247-2_0_5_load_50 | 15 | 0.020794 | 0.0052116 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_247-2_0_5_load_15 | 17 | 0.0033417 | 0.0008375 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_247-2_0_5_load_12 | 18 | 0.051243 | 0.012843 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_247-2_0_5_load_22 | 19 | 0.099487 | 0.024934 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_247-2_0_5_load_14 | 20 | 0.08299 | 0.020799 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_247-2_0_5_load_16 | 21 | 0.018144 | 0.0045473 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_247-2_0_5_load_17 | 22 | 0.01556 | 0.0038997 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_247-2_0_5_load_18 | 23 | 0.00057493 | 0.00014409 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_247-2_0_5_load_23 | 24 | 0.0026476 | 0.00066354 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_247-2_0_5_load_41 | 25 | 0.0054132 | 0.0013567 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_247-2_0_5_load_42 | 26 | 0.0018941 | 0.0004747 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_247-2_0_5_load_43 | 27 | 0.0053361 | 0.0013373 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_247-2_0_5_load_21 | 28 | 0.051326 | 0.012864 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_247-2_0_5_load_20 | 29 | 0.0462 | 0.011579 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_247-2_0_5_load_25 | 30 | 0.0056734 | 0.0014219 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_247-2_0_5_load_26 | 31 | 0.00084825 | 0.00021259 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_247-2_0_5_load_27 | 32 | 0.00080662 | 0.00020216 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_247-2_0_5_load_28 | 33 | 0.042518 | 0.010656 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_247-2_0_5_load_30 | 35 | 0.001961 | 0.00049148 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_247-2_0_5_load_33 | 37 | 0.00084693 | 0.00021226 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_247-2_0_5_load_31 | 38 | 0.0020297 | 0.00050869 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_247-2_0_5_load_44 | 40 | 0.0018043 | 0.0004522 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_247-2_0_5_load_35 | 42 | 0.0096554 | 0.0024199 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_247-2_0_5_load_46 | 43 | 0.00083443 | 0.00020913 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_247-2_0_5_load_45 | 44 | 0.0019601 | 0.00049124 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_247-2_0_5_line_0 |  | 0 | 1 | 0.011703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_247-2_0_5_line_1 |  | 0 | 2 | 0.0049619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_247-2_0_5_line_2 |  | 1 | 3 | 0.31576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_247-2_0_5_line_3 |  | 1 | 4 | 0.22456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_247-2_0_5_line_4 |  | 2 | 5 | 0.21662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_247-2_0_5_line_5 |  | 3 | 11 | 0.0025816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_247-2_0_5_line_6 |  | 4 | 12 | 0.029811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_247-2_0_5_line_7 |  | 4 | 8 | 0.038288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_247-2_0_5_line_8 |  | 5 | 13 | 0.13268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_247-2_0_5_line_9 |  | 5 | 14 | 0.058023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_247-2_0_5_line_10 |  | 6 | 7 | 0.16081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_247-2_0_5_line_11 |  | 6 | 8 | 0.11376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_247-2_0_5_line_12 |  | 7 | 9 | 0.04087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_247-2_0_5_line_13 |  | 7 | 10 | 0.050152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_247-2_0_5_line_14 |  | 12 | 15 | 0.001785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_247-2_0_5_line_15 |  | 13 | 16 | 0.00414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_247-2_0_5_line_16 |  | 13 | 17 | 0.074896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_247-2_0_5_line_17 |  | 14 | 18 | 0.027616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_247-2_0_5_line_18 |  | 16 | 19 | 0.028602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_247-2_0_5_line_19 |  | 17 | 20 | 0.00096652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_247-2_0_5_line_20 |  | 19 | 28 | 0.023061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_247-2_0_5_line_21 |  | 20 | 21 | 0.034925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_247-2_0_5_line_22 |  | 21 | 22 | 0.048063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_247-2_0_5_line_23 |  | 22 | 23 | 0.012687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_247-2_0_5_line_24 |  | 23 | 24 | 0.0042056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_247-2_0_5_line_25 |  | 25 | 26 | 0.02446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_247-2_0_5_line_26 |  | 26 | 27 | 0.0061901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_247-2_0_5_line_27 |  | 27 | 39 | 0.0066961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_247-2_0_5_line_28 |  | 28 | 29 | 0.015781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_247-2_0_5_line_29 |  | 29 | 30 | 0.090264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_247-2_0_5_line_30 |  | 30 | 31 | 0.014495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_247-2_0_5_line_31 |  | 30 | 32 | 0.0099328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_247-2_0_5_line_32 |  | 31 | 33 | 0.0052718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_247-2_0_5_line_33 |  | 32 | 34 | 0.013585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_247-2_0_5_line_34 |  | 33 | 35 | 0.0016269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_247-2_0_5_line_35 |  | 34 | 36 | 0.007815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_247-2_0_5_line_36 |  | 34 | 37 | 0.0062821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_247-2_0_5_line_37 |  | 35 | 38 | 0.0071394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_247-2_0_5_line_38 |  | 36 | 43 | 0.0077751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_247-2_0_5_line_39 |  | 37 | 41 | 0.015026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_247-2_0_5_line_40 |  | 38 | 39 | 0.013688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_247-2_0_5_line_41 |  | 39 | 40 | 0.0097589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_247-2_0_5_line_42 |  | 40 | 44 | 0.00020821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_247-2_0_5_line_43 |  | 41 | 42 | 0.033647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_247-2_0_5_trafo_11 | 0.63 MVA 20/0.4 kV | 45 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2675183.6851 | 1250370.2896 | 2675193.931 | 1250364.6335
1 | 2675198.2749 | 1250362.2354 | 2675193.931 | 1250364.6335
2 | 2675014.113 | 1250325.0752 | 2675029.1111 | 1250336.0397 | 2675043.3333 | 1250345.0818 | 2675048.1943 | 1250348.1345 | 2675029.1747 | 1250374.5351 | 2675025.386 | 1250379.8021 | 2675031.9852 | 1250384.5001 | 2675035.3028 | 1250387.8112 | 2675041.6632 | 1250392.295 | 2675075.7184 | 1250416.7773 | 2675091.444 | 1250415.5867 | 2675102.6538 | 1250414.4946 | 2675112.1421 | 1250415.2042 | 2675126.5486 | 1250415.0422 | 2675143.3718 | 1250413.621 | 2675147.2032 | 1250414.5147 | 2675156.2817 | 1250414.1962 | 2675165.9146 | 1250414.2184 | 2675186.6938 | 1250412.2026 | 2675191.9856 | 1250411.0467 | 2675201.0665 | 1250410.5504 | 2675200.5502 | 1250394.7212 | 2675197.2872 | 1250394.8466 | 2675183.6851 | 1250370.2896
3 | 2675183.6851 | 1250370.2896 | 2675197.2872 | 1250394.8466 | 2675200.5502 | 1250394.7212 | 2675201.0665 | 1250410.5504 | 2675191.9856 | 1250411.0467 | 2675186.6938 | 1250412.2026 | 2675177.2096 | 1250417.7197 | 2675167.7898 | 1250430.6541 | 2675156.3382 | 1250446.0423 | 2675147.4605 | 1250457.905 | 2675155.2367 | 1250463.8413 | 2675154.3765 | 1250466.1876 | 2675153.7559 | 1250469.282 | 2675155.2001 | 1250473.2699 | 2675159.0075 | 1250477.8326 | 2675177.1866 | 1250492.1068 | 2675219.8072 | 1250523.8817
4 | 2675198.2749 | 1250362.2354 | 2675214.4616 | 1250391.9402 | 2675225.5952 | 1250386.1439 | 2675228.7836 | 1250391.8996 | 2675232.6734 | 1250391.1596 | 2675236.6533 | 1250391.6549 | 2675260.5864 | 1250402.2664 | 2675266.1844 | 1250409.098 | 2675279.4569 | 1250409.0665 | 2675302.5395 | 1250408.7706 | 2675349.3164 | 1250408.1756 | 2675372.2165 | 1250409.7679 | 2675386.7494 | 1250410.9535
5 | 2675014.113 | 1250325.0752 | 2675012.0298 | 1250323.5505
6 | 2675219.8072 | 1250523.8817 | 2675226.2495 | 1250517.1363 | 2675233.2503 | 1250511.5878 | 2675239.6631 | 1250508.945 | 2675239.6166 | 1250504.2855
7 | 2675219.8072 | 1250523.8817 | 2675246.8385 | 1250544.9178 | 2675250.0252 | 1250547.3948
8 | 2675351.6361 | 1250313.0582 | 2675349.3164 | 1250408.1756 | 2675372.2165 | 1250409.7679 | 2675386.7494 | 1250410.9535
9 | 2675386.7494 | 1250410.9535 | 2675424.5235 | 1250414.2142 | 2675444.5104 | 1250416.423
10 | 2675213.2554 | 1250552.3414 | 2675237.4319 | 1250568.7046 | 2675247.1127 | 1250555.4289 | 2675263.1798 | 1250567.7418 | 2675271.9533 | 1250574.1801 | 2675300.6334 | 1250593.7586 | 2675310.1741 | 1250596.2594 | 2675320.5067 | 1250603.5738 | 2675326.2794 | 1250605.5486 | 2675330.9708 | 1250608.2546 | 2675339.8445 | 1250615.7173 | 2675342.5639 | 1250613.2056
11 | 2675342.5639 | 1250613.2056 | 2675331.8936 | 1250603.9632 | 2675325.3984 | 1250599.4329 | 2675318.9611 | 1250595.6929 | 2675309.0186 | 1250589.7622 | 2675282.7434 | 1250572.8273 | 2675250.0252 | 1250547.3948
12 | 2675213.2554 | 1250552.3414 | 2675211.4106 | 1250547.8036 | 2675191.0344 | 1250532.3784 | 2675184.9715 | 1250540.8466
13 | 2675213.2554 | 1250552.3414 | 2675211.4106 | 1250547.8036 | 2675191.0344 | 1250532.3784 | 2675179.5677 | 1250548.3942
14 | 2675237.8269 | 1250504.3183 | 2675239.6166 | 1250504.2855
15 | 2675351.6361 | 1250313.0582 | 2675348.4768 | 1250310.3716
16 | 2675351.6361 | 1250313.0582 | 2675426.2399 | 1250319.6675
17 | 2675471.9589 | 1250419.4565 | 2675444.5104 | 1250416.423
18 | 2675348.4768 | 1250310.3716 | 2675341.4269 | 1250309.6593 | 2675328.5321 | 1250308.4723 | 2675326.501 | 1250305.5222 | 2675326.799 | 1250300.5463
19 | 2675427.2026 | 1250319.7528 | 2675426.2399 | 1250319.6675
20 | 2675326.799 | 1250300.5463 | 2675328.1779 | 1250277.5264
21 | 2675427.2026 | 1250319.7528 | 2675461.7055 | 1250314.3418
22 | 2675461.7055 | 1250314.3418 | 2675509.6111 | 1250318.2231
23 | 2675509.6111 | 1250318.2231 | 2675520.2638 | 1250319.0861 | 2675522.2536 | 1250319.2859
24 | 2675526.4381 | 1250319.7061 | 2675522.2536 | 1250319.2859
25 | 2675459.3307 | 1250196.7862 | 2675435.0408 | 1250193.9073
26 | 2675435.0408 | 1250193.9073 | 2675428.8937 | 1250193.1787
27 | 2675422.2442 | 1250192.3906 | 2675428.8937 | 1250193.1787
28 | 2675329.1214 | 1250261.7739 | 2675328.1779 | 1250277.5264
29 | 2675329.1214 | 1250261.7739 | 2675380.3152 | 1250187.4315
30 | 2675380.3152 | 1250187.4315 | 2675380.3152 | 1250187.4315 | 2675394.7097 | 1250189.134
31 | 2675380.3152 | 1250187.4315 | 2675381.6681 | 1250177.5913
32 | 2675394.7097 | 1250189.134 | 2675399.945 | 1250189.7532
33 | 2675383.5184 | 1250164.1331 | 2675381.6681 | 1250177.5913
34 | 2675401.5606 | 1250189.9443 | 2675399.945 | 1250189.7532
35 | 2675383.5184 | 1250164.1331 | 2675391.3061 | 1250165.0217
36 | 2675383.5184 | 1250164.1331 | 2675381.0084 | 1250163.8121 | 2675377.2871 | 1250163.3359
37 | 2675401.5606 | 1250189.9443 | 2675408.6507 | 1250190.7829
38 | 2675391.3061 | 1250165.0217 | 2675393.0772 | 1250157.451
39 | 2675362.383 | 1250161.4291 | 2675377.2871 | 1250163.3359
40 | 2675422.2442 | 1250192.3906 | 2675408.6507 | 1250190.7829
41 | 2675422.2442 | 1250192.3906 | 2675423.4261 | 1250182.7036
42 | 2675423.4513 | 1250182.4969 | 2675423.4261 | 1250182.7036
43 | 2675362.383 | 1250161.4291 | 2675352.1463 | 1250160.1758 | 2675328.9368 | 1250157.7678

## bus_geodata
| x | y | coords
0 | 2675193.931 | 1250364.6335
1 | 2675183.6851 | 1250370.2896
2 | 2675198.2749 | 1250362.2354
3 | 2675014.113 | 1250325.0752
4 | 2675219.8072 | 1250523.8817
5 | 2675386.7494 | 1250410.9535
6 | 2675342.5639 | 1250613.2055
7 | 2675213.2554 | 1250552.3414
8 | 2675250.0252 | 1250547.3948
9 | 2675184.9715 | 1250540.8466
10 | 2675179.5677 | 1250548.3942
11 | 2675012.0298 | 1250323.5505
12 | 2675239.6166 | 1250504.2855
13 | 2675351.6361 | 1250313.0582
14 | 2675444.5104 | 1250416.423
15 | 2675237.8269 | 1250504.3183
16 | 2675348.4768 | 1250310.3716
17 | 2675426.2399 | 1250319.6675
18 | 2675471.9589 | 1250419.4565
19 | 2675326.799 | 1250300.5463
20 | 2675427.2026 | 1250319.7528
21 | 2675461.7055 | 1250314.3418
22 | 2675509.6111 | 1250318.2231
23 | 2675522.2536 | 1250319.2859
24 | 2675526.4381 | 1250319.7061
25 | 2675459.3307 | 1250196.7862
26 | 2675435.0408 | 1250193.9073
27 | 2675428.8937 | 1250193.1787
28 | 2675328.1779 | 1250277.5264
29 | 2675329.1214 | 1250261.7739
30 | 2675380.3152 | 1250187.4315
31 | 2675394.7097 | 1250189.134
32 | 2675381.6681 | 1250177.5913
33 | 2675399.945 | 1250189.7532
34 | 2675383.5184 | 1250164.1331
35 | 2675401.5606 | 1250189.9443
36 | 2675391.3061 | 1250165.0217
37 | 2675377.2871 | 1250163.3359
38 | 2675408.6507 | 1250190.7829
39 | 2675422.2442 | 1250192.3906
40 | 2675423.4261 | 1250182.7036
41 | 2675362.383 | 1250161.4291
42 | 2675328.9368 | 1250157.7678
43 | 2675393.0772 | 1250157.451
44 | 2675423.4513 | 1250182.4969
45 | 2675348.4768 | 1250310.3716

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97397 | -0.50024 | 0.094639 | 0.023719
1 | 0.97377 | -0.5042 | 0 | 0
2 | 0.97428 | -0.49425 | 0 | 0
3 | 0.97112 | -0.55659 | 0 | 0
4 | 0.97086 | -0.56172 | 0 | 0
5 | 0.98755 | -0.23635 | 0 | 0
6 | 0.97055 | -0.56783 | 0 | 0
7 | 0.9703 | -0.57295 | 0 | 0
8 | 0.97074 | -0.5642 | 0.003529 | 0.00088444
9 | 0.97025 | -0.57392 | 0.00128 | 0.0003208
10 | 0.9702 | -0.57495 | 0.0021546 | 0.00053999
11 | 0.9711 | -0.55702 | 0.0089964 | 0.0022547
12 | 0.97028 | -0.57319 | 0 | 0
13 | 1 | 0 | -0.61298 | -0.15617
14 | 0.98378 | -0.30962 | 0.01915 | 0.0047994
15 | 0.97025 | -0.57388 | 0.020794 | 0.0052116
16 | 0.99947 | -0.010057 | 0 | 0
17 | 0.99155 | -0.16228 | 0.0033417 | 0.0008375
18 | 0.98247 | -0.33514 | 0.051243 | 0.012843
19 | 0.99583 | -0.079829 | 0.099487 | 0.024934
20 | 0.99144 | -0.16433 | 0.08299 | 0.020799
21 | 0.99026 | -0.18723 | 0.018144 | 0.0045473
22 | 0.98944 | -0.20329 | 0.01556 | 0.0038997
23 | 0.9894 | -0.20402 | 0.00057493 | 0.00014409
24 | 0.98939 | -0.20421 | 0.0026476 | 0.00066354
25 | 0.98353 | -0.31747 | 0.0054132 | 0.0013567
26 | 0.98366 | -0.31509 | 0.0018941 | 0.0004747
27 | 0.9837 | -0.31427 | 0.0053361 | 0.0013373
28 | 0.99393 | -0.1162 | 0.051326 | 0.012864
29 | 0.99208 | -0.15184 | 0.0462 | 0.011579
30 | 0.98529 | -0.28316 | 0.0056734 | 0.0014219
31 | 0.98444 | -0.29977 | 0.00084825 | 0.00021259
32 | 0.98518 | -0.28533 | 0.00080662 | 0.00020216
33 | 0.98414 | -0.30574 | 0.042518 | 0.010656
34 | 0.98504 | -0.28809 | 0 | 0
35 | 0.9841 | -0.30633 | 0.001961 | 0.00049148
36 | 0.98503 | -0.28821 | 0 | 0
37 | 0.98498 | -0.28928 | 0.00084693 | 0.00021226
38 | 0.98398 | -0.3087 | 0.0020297 | 0.00050869
39 | 0.98378 | -0.31275 | 0 | 0
40 | 0.98374 | -0.31341 | 0.0018043 | 0.0004522
41 | 0.98485 | -0.29188 | 0 | 0
42 | 0.98455 | -0.29772 | 0.0096554 | 0.0024199
43 | 0.98503 | -0.28833 | 0.00083443 | 0.00020913
44 | 0.98374 | -0.31342 | 0.0019601 | 0.00049124
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.036875 | 0.0092696 | -0.036868 | -0.0092654 | 6.9671e-06 | 4.1677e-06 | 0.056347 | 0.056347 | 0.056347 | 0.97397 | -0.50024 | 0.97377 | -0.5042 | 7.7399
1 | -0.13151 | -0.032988 | 0.13155 | 0.033012 | 3.7563e-05 | 2.3916e-05 | 0.20093 | 0.20093 | 0.20093 | 0.97397 | -0.50024 | 0.97428 | -0.49425 | 27.6007
2 | 0.009019 | 0.0022653 | -0.0089965 | -0.0022548 | 2.2499e-05 | 1.0482e-05 | 0.013784 | 0.013785 | 0.013785 | 0.97377 | -0.5042 | 0.97112 | -0.55659 | 3.7871
3 | 0.027849 | 0.0070001 | -0.027773 | -0.0069569 | 7.628e-05 | 4.3249e-05 | 0.042563 | 0.042565 | 0.042565 | 0.97377 | -0.5042 | 0.97086 | -0.56172 | 5.8468
4 | -0.13155 | -0.033012 | 0.13319 | 0.034056 | 0.0016398 | 0.001044 | 0.20093 | 0.20093 | 0.20093 | 0.97428 | -0.49425 | 0.98755 | -0.23635 | 27.6007
5 | 0.0089965 | 0.0022548 | -0.0089964 | -0.0022547 | 1.8397e-07 | 8.5799e-08 | 0.013785 | 0.013785 | 0.013785 | 0.97112 | -0.55659 | 0.9711 | -0.55702 | 3.7871
6 | 0.020806 | 0.0052189 | -0.020795 | -0.005212 | 1.137e-05 | 6.9082e-06 | 0.031891 | 0.031891 | 0.031891 | 0.97086 | -0.56172 | 0.97028 | -0.57319 | 8.7613
7 | 0.0069661 | 0.001738 | -0.0069652 | -0.0017384 | 8.1795e-07 | -4.2333e-07 | 0.010674 | 0.010674 | 0.010674 | 0.97086 | -0.56172 | 0.97074 | -0.5642 | 1.4662
8 | -0.20389 | -0.051895 | 0.20625 | 0.053397 | 0.0023524 | 0.0015021 | 0.30751 | 0.3075 | 0.30751 | 0.98755 | -0.23635 | 1 | 0 | 42.2399
9 | 0.070702 | 0.017839 | -0.070455 | -0.017682 | 0.00024714 | 0.00015743 | 0.10658 | 0.10658 | 0.10658 | 0.98755 | -0.23635 | 0.98378 | -0.30962 | 29.279
10 | 0.0034357 | 0.0008564 | -0.0034349 | -0.00085983 | 8.3629e-07 | -3.4383e-06 | 0.0052658 | 0.0052672 | 0.0052672 | 0.97055 | -0.56783 | 0.9703 | -0.57295 | 0.72352
11 | -0.0034357 | -0.0008564 | 0.0034363 | 0.00085396 | 5.9132e-07 | -2.4337e-06 | 0.0052658 | 0.0052648 | 0.0052658 | 0.97055 | -0.56783 | 0.97074 | -0.5642 | 0.72332
12 | 0.00128 | 0.00032033 | -0.00128 | -0.0003208 | 5.9055e-08 | -4.6698e-07 | 0.0019629 | 0.001963 | 0.001963 | 0.9703 | -0.57295 | 0.97025 | -0.57392 | 0.5393
13 | 0.0021548 | 0.00053951 | -0.0021546 | -0.00053999 | 2.0536e-07 | -4.8796e-07 | 0.0033044 | 0.0033046 | 0.0033046 | 0.9703 | -0.57295 | 0.9702 | -0.57495 | 0.90785
14 | 0.020795 | 0.005212 | -0.020794 | -0.0052116 | 6.8079e-07 | 4.1366e-07 | 0.031891 | 0.031891 | 0.031891 | 0.97028 | -0.57319 | 0.97025 | -0.57388 | 8.7613
15 | 0.2808 | 0.071229 | -0.28066 | -0.071142 | 0.00013572 | 8.6751e-05 | 0.41814 | 0.41814 | 0.41814 | 1 | 0 | 0.99947 | -0.010057 | 57.4364
16 | 0.12429 | 0.031548 | -0.12332 | -0.030933 | 0.00096209 | 0.00061477 | 0.18508 | 0.18508 | 0.18508 | 1 | 0 | 0.99155 | -0.16228 | 50.8467
17 | 0.051305 | 0.012882 | -0.051243 | -0.012843 | 6.2377e-05 | 3.9571e-05 | 0.07761 | 0.07761 | 0.07761 | 0.98378 | -0.30962 | 0.98247 | -0.33514 | 21.3215
18 | 0.28066 | 0.071142 | -0.27973 | -0.070543 | 0.00093762 | 0.00059933 | 0.41814 | 0.41814 | 0.41814 | 0.99947 | -0.010057 | 0.99583 | -0.079829 | 57.4364
19 | 0.11998 | 0.030095 | -0.11997 | -0.030088 | 1.1752e-05 | 7.5088e-06 | 0.18007 | 0.18007 | 0.18007 | 0.99155 | -0.16228 | 0.99144 | -0.16433 | 49.469
20 | 0.18024 | 0.045609 | -0.17993 | -0.045408 | 0.000314 | 0.00020036 | 0.26948 | 0.26948 | 0.26948 | 0.99583 | -0.079829 | 0.99393 | -0.1162 | 37.0163
21 | 0.036981 | 0.0092885 | -0.036941 | -0.0092631 | 4.0357e-05 | 2.5379e-05 | 0.055511 | 0.055511 | 0.055511 | 0.99144 | -0.16433 | 0.99026 | -0.18723 | 15.2503
22 | 0.018797 | 0.0047158 | -0.018783 | -0.0047072 | 1.4381e-05 | 8.5859e-06 | 0.028247 | 0.028247 | 0.028247 | 0.99026 | -0.18723 | 0.98944 | -0.20329 | 7.7602
23 | 0.0032226 | 0.0008075 | -0.0032225 | -0.00080759 | 1.1175e-07 | -9.1423e-08 | 0.0048465 | 0.0048465 | 0.0048465 | 0.98944 | -0.20329 | 0.9894 | -0.20402 | 1.3315
24 | 0.0026476 | 0.0006635 | -0.0026476 | -0.00066354 | 2.5005e-08 | -3.8007e-08 | 0.0039819 | 0.0039819 | 0.0039819 | 0.9894 | -0.20402 | 0.98939 | -0.20421 | 1.0939
25 | -0.0054132 | -0.0013567 | 0.0054138 | 0.0013568 | 6.1521e-07 | 8.3278e-08 | 0.0081898 | 0.0081896 | 0.0081898 | 0.98353 | -0.31747 | 0.98366 | -0.31509 | 2.2499
26 | -0.0073079 | -0.0018315 | 0.0073082 | 0.0018316 | 2.8369e-07 | 1.0298e-07 | 0.011055 | 0.011055 | 0.011055 | 0.98366 | -0.31509 | 0.9837 | -0.31427 | 3.0371
27 | -0.012644 | -0.0031689 | 0.012645 | 0.0031694 | 9.186e-07 | 5.0289e-07 | 0.019127 | 0.019127 | 0.019127 | 0.9837 | -0.31427 | 0.98378 | -0.31275 | 5.2546
28 | 0.1286 | 0.032545 | -0.12838 | -0.032405 | 0.00021961 | 0.00014034 | 0.19264 | 0.19264 | 0.19264 | 0.99393 | -0.1162 | 0.99208 | -0.15184 | 52.9226
29 | 0.08218 | 0.020826 | -0.081665 | -0.020497 | 0.00051496 | 0.00032842 | 0.12334 | 0.12334 | 0.12334 | 0.99208 | -0.15184 | 0.98529 | -0.28316 | 33.8854
30 | 0.063841 | 0.016029 | -0.06379 | -0.015996 | 5.0538e-05 | 3.216e-05 | 0.096424 | 0.096424 | 0.096424 | 0.98529 | -0.28316 | 0.98444 | -0.29977 | 26.4901
31 | 0.012151 | 0.0030469 | -0.012149 | -0.0030462 | 1.2543e-06 | 6.7628e-07 | 0.018351 | 0.018351 | 0.018351 | 0.98529 | -0.28316 | 0.98518 | -0.28533 | 5.0414
32 | 0.062942 | 0.015784 | -0.062924 | -0.015772 | 1.7895e-05 | 1.1386e-05 | 0.095142 | 0.095142 | 0.095142 | 0.98444 | -0.29977 | 0.98414 | -0.30574 | 26.1379
33 | 0.011343 | 0.002844 | -0.011341 | -0.0028432 | 1.4953e-06 | 7.8404e-07 | 0.017133 | 0.017133 | 0.017133 | 0.98518 | -0.28533 | 0.98504 | -0.28809 | 4.7068
34 | 0.020406 | 0.0051164 | -0.020406 | -0.0051161 | 5.8081e-07 | 3.5105e-07 | 0.030855 | 0.030855 | 0.030855 | 0.98414 | -0.30574 | 0.9841 | -0.30633 | 8.4767
35 | 0.00083444 | 0.00020894 | -0.00083444 | -0.00020903 | 4.6561e-09 | -9.6502e-08 | 0.0012605 | 0.0012605 | 0.0012605 | 0.98504 | -0.28809 | 0.98503 | -0.28821 | 0.34629
36 | 0.010507 | 0.0026343 | -0.010506 | -0.002634 | 5.9348e-07 | 2.9987e-07 | 0.015872 | 0.015872 | 0.015872 | 0.98504 | -0.28809 | 0.98498 | -0.28928 | 4.3605
37 | 0.018445 | 0.0046246 | -0.018443 | -0.0046233 | 2.0825e-06 | 1.2421e-06 | 0.02789 | 0.02789 | 0.02789 | 0.9841 | -0.30633 | 0.98398 | -0.3087 | 7.662
38 | 0.00083444 | 0.00020903 | -0.00083443 | -0.00020913 | 4.6326e-09 | -9.6008e-08 | 0.0012605 | 0.0012605 | 0.0012605 | 0.98503 | -0.28821 | 0.98503 | -0.28833 | 0.3463
39 | 0.0096593 | 0.0024217 | -0.0096581 | -0.0024212 | 1.1999e-06 | 5.767e-07 | 0.014593 | 0.014593 | 0.014593 | 0.98498 | -0.28928 | 0.98485 | -0.29188 | 4.009
40 | 0.016413 | 0.0041147 | -0.01641 | -0.0041128 | 3.1623e-06 | 1.85e-06 | 0.024821 | 0.024821 | 0.024821 | 0.98398 | -0.3087 | 0.98378 | -0.31275 | 6.8188
41 | 0.0037645 | 0.00094339 | -0.0037644 | -0.00094344 | 1.1865e-07 | -4.7969e-08 | 0.005694 | 0.005694 | 0.005694 | 0.98378 | -0.31275 | 0.98374 | -0.31341 | 1.5643
42 | 0.0019601 | 0.00049124 | -0.0019601 | -0.00049124 | 6.8797e-10 | -2.2038e-09 | 0.0029648 | 0.0029648 | 0.0029648 | 0.98374 | -0.31341 | 0.98374 | -0.31342 | 0.81452
43 | 0.0096581 | 0.0024212 | -0.0096554 | -0.0024199 | 2.687e-06 | 1.2916e-06 | 0.014593 | 0.014593 | 0.014593 | 0.98485 | -0.29188 | 0.98455 | -0.29772 | 4.0091

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61298 | 0.15617

## res_load
| p_mw | q_mvar
0 | 0.094639 | 0.023719
1 | 0.003529 | 0.00088444
2 | 0.00128 | 0.0003208
3 | 0.0021546 | 0.00053999
4 | 0.0089964 | 0.0022547
5 | 0.01915 | 0.0047994
6 | 0.020794 | 0.0052116
7 | 0.0033417 | 0.0008375
8 | 0.051243 | 0.012843
9 | 0.099487 | 0.024934
10 | 0.08299 | 0.020799
11 | 0.018144 | 0.0045473
12 | 0.01556 | 0.0038997
13 | 0.00057493 | 0.00014409
14 | 0.0026476 | 0.00066354
15 | 0.0054132 | 0.0013567
16 | 0.0018941 | 0.0004747
17 | 0.0053361 | 0.0013373
18 | 0.051326 | 0.012864
19 | 0.0462 | 0.011579
20 | 0.0056734 | 0.0014219
21 | 0.00084825 | 0.00021259
22 | 0.00080662 | 0.00020216
23 | 0.042518 | 0.010656
24 | 0.001961 | 0.00049148
25 | 0.00084693 | 0.00021226
26 | 0.0020297 | 0.00050869
27 | 0.0018043 | 0.0004522
28 | 0.0096554 | 0.0024199
29 | 0.00083443 | 0.00020913
30 | 0.0019601 | 0.00049124

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1