## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_247-5_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_247-5_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_247-5_0_6_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_247-5_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_247-5_0_6_node_33 | 0.4 | n |  | TRUE
5 | bus_LV_247-5_0_6_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_247-5_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_247-5_0_6_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_247-5_0_6_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_247-5_0_6_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_247-5_0_6_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_247-5_0_6_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_247-5_0_6_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_247-5_0_6_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_247-5_0_6_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_247-5_0_6_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_247-5_0_6_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_247-5_0_6_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_247-5_0_6_node_39 | 0.4 | n |  | TRUE
19 | bus_LV_247-5_0_6_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_247-5_0_6_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_247-5_0_6_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_247-5_0_6_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_247-5_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_247-5_0_6_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_247-5_0_6_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_247-5_0_6_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_247-5_0_6_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_247-5_0_6_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_247-5_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_247-5_0_6_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_247-5_0_6_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_247-5_0_6_node_31 | 0.4 | n |  | TRUE
33 | bus_MV_517_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_247-5_0_6_load_0 | 0 | 0.021355 | 0.005352 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_247-5_0_6_load_32 | 5 | 0.0073764 | 0.0018487 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_247-5_0_6_load_37 | 8 | 0.011449 | 0.0028694 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_247-5_0_6_load_34 | 11 | 0.040654 | 0.010189 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_247-5_0_6_load_17 | 12 | 0.013354 | 0.0033469 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_247-5_0_6_load_23 | 13 | 0.022214 | 0.0055674 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_247-5_0_6_load_35 | 16 | 0.025324 | 0.0063468 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_247-5_0_6_load_29 | 17 | 0.030071 | 0.0075365 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_247-5_0_6_load_39 | 18 | 0.015206 | 0.0038109 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_247-5_0_6_load_26 | 19 | 0.02526 | 0.0063306 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_247-5_0_6_load_27 | 20 | 0.017379 | 0.0043555 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_247-5_0_6_load_38 | 22 | 0.011454 | 0.0028706 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_247-5_0_6_load_16 | 23 | 0.013444 | 0.0033693 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_247-5_0_6_load_36 | 25 | 0.030702 | 0.0076945 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_247-5_0_6_load_20 | 27 | 0.093751 | 0.023496 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_247-5_0_6_load_24 | 28 | 0.059596 | 0.014936 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_247-5_0_6_load_30 | 30 | 0.048382 | 0.012126 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_247-5_0_6_load_19 | 31 | 0.094504 | 0.023685 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_247-5_0_6_load_31 | 32 | 0.01745 | 0.0043735 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_247-5_0_6_line_0 |  | 0 | 1 | 0.0087866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_247-5_0_6_line_1 |  | 1 | 2 | 0.01167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_247-5_0_6_line_2 |  | 2 | 9 | 0.15568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_247-5_0_6_line_3 |  | 2 | 10 | 0.12404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_247-5_0_6_line_4 |  | 2 | 11 | 0.09556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_247-5_0_6_line_5 |  | 3 | 4 | 0.059897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_247-5_0_6_line_6 |  | 3 | 5 | 0.031034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_247-5_0_6_line_7 |  | 4 | 18 | 0.011472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_247-5_0_6_line_8 |  | 6 | 7 | 0.01393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_247-5_0_6_line_9 |  | 6 | 8 | 0.04517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_247-5_0_6_line_10 |  | 7 | 20 | 0.010538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_247-5_0_6_line_11 |  | 8 | 21 | 0.042291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_247-5_0_6_line_12 |  | 9 | 12 | 0.031307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_247-5_0_6_line_13 |  | 9 | 13 | 0.044245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_247-5_0_6_line_14 |  | 10 | 15 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_247-5_0_6_line_15 |  | 10 | 17 | 0.016873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_247-5_0_6_line_16 |  | 12 | 23 | 0.042135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_247-5_0_6_line_17 |  | 13 | 29 | 0.045757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_247-5_0_6_line_18 |  | 14 | 15 | 0.032088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_247-5_0_6_line_19 |  | 14 | 16 | 0.027685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_247-5_0_6_line_20 |  | 15 | 18 | 0.029586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_247-5_0_6_line_21 |  | 17 | 30 | 0.030377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_247-5_0_6_line_22 |  | 19 | 20 | 0.037969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_247-5_0_6_line_23 |  | 21 | 22 | 0.024874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_247-5_0_6_line_24 |  | 22 | 26 | 0.021338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_247-5_0_6_line_25 |  | 24 | 25 | 0.025875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_247-5_0_6_line_26 |  | 24 | 26 | 0.065741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_247-5_0_6_line_27 |  | 26 | 27 | 0.033329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_247-5_0_6_line_28 |  | 27 | 31 | 0.042545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_247-5_0_6_line_29 |  | 28 | 29 | 0.036216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_247-5_0_6_line_30 |  | 29 | 31 | 0.0255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_247-5_0_6_line_31 |  | 30 | 32 | 0.056231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_247-5_0_6_trafo_17 | 0.63 MVA 20/0.4 kV | 33 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2676203.2175 | 1250390.9559 | 2676202.8376 | 1250399.7343
1 | 2676202.7182 | 1250379.2966 | 2676203.1471 | 1250389.3872 | 2676203.2175 | 1250390.9559
2 | 2676202.7182 | 1250379.2966 | 2676219.5 | 1250371.7402 | 2676259.8932 | 1250373.8723 | 2676280.9473 | 1250371.0745 | 2676301.8665 | 1250371.722 | 2676337.094 | 1250372.8096 | 2676343.3799 | 1250373.6245 | 2676344.5464 | 1250375.6632 | 2676354.0167 | 1250380.7
3 | 2676172.6896 | 1250310.316 | 2676181.0802 | 1250311.2689 | 2676183.666 | 1250311.5579 | 2676181.5678 | 1250330.3002 | 2676179.996 | 1250344.5014 | 2676178.145 | 1250363.3914 | 2676207.157 | 1250367.0002 | 2676219.5 | 1250371.7402 | 2676202.7182 | 1250379.2966
4 | 2676202.7182 | 1250379.2966 | 2676195.8085 | 1250372.9809 | 2676182.8725 | 1250367.3884 | 2676166.7601 | 1250365.1575 | 2676129.9446 | 1250360.7369 | 2676111.3181 | 1250358.5053
5 | 2676090.8294 | 1250268.512 | 2676104.1238 | 1250270.9178 | 2676119.5486 | 1250273.7957 | 2676129.7917 | 1250275.7064 | 2676138.3276 | 1250277.1059 | 2676149.7772 | 1250279.1211
6 | 2676090.8294 | 1250268.512 | 2676090.5614 | 1250262.9267 | 2676090.8267 | 1250237.4857
7 | 2676149.7772 | 1250279.1211 | 2676148.0535 | 1250290.4628
8 | 2676394.2522 | 1250584.1223 | 2676408.2111 | 1250583.524
9 | 2676394.2522 | 1250584.1223 | 2676391.0006 | 1250539.0697
10 | 2676408.2111 | 1250583.524 | 2676418.7375 | 1250583.0272
11 | 2676387.9562 | 1250496.8886 | 2676391.0006 | 1250539.0697
12 | 2676354.0167 | 1250380.7 | 2676351.2862 | 1250381.6766 | 2676349.1407 | 1250384.7179 | 2676347.0481 | 1250409.3138
13 | 2676354.0167 | 1250380.7 | 2676361.6632 | 1250381.9661 | 2676366.4985 | 1250384.6192 | 2676397.2962 | 1250387.9656
14 | 2676172.6896 | 1250310.316 | 2676173.823 | 1250307.3061 | 2676179.4569 | 1250297.7716 | 2676177.3706 | 1250295.0428
15 | 2676172.6896 | 1250310.316 | 2676155.9492 | 1250308.2044
16 | 2676343.4763 | 1250451.2967 | 2676347.0481 | 1250409.3138
17 | 2676442.7858 | 1250392.9084 | 2676397.2962 | 1250387.9656
18 | 2676177.3706 | 1250295.0428 | 2676177.2213 | 1250292.5613 | 2676179.1921 | 1250284.3139 | 2676199.965 | 1250288.1392
19 | 2676199.965 | 1250288.1392 | 2676200.2885 | 1250281.7721 | 2676201.4666 | 1250280.5752 | 2676202.5027 | 1250278.6761 | 2676203.1155 | 1250273.8804 | 2676203.6413 | 1250261.2587
20 | 2676177.3706 | 1250295.0428 | 2676171.8703 | 1250294.1826 | 2676148.0535 | 1250290.4628
21 | 2676155.9492 | 1250308.2044 | 2676125.8112 | 1250304.403
22 | 2676418.7375 | 1250583.0272 | 2676432.4517 | 1250582.3801 | 2676434.0298 | 1250606.5681
23 | 2676387.9562 | 1250496.8886 | 2676412.704 | 1250494.3836
24 | 2676434.0237 | 1250493.9025 | 2676416.1146 | 1250494.0383 | 2676412.704 | 1250494.3836
25 | 2676484.2786 | 1250509.8289 | 2676485.4104 | 1250525.6662 | 2676487.4302 | 1250528.8502 | 2676487.8151 | 1250535.0652
26 | 2676434.0237 | 1250493.9025 | 2676435.4885 | 1250493.888 | 2676455.8756 | 1250493.6063 | 2676483.1264 | 1250493.2353 | 2676484.2786 | 1250509.8289
27 | 2676434.0237 | 1250493.9025 | 2676436.9045 | 1250460.698
28 | 2676436.9045 | 1250460.698 | 2676440.5818 | 1250418.3127
29 | 2676442.7858 | 1250392.9084 | 2676451.8359 | 1250393.6368 | 2676478.7706 | 1250396.9454
30 | 2676442.7858 | 1250392.9084 | 2676440.5818 | 1250418.3127
31 | 2676070.0218 | 1250297.366 | 2676125.8112 | 1250304.403

## bus_geodata
| x | y | coords
0 | 2676202.8376 | 1250399.7343
1 | 2676203.2175 | 1250390.9559
2 | 2676202.7182 | 1250379.2966
3 | 2676090.8294 | 1250268.512
4 | 2676149.7772 | 1250279.1211
5 | 2676090.8267 | 1250237.4857
6 | 2676394.2522 | 1250584.1223
7 | 2676408.2111 | 1250583.524
8 | 2676391.0006 | 1250539.0697
9 | 2676354.0167 | 1250380.7
10 | 2676172.6896 | 1250310.316
11 | 2676111.3181 | 1250358.5053
12 | 2676347.0481 | 1250409.3138
13 | 2676397.2962 | 1250387.9656
14 | 2676199.965 | 1250288.1392
15 | 2676177.3706 | 1250295.0428
16 | 2676203.6413 | 1250261.2587
17 | 2676155.9492 | 1250308.2044
18 | 2676148.0536 | 1250290.4628
19 | 2676434.0298 | 1250606.5681
20 | 2676418.7375 | 1250583.0272
21 | 2676387.9562 | 1250496.8886
22 | 2676412.704 | 1250494.3836
23 | 2676343.4763 | 1250451.2967
24 | 2676484.2786 | 1250509.8289
25 | 2676487.8151 | 1250535.0652
26 | 2676434.0237 | 1250493.9025
27 | 2676436.9045 | 1250460.698
28 | 2676478.7706 | 1250396.9454
29 | 2676442.7858 | 1250392.9084
30 | 2676125.8112 | 1250304.403
31 | 2676440.5818 | 1250418.3127
32 | 2676070.0218 | 1250297.366
33 | 2676354.0167 | 1250380.7

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98641 | -0.25978 | 0.021355 | 0.005352
1 | 0.98658 | -0.25642 | 0 | 0
2 | 0.98681 | -0.25196 | 0 | 0
3 | 0.97941 | -0.39606 | 0 | 0
4 | 0.97982 | -0.38803 | 0 | 0
5 | 0.9792 | -0.40022 | 0.0073764 | 0.0018487
6 | 0.97629 | -0.45758 | 0 | 0
7 | 0.97574 | -0.46845 | 0 | 0
8 | 0.97808 | -0.42243 | 0.011449 | 0.0028694
9 | 0.99669 | -0.062652 | 0 | 0
10 | 0.9813 | -0.35899 | 0 | 0
11 | 0.98323 | -0.32175 | 0.040654 | 0.010189
12 | 1 | 0 | -0.59582 | -0.15223
13 | 0.99371 | -0.1197 | 0.022214 | 0.0055674
14 | 0.97977 | -0.38912 | 0 | 0
15 | 0.98052 | -0.37437 | 0 | 0
16 | 0.97912 | -0.40185 | 0.025324 | 0.0063468
17 | 0.9808 | -0.36876 | 0.030071 | 0.0075365
18 | 0.9799 | -0.38649 | 0.015206 | 0.0038109
19 | 0.97443 | -0.49427 | 0.02526 | 0.0063306
20 | 0.97532 | -0.47668 | 0.017379 | 0.0043555
21 | 0.98021 | -0.38084 | 0 | 0
22 | 0.98146 | -0.35646 | 0.011454 | 0.0028706
23 | 0.99949 | -0.0098785 | 0.013444 | 0.0033693
24 | 0.98089 | -0.36768 | 0 | 0
25 | 0.98016 | -0.38209 | 0.030702 | 0.0076945
26 | 0.98276 | -0.33119 | 0 | 0
27 | 0.98574 | -0.27347 | 0.093751 | 0.023496
28 | 0.98883 | -0.21384 | 0.059596 | 0.014936
29 | 0.99081 | -0.17545 | 0 | 0
30 | 0.97895 | -0.40506 | 0.048382 | 0.012126
31 | 0.98947 | -0.20124 | 0.094504 | 0.023685
32 | 0.97804 | -0.42292 | 0.01745 | 0.0043735
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021355 | -0.005352 | 0.021358 | 0.005354 | 3.4193e-06 | 2.0762e-06 | 0.032214 | 0.032214 | 0.032214 | 0.98641 | -0.25978 | 0.98658 | -0.25642 | 8.8499
1 | -0.021358 | -0.005354 | 0.021363 | 0.0053568 | 4.5414e-06 | 2.7574e-06 | 0.032214 | 0.032214 | 0.032214 | 0.98658 | -0.25642 | 0.98681 | -0.25196 | 8.8499
2 | -0.20696 | -0.052304 | 0.20886 | 0.053513 | 0.0018972 | 0.0012082 | 0.31223 | 0.31223 | 0.31223 | 0.98681 | -0.25196 | 0.99669 | -0.062652 | 28.5929
3 | 0.14481 | 0.036673 | -0.14407 | -0.036204 | 0.0007402 | 0.000469 | 0.2185 | 0.2185 | 0.2185 | 0.98681 | -0.25196 | 0.9813 | -0.35899 | 20.0089
4 | 0.04079 | 0.010274 | -0.040654 | -0.010189 | 0.00013565 | 8.56e-05 | 0.061526 | 0.061526 | 0.061526 | 0.98681 | -0.25196 | 0.98323 | -0.32175 | 16.9027
5 | -0.0073779 | -0.0018493 | 0.0073807 | 0.0018503 | 2.8221e-06 | 1.0521e-06 | 0.011209 | 0.011209 | 0.011209 | 0.97941 | -0.39606 | 0.97982 | -0.38803 | 3.0795
6 | 0.0073779 | 0.0018493 | -0.0073764 | -0.0018487 | 1.4623e-06 | 5.4539e-07 | 0.011209 | 0.011209 | 0.011209 | 0.97941 | -0.39606 | 0.9792 | -0.40022 | 3.0795
7 | -0.0073807 | -0.0018503 | 0.0073813 | 0.0018505 | 5.4051e-07 | 2.0142e-07 | 0.011209 | 0.011209 | 0.011209 | 0.97982 | -0.38803 | 0.9799 | -0.38649 | 3.0794
8 | 0.042698 | 0.010724 | -0.042676 | -0.01071 | 2.2129e-05 | 1.3989e-05 | 0.065087 | 0.065087 | 0.065087 | 0.97629 | -0.45758 | 0.97574 | -0.46845 | 17.881
9 | -0.042698 | -0.010724 | 0.04277 | 0.010769 | 7.1757e-05 | 4.5359e-05 | 0.065087 | 0.065087 | 0.065087 | 0.97629 | -0.45758 | 0.97808 | -0.42243 | 17.881
10 | 0.042676 | 0.01071 | -0.042659 | -0.010699 | 1.6741e-05 | 1.0583e-05 | 0.065087 | 0.065087 | 0.065087 | 0.97574 | -0.46845 | 0.97532 | -0.47668 | 17.881
11 | -0.054219 | -0.013639 | 0.054327 | 0.013707 | 0.00010795 | 6.8557e-05 | 0.082504 | 0.082504 | 0.082504 | 0.97808 | -0.42243 | 0.98021 | -0.38084 | 22.666
12 | -0.57896 | -0.14773 | 0.58072 | 0.14886 | 0.001758 | 0.0011231 | 0.86529 | 0.86529 | 0.86529 | 0.99669 | -0.062652 | 1 | 0 | 47.5436
13 | 0.3701 | 0.09422 | -0.36908 | -0.093573 | 0.001015 | 0.00064673 | 0.55306 | 0.55306 | 0.55306 | 0.99669 | -0.062652 | 0.99371 | -0.1197 | 30.388
14 | 0.047993 | 0.012059 | -0.047957 | -0.012037 | 3.5215e-05 | 2.2314e-05 | 0.072785 | 0.072785 | 0.072785 | 0.9813 | -0.35899 | 0.98052 | -0.37437 | 19.996
15 | 0.096077 | 0.024145 | -0.096032 | -0.024117 | 4.4781e-05 | 2.8021e-05 | 0.14571 | 0.14571 | 0.14571 | 0.9813 | -0.35899 | 0.9808 | -0.36876 | 13.3436
16 | 0.01345 | 0.0033728 | -0.013444 | -0.0033693 | 6.3296e-06 | 3.4984e-06 | 0.020015 | 0.020015 | 0.020015 | 1 | 0 | 0.99949 | -0.0098785 | 5.4986
17 | 0.34687 | 0.088005 | -0.34594 | -0.087415 | 0.00092724 | 0.00059048 | 0.5198 | 0.5198 | 0.5198 | 0.99371 | -0.1197 | 0.99081 | -0.17545 | 28.5604
18 | -0.02534 | -0.0063563 | 0.025357 | 0.0063673 | 1.7823e-05 | 1.1002e-05 | 0.038486 | 0.038486 | 0.038486 | 0.97977 | -0.38912 | 0.98052 | -0.37437 | 10.5732
19 | 0.02534 | 0.0063563 | -0.025324 | -0.0063468 | 1.5378e-05 | 9.4934e-06 | 0.038486 | 0.038486 | 0.038486 | 0.97977 | -0.38912 | 0.97912 | -0.40185 | 10.5732
20 | 0.0226 | 0.0056694 | -0.022587 | -0.0056614 | 1.3052e-05 | 7.9806e-06 | 0.034299 | 0.034299 | 0.034299 | 0.98052 | -0.37437 | 0.9799 | -0.38649 | 9.4229
21 | 0.065962 | 0.016581 | -0.065847 | -0.016508 | 0.00011412 | 7.2654e-05 | 0.10009 | 0.10009 | 0.10009 | 0.9808 | -0.36876 | 0.97895 | -0.40506 | 27.4974
22 | -0.02526 | -0.0063306 | 0.025281 | 0.0063437 | 2.1185e-05 | 1.3085e-05 | 0.038573 | 0.038573 | 0.038573 | 0.97443 | -0.49427 | 0.97532 | -0.47668 | 10.597
23 | -0.054327 | -0.013707 | 0.05439 | 0.013747 | 6.3494e-05 | 4.0322e-05 | 0.082504 | 0.082504 | 0.082504 | 0.98021 | -0.38084 | 0.98146 | -0.35646 | 22.666
24 | -0.065844 | -0.016618 | 0.065924 | 0.016669 | 7.9807e-05 | 5.0807e-05 | 0.09987 | 0.099869 | 0.09987 | 0.98146 | -0.35646 | 0.98276 | -0.33119 | 27.4367
25 | 0.030723 | 0.0077077 | -0.030702 | -0.0076945 | 2.1079e-05 | 1.3164e-05 | 0.046609 | 0.046609 | 0.046609 | 0.98089 | -0.36768 | 0.98016 | -0.38209 | 12.8047
26 | -0.030723 | -0.0077077 | 0.030776 | 0.0077411 | 5.3556e-05 | 3.3444e-05 | 0.046609 | 0.046609 | 0.046609 | 0.98089 | -0.36768 | 0.98276 | -0.33119 | 12.8047
27 | -0.0967 | -0.02441 | 0.096968 | 0.024581 | 0.00026816 | 0.0001712 | 0.14648 | 0.14648 | 0.14648 | 0.98276 | -0.33119 | 0.98574 | -0.27347 | 40.2412
28 | -0.19072 | -0.048077 | 0.19138 | 0.0485 | 0.00066165 | 0.00042237 | 0.288 | 0.288 | 0.288 | 0.98574 | -0.27347 | 0.98947 | -0.20124 | 39.5604
29 | -0.059596 | -0.014936 | 0.059705 | 0.015005 | 0.00010923 | 6.9441e-05 | 0.089681 | 0.089681 | 0.089681 | 0.98883 | -0.21384 | 0.99081 | -0.17545 | 24.6376
30 | 0.28624 | 0.07241 | -0.28589 | -0.072185 | 0.00035381 | 0.0002248 | 0.43012 | 0.43012 | 0.43012 | 0.99081 | -0.17545 | 0.98947 | -0.20124 | 23.6329
31 | 0.017465 | 0.0043823 | -0.01745 | -0.0043735 | 1.4863e-05 | 8.8062e-06 | 0.026549 | 0.026549 | 0.026549 | 0.97895 | -0.40506 | 0.97804 | -0.42292 | 7.2938

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60917 | 0.15558

## res_load
| p_mw | q_mvar
0 | 0.021355 | 0.005352
1 | 0.0073764 | 0.0018487
2 | 0.011449 | 0.0028694
3 | 0.040654 | 0.010189
4 | 0.013354 | 0.0033469
5 | 0.022214 | 0.0055674
6 | 0.025324 | 0.0063468
7 | 0.030071 | 0.0075365
8 | 0.015206 | 0.0038109
9 | 0.02526 | 0.0063306
10 | 0.017379 | 0.0043555
11 | 0.011454 | 0.0028706
12 | 0.013444 | 0.0033693
13 | 0.030702 | 0.0076945
14 | 0.093751 | 0.023496
15 | 0.059596 | 0.014936
16 | 0.048382 | 0.012126
17 | 0.094504 | 0.023685
18 | 0.01745 | 0.0043735

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1