## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_247-9_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_247-9_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_247-9_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_247-9_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_247-9_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_247-9_0_5_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_247-9_0_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_247-9_0_5_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_247-9_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_247-9_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_247-9_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_247-9_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_247-9_0_5_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_247-9_0_5_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_247-9_0_5_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_247-9_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_247-9_0_5_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_247-9_0_5_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_247-9_0_5_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_247-9_0_5_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_247-9_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_247-9_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_247-9_0_5_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_247-9_0_5_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_247-9_0_5_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_247-9_0_5_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_247-9_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_247-9_0_5_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_247-9_0_5_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_247-9_0_5_node_43 | 0.4 | n |  | TRUE
30 | bus_LV_247-9_0_5_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_247-9_0_5_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_247-9_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_247-9_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_247-9_0_5_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_247-9_0_5_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_247-9_0_5_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_247-9_0_5_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_247-9_0_5_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_247-9_0_5_node_42 | 0.4 | n |  | TRUE
40 | bus_MV_517_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_247-9_0_5_load_0 | 0 | 0.0083926 | 0.0021034 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_247-9_0_5_load_1 | 1 | 0.0016755 | 0.00041992 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_247-9_0_5_load_4 | 3 | 0.004296 | 0.0010767 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_247-9_0_5_load_5 | 4 | 0.0058964 | 0.0014778 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_247-9_0_5_load_10 | 7 | 0.033527 | 0.0084026 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_247-9_0_5_load_6 | 8 | 0.0099843 | 0.0025023 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_247-9_0_5_load_9 | 11 | 0.0079801 | 0.002 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_247-9_0_5_load_18 | 12 | 0.0044321 | 0.0011108 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_247-9_0_5_load_16 | 16 | 0.0043986 | 0.0011024 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_247-9_0_5_load_34 | 17 | 0.098173 | 0.024604 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_247-9_0_5_load_17 | 20 | 0.003042 | 0.0007624 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_247-9_0_5_load_15 | 21 | 0.0031775 | 0.00079636 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_247-9_0_5_load_20 | 22 | 0.0020282 | 0.00050831 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_247-9_0_5_load_21 | 23 | 0.0032078 | 0.00080395 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_247-9_0_5_load_30 | 24 | 0.004723 | 0.0011837 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_247-9_0_5_load_29 | 25 | 0.0037856 | 0.00094877 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_247-9_0_5_load_24 | 26 | 0.0026466 | 0.0006633 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_247-9_0_5_load_26 | 27 | 0.0016203 | 0.00040608 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_247-9_0_5_load_46 | 28 | 0.095494 | 0.023933 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_247-9_0_5_load_43 | 29 | 0.0083053 | 0.0020815 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_247-9_0_5_load_32 | 31 | 0.007677 | 0.001924 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_247-9_0_5_load_31 | 32 | 0.00082673 | 0.0002072 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_247-9_0_5_load_28 | 33 | 0.0032947 | 0.00082573 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_247-9_0_5_load_39 | 35 | 0.0018254 | 0.0004575 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_247-9_0_5_load_40 | 36 | 0.0007744 | 0.00019408 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_247-9_0_5_load_37 | 37 | 0.002903 | 0.00072757 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_247-9_0_5_load_41 | 38 | 0.003846 | 0.0009639 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_247-9_0_5_load_42 | 39 | 0.0024126 | 0.00060465 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_247-9_0_5_line_0 |  | 0 | 1 | 0.027395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_247-9_0_5_line_1 |  | 0 | 2 | 0.018038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_247-9_0_5_line_2 |  | 2 | 3 | 0.015328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_247-9_0_5_line_3 |  | 2 | 4 | 0.031869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_247-9_0_5_line_4 |  | 4 | 5 | 0.013894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_247-9_0_5_line_5 |  | 5 | 6 | 0.039437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_247-9_0_5_line_6 |  | 5 | 7 | 0.043037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_247-9_0_5_line_7 |  | 6 | 16 | 0.004407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_247-9_0_5_line_8 |  | 7 | 15 | 0.030265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_247-9_0_5_line_9 |  | 8 | 9 | 0.037927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_247-9_0_5_line_10 |  | 9 | 10 | 0.027288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_247-9_0_5_line_11 |  | 9 | 11 | 0.018568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_247-9_0_5_line_12 |  | 10 | 12 | 0.059913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_247-9_0_5_line_13 |  | 11 | 13 | 0.030264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_247-9_0_5_line_14 |  | 13 | 14 | 0.067413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_247-9_0_5_line_15 |  | 13 | 15 | 0.03956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_247-9_0_5_line_16 |  | 14 | 17 | 0.048827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_247-9_0_5_line_17 |  | 16 | 20 | 0.027266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_247-9_0_5_line_18 |  | 16 | 21 | 0.018254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_247-9_0_5_line_19 |  | 17 | 29 | 0.13506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_247-9_0_5_line_20 |  | 17 | 18 | 0.051649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_247-9_0_5_line_21 |  | 18 | 19 | 0.079532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_247-9_0_5_line_22 |  | 19 | 28 | 0.022914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_247-9_0_5_line_23 |  | 20 | 22 | 0.0047561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_247-9_0_5_line_24 |  | 22 | 23 | 0.014424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_247-9_0_5_line_25 |  | 23 | 26 | 0.0041763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_247-9_0_5_line_26 |  | 24 | 25 | 0.013047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_247-9_0_5_line_27 |  | 25 | 33 | 0.025729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_247-9_0_5_line_28 |  | 26 | 27 | 0.016125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_247-9_0_5_line_29 |  | 27 | 30 | 0.014427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_247-9_0_5_line_30 |  | 30 | 32 | 0.012335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_247-9_0_5_line_31 |  | 30 | 33 | 0.017313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_247-9_0_5_line_32 |  | 30 | 31 | 0.028834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_247-9_0_5_line_33 |  | 32 | 34 | 0.016774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_247-9_0_5_line_34 |  | 34 | 35 | 0.013557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_247-9_0_5_line_35 |  | 34 | 36 | 0.0079339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_247-9_0_5_line_36 |  | 34 | 37 | 0.072077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_247-9_0_5_line_37 |  | 35 | 38 | 0.00020746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_247-9_0_5_line_38 |  | 36 | 39 | 0.0021517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_247-9_0_5_trafo_12 | 0.63 MVA 20/0.4 kV | 40 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2676901.3662 | 1250211.736 | 2676922.528 | 1250211.2483 | 2676928.7161 | 1250210.5452
1 | 2676883.3327 | 1250212.1516 | 2676901.3662 | 1250211.736
2 | 2676883.3327 | 1250212.1516 | 2676882.8193 | 1250196.8318
3 | 2676883.3327 | 1250212.1516 | 2676851.4908 | 1250213.4652
4 | 2676837.6091 | 1250214.0379 | 2676851.4908 | 1250213.4652
5 | 2676832.3706 | 1250174.9526 | 2676837.6091 | 1250214.0379
6 | 2676837.6091 | 1250214.0379 | 2676794.8487 | 1250218.9084
7 | 2676831.778 | 1250170.5862 | 2676832.3706 | 1250174.9526
8 | 2676765.0802 | 1250224.3502 | 2676793.6117 | 1250219.0492 | 2676794.8487 | 1250218.9084
9 | 2676716.3863 | 1250182.7785 | 2676722.1559 | 1250181.4967 | 2676744.909 | 1250176.4208 | 2676753.5149 | 1250175.1178
10 | 2676716.3863 | 1250182.7785 | 2676710.1468 | 1250156.2117
11 | 2676716.3863 | 1250182.7785 | 2676720.4983 | 1250200.8858
12 | 2676710.1468 | 1250156.2117 | 2676714.7787 | 1250155.3377 | 2676769.0292 | 1250145.1481
13 | 2676725.9062 | 1250230.6143 | 2676724.693 | 1250219.3571 | 2676720.4983 | 1250200.8858
14 | 2676725.9062 | 1250230.6143 | 2676726.4681 | 1250238.5274 | 2676726.679 | 1250241.4767 | 2676727.0558 | 1250246.7743 | 2676729.4584 | 1250249.5519 | 2676730.5086 | 1250251.8227 | 2676729.6571 | 1250258.6945 | 2676733.7047 | 1250259.2028 | 2676731.9041 | 1250271.7331 | 2676731.748 | 1250275.0446 | 2676732.3405 | 1250278.8439 | 2676734.0307 | 1250283.5804 | 2676736.9655 | 1250287.2321 | 2676740.5465 | 1250289.9582
15 | 2676765.0802 | 1250224.3502 | 2676747.003 | 1250227.4963 | 2676725.9062 | 1250230.6143
16 | 2676740.5465 | 1250289.9582 | 2676745.0661 | 1250292.4964 | 2676788.3817 | 1250297.8404
17 | 2676831.778 | 1250170.5862 | 2676827.527 | 1250143.6538
18 | 2676831.778 | 1250170.5862 | 2676813.7066 | 1250173.1653
19 | 2676788.3817 | 1250297.8404 | 2676782.0235 | 1250432.7551
20 | 2676839.6496 | 1250304.0967 | 2676833.8899 | 1250303.455 | 2676788.3817 | 1250297.8404
21 | 2676857.5839 | 1250235.7238 | 2676857.2881 | 1250238.1551 | 2676852.899 | 1250274.4469 | 2676852.4082 | 1250278.5212 | 2676849.1863 | 1250305.1545 | 2676839.6496 | 1250304.0967
22 | 2676857.5839 | 1250235.7238 | 2676880.4255 | 1250237.5462
23 | 2676827.527 | 1250143.6538 | 2676826.7855 | 1250138.9559
24 | 2676824.5367 | 1250124.7085 | 2676826.7855 | 1250138.9559
25 | 2676823.8855 | 1250120.5833 | 2676824.5367 | 1250124.7085
26 | 2676764.3101 | 1250092.2679 | 2676777.3487 | 1250091.7976
27 | 2676803.0605 | 1250090.8703 | 2676777.3487 | 1250091.7976
28 | 2676823.8855 | 1250120.5833 | 2676822.4571 | 1250111.5334 | 2676821.7753 | 1250104.6042
29 | 2676820.3625 | 1250090.2463 | 2676821.7753 | 1250104.6042
30 | 2676820.3625 | 1250090.2463 | 2676818.024 | 1250078.1346
31 | 2676820.3625 | 1250090.2463 | 2676803.0605 | 1250090.8703
32 | 2676820.3625 | 1250090.2463 | 2676847.7312 | 1250089.078 | 2676849.0138 | 1250089.7335
33 | 2676814.8441 | 1250061.6651 | 2676818.024 | 1250078.1346
34 | 2676814.8441 | 1250061.6651 | 2676801.3889 | 1250063.3275
35 | 2676814.8441 | 1250061.6651 | 2676817.9463 | 1250061.1494 | 2676819.5075 | 1250056.6218
36 | 2676814.8441 | 1250061.6651 | 2676815.3227 | 1250037.5648 | 2676767.3795 | 1250039.2225
37 | 2676801.183 | 1250063.353 | 2676801.3889 | 1250063.3275
38 | 2676819.3127 | 1250054.4789 | 2676819.5075 | 1250056.6218 | 2676819.5075 | 1250056.6218

## bus_geodata
| x | y | coords
0 | 2676901.3662 | 1250211.736
1 | 2676928.7161 | 1250210.5452
2 | 2676883.3327 | 1250212.1516
3 | 2676882.8193 | 1250196.8318
4 | 2676851.4908 | 1250213.4652
5 | 2676837.6091 | 1250214.0379
6 | 2676832.3706 | 1250174.9526
7 | 2676794.8487 | 1250218.9084
8 | 2676753.5149 | 1250175.1178
9 | 2676716.3863 | 1250182.7785
10 | 2676710.1468 | 1250156.2117
11 | 2676720.4983 | 1250200.8858
12 | 2676769.0292 | 1250145.1481
13 | 2676725.9062 | 1250230.6143
14 | 2676740.5465 | 1250289.9582
15 | 2676765.0802 | 1250224.3502
16 | 2676831.778 | 1250170.5862
17 | 2676788.3817 | 1250297.8404
18 | 2676839.6496 | 1250304.0967
19 | 2676857.5839 | 1250235.7238
20 | 2676827.527 | 1250143.6538
21 | 2676813.7066 | 1250173.1653
22 | 2676826.7855 | 1250138.9559
23 | 2676824.5367 | 1250124.7085
24 | 2676764.3101 | 1250092.2679
25 | 2676777.3487 | 1250091.7976
26 | 2676823.8855 | 1250120.5833
27 | 2676821.7753 | 1250104.6042
28 | 2676880.4255 | 1250237.5462
29 | 2676782.0235 | 1250432.7551
30 | 2676820.3625 | 1250090.2463
31 | 2676849.0138 | 1250089.7335
32 | 2676818.024 | 1250078.1346
33 | 2676803.0605 | 1250090.8703
34 | 2676814.8441 | 1250061.6651
35 | 2676801.3889 | 1250063.3275
36 | 2676819.5075 | 1250056.6218
37 | 2676767.3795 | 1250039.2225
38 | 2676801.183 | 1250063.353
39 | 2676819.3127 | 1250054.4789
40 | 2676832.3706 | 1250174.9526

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99916 | -0.016066 | 0.0083926 | 0.0021034
1 | 0.99912 | -0.016868 | 0.0016755 | 0.00041992
2 | 0.99933 | -0.012896 | 0 | 0
3 | 0.99927 | -0.014045 | 0.004296 | 0.0010767
4 | 0.99974 | -0.0049083 | 0.0058964 | 0.0014778
5 | 1 | 0 | -0.33648 | -0.08564
6 | 0.99813 | -0.035948 | 0 | 0
7 | 0.99658 | -0.064714 | 0.033527 | 0.0084026
8 | 0.99053 | -0.18032 | 0.0099843 | 0.0025023
9 | 0.99088 | -0.17359 | 0 | 0
10 | 0.99077 | -0.17574 | 0 | 0
11 | 0.99112 | -0.16884 | 0.0079801 | 0.002
12 | 0.99052 | -0.18046 | 0.0044321 | 0.0011108
13 | 0.99174 | -0.15682 | 0 | 0
14 | 0.98753 | -0.2376 | 0 | 0
15 | 0.99448 | -0.10453 | 0 | 0
16 | 0.99792 | -0.039974 | 0.0043986 | 0.0011024
17 | 0.98449 | -0.29653 | 0.098173 | 0.024604
18 | 0.98219 | -0.34099 | 0 | 0
19 | 0.97511 | -0.4792 | 0 | 0
20 | 0.99681 | -0.061292 | 0.003042 | 0.0007624
21 | 0.99786 | -0.040989 | 0.0031775 | 0.00079636
22 | 0.99663 | -0.064761 | 0.0020282 | 0.00050831
23 | 0.99611 | -0.074777 | 0.0032078 | 0.00080395
24 | 0.99461 | -0.10368 | 0.004723 | 0.0011837
25 | 0.99467 | -0.10259 | 0.0037856 | 0.00094877
26 | 0.99597 | -0.077444 | 0.0026466 | 0.0006633
27 | 0.99547 | -0.086995 | 0.0016203 | 0.00040608
28 | 0.97307 | -0.5194 | 0.095494 | 0.023933
29 | 0.98345 | -0.31673 | 0.0083053 | 0.0020815
30 | 0.99505 | -0.095138 | 0 | 0
31 | 0.99485 | -0.099036 | 0.007677 | 0.001924
32 | 0.99491 | -0.097873 | 0.00082673 | 0.0002072
33 | 0.99487 | -0.098736 | 0.0032947 | 0.00082573
34 | 0.99473 | -0.10135 | 0 | 0
35 | 0.99466 | -0.1027 | 0.0018254 | 0.0004575
36 | 0.99471 | -0.10179 | 0.0007744 | 0.00019408
37 | 0.99454 | -0.10504 | 0.002903 | 0.00072757
38 | 0.99466 | -0.10272 | 0.003846 | 0.0009639
39 | 0.9947 | -0.10188 | 0.0024126 | 0.00060465
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0016756 | 0.0004196 | -0.0016755 | -0.00041992 | 6.3966e-08 | -3.1785e-07 | 0.0024952 | 0.0024954 | 0.0024954 | 0.99916 | -0.016066 | 0.99912 | -0.016868 | 0.68554
1 | -0.010068 | -0.002523 | 0.01007 | 0.0025237 | 1.5208e-06 | 7.37e-07 | 0.014994 | 0.014994 | 0.014994 | 0.99916 | -0.016066 | 0.99933 | -0.012896 | 4.1192
2 | 0.0042962 | 0.0010766 | -0.004296 | -0.0010767 | 2.3523e-07 | -5.0267e-08 | 0.0063971 | 0.0063972 | 0.0063972 | 0.99933 | -0.012896 | 0.99927 | -0.014045 | 1.7575
3 | -0.014366 | -0.0036004 | 0.014371 | 0.0036034 | 5.4684e-06 | 3.0821e-06 | 0.021391 | 0.021391 | 0.021391 | 0.99933 | -0.012896 | 0.99974 | -0.0049083 | 5.8767
4 | -0.020268 | -0.0050812 | 0.020273 | 0.0050841 | 4.7415e-06 | 2.8523e-06 | 0.030167 | 0.030167 | 0.030167 | 0.99974 | -0.0049083 | 1 | 0 | 8.2877
5 | 0.052403 | 0.013212 | -0.052313 | -0.013155 | 8.9986e-05 | 5.7075e-05 | 0.078004 | 0.078005 | 0.078005 | 1 | 0 | 0.99813 | -0.035948 | 21.4298
6 | 0.26215 | 0.067344 | -0.26133 | -0.06682 | 0.00082106 | 0.00052379 | 0.39067 | 0.39067 | 0.39067 | 1 | 0 | 0.99658 | -0.064714 | 35.7758
7 | 0.052313 | 0.013155 | -0.052303 | -0.013149 | 1.0056e-05 | 6.3781e-06 | 0.078005 | 0.078005 | 0.078005 | 0.99813 | -0.035948 | 0.99792 | -0.039974 | 21.4298
8 | 0.22781 | 0.058418 | -0.22737 | -0.058138 | 0.0004389 | 0.00027972 | 0.34061 | 0.34061 | 0.34061 | 0.99658 | -0.064714 | 0.99448 | -0.10453 | 31.1917
9 | -0.0099843 | -0.0025023 | 0.0099875 | 0.0025039 | 3.1995e-06 | 1.5593e-06 | 0.014999 | 0.014999 | 0.014999 | 0.99053 | -0.18032 | 0.99088 | -0.17359 | 4.1206
10 | 0.0044336 | 0.0011106 | -0.0044331 | -0.0011107 | 4.536e-07 | -6.1153e-08 | 0.0066578 | 0.0066579 | 0.0066579 | 0.99088 | -0.17359 | 0.99077 | -0.17574 | 1.8291
11 | -0.014421 | -0.0036145 | 0.014424 | 0.0036163 | 3.2657e-06 | 1.8508e-06 | 0.021656 | 0.021656 | 0.021656 | 0.99088 | -0.17359 | 0.99112 | -0.16884 | 5.9496
12 | 0.0044331 | 0.0011107 | -0.0044321 | -0.0011108 | 9.9597e-07 | -1.3395e-07 | 0.0066579 | 0.0066582 | 0.0066582 | 0.99077 | -0.17574 | 0.99052 | -0.18046 | 1.8292
13 | -0.022404 | -0.0056163 | 0.022417 | 0.0056242 | 1.2841e-05 | 7.828e-06 | 0.033637 | 0.033637 | 0.033637 | 0.99112 | -0.16884 | 0.99174 | -0.15682 | 9.241
14 | 0.20438 | 0.052148 | -0.20358 | -0.051643 | 0.00079408 | 0.00050561 | 0.30698 | 0.30698 | 0.30698 | 0.99174 | -0.15682 | 0.98753 | -0.2376 | 28.1115
15 | -0.22679 | -0.057772 | 0.22737 | 0.058138 | 0.00057371 | 0.00036564 | 0.34061 | 0.34061 | 0.34061 | 0.99174 | -0.15682 | 0.99448 | -0.10453 | 31.1917
16 | 0.20358 | 0.051643 | -0.20301 | -0.051276 | 0.00057516 | 0.00036623 | 0.30698 | 0.30698 | 0.30698 | 0.98753 | -0.2376 | 0.98449 | -0.29653 | 28.1116
17 | 0.044727 | 0.01125 | -0.044681 | -0.011221 | 4.5499e-05 | 2.8763e-05 | 0.066708 | 0.066708 | 0.066708 | 0.99792 | -0.039974 | 0.99681 | -0.061292 | 18.3263
18 | 0.0031777 | 0.00079622 | -0.0031775 | -0.00079636 | 1.5369e-07 | -1.4011e-07 | 0.0047383 | 0.0047383 | 0.0047383 | 0.99792 | -0.039974 | 0.99786 | -0.040989 | 1.3017
19 | 0.0083133 | 0.0020849 | -0.0083053 | -0.0020815 | 7.9977e-06 | 3.4029e-06 | 0.012566 | 0.012566 | 0.012566 | 0.98449 | -0.29653 | 0.98345 | -0.31673 | 3.4523
20 | 0.09652 | 0.024587 | -0.096313 | -0.024456 | 0.00020651 | 0.00013085 | 0.14603 | 0.14603 | 0.14603 | 0.98449 | -0.29653 | 0.98219 | -0.34099 | 20.0589
21 | 0.096313 | 0.024456 | -0.095677 | -0.02405 | 0.00063599 | 0.00040604 | 0.14603 | 0.14603 | 0.14603 | 0.98219 | -0.34099 | 0.97511 | -0.4792 | 40.118
22 | 0.095677 | 0.02405 | -0.095494 | -0.023933 | 0.00018324 | 0.00011699 | 0.14603 | 0.14603 | 0.14603 | 0.97511 | -0.4792 | 0.97307 | -0.5194 | 40.118
23 | 0.041639 | 0.010459 | -0.041632 | -0.010455 | 6.8928e-06 | 4.3494e-06 | 0.062167 | 0.062167 | 0.062167 | 0.99681 | -0.061292 | 0.99663 | -0.064761 | 17.0787
24 | 0.039604 | 0.0099462 | -0.039585 | -0.0099343 | 1.8917e-05 | 1.1919e-05 | 0.059138 | 0.059139 | 0.059139 | 0.99663 | -0.064761 | 0.99611 | -0.074777 | 16.2468
25 | 0.036378 | 0.0091303 | -0.036373 | -0.0091274 | 4.6256e-06 | 2.906e-06 | 0.054347 | 0.054347 | 0.054347 | 0.99611 | -0.074777 | 0.99597 | -0.077444 | 14.9304
26 | -0.004723 | -0.0011837 | 0.0047232 | 0.0011837 | 2.4428e-07 | -1.3001e-08 | 0.0070659 | 0.0070659 | 0.0070659 | 0.99461 | -0.10368 | 0.99467 | -0.10259 | 1.9412
27 | -0.0085088 | -0.0021324 | 0.0085104 | 0.0021331 | 1.5633e-06 | 6.665e-07 | 0.012729 | 0.012729 | 0.012729 | 0.99467 | -0.10259 | 0.99487 | -0.098736 | 3.497
28 | 0.033726 | 0.0084641 | -0.033711 | -0.0084545 | 1.5355e-05 | 9.6176e-06 | 0.050393 | 0.050393 | 0.050393 | 0.99597 | -0.077444 | 0.99547 | -0.086995 | 13.8441
29 | 0.032091 | 0.0080484 | -0.032078 | -0.0080407 | 1.245e-05 | 7.7804e-06 | 0.047971 | 0.047971 | 0.047971 | 0.99547 | -0.086995 | 0.99505 | -0.095138 | 13.1788
30 | 0.012593 | 0.0031562 | -0.012591 | -0.0031553 | 1.6404e-06 | 8.8965e-07 | 0.018831 | 0.018831 | 0.018831 | 0.99505 | -0.095138 | 0.99491 | -0.097873 | 5.1735
31 | 0.011807 | 0.0029599 | -0.011805 | -0.0029588 | 2.0241e-06 | 1.0706e-06 | 0.017657 | 0.017657 | 0.017657 | 0.99505 | -0.095138 | 0.99487 | -0.098736 | 4.8508
32 | 0.0076784 | 0.0019246 | -0.007677 | -0.001924 | 1.4256e-06 | 5.3794e-07 | 0.011482 | 0.011483 | 0.011483 | 0.99505 | -0.095138 | 0.99485 | -0.099036 | 3.1546
33 | 0.011764 | 0.0029481 | -0.011762 | -0.0029471 | 1.9473e-06 | 1.0285e-06 | 0.017595 | 0.017595 | 0.017595 | 0.99491 | -0.097873 | 0.99473 | -0.10135 | 4.8338
34 | 0.0056718 | 0.0014215 | -0.0056714 | -0.0014214 | 3.6598e-07 | 5.8245e-08 | 0.0084844 | 0.0084845 | 0.0084845 | 0.99473 | -0.10135 | 0.99466 | -0.1027 | 2.3309
35 | 0.0031871 | 0.00079865 | -0.003187 | -0.00079871 | 6.7623e-08 | -5.9712e-08 | 0.0047675 | 0.0047675 | 0.0047675 | 0.99473 | -0.10135 | 0.99471 | -0.10179 | 1.3098
36 | 0.0029035 | 0.00072696 | -0.002903 | -0.00072757 | 5.0988e-07 | -6.0916e-07 | 0.0043431 | 0.0043435 | 0.0043435 | 0.99473 | -0.10135 | 0.99454 | -0.10504 | 1.1933
37 | 0.003846 | 0.0009639 | -0.003846 | -0.0009639 | 2.5751e-09 | -1.0448e-09 | 0.0057536 | 0.0057536 | 0.0057536 | 0.99466 | -0.1027 | 0.99466 | -0.10272 | 1.5807
38 | 0.0024126 | 0.00060463 | -0.0024126 | -0.00060465 | 1.051e-08 | -2.1204e-08 | 0.0036091 | 0.0036091 | 0.0036091 | 0.99471 | -0.10179 | 0.9947 | -0.10188 | 0.9915

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33648 | 0.08564

## res_load
| p_mw | q_mvar
0 | 0.0083926 | 0.0021034
1 | 0.0016755 | 0.00041992
2 | 0.004296 | 0.0010767
3 | 0.0058964 | 0.0014778
4 | 0.033527 | 0.0084026
5 | 0.0099843 | 0.0025023
6 | 0.0079801 | 0.002
7 | 0.0044321 | 0.0011108
8 | 0.0043986 | 0.0011024
9 | 0.098173 | 0.024604
10 | 0.003042 | 0.0007624
11 | 0.0031775 | 0.00079636
12 | 0.0020282 | 0.00050831
13 | 0.0032078 | 0.00080395
14 | 0.004723 | 0.0011837
15 | 0.0037856 | 0.00094877
16 | 0.0026466 | 0.0006633
17 | 0.0016203 | 0.00040608
18 | 0.095494 | 0.023933
19 | 0.0083053 | 0.0020815
20 | 0.007677 | 0.001924
21 | 0.00082673 | 0.0002072
22 | 0.0032947 | 0.00082573
23 | 0.0018254 | 0.0004575
24 | 0.0007744 | 0.00019408
25 | 0.002903 | 0.00072757
26 | 0.003846 | 0.0009639
27 | 0.0024126 | 0.00060465

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1