## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2473-14_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2473-14_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2473-14_0_6_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_2473-14_0_6_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2473-14_0_6_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_2473-14_0_6_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_2473-14_0_6_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2473-14_0_6_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2473-14_0_6_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_2473-14_0_6_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2473-14_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2473-14_0_6_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2473-14_0_6_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_2473-14_0_6_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2473-14_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2473-14_0_6_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2473-14_0_6_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_2473-14_0_6_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_2473-14_0_6_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2473-14_0_6_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2473-14_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2473-14_0_6_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2473-14_0_6_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2473-14_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_MV_286_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2473-14_0_6_load_0 | 0 | 0.002675 | 0.00067042 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2473-14_0_6_load_23 | 2 | 0.099381 | 0.024907 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2473-14_0_6_load_2 | 3 | 0.001182 | 0.00029623 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2473-14_0_6_load_22 | 4 | 0.009099 | 0.0022804 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2473-14_0_6_load_19 | 5 | 0.040756 | 0.010214 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2473-14_0_6_load_9 | 6 | 0.0014808 | 0.00037113 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2473-14_0_6_load_8 | 7 | 0.0070983 | 0.001779 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2473-14_0_6_load_3 | 8 | 0.039925 | 0.010006 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2473-14_0_6_load_4 | 9 | 0.060437 | 0.015147 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2473-14_0_6_load_5 | 10 | 0.07887 | 0.019767 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2473-14_0_6_load_12 | 11 | 0.065254 | 0.016354 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2473-14_0_6_load_16 | 12 | 0.017794 | 0.0044596 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2473-14_0_6_load_6 | 13 | 0.013564 | 0.0033995 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2473-14_0_6_load_13 | 15 | 0.0083077 | 0.0020821 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2473-14_0_6_load_21 | 17 | 0.014643 | 0.0036698 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2473-14_0_6_load_14 | 18 | 0.023869 | 0.0059821 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2473-14_0_6_load_11 | 20 | 0.0064501 | 0.0016166 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2473-14_0_6_load_18 | 21 | 0.0025881 | 0.00064863 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2473-14_0_6_load_17 | 22 | 0.0035486 | 0.00088937 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2473-14_0_6_load_15 | 23 | 0.016932 | 0.0042436 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2473-14_0_6_line_0 |  | 0 | 1 | 0.019092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_2473-14_0_6_line_1 |  | 0 | 2 | 0.12387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_2473-14_0_6_line_2 |  | 1 | 3 | 0.039132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_2473-14_0_6_line_3 |  | 2 | 5 | 0.20919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_2473-14_0_6_line_4 |  | 2 | 4 | 0.022189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2473-14_0_6_line_5 |  | 3 | 6 | 0.0094996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_2473-14_0_6_line_6 |  | 5 | 16 | 0.037745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_2473-14_0_6_line_7 |  | 6 | 7 | 0.023707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_2473-14_0_6_line_8 |  | 7 | 19 | 0.030104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_2473-14_0_6_line_9 |  | 8 | 9 | 0.0091707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2473-14_0_6_line_10 |  | 9 | 10 | 0.0052259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2473-14_0_6_line_11 |  | 10 | 11 | 0.0086528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_2473-14_0_6_line_12 |  | 11 | 12 | 0.066131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_2473-14_0_6_line_13 |  | 12 | 22 | 0.0061529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_2473-14_0_6_line_14 |  | 13 | 14 | 0.0018409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2473-14_0_6_line_15 |  | 14 | 15 | 0.033695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2473-14_0_6_line_16 |  | 15 | 18 | 0.032026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_2473-14_0_6_line_17 |  | 16 | 17 | 0.12157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_2473-14_0_6_line_18 |  | 17 | 23 | 0.18154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_2473-14_0_6_line_19 |  | 18 | 23 | 0.02059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_2473-14_0_6_line_20 |  | 19 | 20 | 0.00053779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_2473-14_0_6_line_21 |  | 20 | 21 | 0.020568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_2473-14_0_6_line_22 |  | 21 | 22 | 0.027503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2473-14_0_6_trafo_5 | 0.63 MVA 20/0.4 kV | 24 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2612729.3364 | 1258855.894 | 2612733.5918 | 1258857.4486 | 2612748.0525 | 1258855.734
1 | 2612748.0525 | 1258855.734 | 2612863.6394 | 1258811.2085
2 | 2612729.3364 | 1258855.894 | 2612723.8212 | 1258837.2141 | 2612723.1247 | 1258831.5977 | 2612720.3214 | 1258827.7336 | 2612716.1034 | 1258822.8101 | 2612713.9672 | 1258821.0965
3 | 2612863.6394 | 1258811.2085 | 2612894.3681 | 1258604.291
4 | 2612863.6394 | 1258811.2085 | 2612869.87 | 1258832.5043
5 | 2612706.7708 | 1258814.9018 | 2612710.8361 | 1258818.5849 | 2612713.9672 | 1258821.0965
6 | 2612883.2514 | 1258568.2206 | 2612894.3681 | 1258604.291
7 | 2612706.7708 | 1258814.9018 | 2612704.4641 | 1258812.8118 | 2612697.0386 | 1258806.1804 | 2612689.1003 | 1258799.0971
8 | 2612666.2137 | 1258779.5412 | 2612687.2959 | 1258797.4871 | 2612689.1003 | 1258799.0971
9 | 2612629.4391 | 1258646.3133 | 2612629.2472 | 1258655.482
10 | 2612628.854 | 1258660.6899 | 2612629.2154 | 1258657.0022 | 2612629.2472 | 1258655.482
11 | 2612628.854 | 1258660.6899 | 2612628.0101 | 1258669.3015
12 | 2612628.0101 | 1258669.3015 | 2612627.3123 | 1258676.4223 | 2612627.3213 | 1258693.4783 | 2612629.4147 | 1258701.5548 | 2612632.908 | 1258714.193 | 2612637.1098 | 1258726.8438 | 2612638.6046 | 1258733.8198
13 | 2612639.8937 | 1258739.8362 | 2612638.6046 | 1258733.8198
14 | 2612654.8375 | 1258539.6777 | 2612656.5093 | 1258540.4484
15 | 2612654.8375 | 1258539.6777 | 2612657.0737 | 1258516.0888 | 2612658.5477 | 1258506.1981
16 | 2612658.5477 | 1258506.1981 | 2612663.2683 | 1258474.5217
17 | 2612883.2514 | 1258568.2206 | 2612848.8298 | 1258451.6293
18 | 2612667.3069 | 1258454.335 | 2612848.8298 | 1258451.6293
19 | 2612667.3069 | 1258454.335 | 2612663.6581 | 1258471.9064 | 2612663.2683 | 1258474.5217
20 | 2612665.8033 | 1258779.1936 | 2612666.2137 | 1258779.5412
21 | 2612651.2587 | 1258764.7051 | 2612653.9143 | 1258767.9405 | 2612661.6466 | 1258775.6733 | 2612665.8033 | 1258779.1936
22 | 2612639.8937 | 1258739.8362 | 2612639.8937 | 1258739.8362 | 2612645.3501 | 1258754.4465 | 2612649.005 | 1258761.9594 | 2612651.2587 | 1258764.7051

## bus_geodata
| x | y | coords
0 | 2612748.0525 | 1258855.734
1 | 2612729.3364 | 1258855.894
2 | 2612863.6394 | 1258811.2085
3 | 2612713.9672 | 1258821.0965
4 | 2612869.87 | 1258832.5043
5 | 2612894.3681 | 1258604.291
6 | 2612706.7708 | 1258814.9018
7 | 2612689.1003 | 1258799.0971
8 | 2612629.4391 | 1258646.3133
9 | 2612629.2472 | 1258655.482
10 | 2612628.854 | 1258660.6899
11 | 2612628.0101 | 1258669.3015
12 | 2612638.6046 | 1258733.8198
13 | 2612656.5093 | 1258540.4484
14 | 2612654.8375 | 1258539.6777
15 | 2612658.5477 | 1258506.1981
16 | 2612883.2514 | 1258568.2206
17 | 2612848.8298 | 1258451.6293
18 | 2612663.2683 | 1258474.5217
19 | 2612666.2137 | 1258779.5412
20 | 2612665.8033 | 1258779.1936
21 | 2612651.2587 | 1258764.7051
22 | 2612639.8937 | 1258739.8362
23 | 2612667.3069 | 1258454.335
24 | 2612641.7037 | 1258604.7269

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98843 | -0.22048 | 0.002675 | 0.00067042
1 | 0.98924 | -0.20487 | 0 | 0
2 | 0.98323 | -0.32118 | 0.099381 | 0.024907
3 | 0.9909 | -0.17295 | 0.001182 | 0.00029623
4 | 0.98305 | -0.32482 | 0.009099 | 0.0022804
5 | 0.97864 | -0.41072 | 0.040756 | 0.010214
6 | 0.99131 | -0.16518 | 0.0014808 | 0.00037113
7 | 0.99233 | -0.14569 | 0.0070983 | 0.001779
8 | 0.99919 | -0.015536 | 0.039925 | 0.010006
9 | 0.99952 | -0.0091458 | 0.060437 | 0.015147
10 | 1 | 0 | -0.44131 | -0.11195
11 | 0.99947 | -0.010103 | 0.065254 | 0.016354
12 | 0.99617 | -0.072507 | 0.017794 | 0.0044596
13 | 0.97369 | -0.50809 | 0.013564 | 0.0033995
14 | 0.97371 | -0.50764 | 0 | 0
15 | 0.97393 | -0.50343 | 0.0083077 | 0.0020821
16 | 0.9781 | -0.42136 | 0 | 0
17 | 0.97635 | -0.45569 | 0.014643 | 0.0036698
18 | 0.97406 | -0.50086 | 0.023869 | 0.0059821
19 | 0.99366 | -0.12024 | 0 | 0
20 | 0.99369 | -0.11979 | 0.0064501 | 0.0016166
21 | 0.99462 | -0.10197 | 0.0025881 | 0.00064863
22 | 0.99588 | -0.07795 | 0.0035486 | 0.00088937
23 | 0.97423 | -0.4974 | 0.016932 | 0.0042436
24 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23114 | -0.058628 | 0.23131 | 0.058738 | 0.00017363 | 0.0001099 | 0.34822 | 0.34822 | 0.34822 | 0.98843 | -0.22048 | 0.98924 | -0.20487 | 19.1328
1 | 0.22847 | 0.057958 | -0.22737 | -0.057261 | 0.0011006 | 0.00069646 | 0.34419 | 0.34419 | 0.34419 | 0.98843 | -0.22048 | 0.98323 | -0.32118 | 18.9117
2 | -0.23131 | -0.058738 | 0.23167 | 0.058963 | 0.00035587 | 0.00022524 | 0.34822 | 0.34822 | 0.34822 | 0.98924 | -0.20487 | 0.9909 | -0.17295 | 19.1328
3 | 0.11888 | 0.030073 | -0.11838 | -0.029761 | 0.00050844 | 0.0003122 | 0.18002 | 0.18002 | 0.18002 | 0.98323 | -0.32118 | 0.97864 | -0.41072 | 9.8913
4 | 0.0091006 | 0.0022812 | -0.009099 | -0.0022804 | 1.5784e-06 | 7.2881e-07 | 0.013773 | 0.013773 | 0.013773 | 0.98323 | -0.32118 | 0.98305 | -0.32482 | 3.7838
5 | -0.23285 | -0.05926 | 0.23294 | 0.059315 | 8.7272e-05 | 5.5242e-05 | 0.34999 | 0.34999 | 0.34999 | 0.9909 | -0.17295 | 0.99131 | -0.16518 | 19.2302
6 | 0.07762 | 0.019547 | -0.07758 | -0.019524 | 3.9453e-05 | 2.288e-05 | 0.11805 | 0.11805 | 0.11805 | 0.97864 | -0.41072 | 0.9781 | -0.42136 | 6.4865
7 | -0.23442 | -0.059686 | 0.23464 | 0.059826 | 0.00022057 | 0.00013964 | 0.35221 | 0.35221 | 0.35221 | 0.99131 | -0.16518 | 0.99233 | -0.14569 | 19.3524
8 | -0.24174 | -0.061605 | 0.24204 | 0.061793 | 0.00029727 | 0.00018831 | 0.36286 | 0.36286 | 0.36286 | 0.99233 | -0.14569 | 0.99366 | -0.12024 | 19.9372
9 | -0.039925 | -0.010006 | 0.039937 | 0.010014 | 1.2157e-05 | 7.6604e-06 | 0.059457 | 0.059457 | 0.059457 | 0.99919 | -0.015536 | 0.99952 | -0.0091458 | 16.3342
10 | -0.10037 | -0.025161 | 0.10042 | 0.025189 | 4.376e-05 | 2.7938e-05 | 0.14943 | 0.14943 | 0.14943 | 0.99952 | -0.0091458 | 1 | 0 | 41.0525
11 | 0.33924 | 0.086759 | -0.33908 | -0.086653 | 0.00016577 | 0.00010553 | 0.50541 | 0.50541 | 0.50541 | 1 | 0 | 0.99947 | -0.010103 | 27.77
12 | 0.27382 | 0.070299 | -0.273 | -0.069774 | 0.00082671 | 0.00052477 | 0.40826 | 0.40827 | 0.40827 | 0.99947 | -0.010103 | 0.99617 | -0.072507 | 22.4322
13 | 0.2552 | 0.065314 | -0.25514 | -0.065272 | 6.7229e-05 | 4.2626e-05 | 0.38169 | 0.38169 | 0.38169 | 0.99617 | -0.072507 | 0.99588 | -0.07795 | 20.9718
14 | -0.013564 | -0.0033995 | 0.013564 | 0.0033997 | 2.9663e-07 | 1.6695e-07 | 0.020729 | 0.020729 | 0.020729 | 0.97369 | -0.50809 | 0.97371 | -0.50764 | 5.6948
15 | -0.013564 | -0.0033997 | 0.013567 | 0.0034005 | 2.7146e-06 | 8.9895e-07 | 0.020729 | 0.020729 | 0.020729 | 0.97371 | -0.50764 | 0.97393 | -0.50343 | 2.8474
16 | -0.021875 | -0.0054827 | 0.021877 | 0.0054824 | 2.6829e-06 | -2.7586e-07 | 0.033422 | 0.033421 | 0.033422 | 0.97393 | -0.50343 | 0.97406 | -0.50086 | 1.8364
17 | 0.07758 | 0.019524 | -0.077453 | -0.01945 | 0.00012707 | 7.3711e-05 | 0.11805 | 0.11806 | 0.11806 | 0.9781 | -0.42136 | 0.97635 | -0.45569 | 6.4867
18 | 0.062811 | 0.01578 | -0.062686 | -0.015712 | 0.00012481 | 6.8553e-05 | 0.095741 | 0.095745 | 0.095745 | 0.97635 | -0.45569 | 0.97423 | -0.4974 | 5.2607
19 | -0.045746 | -0.011464 | 0.045754 | 0.011468 | 7.5419e-06 | 3.5451e-06 | 0.069884 | 0.069884 | 0.069884 | 0.97406 | -0.50086 | 0.97423 | -0.4974 | 3.8398
20 | -0.24204 | -0.061793 | 0.24204 | 0.061796 | 5.3106e-06 | 3.3639e-06 | 0.36286 | 0.36286 | 0.36286 | 0.99366 | -0.12024 | 0.99369 | -0.11979 | 19.9371
21 | -0.24849 | -0.063413 | 0.24871 | 0.063549 | 0.00021406 | 0.00013567 | 0.37251 | 0.37251 | 0.37251 | 0.99369 | -0.11979 | 0.99462 | -0.10197 | 20.4678
22 | -0.25129 | -0.064197 | 0.25159 | 0.064382 | 0.00029222 | 0.00018523 | 0.37639 | 0.37638 | 0.37639 | 0.99462 | -0.10197 | 0.99588 | -0.07795 | 20.6805

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52018 | 0.13171

## res_load
| p_mw | q_mvar
0 | 0.002675 | 0.00067042
1 | 0.099381 | 0.024907
2 | 0.001182 | 0.00029623
3 | 0.009099 | 0.0022804
4 | 0.040756 | 0.010214
5 | 0.0014808 | 0.00037113
6 | 0.0070983 | 0.001779
7 | 0.039925 | 0.010006
8 | 0.060437 | 0.015147
9 | 0.07887 | 0.019767
10 | 0.065254 | 0.016354
11 | 0.017794 | 0.0044596
12 | 0.013564 | 0.0033995
13 | 0.0083077 | 0.0020821
14 | 0.014643 | 0.0036698
15 | 0.023869 | 0.0059821
16 | 0.0064501 | 0.0016166
17 | 0.0025881 | 0.00064863
18 | 0.0035486 | 0.00088937
19 | 0.016932 | 0.0042436

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1