## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2473-18_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2473-18_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2473-18_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2473-18_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2473-18_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2473-18_0_4_node_62 | 0.4 | n |  | TRUE
6 | bus_LV_2473-18_0_4_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_2473-18_0_4_node_64 | 0.4 | n |  | TRUE
8 | bus_LV_2473-18_0_4_node_60 | 0.4 | n |  | TRUE
9 | bus_LV_2473-18_0_4_node_56 | 0.4 | n |  | TRUE
10 | bus_LV_2473-18_0_4_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_2473-18_0_4_node_69 | 0.4 | n |  | TRUE
12 | bus_LV_2473-18_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2473-18_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2473-18_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2473-18_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2473-18_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2473-18_0_4_node_71 | 0.4 | n |  | TRUE
18 | bus_LV_2473-18_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2473-18_0_4_node_90 | 0.4 | n |  | TRUE
20 | bus_LV_2473-18_0_4_node_72 | 0.4 | n |  | TRUE
21 | bus_LV_2473-18_0_4_node_97 | 0.4 | n |  | TRUE
22 | bus_LV_2473-18_0_4_node_66 | 0.4 | n |  | TRUE
23 | bus_LV_2473-18_0_4_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_2473-18_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_2473-18_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_2473-18_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2473-18_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2473-18_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2473-18_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2473-18_0_4_node_85 | 0.4 | n |  | TRUE
31 | bus_LV_2473-18_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2473-18_0_4_node_80 | 0.4 | n |  | TRUE
33 | bus_LV_2473-18_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2473-18_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_2473-18_0_4_node_93 | 0.4 | n |  | TRUE
36 | bus_LV_2473-18_0_4_node_79 | 0.4 | n |  | TRUE
37 | bus_LV_2473-18_0_4_node_81 | 0.4 | n |  | TRUE
38 | bus_LV_2473-18_0_4_node_84 | 0.4 | n |  | TRUE
39 | bus_LV_2473-18_0_4_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_2473-18_0_4_node_18 | 0.4 | n |  | TRUE
41 | bus_LV_2473-18_0_4_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2473-18_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2473-18_0_4_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_2473-18_0_4_node_94 | 0.4 | n |  | TRUE
45 | bus_LV_2473-18_0_4_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_2473-18_0_4_node_70 | 0.4 | n |  | TRUE
47 | bus_LV_2473-18_0_4_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_2473-18_0_4_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_2473-18_0_4_node_96 | 0.4 | n |  | TRUE
50 | bus_LV_2473-18_0_4_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_2473-18_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_2473-18_0_4_node_95 | 0.4 | n |  | TRUE
53 | bus_LV_2473-18_0_4_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_2473-18_0_4_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_2473-18_0_4_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_2473-18_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_2473-18_0_4_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_2473-18_0_4_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_2473-18_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2473-18_0_4_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_2473-18_0_4_node_82 | 0.4 | n |  | TRUE
62 | bus_LV_2473-18_0_4_node_39 | 0.4 | n |  | TRUE
63 | bus_LV_2473-18_0_4_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_2473-18_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_2473-18_0_4_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2473-18_0_4_node_35 | 0.4 | n |  | TRUE
67 | bus_LV_2473-18_0_4_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_2473-18_0_4_node_37 | 0.4 | n |  | TRUE
69 | bus_LV_2473-18_0_4_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_2473-18_0_4_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2473-18_0_4_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_2473-18_0_4_node_42 | 0.4 | n |  | TRUE
73 | bus_LV_2473-18_0_4_node_43 | 0.4 | n |  | TRUE
74 | bus_LV_2473-18_0_4_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_2473-18_0_4_node_77 | 0.4 | n |  | TRUE
76 | bus_LV_2473-18_0_4_node_87 | 0.4 | n |  | TRUE
77 | bus_LV_2473-18_0_4_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_2473-18_0_4_node_86 | 0.4 | n |  | TRUE
79 | bus_LV_2473-18_0_4_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_2473-18_0_4_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_2473-18_0_4_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_2473-18_0_4_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_2473-18_0_4_node_58 | 0.4 | n |  | TRUE
84 | bus_LV_2473-18_0_4_node_59 | 0.4 | n |  | TRUE
85 | bus_LV_2473-18_0_4_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_2473-18_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_2473-18_0_4_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_2473-18_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2473-18_0_4_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2473-18_0_4_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_2473-18_0_4_node_88 | 0.4 | n |  | TRUE
92 | bus_MV_286_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2473-18_0_4_load_0 | 0 | 0.0056481 | 0.0014155 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2473-18_0_4_load_1 | 1 | 0.0021488 | 0.00053854 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2473-18_0_4_load_2 | 2 | 0.0027066 | 0.00067834 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2473-18_0_4_load_3 | 3 | 0.0019637 | 0.00049214 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2473-18_0_4_load_28 | 6 | 0.0032111 | 0.00080478 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2473-18_0_4_load_64 | 7 | 0.0048723 | 0.0012211 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2473-18_0_4_load_56 | 9 | 0.0059419 | 0.0014892 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2473-18_0_4_load_29 | 10 | 0.0055435 | 0.0013893 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2473-18_0_4_load_69 | 11 | 0.0055457 | 0.0013899 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2473-18_0_4_load_5 | 12 | 0.0076272 | 0.0019116 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2473-18_0_4_load_6 | 13 | 0.0060836 | 0.0015247 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2473-18_0_4_load_7 | 14 | 0.0051624 | 0.0012938 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2473-18_0_4_load_9 | 16 | 0.0026098 | 0.00065407 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2473-18_0_4_load_16 | 18 | 0.0025516 | 0.0006395 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2473-18_0_4_load_90 | 19 | 0.0034603 | 0.00086724 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2473-18_0_4_load_97 | 21 | 0.0034618 | 0.0008676 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2473-18_0_4_load_53 | 23 | 0.003019 | 0.00075664 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2473-18_0_4_load_10 | 24 | 0.0039317 | 0.00098539 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2473-18_0_4_load_11 | 25 | 0.013741 | 0.0034438 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2473-18_0_4_load_13 | 27 | 0.0071099 | 0.0017819 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2473-18_0_4_load_15 | 31 | 0.0022877 | 0.00057336 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2473-18_0_4_load_80 | 32 | 0.010261 | 0.0025715 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2473-18_0_4_load_93 | 35 | 0.075068 | 0.018814 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2473-18_0_4_load_84 | 38 | 0.0037937 | 0.00095078 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2473-18_0_4_load_17 | 39 | 0.0079861 | 0.0020015 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2473-18_0_4_load_18 | 40 | 0.0065448 | 0.0016403 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2473-18_0_4_load_20 | 41 | 0.0047217 | 0.0011834 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2473-18_0_4_load_27 | 42 | 0.0075513 | 0.0018925 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2473-18_0_4_load_94 | 44 | 0.0015569 | 0.0003902 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2473-18_0_4_load_46 | 45 | 0.0040276 | 0.0010094 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2473-18_0_4_load_70 | 46 | 0.0093589 | 0.0023456 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2473-18_0_4_load_45 | 51 | 0.0039358 | 0.0009864 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2473-18_0_4_load_95 | 52 | 0.0083308 | 0.0020879 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2473-18_0_4_load_47 | 54 | 0.0050666 | 0.0012698 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2473-18_0_4_load_30 | 55 | 0.003139 | 0.00078671 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2473-18_0_4_load_44 | 59 | 0.030208 | 0.0075708 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2473-18_0_4_load_40 | 60 | 0.011014 | 0.0027604 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2473-18_0_4_load_82 | 61 | 0.012214 | 0.0030612 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2473-18_0_4_load_54 | 65 | 0.0030821 | 0.00077245 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2473-18_0_4_load_35 | 66 | 0.0030249 | 0.00075812 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2473-18_0_4_load_36 | 67 | 0.0030961 | 0.00077595 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2473-18_0_4_load_37 | 68 | 0.0023449 | 0.00058768 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2473-18_0_4_load_50 | 70 | 0.0027844 | 0.00069783 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2473-18_0_4_load_51 | 71 | 0.0076292 | 0.0019121 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2473-18_0_4_load_42 | 72 | 0.003455 | 0.00086591 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2473-18_0_4_load_43 | 73 | 0.010961 | 0.002747 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2473-18_0_4_load_63 | 74 | 0.0040171 | 0.0010068 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2473-18_0_4_load_87 | 76 | 0.0026988 | 0.00067638 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2473-18_0_4_load_75 | 77 | 0.0035008 | 0.00087738 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2473-18_0_4_load_86 | 78 | 0.0045939 | 0.0011513 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2473-18_0_4_load_52 | 79 | 0.0055893 | 0.0014008 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2473-18_0_4_load_67 | 80 | 0.0080767 | 0.0020242 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2473-18_0_4_load_68 | 81 | 0.0070468 | 0.0017661 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2473-18_0_4_load_65 | 82 | 0.0052049 | 0.0013045 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2473-18_0_4_load_58 | 83 | 0.0068028 | 0.0017049 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2473-18_0_4_load_59 | 84 | 0.0067777 | 0.0016987 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2473-18_0_4_load_61 | 85 | 0.0055779 | 0.0013979 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2473-18_0_4_load_78 | 86 | 0.0055571 | 0.0013927 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2473-18_0_4_load_91 | 87 | 0.0033779 | 0.00084658 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2473-18_0_4_load_73 | 88 | 0.00257 | 0.00064411 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2473-18_0_4_load_74 | 89 | 0.0023946 | 0.00060015 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2473-18_0_4_load_76 | 90 | 0.0030063 | 0.00075346 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2473-18_0_4_load_88 | 91 | 0.0059452 | 0.00149 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2473-18_0_4_line_0 |  | 0 | 1 | 0.011747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2473-18_0_4_line_1 |  | 0 | 2 | 0.011931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2473-18_0_4_line_2 |  | 1 | 3 | 0.0017869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2473-18_0_4_line_3 |  | 2 | 4 | 0.020672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2473-18_0_4_line_4 |  | 3 | 5 | 0.032708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2473-18_0_4_line_5 |  | 4 | 6 | 0.011047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2473-18_0_4_line_6 |  | 5 | 7 | 0.043646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2473-18_0_4_line_7 |  | 5 | 8 | 0.002554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2473-18_0_4_line_8 |  | 6 | 9 | 0.029835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2473-18_0_4_line_9 |  | 7 | 82 | 0.016877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2473-18_0_4_line_10 |  | 8 | 74 | 0.034373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2473-18_0_4_line_11 |  | 8 | 83 | 0.035041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2473-18_0_4_line_12 |  | 10 | 11 | 0.018009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2473-18_0_4_line_13 |  | 11 | 33 | 0.038755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2473-18_0_4_line_14 |  | 12 | 13 | 0.0086347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2473-18_0_4_line_15 |  | 12 | 14 | 0.010027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2473-18_0_4_line_16 |  | 13 | 15 | 0.066802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2473-18_0_4_line_17 |  | 14 | 16 | 0.016234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2473-18_0_4_line_18 |  | 15 | 17 | 0.065209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2473-18_0_4_line_19 |  | 16 | 18 | 0.013673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2473-18_0_4_line_20 |  | 17 | 19 | 0.020448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2473-18_0_4_line_21 |  | 18 | 23 | 0.0032176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2473-18_0_4_line_22 |  | 19 | 87 | 0.014408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2473-18_0_4_line_23 |  | 20 | 21 | 0.015226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2473-18_0_4_line_24 |  | 20 | 22 | 0.12231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2473-18_0_4_line_25 |  | 21 | 53 | 0.098075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2473-18_0_4_line_26 |  | 22 | 82 | 0.10546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2473-18_0_4_line_27 |  | 23 | 38 | 0.032246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2473-18_0_4_line_28 |  | 24 | 25 | 0.02106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2473-18_0_4_line_29 |  | 24 | 26 | 0.015282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2473-18_0_4_line_30 |  | 25 | 27 | 0.0020843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2473-18_0_4_line_31 |  | 26 | 28 | 0.010341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2473-18_0_4_line_32 |  | 27 | 29 | 0.026685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2473-18_0_4_line_33 |  | 28 | 30 | 0.003518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2473-18_0_4_line_34 |  | 29 | 33 | 0.043524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2473-18_0_4_line_35 |  | 29 | 34 | 0.024623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2473-18_0_4_line_36 |  | 30 | 35 | 0.022436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2473-18_0_4_line_37 |  | 30 | 36 | 0.028989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2473-18_0_4_line_38 |  | 31 | 32 | 0.012657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2473-18_0_4_line_39 |  | 32 | 37 | 0.0094753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2473-18_0_4_line_40 |  | 33 | 46 | 0.022773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2473-18_0_4_line_41 |  | 33 | 43 | 0.075391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2473-18_0_4_line_42 |  | 34 | 45 | 0.018933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2473-18_0_4_line_43 |  | 36 | 86 | 0.038306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2473-18_0_4_line_44 |  | 37 | 81 | 0.020501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2473-18_0_4_line_45 |  | 38 | 75 | 0.010746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2473-18_0_4_line_46 |  | 39 | 40 | 0.010543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2473-18_0_4_line_47 |  | 40 | 41 | 0.017386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2473-18_0_4_line_48 |  | 41 | 42 | 0.0004246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2473-18_0_4_line_49 |  | 42 | 50 | 0.021995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2473-18_0_4_line_50 |  | 43 | 44 | 0.0084683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2473-18_0_4_line_51 |  | 44 | 47 | 0.0063589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2473-18_0_4_line_52 |  | 45 | 51 | 0.0085793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2473-18_0_4_line_53 |  | 47 | 48 | 0.097072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2473-18_0_4_line_54 |  | 48 | 49 | 0.046662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2473-18_0_4_line_55 |  | 49 | 52 | 0.0252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2473-18_0_4_line_56 |  | 50 | 53 | 0.014205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2473-18_0_4_line_57 |  | 50 | 54 | 0.0046407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2473-18_0_4_line_58 |  | 53 | 75 | 0.01875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2473-18_0_4_line_59 |  | 53 | 76 | 0.023802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2473-18_0_4_line_60 |  | 55 | 56 | 0.0039179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2473-18_0_4_line_61 |  | 56 | 57 | 0.040487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2473-18_0_4_line_62 |  | 57 | 61 | 0.0062155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2473-18_0_4_line_63 |  | 58 | 59 | 0.016327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2473-18_0_4_line_64 |  | 58 | 60 | 0.033248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2473-18_0_4_line_65 |  | 59 | 62 | 0.03624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2473-18_0_4_line_66 |  | 60 | 63 | 0.012781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2473-18_0_4_line_67 |  | 61 | 64 | 0.014988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2473-18_0_4_line_68 |  | 62 | 68 | 0.01639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2473-18_0_4_line_69 |  | 63 | 72 | 0.032346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2473-18_0_4_line_70 |  | 63 | 73 | 0.0045031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2473-18_0_4_line_71 |  | 64 | 65 | 0.014298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2473-18_0_4_line_72 |  | 65 | 72 | 0.013927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2473-18_0_4_line_73 |  | 66 | 67 | 0.030391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2473-18_0_4_line_74 |  | 66 | 68 | 0.012868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2473-18_0_4_line_75 |  | 67 | 69 | 0.018828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2473-18_0_4_line_76 |  | 69 | 70 | 0.003663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2473-18_0_4_line_77 |  | 70 | 71 | 0.024372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2473-18_0_4_line_78 |  | 71 | 79 | 0.0028159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2473-18_0_4_line_79 |  | 73 | 74 | 0.038218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2473-18_0_4_line_80 |  | 75 | 77 | 0.022928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2473-18_0_4_line_81 |  | 76 | 78 | 0.021443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2473-18_0_4_line_82 |  | 77 | 88 | 0.00069565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2473-18_0_4_line_83 |  | 78 | 91 | 0.013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2473-18_0_4_line_84 |  | 79 | 80 | 0.011711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2473-18_0_4_line_85 |  | 80 | 81 | 0.018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2473-18_0_4_line_86 |  | 83 | 84 | 0.015686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2473-18_0_4_line_87 |  | 84 | 85 | 0.0026903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2473-18_0_4_line_88 |  | 85 | 86 | 0.018035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2473-18_0_4_line_89 |  | 88 | 89 | 0.012275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2473-18_0_4_line_90 |  | 89 | 90 | 0.017738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2473-18_0_4_trafo_78 | 0.63 MVA 20/0.4 kV | 92 | 86 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2613063.2308 | 1259596.8928 | 2613074.8828 | 1259598.381
1 | 2613063.2308 | 1259596.8928 | 2613052.7162 | 1259595.5499 | 2613051.3873 | 1259595.4824
2 | 2613076.6553 | 1259598.6074 | 2613074.8828 | 1259598.381
3 | 2613030.7419 | 1259594.4343 | 2613051.3873 | 1259595.4824
4 | 2613107.9992 | 1259594.7043 | 2613100.3678 | 1259596.6777 | 2613097.8165 | 1259598.4288 | 2613095.7567 | 1259599.4916 | 2613092.4004 | 1259600.6183 | 2613076.6553 | 1259598.6074
5 | 2613030.7419 | 1259594.4343 | 2613031.5722 | 1259583.4186
6 | 2613107.9992 | 1259594.7043 | 2613105.6021 | 1259591.4968 | 2613102.5987 | 1259586.3979 | 2613099.8018 | 1259579.8984 | 2613098.1989 | 1259572.0006 | 2613097.7998 | 1259565.0062 | 2613098.9981 | 1259553.485
7 | 2613107.9992 | 1259594.7043 | 2613109.6001 | 1259596.698
8 | 2613031.5722 | 1259583.4186 | 2613033.8148 | 1259553.6677
9 | 2613098.9981 | 1259553.485 | 2613100.744 | 1259536.6981
10 | 2613109.6001 | 1259596.698 | 2613113.7731 | 1259601.1658 | 2613117.6553 | 1259604.1986 | 2613126.2339 | 1259610.1105 | 2613136.5893 | 1259617.8274
11 | 2613109.6001 | 1259596.698 | 2613104.1042 | 1259600.8999 | 2613101.4808 | 1259604.6188 | 2613100.3335 | 1259608.8303 | 2613098.5575 | 1259627.9548
12 | 2613027.1841 | 1259658.5626 | 2613028.1817 | 1259640.5813
13 | 2613025.0374 | 1259697.258 | 2613027.1841 | 1259658.5626
14 | 2612957.8775 | 1259468.0985 | 2612956.3822 | 1259459.5943
15 | 2612957.8775 | 1259468.0985 | 2612958.0383 | 1259469.0128 | 2612959.6537 | 1259477.9667
16 | 2612948.1717 | 1259393.3291 | 2612951.4121 | 1259424.6907 | 2612953.4227 | 1259442.7628 | 2612956.3822 | 1259459.5943
17 | 2612962.5362 | 1259493.943 | 2612959.6537 | 1259477.9667
18 | 2612948.1717 | 1259393.3291 | 2612900.9012 | 1259399.8974 | 2612887.6979 | 1259402.793 | 2612884.1434 | 1259404.9423
19 | 2612962.5362 | 1259493.943 | 2612964.964 | 1259507.3992
20 | 2612884.1434 | 1259404.9423 | 2612880.2266 | 1259407.3132 | 2612876.804 | 1259411.1973 | 2612874.5995 | 1259416.396 | 2612873.4854 | 1259421.3177
21 | 2612965.5353 | 1259510.5656 | 2612964.964 | 1259507.3992
22 | 2612873.4854 | 1259421.3177 | 2612870.3044 | 1259435.3703
23 | 2613006.1783 | 1259460.9236 | 2613005.4441 | 1259476.1322
24 | 2613006.1783 | 1259460.9236 | 2613006.7993 | 1259456.1328 | 2613009.794 | 1259448.0784 | 2613013.8565 | 1259441.0825 | 2613019.778 | 1259435.3583 | 2613027.5216 | 1259430.383 | 2613033.85 | 1259428.1287 | 2613040.8772 | 1259426.8321 | 2613052.8566 | 1259425.3018 | 2613062.0214 | 1259425.2997 | 2613067.3575 | 1259425.2558 | 2613074.918 | 1259424.7832 | 2613082.2535 | 1259423.8098 | 2613094.855 | 1259420.4242 | 2613101.1041 | 1259430.2001 | 2613103.1032 | 1259432.8063
25 | 2612984.231 | 1259567.9257 | 2612997.0872 | 1259551.3315 | 2613002.1099 | 1259542.9368 | 2613004.1961 | 1259536.6927 | 2613005.4261 | 1259529.1347 | 2613006.3021 | 1259521.4314 | 2613005.4441 | 1259476.1322
26 | 2613103.1032 | 1259432.8063 | 2613105.041 | 1259435.8459 | 2613106.8494 | 1259439.4746 | 2613107.7532 | 1259443.1568 | 2613108.399 | 1259447.6391 | 2613108.8931 | 1259452.5768 | 2613108.066 | 1259461.948 | 2613105.8378 | 1259484.614 | 2613102.0116 | 1259524.5103 | 2613100.744 | 1259536.6981
27 | 2612965.5353 | 1259510.5656 | 2612968.4115 | 1259526.5076 | 2612971.1164 | 1259542.3244
28 | 2613072.3489 | 1259743.9985 | 2613051.3348 | 1259742.6109
29 | 2613087.5981 | 1259745.0054 | 2613072.3489 | 1259743.9985
30 | 2613049.2551 | 1259742.4736 | 2613051.3348 | 1259742.6109
31 | 2613087.5981 | 1259745.0054 | 2613088.5779 | 1259734.7117
32 | 2613022.6284 | 1259740.7154 | 2613049.2551 | 1259742.4736
33 | 2613088.5779 | 1259734.7117 | 2613088.9097 | 1259731.2101
34 | 2613022.6284 | 1259740.7154 | 2613023.884 | 1259718.0251 | 2613025.0374 | 1259697.258
35 | 2613021.7003 | 1259765.3189 | 2613022.6284 | 1259740.7154
36 | 2613088.9097 | 1259731.2101 | 2613108.9915 | 1259729.0751 | 2613111.1608 | 1259729.6358
37 | 2613091.6487 | 1259702.3522 | 2613088.9097 | 1259731.2101
38 | 2613135.0918 | 1259773.7669 | 2613132.6038 | 1259769.6992 | 2613129.2005 | 1259764.8995 | 2613127.9054 | 1259763.3694
39 | 2613139.4042 | 1259782.2004 | 2613139.2991 | 1259782.0001 | 2613135.6 | 1259774.598 | 2613135.0918 | 1259773.7669
40 | 2613025.0374 | 1259697.258 | 2613047.7441 | 1259698.9898
41 | 2612999.6542 | 1259749.0597 | 2613000.8177 | 1259733.9409 | 2613001.0979 | 1259726.4587 | 2613019.8307 | 1259727.7339 | 2613020.7041 | 1259717.7957 | 2613023.884 | 1259718.0251 | 2613025.0374 | 1259697.258
42 | 2613021.7003 | 1259765.3189 | 2613020.4609 | 1259784.2113
43 | 2613091.6487 | 1259702.3522 | 2613095.1907 | 1259664.2099
44 | 2613139.4042 | 1259782.2004 | 2613143.2032 | 1259781.8975 | 2613159.5148 | 1259785.4325
45 | 2612973.5998 | 1259552.7589 | 2612971.9761 | 1259547.3517 | 2612971.1164 | 1259542.3244
46 | 2612974.1969 | 1259622.7955 | 2612978.7112 | 1259613.2681
47 | 2612986.1559 | 1259597.5564 | 2612978.7112 | 1259613.2681
48 | 2612986.3377 | 1259597.1727 | 2612986.1559 | 1259597.5564
49 | 2612995.1468 | 1259577.0446 | 2612993.0006 | 1259583.1107 | 2612986.3377 | 1259597.1727
50 | 2612999.6542 | 1259749.0597 | 2613002.2817 | 1259750.2663 | 2613001.8893 | 1259755.8294
51 | 2613001.4418 | 1259762.1725 | 2613001.8893 | 1259755.8294
52 | 2613019.8992 | 1259792.7721 | 2613020.4609 | 1259784.2113
53 | 2612984.3223 | 1259726.1774 | 2612978.7702 | 1259745.8675 | 2612960.6624 | 1259755.201 | 2612958.1409 | 1259764.1015 | 2612969.2579 | 1259767.1722 | 2612971.2076 | 1259768.2105 | 2612978.7449 | 1259760.8776 | 2612989.4378 | 1259761.4458 | 2613001.4418 | 1259762.1725
54 | 2612975.8796 | 1259692.5473 | 2612968.5651 | 1259722.018 | 2612984.3223 | 1259726.1774
55 | 2612975.8796 | 1259692.5473 | 2612981.9471 | 1259668.0885
56 | 2612995.1468 | 1259577.0446 | 2612987.7673 | 1259570.6353 | 2612984.231 | 1259567.9257
57 | 2612995.1468 | 1259577.0446 | 2612999.0156 | 1259579.6074
58 | 2612973.5998 | 1259552.7589 | 2612975.6087 | 1259557.7556 | 2612976.9078 | 1259559.9043 | 2612978.9675 | 1259562.3438 | 2612981.4784 | 1259565.2512 | 2612984.231 | 1259567.9257
59 | 2612984.231 | 1259567.9257 | 2612969.0558 | 1259586.2631
60 | 2613206.69 | 1259612.2345 | 2613206.3798 | 1259616.1401
61 | 2613206.69 | 1259612.2345 | 2613207.2555 | 1259605.3533 | 2613209.3852 | 1259603.3456 | 2613205.5537 | 1259597.889 | 2613201.2053 | 1259597.7792 | 2613198.0723 | 1259596.7716 | 2613194.7461 | 1259594.5405 | 2613194.1437 | 1259590.9145 | 2613189.2608 | 1259583.7543
62 | 2613189.2608 | 1259583.7543 | 2613183.5951 | 1259586.3102
63 | 2613195.7928 | 1259683.1694 | 2613198.3988 | 1259687.3002 | 2613202.7507 | 1259692.5579 | 2613205.6898 | 1259696.1195
64 | 2613195.7928 | 1259683.1694 | 2613191.1338 | 1259677.0105 | 2613186.5275 | 1259670.885 | 2613175.9078 | 1259656.5234
65 | 2613230.1012 | 1259722.8058 | 2613223.4973 | 1259716.8982 | 2613220.1064 | 1259713.2771 | 2613215.9037 | 1259708.698 | 2613206.9974 | 1259697.7041 | 2613205.6898 | 1259696.1195
66 | 2613168.2004 | 1259646.3278 | 2613175.4594 | 1259655.917 | 2613175.9078 | 1259656.5234
67 | 2613168.6624 | 1259587.489 | 2613174.3455 | 1259587.2903 | 2613183.5951 | 1259586.3102
68 | 2613230.1012 | 1259722.8058 | 2613227.5823 | 1259739.001
69 | 2613168.2004 | 1259646.3278 | 2613170.1273 | 1259644.0194 | 2613172.1548 | 1259640.5437 | 2613172.8708 | 1259637.1208 | 2613172.4726 | 1259633.1839 | 2613168.8025 | 1259616.0975 | 2613168.8025 | 1259615.7121
70 | 2613168.2004 | 1259646.3278 | 2613165.1334 | 1259643.0305
71 | 2613168.6624 | 1259587.489 | 2613168.8011 | 1259592.9041 | 2613168.8016 | 1259601.7851
72 | 2613168.8025 | 1259615.7121 | 2613168.8016 | 1259601.7851
73 | 2613221.4867 | 1259781.8247 | 2613224.0991 | 1259761.3963 | 2613225.6047 | 1259751.7161
74 | 2613227.5823 | 1259739.001 | 2613225.6047 | 1259751.7161
75 | 2613219.0984 | 1259800.5006 | 2613221.4867 | 1259781.8247
76 | 2613219.0984 | 1259800.5006 | 2613215.5626 | 1259799.5439
77 | 2613215.5626 | 1259799.5439 | 2613201.3233 | 1259795.6912 | 2613191.9986 | 1259793.3251
78 | 2613189.2692 | 1259792.6325 | 2613191.9986 | 1259793.3251
79 | 2613136.5893 | 1259617.8274 | 2613139.6571 | 1259620.1135 | 2613153.93 | 1259630.9858 | 2613165.1334 | 1259643.0305
80 | 2612973.5998 | 1259552.7589 | 2612959.797 | 1259554.1965 | 2612952.8029 | 1259554.2034 | 2612950.7757 | 1259553.8572
81 | 2612955.3846 | 1259602.783 | 2612969.0558 | 1259586.2631
82 | 2612950.09 | 1259553.7401 | 2612950.7757 | 1259553.8572
83 | 2612946.9912 | 1259613.4419 | 2612950.7252 | 1259608.4133 | 2612955.3846 | 1259602.783
84 | 2613189.2692 | 1259792.6325 | 2613177.9176 | 1259789.7521
85 | 2613177.9176 | 1259789.7521 | 2613168.9652 | 1259787.4805 | 2613159.5148 | 1259785.4325
86 | 2613098.5575 | 1259627.9548 | 2613097.1071 | 1259643.5735
87 | 2613096.8583 | 1259646.2522 | 2613097.1071 | 1259643.5735
88 | 2613096.8583 | 1259646.2522 | 2613095.1907 | 1259664.2099
89 | 2612950.09 | 1259553.7401 | 2612947.1977 | 1259553.2461 | 2612943.3134 | 1259551.1363 | 2612939.4407 | 1259548.1004
90 | 2612939.4407 | 1259548.1004 | 2612927.6111 | 1259538.8271 | 2612925.1795 | 1259537.637

## bus_geodata
| x | y | coords
0 | 2613063.2308 | 1259596.8928
1 | 2613074.8828 | 1259598.381
2 | 2613051.3873 | 1259595.4824
3 | 2613076.6553 | 1259598.6074
4 | 2613030.7419 | 1259594.4343
5 | 2613107.9992 | 1259594.7043
6 | 2613031.5722 | 1259583.4186
7 | 2613098.9981 | 1259553.485
8 | 2613109.6001 | 1259596.698
9 | 2613033.8148 | 1259553.6677
10 | 2613028.1817 | 1259640.5813
11 | 2613027.1841 | 1259658.5626
12 | 2612957.8775 | 1259468.0985
13 | 2612956.3822 | 1259459.5943
14 | 2612959.6537 | 1259477.9667
15 | 2612948.1717 | 1259393.3291
16 | 2612962.5362 | 1259493.943
17 | 2612884.1434 | 1259404.9423
18 | 2612964.964 | 1259507.3992
19 | 2612873.4854 | 1259421.3177
20 | 2613006.1783 | 1259460.9236
21 | 2613005.4441 | 1259476.1322
22 | 2613103.1032 | 1259432.8063
23 | 2612965.5353 | 1259510.5656
24 | 2613072.3489 | 1259743.9985
25 | 2613051.3348 | 1259742.6109
26 | 2613087.5981 | 1259745.0054
27 | 2613049.2551 | 1259742.4736
28 | 2613088.5779 | 1259734.7117
29 | 2613022.6284 | 1259740.7154
30 | 2613088.9097 | 1259731.2101
31 | 2613127.9054 | 1259763.3694
32 | 2613135.0918 | 1259773.7669
33 | 2613025.0374 | 1259697.258
34 | 2613021.7003 | 1259765.3189
35 | 2613111.1608 | 1259729.6358
36 | 2613091.6487 | 1259702.3522
37 | 2613139.4042 | 1259782.2004
38 | 2612971.1164 | 1259542.3244
39 | 2612974.1969 | 1259622.7955
40 | 2612978.7112 | 1259613.2681
41 | 2612986.1559 | 1259597.5564
42 | 2612986.3377 | 1259597.1726
43 | 2612999.6542 | 1259749.0597
44 | 2613001.8893 | 1259755.8294
45 | 2613020.4609 | 1259784.2113
46 | 2613047.7441 | 1259698.9898
47 | 2613001.4418 | 1259762.1725
48 | 2612984.3223 | 1259726.1774
49 | 2612975.8796 | 1259692.5473
50 | 2612995.1468 | 1259577.0446
51 | 2613019.8992 | 1259792.7721
52 | 2612981.9471 | 1259668.0885
53 | 2612984.231 | 1259567.9257
54 | 2612999.0156 | 1259579.6074
55 | 2613206.3798 | 1259616.1401
56 | 2613206.69 | 1259612.2345
57 | 2613189.2608 | 1259583.7543
58 | 2613195.7928 | 1259683.1694
59 | 2613205.6898 | 1259696.1195
60 | 2613175.9078 | 1259656.5234
61 | 2613183.5951 | 1259586.3102
62 | 2613230.1012 | 1259722.8058
63 | 2613168.2004 | 1259646.3278
64 | 2613168.6624 | 1259587.489
65 | 2613168.8016 | 1259601.7851
66 | 2613225.6047 | 1259751.7161
67 | 2613221.4867 | 1259781.8247
68 | 2613227.5823 | 1259739.001
69 | 2613219.0984 | 1259800.5006
70 | 2613215.5626 | 1259799.5439
71 | 2613191.9986 | 1259793.3251
72 | 2613168.8025 | 1259615.7121
73 | 2613165.1334 | 1259643.0305
74 | 2613136.5893 | 1259617.8274
75 | 2612973.5998 | 1259552.7589
76 | 2612969.0558 | 1259586.2631
77 | 2612950.7757 | 1259553.8572
78 | 2612955.3846 | 1259602.783
79 | 2613189.2692 | 1259792.6325
80 | 2613177.9176 | 1259789.7521
81 | 2613159.5148 | 1259785.4325
82 | 2613100.744 | 1259536.6981
83 | 2613098.5575 | 1259627.9548
84 | 2613097.1071 | 1259643.5735
85 | 2613096.8583 | 1259646.2522
86 | 2613095.1907 | 1259664.2099
87 | 2612870.3044 | 1259435.3703
88 | 2612950.09 | 1259553.7401
89 | 2612939.4407 | 1259548.1004
90 | 2612925.1795 | 1259537.637
91 | 2612946.9912 | 1259613.4419
92 | 2613091.6487 | 1259702.3522

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99315 | -0.12999 | 0.0056481 | 0.0014155
1 | 0.99334 | -0.12636 | 0.0021488 | 0.00053854
2 | 0.99302 | -0.1325 | 0.0027066 | 0.00067834
3 | 0.99337 | -0.12574 | 0.0019637 | 0.00049214
4 | 0.99285 | -0.13584 | 0 | 0
5 | 0.99402 | -0.11326 | 0 | 0
6 | 0.99276 | -0.13763 | 0.0032111 | 0.00080478
7 | 0.99256 | -0.14097 | 0.0048723 | 0.0012211
8 | 0.99412 | -0.11131 | 0 | 0
9 | 0.9926 | -0.14077 | 0.0059419 | 0.0014892
10 | 0.98591 | -0.27137 | 0.0055435 | 0.0013893
11 | 0.986 | -0.26958 | 0.0055457 | 0.0013899
12 | 0.97501 | -0.48122 | 0.0076272 | 0.0019116
13 | 0.97491 | -0.48326 | 0.0060836 | 0.0015247
14 | 0.9752 | -0.47744 | 0.0051624 | 0.0012938
15 | 0.97448 | -0.49165 | 0 | 0
16 | 0.97559 | -0.46979 | 0.0026098 | 0.00065407
17 | 0.97407 | -0.49984 | 0 | 0
18 | 0.97595 | -0.4627 | 0.0025516 | 0.0006395
19 | 0.97394 | -0.50241 | 0.0034603 | 0.00086724
20 | 0.98328 | -0.31945 | 0 | 0
21 | 0.98259 | -0.33288 | 0.0034618 | 0.0008676
22 | 0.98883 | -0.21229 | 0 | 0
23 | 0.97604 | -0.46088 | 0.003019 | 0.00075664
24 | 0.98978 | -0.19611 | 0.0039317 | 0.00098539
25 | 0.98863 | -0.21831 | 0.013741 | 0.0034438
26 | 0.99066 | -0.17897 | 0 | 0
27 | 0.98855 | -0.22 | 0.0071099 | 0.0017819
28 | 0.99126 | -0.16739 | 0 | 0
29 | 0.98761 | -0.23825 | 0 | 0
30 | 0.99147 | -0.16345 | 0 | 0
31 | 0.97268 | -0.52723 | 0.0022877 | 0.00057336
32 | 0.97271 | -0.5267 | 0.010261 | 0.0025715
33 | 0.98639 | -0.26188 | 0 | 0
34 | 0.98743 | -0.24175 | 0 | 0
35 | 0.98993 | -0.19336 | 0.075068 | 0.018814
36 | 0.99514 | -0.0927 | 0 | 0
37 | 0.97282 | -0.52451 | 0 | 0
38 | 0.97706 | -0.4409 | 0.0037937 | 0.00095078
39 | 0.97701 | -0.44201 | 0.0079861 | 0.0020015
40 | 0.97709 | -0.44047 | 0.0065448 | 0.0016403
41 | 0.97732 | -0.43586 | 0.0047217 | 0.0011834
42 | 0.97733 | -0.43571 | 0.0075513 | 0.0018925
43 | 0.98571 | -0.27525 | 0 | 0
44 | 0.98563 | -0.27676 | 0.0015569 | 0.0003902
45 | 0.98729 | -0.24445 | 0.0040276 | 0.0010094
46 | 0.9862 | -0.2657 | 0.0093589 | 0.0023456
47 | 0.98558 | -0.27771 | 0 | 0
48 | 0.98484 | -0.29223 | 0 | 0
49 | 0.98448 | -0.29922 | 0 | 0
50 | 0.97787 | -0.42496 | 0 | 0
51 | 0.98726 | -0.24505 | 0.0039358 | 0.0009864
52 | 0.98428 | -0.303 | 0.0083308 | 0.0020879
53 | 0.97829 | -0.41671 | 0 | 0
54 | 0.97785 | -0.42538 | 0.0050666 | 0.0012698
55 | 0.98357 | -0.31441 | 0.003139 | 0.00078671
56 | 0.98358 | -0.31419 | 0 | 0
57 | 0.9837 | -0.3119 | 0 | 0
58 | 0.98137 | -0.35699 | 0 | 0
59 | 0.98012 | -0.38136 | 0.030208 | 0.0075708
60 | 0.98391 | -0.30756 | 0.011014 | 0.0027604
61 | 0.98371 | -0.31155 | 0.012214 | 0.0030612
62 | 0.97836 | -0.41571 | 0 | 0
63 | 0.98502 | -0.2861 | 0 | 0
64 | 0.98393 | -0.3074 | 0 | 0
65 | 0.98413 | -0.30345 | 0.0030821 | 0.00077245
66 | 0.97696 | -0.44298 | 0.0030249 | 0.00075812
67 | 0.97564 | -0.46897 | 0.0030961 | 0.00077595
68 | 0.97756 | -0.43128 | 0.0023449 | 0.00058768
69 | 0.97487 | -0.48404 | 0 | 0
70 | 0.97472 | -0.48697 | 0.0027844 | 0.00069783
71 | 0.9738 | -0.50528 | 0.0076292 | 0.0019121
72 | 0.98437 | -0.29883 | 0.003455 | 0.00086591
73 | 0.9855 | -0.27678 | 0.010961 | 0.002747
74 | 0.98997 | -0.1906 | 0.0040171 | 0.0010068
75 | 0.97744 | -0.43351 | 0 | 0
76 | 0.978 | -0.42245 | 0.0026988 | 0.00067638
77 | 0.97719 | -0.43831 | 0.0035008 | 0.00087738
78 | 0.97779 | -0.42657 | 0.0045939 | 0.0011513
79 | 0.97371 | -0.507 | 0.0055893 | 0.0014008
80 | 0.97341 | -0.51296 | 0.0080767 | 0.0020242
81 | 0.97306 | -0.51977 | 0.0070468 | 0.0017661
82 | 0.99202 | -0.15123 | 0.0052049 | 0.0013045
83 | 0.99693 | -0.05796 | 0.0068028 | 0.0017049
84 | 0.99822 | -0.033553 | 0.0067777 | 0.0016987
85 | 0.99845 | -0.029267 | 0.0055779 | 0.0013979
86 | 1 | 0 | -0.42497 | -0.10853
87 | 0.97389 | -0.5033 | 0.0033779 | 0.00084658
88 | 0.97719 | -0.43841 | 0.00257 | 0.00064411
89 | 0.97713 | -0.43962 | 0.0023946 | 0.00060015
90 | 0.97708 | -0.4406 | 0.0030063 | 0.00075346
91 | 0.97772 | -0.42804 | 0.0059452 | 0.00149
92 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.017512 | -0.0043898 | 0.017515 | 0.0043916 | 3.0326e-06 | 1.7888e-06 | 0.026238 | 0.026238 | 0.026238 | 0.99315 | -0.12999 | 0.99334 | -0.12636 | 7.2083
1 | 0.011864 | 0.0029742 | -0.011863 | -0.0029735 | 1.4137e-06 | 7.5042e-07 | 0.017776 | 0.017776 | 0.017776 | 0.99315 | -0.12999 | 0.99302 | -0.1325 | 4.8835
2 | -0.019664 | -0.0049301 | 0.019665 | 0.0049305 | 5.8147e-07 | 3.4901e-07 | 0.029457 | 0.029457 | 0.029457 | 0.99334 | -0.12636 | 0.99337 | -0.12574 | 8.0926
3 | 0.0091561 | 0.0022952 | -0.0091546 | -0.0022945 | 1.4593e-06 | 6.6656e-07 | 0.01372 | 0.01372 | 0.01372 | 0.99302 | -0.1325 | 0.99285 | -0.13584 | 3.7693
4 | -0.021628 | -0.0054226 | 0.021641 | 0.0054304 | 1.2875e-05 | 7.8161e-06 | 0.032399 | 0.032398 | 0.032399 | 0.99337 | -0.12574 | 0.99402 | -0.11326 | 8.9007
5 | 0.0091546 | 0.0022945 | -0.0091539 | -0.0022941 | 7.7984e-07 | 3.5625e-07 | 0.01372 | 0.01372 | 0.01372 | 0.99285 | -0.13584 | 0.99276 | -0.13763 | 3.7693
6 | 0.1094 | 0.028024 | -0.10926 | -0.027932 | 0.00014672 | 9.2206e-05 | 0.16399 | 0.16399 | 0.16399 | 0.99402 | -0.11326 | 0.99256 | -0.14097 | 15.0175
7 | -0.13105 | -0.033454 | 0.13106 | 0.033462 | 1.2313e-05 | 7.781e-06 | 0.19639 | 0.19639 | 0.19639 | 0.99402 | -0.11326 | 0.99412 | -0.11131 | 17.9843
8 | 0.0059427 | 0.0014894 | -0.0059419 | -0.0014892 | 8.8771e-07 | 1.8243e-07 | 0.0089074 | 0.0089075 | 0.0089075 | 0.99276 | -0.13763 | 0.9926 | -0.14077 | 2.4471
9 | 0.10439 | 0.026711 | -0.10433 | -0.026678 | 5.1794e-05 | 3.2494e-05 | 0.15669 | 0.15669 | 0.15669 | 0.99256 | -0.14097 | 0.99202 | -0.15123 | 14.3486
10 | 0.13203 | 0.033787 | -0.13153 | -0.033464 | 0.00050471 | 0.00032257 | 0.19788 | 0.19788 | 0.19788 | 0.99412 | -0.11131 | 0.98997 | -0.1906 | 54.3624
11 | -0.26309 | -0.067249 | 0.26377 | 0.067683 | 0.00068088 | 0.00043439 | 0.39427 | 0.39427 | 0.39427 | 0.99412 | -0.11131 | 0.99693 | -0.05796 | 36.1051
12 | -0.0055435 | -0.0013893 | 0.0055439 | 0.0013894 | 4.7274e-07 | 7.2881e-08 | 0.0083667 | 0.0083666 | 0.0083667 | 0.98591 | -0.27137 | 0.986 | -0.26958 | 2.2985
13 | -0.01109 | -0.0027793 | 0.011094 | 0.0027814 | 4.0705e-06 | 2.1106e-06 | 0.016736 | 0.016736 | 0.016736 | 0.986 | -0.26958 | 0.98639 | -0.26188 | 4.5978
14 | 0.012929 | 0.0032412 | -0.012928 | -0.0032405 | 1.2608e-06 | 6.9923e-07 | 0.019733 | 0.019733 | 0.019733 | 0.97501 | -0.48122 | 0.97491 | -0.48326 | 5.421
15 | -0.020557 | -0.0051528 | 0.02056 | 0.005155 | 3.7009e-06 | 2.2435e-06 | 0.031373 | 0.031373 | 0.031373 | 0.97501 | -0.48122 | 0.9752 | -0.47744 | 8.6189
16 | 0.0068446 | 0.0017158 | -0.0068419 | -0.0017149 | 2.7342e-06 | 9.1729e-07 | 0.010447 | 0.010447 | 0.010447 | 0.97491 | -0.48326 | 0.97448 | -0.49165 | 2.8702
17 | -0.025723 | -0.0064489 | 0.025732 | 0.0064547 | 9.3787e-06 | 5.7997e-06 | 0.03925 | 0.03925 | 0.03925 | 0.9752 | -0.47744 | 0.97559 | -0.46979 | 10.783
18 | 0.0068419 | 0.0017149 | -0.0068392 | -0.001714 | 2.6692e-06 | 8.9621e-07 | 0.010447 | 0.010448 | 0.010448 | 0.97448 | -0.49165 | 0.97407 | -0.49984 | 2.8703
19 | -0.028342 | -0.0071087 | 0.028352 | 0.0071147 | 9.5826e-06 | 5.9621e-06 | 0.04323 | 0.04323 | 0.04323 | 0.97559 | -0.46979 | 0.97595 | -0.4627 | 11.8765
20 | 0.0068392 | 0.001714 | -0.0068384 | -0.0017137 | 8.3703e-07 | 2.812e-07 | 0.010448 | 0.010448 | 0.010448 | 0.97407 | -0.49984 | 0.97394 | -0.50241 | 2.8703
21 | -0.030903 | -0.0077542 | 0.030906 | 0.0077559 | 2.6791e-06 | 1.6744e-06 | 0.047121 | 0.047121 | 0.047121 | 0.97595 | -0.4627 | 0.97604 | -0.46088 | 12.9453
22 | 0.0033781 | 0.0008465 | -0.0033779 | -0.00084658 | 1.4392e-07 | -8.7183e-08 | 0.0051611 | 0.0051611 | 0.0051611 | 0.97394 | -0.50241 | 0.97389 | -0.5033 | 1.4179
23 | 0.098328 | 0.024868 | -0.098265 | -0.024828 | 6.3283e-05 | 4.0115e-05 | 0.14888 | 0.14888 | 0.14888 | 0.98328 | -0.31945 | 0.98259 | -0.33288 | 20.4509
24 | -0.098328 | -0.024868 | 0.098836 | 0.025191 | 0.00050832 | 0.0003222 | 0.14888 | 0.14888 | 0.14888 | 0.98328 | -0.31945 | 0.98883 | -0.21229 | 20.4509
25 | 0.094803 | 0.023961 | -0.094423 | -0.02372 | 0.00037942 | 0.00024035 | 0.14364 | 0.14364 | 0.14364 | 0.98259 | -0.33288 | 0.97829 | -0.41671 | 19.7309
26 | -0.098836 | -0.025191 | 0.099128 | 0.025374 | 0.00029219 | 0.00018293 | 0.14888 | 0.14888 | 0.14888 | 0.98883 | -0.21229 | 0.99202 | -0.15123 | 13.6338
27 | -0.033925 | -0.0085125 | 0.033957 | 0.0085328 | 3.235e-05 | 2.0301e-05 | 0.051723 | 0.051723 | 0.051723 | 0.97604 | -0.46088 | 0.97706 | -0.4409 | 14.2097
28 | 0.05931 | 0.014921 | -0.059247 | -0.014881 | 6.2818e-05 | 3.9933e-05 | 0.089186 | 0.089186 | 0.089186 | 0.98978 | -0.19611 | 0.98863 | -0.21831 | 24.5017
29 | -0.063242 | -0.015906 | 0.063294 | 0.015939 | 5.1827e-05 | 3.2973e-05 | 0.095097 | 0.095097 | 0.095097 | 0.98978 | -0.19611 | 0.99066 | -0.17897 | 26.1255
30 | 0.045507 | 0.011437 | -0.045503 | -0.011435 | 3.6679e-06 | 2.3207e-06 | 0.068504 | 0.068504 | 0.068504 | 0.98863 | -0.21831 | 0.98855 | -0.22 | 18.8199
31 | -0.063294 | -0.015939 | 0.063329 | 0.015961 | 3.5069e-05 | 2.2311e-05 | 0.095097 | 0.095097 | 0.095097 | 0.99066 | -0.17897 | 0.99126 | -0.16739 | 26.1255
32 | 0.038393 | 0.0096528 | -0.03836 | -0.0096318 | 3.3433e-05 | 2.1056e-05 | 0.057802 | 0.057802 | 0.057802 | 0.98855 | -0.22 | 0.98761 | -0.23825 | 15.8797
33 | -0.063329 | -0.015961 | 0.063341 | 0.015969 | 1.193e-05 | 7.5902e-06 | 0.095097 | 0.095097 | 0.095097 | 0.99126 | -0.16739 | 0.99147 | -0.16345 | 26.1255
34 | 0.030394 | 0.0076351 | -0.030359 | -0.0076137 | 3.4237e-05 | 2.1355e-05 | 0.0458 | 0.0458 | 0.0458 | 0.98761 | -0.23825 | 0.98639 | -0.26188 | 12.5825
35 | 0.0079658 | 0.0019967 | -0.0079645 | -0.0019962 | 1.3301e-06 | 5.3626e-07 | 0.012002 | 0.012002 | 0.012002 | 0.98761 | -0.23825 | 0.98743 | -0.24175 | 3.2973
36 | 0.075175 | 0.018882 | -0.075068 | -0.018814 | 0.00010712 | 6.827e-05 | 0.11284 | 0.11284 | 0.11284 | 0.99147 | -0.16345 | 0.98993 | -0.19336 | 30.9997
37 | -0.13852 | -0.034851 | 0.13899 | 0.035152 | 0.00047003 | 0.00030044 | 0.20794 | 0.20794 | 0.20794 | 0.99147 | -0.16345 | 0.99514 | -0.0927 | 57.1251
38 | -0.0022877 | -0.00057336 | 0.0022878 | 0.00057324 | 5.8134e-08 | -1.199e-07 | 0.0034998 | 0.0034997 | 0.0034998 | 0.97268 | -0.52723 | 0.97271 | -0.5267 | 0.96148
39 | -0.012548 | -0.0031448 | 0.01255 | 0.0031455 | 1.3093e-06 | 7.2032e-07 | 0.019196 | 0.019196 | 0.019196 | 0.97271 | -0.5267 | 0.97282 | -0.52451 | 5.2736
40 | 0.0093606 | 0.0023464 | -0.0093589 | -0.0023456 | 1.7029e-06 | 7.992e-07 | 0.014121 | 0.014121 | 0.014121 | 0.98639 | -0.26188 | 0.9862 | -0.2657 | 3.8794
41 | 0.0099052 | 0.002486 | -0.0098988 | -0.0024829 | 6.3135e-06 | 3.079e-06 | 0.014944 | 0.014944 | 0.014944 | 0.98639 | -0.26188 | 0.98571 | -0.27525 | 4.1055
42 | 0.0079645 | 0.0019962 | -0.0079635 | -0.0019958 | 1.0228e-06 | 4.1242e-07 | 0.012002 | 0.012002 | 0.012002 | 0.98743 | -0.24175 | 0.98729 | -0.24445 | 3.2973
43 | -0.13899 | -0.035152 | 0.13961 | 0.035549 | 0.0006211 | 0.000397 | 0.20794 | 0.20794 | 0.20794 | 0.99514 | -0.0927 | 1 | 0 | 57.1251
44 | -0.01255 | -0.0031455 | 0.012552 | 0.003147 | 2.8329e-06 | 1.5584e-06 | 0.019196 | 0.019196 | 0.019196 | 0.97282 | -0.52451 | 0.97306 | -0.51977 | 5.2736
45 | -0.037751 | -0.0094836 | 0.037764 | 0.009492 | 1.3324e-05 | 8.3926e-06 | 0.057501 | 0.057501 | 0.057501 | 0.97706 | -0.4409 | 0.97744 | -0.43351 | 15.7969
46 | -0.0079861 | -0.0020015 | 0.0079867 | 0.0020017 | 5.8488e-07 | 2.4229e-07 | 0.012163 | 0.012163 | 0.012163 | 0.97701 | -0.44201 | 0.97709 | -0.44047 | 3.3415
47 | -0.014532 | -0.003642 | 0.014535 | 0.0036439 | 3.1931e-06 | 1.8258e-06 | 0.02213 | 0.02213 | 0.02213 | 0.97709 | -0.44047 | 0.97732 | -0.43586 | 6.0797
48 | -0.019256 | -0.0048272 | 0.019257 | 0.0048273 | 1.3687e-07 | 8.2277e-08 | 0.029319 | 0.029319 | 0.029319 | 0.97732 | -0.43586 | 0.97733 | -0.43571 | 8.0547
49 | -0.026808 | -0.0067198 | 0.026822 | 0.0067284 | 1.3741e-05 | 8.5186e-06 | 0.040816 | 0.040816 | 0.040816 | 0.97733 | -0.43571 | 0.97787 | -0.42496 | 11.2133
50 | 0.0098988 | 0.0024829 | -0.0098981 | -0.0024825 | 7.0918e-07 | 3.4594e-07 | 0.014944 | 0.014944 | 0.014944 | 0.98571 | -0.27525 | 0.98563 | -0.27676 | 4.1055
51 | 0.0083412 | 0.0020923 | -0.0083409 | -0.0020922 | 3.7819e-07 | 1.61e-07 | 0.012594 | 0.012594 | 0.012594 | 0.98563 | -0.27676 | 0.98558 | -0.27771 | 3.4598
52 | 0.0039359 | 0.00098636 | -0.0039358 | -0.0009864 | 1.1321e-07 | -3.7252e-08 | 0.005932 | 0.0059321 | 0.0059321 | 0.98729 | -0.24445 | 0.98726 | -0.24505 | 1.6297
53 | 0.0083409 | 0.0020922 | -0.0083351 | -0.0020897 | 5.7735e-06 | 2.4589e-06 | 0.012594 | 0.012594 | 0.012594 | 0.98558 | -0.27771 | 0.98484 | -0.29223 | 3.4599
54 | 0.0083351 | 0.0020897 | -0.0083323 | -0.0020885 | 2.7754e-06 | 1.1827e-06 | 0.012594 | 0.012594 | 0.012594 | 0.98484 | -0.29223 | 0.98448 | -0.29922 | 3.4599
55 | 0.0083323 | 0.0020885 | -0.0083308 | -0.0020879 | 1.4989e-06 | 6.3895e-07 | 0.012594 | 0.012594 | 0.012594 | 0.98448 | -0.29922 | 0.98428 | -0.303 | 3.46
56 | -0.031888 | -0.0079982 | 0.031901 | 0.008006 | 1.2544e-05 | 7.8496e-06 | 0.048526 | 0.048526 | 0.048526 | 0.97787 | -0.42496 | 0.97829 | -0.41671 | 13.3313
57 | 0.0050667 | 0.0012698 | -0.0050666 | -0.0012698 | 1.0344e-07 | 7.9877e-09 | 0.0077099 | 0.0077099 | 0.0077099 | 0.97787 | -0.42496 | 0.97785 | -0.42538 | 2.1181
58 | 0.049279 | 0.012393 | -0.049239 | -0.012368 | 3.9519e-05 | 2.5057e-05 | 0.07497 | 0.07497 | 0.07497 | 0.97829 | -0.41671 | 0.97744 | -0.43351 | 20.5962
59 | 0.013244 | 0.0033209 | -0.01324 | -0.0033189 | 3.6224e-06 | 2.0195e-06 | 0.020145 | 0.020145 | 0.020145 | 0.97829 | -0.41671 | 0.978 | -0.42245 | 5.5344
60 | -0.003139 | -0.00078671 | 0.003139 | 0.00078668 | 3.3134e-08 | -2.8519e-08 | 0.0047489 | 0.0047489 | 0.0047489 | 0.98357 | -0.31441 | 0.98358 | -0.31419 | 1.3047
61 | -0.003139 | -0.00078668 | 0.0031394 | 0.00078639 | 3.4239e-07 | -2.9479e-07 | 0.0047489 | 0.0047487 | 0.0047489 | 0.98358 | -0.31419 | 0.9837 | -0.3119 | 1.3046
62 | -0.0031394 | -0.00078639 | 0.0031394 | 0.00078634 | 5.256e-08 | -4.5268e-08 | 0.0047487 | 0.0047487 | 0.0047487 | 0.9837 | -0.3119 | 0.98371 | -0.31155 | 1.3046
63 | 0.082751 | 0.020893 | -0.082654 | -0.020832 | 9.6475e-05 | 6.1538e-05 | 0.12553 | 0.12553 | 0.12553 | 0.98137 | -0.35699 | 0.98012 | -0.38136 | 34.4857
64 | -0.082751 | -0.020893 | 0.082947 | 0.021018 | 0.00019646 | 0.00012531 | 0.12553 | 0.12553 | 0.12553 | 0.98137 | -0.35699 | 0.98391 | -0.30756 | 34.4857
65 | 0.052446 | 0.013261 | -0.05236 | -0.013206 | 8.6252e-05 | 5.4746e-05 | 0.079666 | 0.079666 | 0.079666 | 0.98012 | -0.38136 | 0.97836 | -0.41571 | 21.8864
66 | -0.093961 | -0.023779 | 0.094058 | 0.023841 | 9.6896e-05 | 6.1851e-05 | 0.14218 | 0.14218 | 0.14218 | 0.98391 | -0.30756 | 0.98502 | -0.2861 | 39.0617
67 | -0.015354 | -0.0038475 | 0.015357 | 0.0038493 | 3.0316e-06 | 1.7499e-06 | 0.023225 | 0.023225 | 0.023225 | 0.98371 | -0.31155 | 0.98393 | -0.3074 | 6.3804
68 | 0.05236 | 0.013206 | -0.052321 | -0.013181 | 3.9008e-05 | 2.476e-05 | 0.079666 | 0.079666 | 0.079666 | 0.97836 | -0.41571 | 0.97756 | -0.43128 | 21.8864
69 | 0.021914 | 0.0054998 | -0.021901 | -0.0054917 | 1.3295e-05 | 8.0976e-06 | 0.033107 | 0.033107 | 0.033107 | 0.98502 | -0.2861 | 0.98437 | -0.29883 | 9.0954
70 | -0.11597 | -0.02934 | 0.11602 | 0.029374 | 5.1888e-05 | 3.3151e-05 | 0.17529 | 0.17529 | 0.17529 | 0.98502 | -0.2861 | 0.9855 | -0.27678 | 48.1571
71 | -0.015357 | -0.0038493 | 0.01536 | 0.0038509 | 2.892e-06 | 1.6692e-06 | 0.023225 | 0.023224 | 0.023225 | 0.98393 | -0.3074 | 0.98413 | -0.30345 | 6.3804
72 | -0.018442 | -0.0046234 | 0.018446 | 0.0046258 | 4.0609e-06 | 2.422e-06 | 0.027885 | 0.027885 | 0.027885 | 0.98413 | -0.30345 | 0.98437 | -0.29883 | 7.6606
73 | 0.046923 | 0.011818 | -0.046865 | -0.011781 | 5.8247e-05 | 3.6898e-05 | 0.07149 | 0.07149 | 0.07149 | 0.97696 | -0.44298 | 0.97564 | -0.46897 | 19.6401
74 | -0.049948 | -0.012576 | 0.049976 | 0.012594 | 2.7943e-05 | 1.7723e-05 | 0.076097 | 0.076097 | 0.076097 | 0.97696 | -0.44298 | 0.97756 | -0.43128 | 20.9058
75 | 0.043769 | 0.011005 | -0.043738 | -0.010985 | 3.1476e-05 | 1.9909e-05 | 0.066768 | 0.066768 | 0.066768 | 0.97564 | -0.46897 | 0.97487 | -0.48404 | 18.3429
76 | 0.043738 | 0.010985 | -0.043732 | -0.010981 | 6.1235e-06 | 3.8734e-06 | 0.066768 | 0.066768 | 0.066768 | 0.97487 | -0.48404 | 0.97472 | -0.48697 | 18.3429
77 | 0.040947 | 0.010283 | -0.040911 | -0.010261 | 3.5721e-05 | 2.2558e-05 | 0.062518 | 0.062518 | 0.062518 | 0.97472 | -0.48697 | 0.9738 | -0.50528 | 17.1752
78 | 0.033282 | 0.0083486 | -0.03328 | -0.0083469 | 2.7314e-06 | 1.7131e-06 | 0.05086 | 0.05086 | 0.05086 | 0.9738 | -0.50528 | 0.97371 | -0.507 | 13.9725
79 | -0.12698 | -0.032121 | 0.12751 | 0.032458 | 0.00052745 | 0.00033708 | 0.19184 | 0.19184 | 0.19184 | 0.9855 | -0.27678 | 0.98997 | -0.1906 | 52.7036
80 | 0.011475 | 0.0028764 | -0.011472 | -0.002875 | 2.6239e-06 | 1.392e-06 | 0.017469 | 0.017469 | 0.017469 | 0.97744 | -0.43351 | 0.97719 | -0.43831 | 4.7993
81 | 0.010542 | 0.0026425 | -0.01054 | -0.0026414 | 2.0686e-06 | 1.0549e-06 | 0.016039 | 0.016039 | 0.016039 | 0.978 | -0.42245 | 0.97779 | -0.42657 | 4.4064
82 | 0.0079715 | 0.0019976 | -0.0079714 | -0.0019976 | 3.8437e-08 | 1.5885e-08 | 0.012138 | 0.012138 | 0.012138 | 0.97719 | -0.43831 | 0.97719 | -0.43841 | 3.3347
83 | 0.0059456 | 0.0014901 | -0.0059452 | -0.00149 | 4.1666e-07 | 9.6446e-08 | 0.0090481 | 0.0090482 | 0.0090482 | 0.97779 | -0.42657 | 0.97772 | -0.42804 | 2.4858
84 | 0.02769 | 0.0069461 | -0.027682 | -0.0069412 | 7.8649e-06 | 4.8879e-06 | 0.042318 | 0.042318 | 0.042318 | 0.97371 | -0.507 | 0.97341 | -0.51296 | 11.6259
85 | 0.019606 | 0.004917 | -0.019599 | -0.0049131 | 6.3687e-06 | 3.8411e-06 | 0.029972 | 0.029972 | 0.029972 | 0.97341 | -0.51296 | 0.97306 | -0.51977 | 8.234
86 | -0.27058 | -0.069388 | 0.2709 | 0.069593 | 0.00032069 | 0.00020463 | 0.40442 | 0.40442 | 0.40442 | 0.99693 | -0.05796 | 0.99822 | -0.033553 | 37.0348
87 | -0.27767 | -0.071292 | 0.27773 | 0.071329 | 5.7784e-05 | 3.6876e-05 | 0.41452 | 0.41452 | 0.41452 | 0.99822 | -0.033553 | 0.99845 | -0.029267 | 37.96
88 | -0.28331 | -0.072726 | 0.28371 | 0.072984 | 0.00040306 | 0.00025725 | 0.42284 | 0.42284 | 0.42284 | 0.99845 | -0.029267 | 1 | 0 | 38.7213
89 | 0.0054014 | 0.0013535 | -0.0054011 | -0.0013535 | 3.1141e-07 | 4.5531e-08 | 0.0082249 | 0.008225 | 0.008225 | 0.97719 | -0.43841 | 0.97713 | -0.43962 | 2.2596
90 | 0.0030065 | 0.00075332 | -0.0030063 | -0.00075346 | 1.3943e-07 | -1.3294e-07 | 0.0045783 | 0.0045784 | 0.0045784 | 0.97713 | -0.43962 | 0.97708 | -0.4406 | 1.2578

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43053 | 0.10993

## res_load
| p_mw | q_mvar
0 | 0.0056481 | 0.0014155
1 | 0.0021488 | 0.00053854
2 | 0.0027066 | 0.00067834
3 | 0.0019637 | 0.00049214
4 | 0.0032111 | 0.00080478
5 | 0.0048723 | 0.0012211
6 | 0.0059419 | 0.0014892
7 | 0.0055435 | 0.0013893
8 | 0.0055457 | 0.0013899
9 | 0.0076272 | 0.0019116
10 | 0.0060836 | 0.0015247
11 | 0.0051624 | 0.0012938
12 | 0.0026098 | 0.00065407
13 | 0.0025516 | 0.0006395
14 | 0.0034603 | 0.00086724
15 | 0.0034618 | 0.0008676
16 | 0.003019 | 0.00075664
17 | 0.0039317 | 0.00098539
18 | 0.013741 | 0.0034438
19 | 0.0071099 | 0.0017819
20 | 0.0022877 | 0.00057336
21 | 0.010261 | 0.0025715
22 | 0.075068 | 0.018814
23 | 0.0037937 | 0.00095078
24 | 0.0079861 | 0.0020015
25 | 0.0065448 | 0.0016403
26 | 0.0047217 | 0.0011834
27 | 0.0075513 | 0.0018925
28 | 0.0015569 | 0.0003902
29 | 0.0040276 | 0.0010094
30 | 0.0093589 | 0.0023456
31 | 0.0039358 | 0.0009864
32 | 0.0083308 | 0.0020879
33 | 0.0050666 | 0.0012698
34 | 0.003139 | 0.00078671
35 | 0.030208 | 0.0075708
36 | 0.011014 | 0.0027604
37 | 0.012214 | 0.0030612
38 | 0.0030821 | 0.00077245
39 | 0.0030249 | 0.00075812
40 | 0.0030961 | 0.00077595
41 | 0.0023449 | 0.00058768
42 | 0.0027844 | 0.00069783
43 | 0.0076292 | 0.0019121
44 | 0.003455 | 0.00086591
45 | 0.010961 | 0.002747
46 | 0.0040171 | 0.0010068
47 | 0.0026988 | 0.00067638
48 | 0.0035008 | 0.00087738
49 | 0.0045939 | 0.0011513
50 | 0.0055893 | 0.0014008
51 | 0.0080767 | 0.0020242
52 | 0.0070468 | 0.0017661
53 | 0.0052049 | 0.0013045
54 | 0.0068028 | 0.0017049
55 | 0.0067777 | 0.0016987
56 | 0.0055779 | 0.0013979
57 | 0.0055571 | 0.0013927
58 | 0.0033779 | 0.00084658
59 | 0.00257 | 0.00064411
60 | 0.0023946 | 0.00060015
61 | 0.0030063 | 0.00075346
62 | 0.0059452 | 0.00149

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1