## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2473-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2473-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2473-7_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2473-7_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2473-7_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_2473-7_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2473-7_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2473-7_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2473-7_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2473-7_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2473-7_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2473-7_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2473-7_0_4_node_127 | 0.4 | n |  | TRUE
13 | bus_LV_2473-7_0_4_node_122 | 0.4 | n |  | TRUE
14 | bus_LV_2473-7_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2473-7_0_4_node_112 | 0.4 | n |  | TRUE
16 | bus_LV_2473-7_0_4_node_90 | 0.4 | n |  | TRUE
17 | bus_LV_2473-7_0_4_node_91 | 0.4 | n |  | TRUE
18 | bus_LV_2473-7_0_4_node_123 | 0.4 | n |  | TRUE
19 | bus_LV_2473-7_0_4_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_2473-7_0_4_node_54 | 0.4 | n |  | TRUE
21 | bus_LV_2473-7_0_4_node_128 | 0.4 | n |  | TRUE
22 | bus_LV_2473-7_0_4_node_120 | 0.4 | n |  | TRUE
23 | bus_LV_2473-7_0_4_node_113 | 0.4 | n |  | TRUE
24 | bus_LV_2473-7_0_4_node_104 | 0.4 | n |  | TRUE
25 | bus_LV_2473-7_0_4_node_89 | 0.4 | n |  | TRUE
26 | bus_LV_2473-7_0_4_node_121 | 0.4 | n |  | TRUE
27 | bus_LV_2473-7_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2473-7_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2473-7_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2473-7_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2473-7_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2473-7_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2473-7_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2473-7_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2473-7_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_2473-7_0_4_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_2473-7_0_4_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_2473-7_0_4_node_98 | 0.4 | n |  | TRUE
39 | bus_LV_2473-7_0_4_node_49 | 0.4 | n |  | TRUE
40 | bus_LV_2473-7_0_4_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_2473-7_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2473-7_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2473-7_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2473-7_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2473-7_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_2473-7_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2473-7_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_2473-7_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2473-7_0_4_node_73 | 0.4 | n |  | TRUE
50 | bus_LV_2473-7_0_4_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_2473-7_0_4_node_92 | 0.4 | n |  | TRUE
52 | bus_LV_2473-7_0_4_node_131 | 0.4 | n |  | TRUE
53 | bus_LV_2473-7_0_4_node_30 | 0.4 | n |  | TRUE
54 | bus_LV_2473-7_0_4_node_107 | 0.4 | n |  | TRUE
55 | bus_LV_2473-7_0_4_node_105 | 0.4 | n |  | TRUE
56 | bus_LV_2473-7_0_4_node_77 | 0.4 | n |  | TRUE
57 | bus_LV_2473-7_0_4_node_72 | 0.4 | n |  | TRUE
58 | bus_LV_2473-7_0_4_node_106 | 0.4 | n |  | TRUE
59 | bus_LV_2473-7_0_4_node_76 | 0.4 | n |  | TRUE
60 | bus_LV_2473-7_0_4_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_2473-7_0_4_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_2473-7_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2473-7_0_4_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_2473-7_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2473-7_0_4_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_2473-7_0_4_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_2473-7_0_4_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_2473-7_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_2473-7_0_4_node_103 | 0.4 | n |  | TRUE
70 | bus_LV_2473-7_0_4_node_94 | 0.4 | n |  | TRUE
71 | bus_LV_2473-7_0_4_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_2473-7_0_4_node_102 | 0.4 | n |  | TRUE
73 | bus_LV_2473-7_0_4_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_2473-7_0_4_node_93 | 0.4 | n |  | TRUE
75 | bus_LV_2473-7_0_4_node_41 | 0.4 | n |  | TRUE
76 | bus_LV_2473-7_0_4_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_2473-7_0_4_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_2473-7_0_4_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_2473-7_0_4_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_2473-7_0_4_node_101 | 0.4 | n |  | TRUE
81 | bus_LV_2473-7_0_4_node_100 | 0.4 | n |  | TRUE
82 | bus_LV_2473-7_0_4_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_2473-7_0_4_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_2473-7_0_4_node_52 | 0.4 | n |  | TRUE
85 | bus_LV_2473-7_0_4_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_2473-7_0_4_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_2473-7_0_4_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_2473-7_0_4_node_58 | 0.4 | n |  | TRUE
89 | bus_LV_2473-7_0_4_node_129 | 0.4 | n |  | TRUE
90 | bus_LV_2473-7_0_4_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_2473-7_0_4_node_97 | 0.4 | n |  | TRUE
92 | bus_LV_2473-7_0_4_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_2473-7_0_4_node_59 | 0.4 | n |  | TRUE
94 | bus_LV_2473-7_0_4_node_60 | 0.4 | n |  | TRUE
95 | bus_LV_2473-7_0_4_node_61 | 0.4 | n |  | TRUE
96 | bus_LV_2473-7_0_4_node_62 | 0.4 | n |  | TRUE
97 | bus_LV_2473-7_0_4_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_2473-7_0_4_node_64 | 0.4 | n |  | TRUE
99 | bus_LV_2473-7_0_4_node_65 | 0.4 | n |  | TRUE
100 | bus_LV_2473-7_0_4_node_66 | 0.4 | n |  | TRUE
101 | bus_LV_2473-7_0_4_node_67 | 0.4 | n |  | TRUE
102 | bus_LV_2473-7_0_4_node_68 | 0.4 | n |  | TRUE
103 | bus_LV_2473-7_0_4_node_69 | 0.4 | n |  | TRUE
104 | bus_LV_2473-7_0_4_node_78 | 0.4 | n |  | TRUE
105 | bus_LV_2473-7_0_4_node_79 | 0.4 | n |  | TRUE
106 | bus_LV_2473-7_0_4_node_118 | 0.4 | n |  | TRUE
107 | bus_LV_2473-7_0_4_node_70 | 0.4 | n |  | TRUE
108 | bus_LV_2473-7_0_4_node_84 | 0.4 | n |  | TRUE
109 | bus_LV_2473-7_0_4_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_2473-7_0_4_node_125 | 0.4 | n |  | TRUE
111 | bus_LV_2473-7_0_4_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_2473-7_0_4_node_130 | 0.4 | n |  | TRUE
113 | bus_LV_2473-7_0_4_node_124 | 0.4 | n |  | TRUE
114 | bus_LV_2473-7_0_4_node_81 | 0.4 | n |  | TRUE
115 | bus_LV_2473-7_0_4_node_83 | 0.4 | n |  | TRUE
116 | bus_LV_2473-7_0_4_node_85 | 0.4 | n |  | TRUE
117 | bus_LV_2473-7_0_4_node_86 | 0.4 | n |  | TRUE
118 | bus_LV_2473-7_0_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_2473-7_0_4_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2473-7_0_4_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_2473-7_0_4_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_2473-7_0_4_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_2473-7_0_4_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2473-7_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_2473-7_0_4_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_2473-7_0_4_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_2473-7_0_4_node_126 | 0.4 | n |  | TRUE
128 | bus_MV_286_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2473-7_0_4_load_0 | 0 | 0.0060481 | 0.0015158 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2473-7_0_4_load_3 | 2 | 0.0018624 | 0.00046676 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2473-7_0_4_load_4 | 3 | 0.0028909 | 0.00072452 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2473-7_0_4_load_7 | 7 | 0.0021034 | 0.00052716 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2473-7_0_4_load_10 | 9 | 0.022874 | 0.0057326 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2473-7_0_4_load_11 | 10 | 0.0068378 | 0.0017137 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2473-7_0_4_load_12 | 11 | 0.036029 | 0.0090298 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2473-7_0_4_load_127 | 12 | 0.0090266 | 0.0022623 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2473-7_0_4_load_122 | 13 | 0.0090452 | 0.0022669 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2473-7_0_4_load_112 | 15 | 0.0031061 | 0.00077846 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2473-7_0_4_load_91 | 17 | 0.0054976 | 0.0013778 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2473-7_0_4_load_123 | 18 | 0.035323 | 0.0088529 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2473-7_0_4_load_56 | 19 | 0.0039022 | 0.00097798 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2473-7_0_4_load_128 | 21 | 0.0073759 | 0.0018486 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2473-7_0_4_load_104 | 24 | 0.0029959 | 0.00075085 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2473-7_0_4_load_13 | 27 | 0.0062985 | 0.0015786 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2473-7_0_4_load_14 | 28 | 0.0036321 | 0.0009103 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2473-7_0_4_load_16 | 30 | 0.0035047 | 0.00087837 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2473-7_0_4_load_17 | 31 | 0.0051563 | 0.0012923 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2473-7_0_4_load_18 | 32 | 0.0093269 | 0.0023375 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2473-7_0_4_load_19 | 33 | 0.0045483 | 0.0011399 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2473-7_0_4_load_21 | 35 | 0.0034655 | 0.00086854 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2473-7_0_4_load_51 | 36 | 0.0047782 | 0.0011975 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2473-7_0_4_load_74 | 37 | 0.0051389 | 0.0012879 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2473-7_0_4_load_98 | 38 | 0.004987 | 0.0012499 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2473-7_0_4_load_49 | 39 | 0.0072283 | 0.0018116 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2473-7_0_4_load_75 | 40 | 0.0072843 | 0.0018256 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2473-7_0_4_load_22 | 41 | 0.0025477 | 0.00063852 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2473-7_0_4_load_23 | 42 | 0.0038958 | 0.00097639 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2473-7_0_4_load_24 | 43 | 0.0013188 | 0.00033051 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2473-7_0_4_load_26 | 45 | 0.0012004 | 0.00030084 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2473-7_0_4_load_27 | 46 | 0.012174 | 0.0030511 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2473-7_0_4_load_31 | 48 | 0.0017765 | 0.00044523 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2473-7_0_4_load_92 | 51 | 0.0074463 | 0.0018662 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2473-7_0_4_load_131 | 52 | 0.0039432 | 0.00098825 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2473-7_0_4_load_107 | 54 | 0.0024884 | 0.00062365 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2473-7_0_4_load_105 | 55 | 0.002139 | 0.00053608 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2473-7_0_4_load_77 | 56 | 0.0020736 | 0.00051969 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2473-7_0_4_load_72 | 57 | 0.011156 | 0.0027959 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2473-7_0_4_load_76 | 59 | 0.0014288 | 0.0003581 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2473-7_0_4_load_32 | 60 | 0.0036527 | 0.00091546 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2473-7_0_4_load_33 | 61 | 0.0032964 | 0.00082617 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2473-7_0_4_load_35 | 63 | 0.002339 | 0.00058621 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2473-7_0_4_load_36 | 64 | 0.00513 | 0.0012857 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2473-7_0_4_load_37 | 65 | 0.0015539 | 0.00038945 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2473-7_0_4_load_38 | 66 | 0.0015016 | 0.00037633 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2473-7_0_4_load_39 | 67 | 0.0028386 | 0.00071142 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2473-7_0_4_load_40 | 68 | 0.0020288 | 0.00050846 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2473-7_0_4_load_94 | 70 | 0.0045371 | 0.0011371 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2473-7_0_4_load_46 | 71 | 0.0049539 | 0.0012416 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2473-7_0_4_load_102 | 72 | 0.002498 | 0.00062605 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2473-7_0_4_load_93 | 74 | 0.0015579 | 0.00039045 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2473-7_0_4_load_41 | 75 | 0.0029651 | 0.00074313 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2473-7_0_4_load_44 | 77 | 0.0038489 | 0.00096462 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2473-7_0_4_load_45 | 78 | 0.0019277 | 0.00048313 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2473-7_0_4_load_47 | 79 | 0.0046039 | 0.0011539 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2473-7_0_4_load_101 | 80 | 0.0030106 | 0.00075454 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2473-7_0_4_load_100 | 81 | 0.0030177 | 0.00075631 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2473-7_0_4_load_48 | 82 | 0.0064911 | 0.0016268 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2473-7_0_4_load_50 | 83 | 0.002217 | 0.00055563 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2473-7_0_4_load_52 | 84 | 0.01682 | 0.0042155 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2473-7_0_4_load_53 | 85 | 0.023158 | 0.005804 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2473-7_0_4_load_71 | 86 | 0.0093428 | 0.0023415 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2473-7_0_4_load_57 | 87 | 0.0028172 | 0.00070606 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2473-7_0_4_load_58 | 88 | 0.0056539 | 0.001417 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2473-7_0_4_load_129 | 89 | 0.0026335 | 0.00066001 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2473-7_0_4_load_87 | 90 | 0.0041372 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2473-7_0_4_load_88 | 92 | 0.0027525 | 0.00068985 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2473-7_0_4_load_59 | 93 | 0.0014019 | 0.00035136 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2473-7_0_4_load_60 | 94 | 0.0015847 | 0.00039717 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2473-7_0_4_load_63 | 97 | 0.0019108 | 0.00047888 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2473-7_0_4_load_65 | 99 | 0.0014859 | 0.00037241 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2473-7_0_4_load_66 | 100 | 0.0019344 | 0.0004848 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2473-7_0_4_load_67 | 101 | 0.0013388 | 0.00033555 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2473-7_0_4_load_68 | 102 | 0.0022695 | 0.00056878 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2473-7_0_4_load_69 | 103 | 0.0022053 | 0.00055271 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2473-7_0_4_load_78 | 104 | 0.0045059 | 0.0011293 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2473-7_0_4_load_79 | 105 | 0.0020957 | 0.00052524 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2473-7_0_4_load_118 | 106 | 0.0021522 | 0.00053938 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2473-7_0_4_load_70 | 107 | 0.0053973 | 0.0013527 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2473-7_0_4_load_84 | 108 | 0.0048256 | 0.0012094 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2473-7_0_4_load_80 | 109 | 0.0045059 | 0.0011293 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2473-7_0_4_load_125 | 110 | 0.0023985 | 0.00060113 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2473-7_0_4_load_130 | 112 | 0.0039045 | 0.00097857 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2473-7_0_4_load_124 | 113 | 0.0024447 | 0.0006127 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2473-7_0_4_load_83 | 115 | 0.00717 | 0.001797 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2473-7_0_4_load_85 | 116 | 0.002369 | 0.00059372 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2473-7_0_4_load_119 | 118 | 0.059847 | 0.014999 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2473-7_0_4_load_108 | 119 | 0.0029959 | 0.00075085 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2473-7_0_4_load_96 | 120 | 0.0024283 | 0.00060859 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2473-7_0_4_load_109 | 121 | 0.0033727 | 0.00084527 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2473-7_0_4_load_110 | 122 | 0.0033801 | 0.00084714 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2473-7_0_4_load_111 | 123 | 0.0029943 | 0.00075044 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2473-7_0_4_load_116 | 124 | 0.0029997 | 0.00075179 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2473-7_0_4_load_117 | 125 | 0.0031378 | 0.00078642 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2473-7_0_4_load_114 | 126 | 0.0090509 | 0.0022684 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2473-7_0_4_load_126 | 127 | 0.0023042 | 0.00057748 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 114 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2473-7_0_4_line_0 |  | 0 | 1 | 0.0076659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2473-7_0_4_line_1 |  | 1 | 2 | 0.012573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2473-7_0_4_line_2 |  | 1 | 3 | 0.022187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2473-7_0_4_line_3 |  | 2 | 7 | 0.0078403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2473-7_0_4_line_4 |  | 3 | 8 | 0.0015344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2473-7_0_4_line_5 |  | 4 | 5 | 0.0229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2473-7_0_4_line_6 |  | 4 | 6 | 0.004447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2473-7_0_4_line_7 |  | 5 | 9 | 0.023672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2473-7_0_4_line_8 |  | 6 | 10 | 0.009099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2473-7_0_4_line_9 |  | 6 | 11 | 0.013827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2473-7_0_4_line_10 |  | 8 | 12 | 0.014621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2473-7_0_4_line_11 |  | 8 | 13 | 0.0019026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2473-7_0_4_line_12 |  | 9 | 17 | 0.023341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2473-7_0_4_line_13 |  | 11 | 18 | 0.0085617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2473-7_0_4_line_14 |  | 12 | 21 | 0.0058844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2473-7_0_4_line_15 |  | 13 | 22 | 0.022017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2473-7_0_4_line_16 |  | 14 | 15 | 0.0043612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2473-7_0_4_line_17 |  | 14 | 16 | 0.003884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2473-7_0_4_line_18 |  | 15 | 23 | 0.058567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2473-7_0_4_line_19 |  | 16 | 24 | 0.010372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2473-7_0_4_line_20 |  | 16 | 25 | 0.017657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2473-7_0_4_line_21 |  | 17 | 25 | 0.016755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2473-7_0_4_line_22 |  | 18 | 26 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2473-7_0_4_line_23 |  | 19 | 20 | 0.01022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2473-7_0_4_line_24 |  | 20 | 73 | 0.024424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2473-7_0_4_line_25 |  | 21 | 116 | 0.012499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2473-7_0_4_line_26 |  | 22 | 118 | 0.018503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2473-7_0_4_line_27 |  | 22 | 117 | 0.013333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2473-7_0_4_line_28 |  | 23 | 126 | 0.025822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2473-7_0_4_line_29 |  | 24 | 119 | 0.0057686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2473-7_0_4_line_30 |  | 25 | 92 | 0.0067587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2473-7_0_4_line_31 |  | 26 | 118 | 0.01845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2473-7_0_4_line_32 |  | 27 | 28 | 0.0031104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2473-7_0_4_line_33 |  | 27 | 29 | 0.014342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2473-7_0_4_line_34 |  | 28 | 30 | 0.010054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2473-7_0_4_line_35 |  | 29 | 31 | 0.011411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2473-7_0_4_line_36 |  | 29 | 32 | 0.014359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2473-7_0_4_line_37 |  | 30 | 33 | 0.011886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2473-7_0_4_line_38 |  | 31 | 34 | 0.012971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2473-7_0_4_line_39 |  | 32 | 35 | 0.0069194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2473-7_0_4_line_40 |  | 33 | 36 | 0.00090359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2473-7_0_4_line_41 |  | 34 | 37 | 0.013002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2473-7_0_4_line_42 |  | 35 | 38 | 0.014599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2473-7_0_4_line_43 |  | 36 | 39 | 0.0002411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2473-7_0_4_line_44 |  | 37 | 40 | 0.0062713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2473-7_0_4_line_45 |  | 39 | 82 | 0.0011493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2473-7_0_4_line_46 |  | 40 | 112 | 0.012125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2473-7_0_4_line_47 |  | 41 | 42 | 0.018174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2473-7_0_4_line_48 |  | 41 | 43 | 0.0066831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2473-7_0_4_line_49 |  | 42 | 44 | 0.018996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2473-7_0_4_line_50 |  | 43 | 45 | 0.0031844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2473-7_0_4_line_51 |  | 44 | 46 | 0.017176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2473-7_0_4_line_52 |  | 44 | 47 | 0.015253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2473-7_0_4_line_53 |  | 45 | 48 | 0.010196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2473-7_0_4_line_54 |  | 46 | 49 | 0.011044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2473-7_0_4_line_55 |  | 47 | 52 | 0.029185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2473-7_0_4_line_56 |  | 48 | 56 | 0.016414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2473-7_0_4_line_57 |  | 49 | 57 | 0.0085827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2473-7_0_4_line_58 |  | 49 | 50 | 0.007194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2473-7_0_4_line_59 |  | 50 | 51 | 0.0031749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2473-7_0_4_line_60 |  | 53 | 54 | 0.024823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2473-7_0_4_line_61 |  | 53 | 55 | 0.021326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2473-7_0_4_line_62 |  | 55 | 58 | 0.023446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2473-7_0_4_line_63 |  | 56 | 59 | 0.0083033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2473-7_0_4_line_64 |  | 57 | 86 | 0.018661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_2473-7_0_4_line_65 |  | 58 | 105 | 0.032864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2473-7_0_4_line_66 |  | 59 | 101 | 0.011698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2473-7_0_4_line_67 |  | 60 | 61 | 0.001053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2473-7_0_4_line_68 |  | 60 | 62 | 0.014629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2473-7_0_4_line_69 |  | 61 | 63 | 0.0049297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2473-7_0_4_line_70 |  | 62 | 64 | 0.029451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2473-7_0_4_line_71 |  | 62 | 65 | 0.015542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2473-7_0_4_line_72 |  | 63 | 66 | 0.0095308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2473-7_0_4_line_73 |  | 64 | 67 | 0.0028555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2473-7_0_4_line_74 |  | 65 | 68 | 0.0096021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2473-7_0_4_line_75 |  | 66 | 69 | 0.029794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2473-7_0_4_line_76 |  | 68 | 70 | 0.0063499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2473-7_0_4_line_77 |  | 69 | 71 | 0.0039841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2473-7_0_4_line_78 |  | 69 | 72 | 0.0075486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2473-7_0_4_line_79 |  | 70 | 74 | 0.019005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2473-7_0_4_line_80 |  | 71 | 77 | 0.027666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2473-7_0_4_line_81 |  | 73 | 87 | 0.0016183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2473-7_0_4_line_82 |  | 73 | 88 | 0.014615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2473-7_0_4_line_83 |  | 75 | 76 | 0.0090299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2473-7_0_4_line_84 |  | 76 | 77 | 0.012281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2473-7_0_4_line_85 |  | 76 | 78 | 0.017065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2473-7_0_4_line_86 |  | 78 | 79 | 0.017829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2473-7_0_4_line_87 |  | 79 | 80 | 0.033188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2473-7_0_4_line_88 |  | 80 | 81 | 0.012308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2473-7_0_4_line_89 |  | 81 | 102 | 0.0078672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2473-7_0_4_line_90 |  | 82 | 83 | 0.0072393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2473-7_0_4_line_91 |  | 83 | 84 | 0.01735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2473-7_0_4_line_92 |  | 84 | 85 | 0.00033172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2473-7_0_4_line_93 |  | 85 | 86 | 0.003497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2473-7_0_4_line_94 |  | 87 | 89 | 0.039895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2473-7_0_4_line_95 |  | 88 | 90 | 0.0025092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2473-7_0_4_line_96 |  | 89 | 91 | 0.0080376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2473-7_0_4_line_97 |  | 90 | 92 | 0.020919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2473-7_0_4_line_98 |  | 91 | 120 | 0.013568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2473-7_0_4_line_99 |  | 93 | 94 | 0.0059929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2473-7_0_4_line_100 |  | 93 | 95 | 0.02691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2473-7_0_4_line_101 |  | 94 | 96 | 0.012662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2473-7_0_4_line_102 |  | 95 | 97 | 0.010091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2473-7_0_4_line_103 |  | 95 | 98 | 0.013371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2473-7_0_4_line_104 |  | 96 | 99 | 0.0073229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2473-7_0_4_line_105 |  | 96 | 100 | 0.028525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2473-7_0_4_line_106 |  | 96 | 101 | 0.018729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_2473-7_0_4_line_107 |  | 97 | 102 | 0.012979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2473-7_0_4_line_108 |  | 98 | 103 | 0.022964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2473-7_0_4_line_109 |  | 99 | 104 | 0.030738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2473-7_0_4_line_110 |  | 100 | 105 | 0.041903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2473-7_0_4_line_111 |  | 103 | 106 | 0.0016535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2473-7_0_4_line_112 |  | 104 | 109 | 0.023504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2473-7_0_4_line_113 |  | 106 | 110 | 0.0050659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2473-7_0_4_line_114 |  | 107 | 108 | 0.0044137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2473-7_0_4_line_115 |  | 108 | 111 | 0.0094878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2473-7_0_4_line_116 |  | 110 | 127 | 0.00069775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2473-7_0_4_line_117 |  | 111 | 116 | 0.022256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2473-7_0_4_line_118 |  | 112 | 113 | 0.0010576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2473-7_0_4_line_119 |  | 113 | 117 | 0.029462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2473-7_0_4_line_120 |  | 114 | 115 | 0.02328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2473-7_0_4_line_121 |  | 115 | 117 | 0.013935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2473-7_0_4_line_122 |  | 119 | 121 | 0.0044341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2473-7_0_4_line_123 |  | 121 | 122 | 7.7179e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2473-7_0_4_line_124 |  | 122 | 123 | 0.0012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2473-7_0_4_line_125 |  | 123 | 124 | 0.0057708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2473-7_0_4_line_126 |  | 124 | 125 | 0.0059083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2473-7_0_4_trafo_81 | 0.63 MVA 20/0.4 kV | 128 | 114 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2613489.6 | 1258705.5021 | 2613487.6735 | 1258698.0822
1 | 2613489.6 | 1258705.5021 | 2613497.1028 | 1258704.2961 | 2613502.0683 | 1258704.0012
2 | 2613489.6 | 1258705.5021 | 2613476.499 | 1258708.9969 | 2613468.0539 | 1258710.7619
3 | 2613502.0683 | 1258704.0012 | 2613509.8948 | 1258703.5365
4 | 2613466.552 | 1258711.0758 | 2613468.0539 | 1258710.7619
5 | 2613480.2295 | 1258669.4121 | 2613495.8661 | 1258664.7222 | 2613498.1641 | 1258658.5121
6 | 2613479.1162 | 1258665.1066 | 2613480.2295 | 1258669.4121
7 | 2613498.1641 | 1258658.5121 | 2613521.7517 | 1258656.5145
8 | 2613478.6167 | 1258656.0216 | 2613479.1162 | 1258665.1066
9 | 2613479.1162 | 1258665.1066 | 2613465.5566 | 1258667.8117
10 | 2613466.552 | 1258711.0758 | 2613467.1939 | 1258725.6823
11 | 2613466.552 | 1258711.0758 | 2613464.6896 | 1258711.4648
12 | 2613521.7517 | 1258656.5145 | 2613545.0095 | 1258654.5448
13 | 2613465.5566 | 1258667.8117 | 2613457.1603 | 1258669.4866
14 | 2613467.4522 | 1258731.5611 | 2613467.1939 | 1258725.6823
15 | 2613443.5895 | 1258708.8334 | 2613451.7972 | 1258712.599 | 2613460.4963 | 1258712.3407 | 2613464.6896 | 1258711.4648
16 | 2613551.0426 | 1258635.0833 | 2613547.9742 | 1258631.984
17 | 2613551.0426 | 1258635.0833 | 2613553.7801 | 1258637.8469
18 | 2613506.7689 | 1258590.3635 | 2613547.9742 | 1258631.984
19 | 2613553.7801 | 1258637.8469 | 2613563.7721 | 1258635.0638
20 | 2613561.7052 | 1258653.1308 | 2613558.2774 | 1258642.3824 | 2613553.7801 | 1258637.8469
21 | 2613561.7052 | 1258653.1308 | 2613545.0095 | 1258654.5448
22 | 2613440.7245 | 1258672.4914 | 2613449.6303 | 1258670.8549 | 2613454.0416 | 1258670.1088 | 2613457.1603 | 1258669.4866
23 | 2613551.599 | 1258701.7961 | 2613544.0969 | 1258702.7019 | 2613541.435 | 1258702.8026
24 | 2613551.599 | 1258701.7961 | 2613568.2501 | 1258698.4207 | 2613575.2888 | 1258695.8239
25 | 2613467.4522 | 1258731.5611 | 2613467.6129 | 1258735.2167 | 2613470.1008 | 1258741.6378 | 2613471.7998 | 1258742.6032
26 | 2613443.5895 | 1258708.8334 | 2613444.9177 | 1258704.8115 | 2613445.2592 | 1258700.4649 | 2613444.685 | 1258694.3929 | 2613443.9592 | 1258690.6542
27 | 2613432.426 | 1258715.5572 | 2613437.1779 | 1258714.1781 | 2613439.9329 | 1258712.5499 | 2613443.5895 | 1258708.8334
28 | 2613506.7689 | 1258590.3635 | 2613531.727 | 1258583.738
29 | 2613569.3292 | 1258633.5159 | 2613563.7721 | 1258635.0638
30 | 2613561.7052 | 1258653.1308 | 2613563.7543 | 1258659.5714
31 | 2613440.7245 | 1258672.4914 | 2613442.4349 | 1258682.8022 | 2613443.9592 | 1258690.6542
32 | 2613364.4765 | 1258771.2745 | 2613364.3519 | 1258774.3824
33 | 2613365.051 | 1258756.9444 | 2613364.4765 | 1258771.2745
34 | 2613364.3519 | 1258774.3824 | 2613363.9492 | 1258784.4281
35 | 2613365.051 | 1258756.9444 | 2613366.2808 | 1258749.72 | 2613367.8505 | 1258745.9506
36 | 2613365.051 | 1258756.9444 | 2613354.6418 | 1258756.7653 | 2613350.694 | 1258756.7789
37 | 2613363.9492 | 1258784.4281 | 2613363.4731 | 1258796.3044
38 | 2613374.2894 | 1258734.7613 | 2613369.6761 | 1258741.5666 | 2613367.8505 | 1258745.9506
39 | 2613350.694 | 1258756.7789 | 2613343.7746 | 1258756.8026
40 | 2613363.4731 | 1258796.3044 | 2613363.4369 | 1258797.2073
41 | 2613374.2894 | 1258734.7613 | 2613382.6843 | 1258729.0096 | 2613385.1884 | 1258727.7005
42 | 2613329.6608 | 1258753.6987 | 2613337.1326 | 1258756.3924 | 2613342.898 | 1258756.8056 | 2613343.7746 | 1258756.8026
43 | 2613363.4369 | 1258797.2073 | 2613363.4272 | 1258797.4482
44 | 2613390.8847 | 1258725.1346 | 2613389.0159 | 1258725.6994 | 2613385.1884 | 1258727.7005
45 | 2613363.3812 | 1258798.5966 | 2613363.4272 | 1258797.4482
46 | 2613390.8847 | 1258725.1346 | 2613395.9176 | 1258723.6136 | 2613402.6232 | 1258722.1338
47 | 2613389.0889 | 1258867.8145 | 2613372.1513 | 1258874.4033
48 | 2613389.0889 | 1258867.8145 | 2613395.3174 | 1258865.3917
49 | 2613354.8406 | 1258876.2796 | 2613359.8389 | 1258879.1928 | 2613372.1513 | 1258874.4033
50 | 2613398.2852 | 1258864.2372 | 2613395.3174 | 1258865.3917
51 | 2613354.8406 | 1258876.2796 | 2613358.8109 | 1258867.1046 | 2613359.4131 | 1258864.1039 | 2613359.7111 | 1258862.3034 | 2613359.6107 | 1258860.0127
52 | 2613349.4569 | 1258890.5438 | 2613351.5511 | 1258884.3666 | 2613354.8406 | 1258876.2796
53 | 2613407.7878 | 1258860.5407 | 2613398.2852 | 1258864.2372
54 | 2613351.7274 | 1258852.8902 | 2613356.7412 | 1258855.6589 | 2613358.7114 | 1258857.7091 | 2613359.6107 | 1258860.0127
55 | 2613349.4569 | 1258890.5438 | 2613348.7201 | 1258896.4239 | 2613348.7155 | 1258901.8053 | 2613349.0299 | 1258906.1089 | 2613349.4249 | 1258911.5023 | 2613350.1249 | 1258918.6087 | 2613350.3193 | 1258919.6033
56 | 2613422.4732 | 1258853.2457 | 2613410.7922 | 1258859.3719 | 2613407.7878 | 1258860.5407
57 | 2613351.7274 | 1258852.8902 | 2613353.9977 | 1258845.4903 | 2613354.245 | 1258844.6851
58 | 2613351.7274 | 1258852.8902 | 2613349.4733 | 1258859.7231
59 | 2613349.4733 | 1258859.7231 | 2613348.3653 | 1258862.6983
60 | 2613394.1999 | 1258903.7978 | 2613393.6012 | 1258905.1974 | 2613393.297 | 1258906.3975 | 2613393.5984 | 1258909.8005 | 2613395.3974 | 1258927.6055 | 2613395.4832 | 1258928.351
61 | 2613394.1999 | 1258903.7978 | 2613407.3984 | 1258910.2986 | 2613412.9726 | 1258913.8572
62 | 2613431.6216 | 1258928.0097 | 2613423.399 | 1258920.9975 | 2613415.7003 | 1258915.5987 | 2613412.9726 | 1258913.8572
63 | 2613429.8266 | 1258849.3892 | 2613422.4732 | 1258853.2457
64 | 2613354.245 | 1258844.6851 | 2613357.6348 | 1258833.646 | 2613358.897 | 1258826.6454
65 | 2613431.6216 | 1258928.0097 | 2613435.8987 | 1258923.205 | 2613443.3026 | 1258915.6055 | 2613453.9766 | 1258903.9276
66 | 2613440.0693 | 1258843.7407 | 2613433.5902 | 1258847.4153 | 2613429.8266 | 1258849.3892
67 | 2613573.8005 | 1258775.3817 | 2613573.5403 | 1258776.4021
68 | 2613579.5999 | 1258762.0006 | 2613576.8977 | 1258766.8977 | 2613574.0007 | 1258774.5963 | 2613573.8005 | 1258775.3817
69 | 2613573.5403 | 1258776.4021 | 2613572.3222 | 1258781.1789
70 | 2613579.5999 | 1258762.0006 | 2613578.1031 | 1258757.3051 | 2613575.9032 | 1258753.4975 | 2613569.1008 | 1258741.7963 | 2613566.1172 | 1258735.9198
71 | 2613579.5999 | 1258762.0006 | 2613581.0978 | 1258762.9046 | 2613587.4023 | 1258764.8981 | 2613594.3157 | 1258766.8364
72 | 2613569.936 | 1258790.4061 | 2613571.3996 | 1258784.7972 | 2613572.3222 | 1258781.1789
73 | 2613564.8245 | 1258733.3737 | 2613566.1172 | 1258735.9198
74 | 2613594.3157 | 1258766.8364 | 2613598.9577 | 1258768.1378 | 2613603.7315 | 1258768.4035
75 | 2613569.1033 | 1258819.9045 | 2613568.4016 | 1258813.5987 | 2613567.7998 | 1258806.5036 | 2613567.8041 | 1258801.3001 | 2613568.0978 | 1258798.0986 | 2613569.1031 | 1258793.5979 | 2613569.936 | 1258790.4061
76 | 2613610.0721 | 1258768.714 | 2613609.5845 | 1258768.7292 | 2613603.7315 | 1258768.4035
77 | 2613569.1033 | 1258819.9045 | 2613569.5182 | 1258823.867
78 | 2613569.1033 | 1258819.9045 | 2613565.7998 | 1258820.7976 | 2613562.3969 | 1258822.302 | 2613562.0459 | 1258822.5058
79 | 2613629.0122 | 1258767.3398 | 2613619.2032 | 1258768.4288 | 2613610.0721 | 1258768.714
80 | 2613569.5182 | 1258823.867 | 2613570.2024 | 1258830.403 | 2613573.1719 | 1258843.7743 | 2613575.6407 | 1258850.747
81 | 2613575.2888 | 1258695.8239 | 2613576.8069 | 1258695.2636
82 | 2613575.2888 | 1258695.8239 | 2613570.8575 | 1258681.8964
83 | 2613579.7399 | 1258862.3241 | 2613580.8868 | 1258871.2809
84 | 2613579.7399 | 1258862.3241 | 2613575.6407 | 1258850.747
85 | 2613579.7399 | 1258862.3241 | 2613562.6974 | 1258861.4444
86 | 2613562.6974 | 1258861.4444 | 2613544.8919 | 1258860.5253
87 | 2613516.2946 | 1258852.7557 | 2613516.4303 | 1258853.0958 | 2613518.6399 | 1258859.2494 | 2613524.3001 | 1258859.4624 | 2613544.8919 | 1258860.5253
88 | 2613516.2946 | 1258852.7557 | 2613511.7335 | 1258841.3238
89 | 2613508.8181 | 1258834.0167 | 2613511.7335 | 1258841.3238
90 | 2613363.3812 | 1258798.5966 | 2613363.3181 | 1258800.1696 | 2613362.4109 | 1258805.7615
91 | 2613359.5764 | 1258822.8775 | 2613360.1537 | 1258819.6756 | 2613362.4109 | 1258805.7615
92 | 2613359.5764 | 1258822.8775 | 2613359.5175 | 1258823.2039
93 | 2613358.897 | 1258826.6454 | 2613359.5175 | 1258823.2039
94 | 2613614.2342 | 1258681.4511 | 2613576.8069 | 1258695.2636
95 | 2613570.0967 | 1258679.5053 | 2613570.8575 | 1258681.8964
96 | 2613621.8358 | 1258678.8412 | 2613615.7103 | 1258680.9063 | 2613614.2342 | 1258681.4511
97 | 2613570.0967 | 1258679.5053 | 2613563.7543 | 1258659.5714
98 | 2613621.8358 | 1258678.8412 | 2613626.3631 | 1258691.632
99 | 2613467.1254 | 1258828.5475 | 2613472.664 | 1258826.2586
100 | 2613497.0983 | 1258815.8045 | 2613496.1986 | 1258817.0033 | 2613494.9001 | 1258817.901 | 2613492.8014 | 1258819.2971 | 2613490.5984 | 1258820.2039 | 2613472.8036 | 1258826.2009 | 2613472.664 | 1258826.2586
101 | 2613456.9005 | 1258835.6045 | 2613457.8989 | 1258834.1058 | 2613460.2024 | 1258832.0985 | 2613463.5991 | 1258830.0048 | 2613467.1254 | 1258828.5475
102 | 2613497.0983 | 1258815.8045 | 2613502.355 | 1258817.8178 | 2613504.0083 | 1258821.9617
103 | 2613500.7977 | 1258803.2044 | 2613499.7007 | 1258805.0032 | 2613498.7976 | 1258807.7029 | 2613498.6032 | 1258810.3042 | 2613498.3033 | 1258812.9053 | 2613497.9984 | 1258814.4056 | 2613497.0983 | 1258815.8045
104 | 2613456.9005 | 1258835.6045 | 2613455.5881 | 1258832.6774 | 2613455.5808 | 1258828.5624
105 | 2613456.9005 | 1258835.6045 | 2613456.3028 | 1258836.6039 | 2613455.3022 | 1258839.1033 | 2613455.1014 | 1258841.2042 | 2613454.9971 | 1258844.0059 | 2613455.2001 | 1258850.8999 | 2613456.333 | 1258863.7068
106 | 2613456.9005 | 1258835.6045 | 2613450.7973 | 1258837.9701 | 2613443.6658 | 1258841.7009 | 2613440.0693 | 1258843.7407
107 | 2613508.8181 | 1258834.0167 | 2613504.0083 | 1258821.9617
108 | 2613500.7977 | 1258803.2044 | 2613502.898 | 1258801.0967 | 2613510.9972 | 1258796.1006 | 2613517.8037 | 1258792.8027 | 2613519.2979 | 1258792.0056 | 2613520.2043 | 1258791.196
109 | 2613455.5808 | 1258828.5624 | 2613455.5262 | 1258797.8248
110 | 2613453.9766 | 1258903.9276 | 2613454.0022 | 1258903.8996 | 2613455.3998 | 1258902.5018 | 2613456.7981 | 1258900.8038 | 2613457.9031 | 1258898.805 | 2613458.9976 | 1258894.8047 | 2613459.2019 | 1258891.1027 | 2613458.7021 | 1258885.4978 | 2613457.1991 | 1258873.4974 | 2613456.333 | 1258863.7068
111 | 2613520.2043 | 1258791.196 | 2613520.9012 | 1258789.6966 | 2613520.9012 | 1258789.6966
112 | 2613455.4845 | 1258774.3205 | 2613455.5262 | 1258797.8248
113 | 2613520.0577 | 1258784.7492 | 2613520.6003 | 1258786.1046 | 2613520.7997 | 1258787.9062 | 2613520.9012 | 1258789.6966
114 | 2613490.6955 | 1258771.5077 | 2613489.3763 | 1258767.2958
115 | 2613486.5406 | 1258758.2418 | 2613489.3763 | 1258767.2958
116 | 2613520.0577 | 1258784.7492 | 2613519.7983 | 1258784.1014
117 | 2613486.5406 | 1258758.2418 | 2613483.3444 | 1258751.7079 | 2613479.8647 | 1258747.1859 | 2613471.7998 | 1258742.6032
118 | 2613403.6559 | 1258721.9059 | 2613402.6232 | 1258722.1338
119 | 2613432.426 | 1258715.5572 | 2613403.6559 | 1258721.9059
120 | 2613456.6288 | 1258742.5968 | 2613454.0997 | 1258741.0011 | 2613446.7985 | 1258736.4037 | 2613444.0006 | 1258733.7067 | 2613441.7977 | 1258731.2 | 2613439.4977 | 1258728.304 | 2613439.0684 | 1258727.7012
121 | 2613432.426 | 1258715.5572 | 2613436.903 | 1258722.4053 | 2613438.4984 | 1258726.9008 | 2613439.0684 | 1258727.7012
122 | 2613569.3292 | 1258633.5159 | 2613573.6007 | 1258632.3262
123 | 2613573.6751 | 1258632.3055 | 2613573.6007 | 1258632.3262
124 | 2613573.6751 | 1258632.3055 | 2613574.8848 | 1258631.9685
125 | 2613574.8848 | 1258631.9685 | 2613580.444 | 1258630.4201
126 | 2613580.444 | 1258630.4201 | 2613586.1356 | 1258628.8347

## bus_geodata
| x | y | coords
0 | 2613487.6735 | 1258698.0822
1 | 2613489.6 | 1258705.5021
2 | 2613502.0683 | 1258704.0012
3 | 2613468.0539 | 1258710.7619
4 | 2613480.2295 | 1258669.4121
5 | 2613498.1641 | 1258658.5121
6 | 2613479.1162 | 1258665.1066
7 | 2613509.8948 | 1258703.5365
8 | 2613466.552 | 1258711.0758
9 | 2613521.7517 | 1258656.5145
10 | 2613478.6167 | 1258656.0216
11 | 2613465.5566 | 1258667.8117
12 | 2613467.1939 | 1258725.6823
13 | 2613464.6896 | 1258711.4648
14 | 2613551.0426 | 1258635.0833
15 | 2613547.9742 | 1258631.984
16 | 2613553.7801 | 1258637.8469
17 | 2613545.0095 | 1258654.5448
18 | 2613457.1603 | 1258669.4866
19 | 2613541.435 | 1258702.8026
20 | 2613551.599 | 1258701.7961
21 | 2613467.4522 | 1258731.5611
22 | 2613443.5895 | 1258708.8334
23 | 2613506.7689 | 1258590.3635
24 | 2613563.7721 | 1258635.0638
25 | 2613561.7052 | 1258653.1308
26 | 2613440.7245 | 1258672.4914
27 | 2613364.4765 | 1258771.2745
28 | 2613364.3519 | 1258774.3824
29 | 2613365.051 | 1258756.9444
30 | 2613363.9492 | 1258784.4281
31 | 2613367.8505 | 1258745.9506
32 | 2613350.694 | 1258756.7789
33 | 2613363.4731 | 1258796.3044
34 | 2613374.2894 | 1258734.7613
35 | 2613343.7746 | 1258756.8026
36 | 2613363.4369 | 1258797.2073
37 | 2613385.1884 | 1258727.7005
38 | 2613329.6608 | 1258753.6987
39 | 2613363.4272 | 1258797.4482
40 | 2613390.8847 | 1258725.1346
41 | 2613389.0889 | 1258867.8145
42 | 2613372.1513 | 1258874.4033
43 | 2613395.3174 | 1258865.3917
44 | 2613354.8406 | 1258876.2796
45 | 2613398.2852 | 1258864.2372
46 | 2613359.6107 | 1258860.0127
47 | 2613349.4569 | 1258890.5438
48 | 2613407.7878 | 1258860.5407
49 | 2613351.7274 | 1258852.8902
50 | 2613349.4733 | 1258859.7231
51 | 2613348.3653 | 1258862.6983
52 | 2613350.3193 | 1258919.6033
53 | 2613394.1999 | 1258903.7978
54 | 2613395.4832 | 1258928.351
55 | 2613412.9726 | 1258913.8572
56 | 2613422.4732 | 1258853.2457
57 | 2613354.245 | 1258844.6851
58 | 2613431.6216 | 1258928.0097
59 | 2613429.8266 | 1258849.3892
60 | 2613573.8005 | 1258775.3817
61 | 2613573.5403 | 1258776.4021
62 | 2613579.5999 | 1258762.0006
63 | 2613572.3222 | 1258781.1789
64 | 2613566.1172 | 1258735.9198
65 | 2613594.3157 | 1258766.8364
66 | 2613569.936 | 1258790.4061
67 | 2613564.8245 | 1258733.3737
68 | 2613603.7315 | 1258768.4035
69 | 2613569.1033 | 1258819.9045
70 | 2613610.0721 | 1258768.714
71 | 2613569.5182 | 1258823.867
72 | 2613562.0459 | 1258822.5058
73 | 2613575.2888 | 1258695.8239
74 | 2613629.0122 | 1258767.3398
75 | 2613580.8868 | 1258871.2809
76 | 2613579.7399 | 1258862.3241
77 | 2613575.6407 | 1258850.747
78 | 2613562.6974 | 1258861.4444
79 | 2613544.8919 | 1258860.5253
80 | 2613516.2946 | 1258852.7557
81 | 2613511.7335 | 1258841.3238
82 | 2613363.3812 | 1258798.5966
83 | 2613362.4109 | 1258805.7615
84 | 2613359.5764 | 1258822.8775
85 | 2613359.5175 | 1258823.2039
86 | 2613358.897 | 1258826.6454
87 | 2613576.8069 | 1258695.2636
88 | 2613570.8575 | 1258681.8964
89 | 2613614.2342 | 1258681.4511
90 | 2613570.0967 | 1258679.5053
91 | 2613621.8358 | 1258678.8412
92 | 2613563.7543 | 1258659.5714
93 | 2613472.664 | 1258826.2586
94 | 2613467.1254 | 1258828.5475
95 | 2613497.0983 | 1258815.8045
96 | 2613456.9005 | 1258835.6045
97 | 2613504.0083 | 1258821.9617
98 | 2613500.7977 | 1258803.2044
99 | 2613455.5808 | 1258828.5624
100 | 2613456.333 | 1258863.7068
101 | 2613440.0693 | 1258843.7407
102 | 2613508.8181 | 1258834.0167
103 | 2613520.2043 | 1258791.196
104 | 2613455.5262 | 1258797.8248
105 | 2613453.9766 | 1258903.9276
106 | 2613520.9012 | 1258789.6966
107 | 2613490.6955 | 1258771.5077
108 | 2613489.3763 | 1258767.2958
109 | 2613455.4845 | 1258774.3205
110 | 2613520.0577 | 1258784.7492
111 | 2613486.5406 | 1258758.2418
112 | 2613402.6232 | 1258722.1338
113 | 2613403.6559 | 1258721.9059
114 | 2613456.6288 | 1258742.5968
115 | 2613439.0684 | 1258727.7012
116 | 2613471.7998 | 1258742.6032
117 | 2613432.426 | 1258715.5572
118 | 2613443.9592 | 1258690.6542
119 | 2613569.3292 | 1258633.5159
120 | 2613626.3631 | 1258691.632
121 | 2613573.6007 | 1258632.3262
122 | 2613573.6751 | 1258632.3055
123 | 2613574.8848 | 1258631.9685
124 | 2613580.444 | 1258630.4201
125 | 2613586.1356 | 1258628.8347
126 | 2613531.727 | 1258583.738
127 | 2613519.7983 | 1258784.1014
128 | 2613486.5406 | 1258758.2418

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99308 | -0.13224 | 0.0060481 | 0.0015158
1 | 0.99312 | -0.13142 | 0 | 0
2 | 0.99308 | -0.13231 | 0.0018624 | 0.00046676
3 | 0.99333 | -0.1275 | 0.0028909 | 0.00072452
4 | 0.98895 | -0.21172 | 0 | 0
5 | 0.98712 | -0.24718 | 0 | 0
6 | 0.98931 | -0.20484 | 0 | 0
7 | 0.99306 | -0.1326 | 0.0021034 | 0.00052716
8 | 0.99335 | -0.12715 | 0 | 0
9 | 0.98523 | -0.28398 | 0.022874 | 0.0057326
10 | 0.98925 | -0.20595 | 0.0068378 | 0.0017137
11 | 0.9905 | -0.18183 | 0.036029 | 0.0090298
12 | 0.99296 | -0.13464 | 0.0090266 | 0.0022623
13 | 0.99342 | -0.12574 | 0.0090452 | 0.0022669
14 | 0.98235 | -0.34011 | 0 | 0
15 | 0.9823 | -0.34107 | 0.0031061 | 0.00077846
16 | 0.98239 | -0.33926 | 0 | 0
17 | 0.98385 | -0.31078 | 0.0054976 | 0.0013778
18 | 0.99152 | -0.16214 | 0.035323 | 0.0088529
19 | 0.98205 | -0.34587 | 0.0039022 | 0.00097798
20 | 0.98209 | -0.34515 | 0 | 0
21 | 0.99285 | -0.13672 | 0.0073759 | 0.0018486
22 | 0.99444 | -0.10595 | 0 | 0
23 | 0.98181 | -0.35065 | 0 | 0
24 | 0.98218 | -0.34336 | 0.0029959 | 0.00075085
25 | 0.98295 | -0.32841 | 0 | 0
26 | 0.99279 | -0.13774 | 0 | 0
27 | 0.98935 | -0.20359 | 0.0062985 | 0.0015786
28 | 0.98919 | -0.20668 | 0.0036321 | 0.0009103
29 | 0.99011 | -0.18898 | 0 | 0
30 | 0.98868 | -0.21649 | 0.0035047 | 0.00087837
31 | 0.99076 | -0.17647 | 0.0051563 | 0.0012923
32 | 0.98988 | -0.19352 | 0.0093269 | 0.0023375
33 | 0.98809 | -0.22792 | 0.0045483 | 0.0011399
34 | 0.99151 | -0.16198 | 0 | 0
35 | 0.98982 | -0.19456 | 0.0034655 | 0.00086854
36 | 0.98805 | -0.22877 | 0.0047782 | 0.0011975
37 | 0.99227 | -0.14747 | 0.0051389 | 0.0012879
38 | 0.98976 | -0.19586 | 0.004987 | 0.0012499
39 | 0.98804 | -0.22899 | 0.0072283 | 0.0018116
40 | 0.99264 | -0.14033 | 0.0072843 | 0.0018256
41 | 0.98424 | -0.30237 | 0.0025477 | 0.00063852
42 | 0.98467 | -0.294 | 0.0038958 | 0.00097639
43 | 0.98409 | -0.30537 | 0.0013188 | 0.00033051
44 | 0.98514 | -0.28494 | 0 | 0
45 | 0.98401 | -0.30678 | 0.0012004 | 0.00030084
46 | 0.98558 | -0.27644 | 0.012174 | 0.0030511
47 | 0.98509 | -0.28602 | 0 | 0
48 | 0.98378 | -0.31124 | 0.0017765 | 0.00044523
49 | 0.9859 | -0.27038 | 0 | 0
50 | 0.98585 | -0.27134 | 0 | 0
51 | 0.98582 | -0.27176 | 0.0074463 | 0.0018662
52 | 0.98498 | -0.28808 | 0.0039432 | 0.00098825
53 | 0.98142 | -0.35722 | 0 | 0
54 | 0.98137 | -0.35834 | 0.0024884 | 0.00062365
55 | 0.98147 | -0.35626 | 0.002139 | 0.00053608
56 | 0.98342 | -0.3183 | 0.0020736 | 0.00051969
57 | 0.98615 | -0.26539 | 0.011156 | 0.0027959
58 | 0.98157 | -0.35429 | 0 | 0
59 | 0.98324 | -0.3218 | 0.0014288 | 0.0003581
60 | 0.97138 | -0.55396 | 0.0036527 | 0.00091546
61 | 0.9714 | -0.55354 | 0.0032964 | 0.00082617
62 | 0.97114 | -0.55873 | 0 | 0
63 | 0.97152 | -0.5513 | 0.002339 | 0.00058621
64 | 0.97092 | -0.56307 | 0.00513 | 0.0012857
65 | 0.971 | -0.56151 | 0.0015539 | 0.00038945
66 | 0.97176 | -0.54656 | 0.0015016 | 0.00037633
67 | 0.97091 | -0.56322 | 0.0028386 | 0.00071142
68 | 0.97093 | -0.56295 | 0.0020288 | 0.00050846
69 | 0.97255 | -0.53094 | 0 | 0
70 | 0.97089 | -0.56367 | 0.0045371 | 0.0011371
71 | 0.97266 | -0.52867 | 0.0049539 | 0.0012416
72 | 0.97253 | -0.53128 | 0.002498 | 0.00062605
73 | 0.98218 | -0.34343 | 0 | 0
74 | 0.97086 | -0.56421 | 0.0015579 | 0.00039045
75 | 0.97402 | -0.50191 | 0.0029651 | 0.00074313
76 | 0.97404 | -0.50142 | 0 | 0
77 | 0.97359 | -0.51039 | 0.0038489 | 0.00096462
78 | 0.97472 | -0.48804 | 0.0019277 | 0.00048313
79 | 0.97547 | -0.47345 | 0.0046039 | 0.0011539
80 | 0.97699 | -0.44356 | 0.0030106 | 0.00075454
81 | 0.97759 | -0.43182 | 0.0030177 | 0.00075631
82 | 0.98798 | -0.23001 | 0.0064911 | 0.0016268
83 | 0.98766 | -0.23624 | 0.002217 | 0.00055563
84 | 0.9869 | -0.251 | 0.01682 | 0.0042155
85 | 0.98688 | -0.25125 | 0.023158 | 0.005804
86 | 0.98676 | -0.2536 | 0.0093428 | 0.0023415
87 | 0.98217 | -0.34366 | 0.0028172 | 0.00070606
88 | 0.98234 | -0.34031 | 0.0056539 | 0.001417
89 | 0.98198 | -0.34731 | 0.0026335 | 0.00066001
90 | 0.98238 | -0.33952 | 0.0041372 | 0.0010369
91 | 0.98196 | -0.34766 | 0 | 0
92 | 0.98279 | -0.33138 | 0.0027525 | 0.00068985
93 | 0.98097 | -0.36594 | 0.0014019 | 0.00035136
94 | 0.98136 | -0.35835 | 0.0015847 | 0.00039717
95 | 0.97925 | -0.39939 | 0 | 0
96 | 0.9822 | -0.34198 | 0 | 0
97 | 0.97869 | -0.4103 | 0.0019108 | 0.00047888
98 | 0.97914 | -0.40159 | 0 | 0
99 | 0.98213 | -0.34337 | 0.0014859 | 0.00037241
100 | 0.98197 | -0.34644 | 0.0019344 | 0.0004848
101 | 0.98299 | -0.32665 | 0.0013388 | 0.00033555
102 | 0.978 | -0.4239 | 0.0022695 | 0.00056878
103 | 0.97895 | -0.40537 | 0.0022053 | 0.00055271
104 | 0.98187 | -0.34838 | 0.0045059 | 0.0011293
105 | 0.98171 | -0.35154 | 0.0020957 | 0.00052524
106 | 0.97894 | -0.40558 | 0.0021522 | 0.00053938
107 | 0.99239 | -0.14566 | 0.0053973 | 0.0013527
108 | 0.99241 | -0.14524 | 0.0048256 | 0.0012094
109 | 0.98178 | -0.35029 | 0.0045059 | 0.0011293
110 | 0.97891 | -0.40601 | 0.0023985 | 0.00060113
111 | 0.9925 | -0.14353 | 0 | 0
112 | 0.99338 | -0.12617 | 0.0039045 | 0.00097857
113 | 0.99345 | -0.12492 | 0.0024447 | 0.0006127
114 | 1 | 0 | -0.56204 | -0.14307
115 | 0.99704 | -0.056328 | 0.00717 | 0.001797
116 | 0.99271 | -0.1395 | 0.002369 | 0.00059372
117 | 0.99529 | -0.089765 | 0 | 0
118 | 0.99349 | -0.12429 | 0.059847 | 0.014999
119 | 0.98208 | -0.34532 | 0.0029959 | 0.00075085
120 | 0.98193 | -0.34826 | 0.0024283 | 0.00060859
121 | 0.98202 | -0.3466 | 0.0033727 | 0.00084527
122 | 0.98202 | -0.34662 | 0.0033801 | 0.00084714
123 | 0.982 | -0.34682 | 0.0029943 | 0.00075044
124 | 0.98197 | -0.34746 | 0.0029997 | 0.00075179
125 | 0.98196 | -0.3478 | 0.0031378 | 0.00078642
126 | 0.98159 | -0.35488 | 0.0090509 | 0.0022684
127 | 0.97891 | -0.40604 | 0.0023042 | 0.00057748
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0060481 | -0.0015158 | 0.0060484 | 0.0015159 | 2.3609e-07 | 5.1909e-08 | 0.0090624 | 0.0090624 | 0.0090624 | 0.99308 | -0.13224 | 0.99312 | -0.13142 | 2.4897
1 | 0.003966 | 0.00099378 | -0.0039658 | -0.00099384 | 1.6649e-07 | -5.6132e-08 | 0.0059422 | 0.0059423 | 0.0059423 | 0.99312 | -0.13142 | 0.99308 | -0.13231 | 1.6325
2 | -0.010014 | -0.0025096 | 0.010016 | 0.0025105 | 1.8731e-06 | 9.1166e-07 | 0.015005 | 0.015004 | 0.015005 | 0.99312 | -0.13142 | 0.99333 | -0.1275 | 4.1221
3 | 0.0021034 | 0.00052708 | -0.0021034 | -0.00052716 | 2.9205e-08 | -8.2747e-08 | 0.0031517 | 0.0031517 | 0.0031517 | 0.99308 | -0.13231 | 0.99306 | -0.1326 | 0.86586
4 | -0.012907 | -0.0032351 | 0.012907 | 0.0032352 | 2.1511e-07 | 1.1781e-07 | 0.019335 | 0.019335 | 0.019335 | 0.99333 | -0.1275 | 0.99335 | -0.12715 | 5.3118
5 | 0.087209 | 0.022039 | -0.087061 | -0.021944 | 0.00014801 | 9.4432e-05 | 0.13128 | 0.13128 | 0.13128 | 0.98895 | -0.21172 | 0.98712 | -0.24718 | 36.0668
6 | -0.087209 | -0.022039 | 0.087238 | 0.022057 | 2.8742e-05 | 1.8338e-05 | 0.13128 | 0.13128 | 0.13128 | 0.98895 | -0.21172 | 0.98931 | -0.20484 | 36.0668
7 | 0.087061 | 0.021944 | -0.086908 | -0.021847 | 0.000153 | 9.7616e-05 | 0.13128 | 0.13128 | 0.13128 | 0.98712 | -0.24718 | 0.98523 | -0.28398 | 36.0668
8 | 0.0068382 | 0.0017138 | -0.0068378 | -0.0017137 | 3.6096e-07 | 1.1419e-07 | 0.010285 | 0.010285 | 0.010285 | 0.98931 | -0.20484 | 0.98925 | -0.20595 | 2.8257
9 | -0.094076 | -0.023771 | 0.09418 | 0.023837 | 0.00010392 | 6.6329e-05 | 0.14157 | 0.14157 | 0.14157 | 0.98931 | -0.20484 | 0.9905 | -0.18183 | 38.8924
10 | 0.029011 | 0.0072766 | -0.029001 | -0.0072702 | 1.0356e-05 | 6.4386e-06 | 0.043461 | 0.043461 | 0.043461 | 0.99335 | -0.12715 | 0.99296 | -0.13464 | 11.9397
11 | -0.041919 | -0.010512 | 0.041921 | 0.010514 | 2.8135e-06 | 1.776e-06 | 0.062796 | 0.062796 | 0.062796 | 0.99335 | -0.12715 | 0.99342 | -0.12574 | 17.2515
12 | 0.064034 | 0.016114 | -0.063953 | -0.016062 | 8.191e-05 | 5.2125e-05 | 0.096737 | 0.096737 | 0.096737 | 0.98523 | -0.28398 | 0.98385 | -0.31078 | 26.576
13 | -0.13021 | -0.032867 | 0.13033 | 0.032946 | 0.00012296 | 7.8582e-05 | 0.19569 | 0.19569 | 0.19569 | 0.9905 | -0.18183 | 0.99152 | -0.16214 | 53.7623
14 | 0.019974 | 0.0050079 | -0.019972 | -0.0050067 | 1.9772e-06 | 1.1893e-06 | 0.029934 | 0.029934 | 0.029934 | 0.99296 | -0.13464 | 0.99285 | -0.13672 | 8.2236
15 | -0.050967 | -0.012781 | 0.051015 | 0.012811 | 4.8122e-05 | 3.0513e-05 | 0.076344 | 0.076344 | 0.076344 | 0.99342 | -0.12574 | 0.99444 | -0.10595 | 20.9737
16 | 0.012163 | 0.0030499 | -0.012163 | -0.0030496 | 5.5522e-07 | 3.0013e-07 | 0.018425 | 0.018425 | 0.018425 | 0.98235 | -0.34011 | 0.9823 | -0.34107 | 5.0619
17 | -0.012163 | -0.0030499 | 0.012164 | 0.0030501 | 4.9446e-07 | 2.6728e-07 | 0.018425 | 0.018425 | 0.018425 | 0.98235 | -0.34011 | 0.98239 | -0.33926 | 5.0619
18 | 0.0090568 | 0.0022711 | -0.0090527 | -0.0022692 | 4.1343e-06 | 1.9049e-06 | 0.01372 | 0.01372 | 0.01372 | 0.9823 | -0.34107 | 0.98181 | -0.35065 | 3.7693
19 | 0.021884 | 0.005487 | -0.02188 | -0.0054844 | 4.2739e-06 | 2.604e-06 | 0.033148 | 0.033148 | 0.033148 | 0.98239 | -0.33926 | 0.98218 | -0.34336 | 9.1066
20 | -0.034048 | -0.0085372 | 0.034065 | 0.0085482 | 1.7611e-05 | 1.1048e-05 | 0.051573 | 0.051573 | 0.051573 | 0.98239 | -0.33926 | 0.98295 | -0.32841 | 14.1684
21 | 0.058455 | 0.014684 | -0.058406 | -0.014653 | 4.9126e-05 | 3.1228e-05 | 0.088422 | 0.088422 | 0.088422 | 0.98385 | -0.31078 | 0.98295 | -0.32841 | 24.2918
22 | -0.16566 | -0.041798 | 0.16585 | 0.041922 | 0.00019379 | 0.00012359 | 0.24871 | 0.24871 | 0.24871 | 0.99152 | -0.16214 | 0.99279 | -0.13774 | 34.1629
23 | -0.0039022 | -0.00097798 | 0.0039023 | 0.00097793 | 1.3398e-07 | -4.357e-08 | 0.0059126 | 0.0059125 | 0.0059126 | 0.98205 | -0.34587 | 0.98209 | -0.34515 | 1.6243
24 | -0.0039023 | -0.00097793 | 0.0039026 | 0.00097783 | 3.2018e-07 | -1.0417e-07 | 0.0059125 | 0.0059124 | 0.0059125 | 0.98209 | -0.34515 | 0.98218 | -0.34343 | 1.6243
25 | 0.012597 | 0.0031581 | -0.012595 | -0.0031572 | 1.6707e-06 | 9.0761e-07 | 0.018879 | 0.018879 | 0.018879 | 0.99285 | -0.13672 | 0.99271 | -0.1395 | 5.1866
26 | 0.226 | 0.057115 | -0.2258 | -0.056989 | 0.00019858 | 0.00012613 | 0.33834 | 0.33834 | 0.33834 | 0.99444 | -0.10595 | 0.99349 | -0.12429 | 23.2378
27 | -0.27702 | -0.069926 | 0.27723 | 0.070063 | 0.00021495 | 0.00013688 | 0.41469 | 0.41469 | 0.41469 | 0.99444 | -0.10595 | 0.99529 | -0.089765 | 28.4811
28 | 0.0090527 | 0.0022692 | -0.0090509 | -0.0022684 | 1.8229e-06 | 8.4016e-07 | 0.01372 | 0.01372 | 0.01372 | 0.98181 | -0.35065 | 0.98159 | -0.35488 | 3.7693
29 | 0.018884 | 0.0047336 | -0.018882 | -0.0047325 | 1.7706e-06 | 1.0602e-06 | 0.028609 | 0.028609 | 0.028609 | 0.98218 | -0.34336 | 0.98208 | -0.34532 | 7.8597
30 | 0.02434 | 0.0061046 | -0.024337 | -0.0061025 | 3.4415e-06 | 2.1169e-06 | 0.036849 | 0.036849 | 0.036849 | 0.98295 | -0.32841 | 0.98279 | -0.33138 | 10.1234
31 | -0.16585 | -0.041922 | 0.16596 | 0.04199 | 0.00010699 | 6.7519e-05 | 0.24871 | 0.24871 | 0.24871 | 0.99279 | -0.13774 | 0.99349 | -0.12429 | 17.0814
32 | 0.22416 | 0.056741 | -0.22412 | -0.056719 | 3.3183e-05 | 2.1078e-05 | 0.33734 | 0.33734 | 0.33734 | 0.98935 | -0.20359 | 0.98919 | -0.20668 | 23.1689
33 | -0.23046 | -0.058319 | 0.23062 | 0.058422 | 0.00016172 | 0.00010276 | 0.34681 | 0.34681 | 0.34681 | 0.98935 | -0.20359 | 0.99011 | -0.18898 | 23.8195
34 | 0.22049 | 0.055809 | -0.22039 | -0.055743 | 0.00010381 | 6.5924e-05 | 0.33188 | 0.33188 | 0.33188 | 0.98919 | -0.20668 | 0.98868 | -0.21649 | 22.7937
35 | -0.2484 | -0.06288 | 0.24855 | 0.062975 | 0.00014927 | 9.4948e-05 | 0.37354 | 0.37354 | 0.37354 | 0.99011 | -0.18898 | 0.99076 | -0.17647 | 25.6552
36 | 0.017784 | 0.0044584 | -0.01778 | -0.0044561 | 3.8465e-06 | 2.2771e-06 | 0.026728 | 0.026728 | 0.026728 | 0.99011 | -0.18898 | 0.98988 | -0.19352 | 7.3428
37 | 0.21688 | 0.054865 | -0.21676 | -0.054789 | 0.00011886 | 7.5462e-05 | 0.3266 | 0.3266 | 0.3266 | 0.98868 | -0.21649 | 0.98809 | -0.22792 | 22.4314
38 | -0.25371 | -0.064267 | 0.25388 | 0.06438 | 0.00017678 | 0.00011247 | 0.38128 | 0.38128 | 0.38128 | 0.99076 | -0.17647 | 0.99151 | -0.16198 | 26.1871
39 | 0.0084532 | 0.0021186 | -0.0084528 | -0.0021184 | 4.1898e-07 | 1.7921e-07 | 0.012707 | 0.012707 | 0.012707 | 0.98988 | -0.19352 | 0.98982 | -0.19456 | 3.491
40 | 0.21222 | 0.053649 | -0.21221 | -0.053644 | 8.661e-06 | 5.4967e-06 | 0.31975 | 0.31975 | 0.31975 | 0.98809 | -0.22792 | 0.98805 | -0.22877 | 21.961
41 | -0.25388 | -0.06438 | 0.25406 | 0.064493 | 0.0001772 | 0.00011274 | 0.38128 | 0.38128 | 0.38128 | 0.99151 | -0.16198 | 0.99227 | -0.14747 | 26.1871
42 | 0.0049873 | 0.0012499 | -0.004987 | -0.0012499 | 3.0775e-07 | 9.3183e-09 | 0.0074975 | 0.0074975 | 0.0074975 | 0.98982 | -0.19456 | 0.98976 | -0.19586 | 2.0598
43 | 0.20743 | 0.052446 | -0.20743 | -0.052445 | 2.2081e-06 | 1.4008e-06 | 0.31256 | 0.31256 | 0.31256 | 0.98805 | -0.22877 | 0.98804 | -0.22899 | 21.4667
44 | -0.2592 | -0.065781 | 0.25929 | 0.065837 | 8.8962e-05 | 5.6612e-05 | 0.38899 | 0.38899 | 0.38899 | 0.99227 | -0.14747 | 0.99264 | -0.14033 | 26.7163
45 | 0.2002 | 0.050633 | -0.20019 | -0.050627 | 9.8055e-06 | 6.2166e-06 | 0.30167 | 0.30167 | 0.30167 | 0.98804 | -0.22899 | 0.98798 | -0.23001 | 20.7191
46 | -0.26657 | -0.067663 | 0.26675 | 0.067779 | 0.00018179 | 0.00011572 | 0.39991 | 0.39991 | 0.39991 | 0.99264 | -0.14033 | 0.99338 | -0.12617 | 27.4663
47 | -0.10305 | -0.026096 | 0.10309 | 0.026122 | 4.1407e-05 | 2.5576e-05 | 0.15589 | 0.15589 | 0.15589 | 0.98424 | -0.30237 | 0.98467 | -0.294 | 10.7069
48 | 0.1005 | 0.025458 | -0.10049 | -0.025449 | 1.4483e-05 | 8.9296e-06 | 0.15204 | 0.15204 | 0.15204 | 0.98424 | -0.30237 | 0.98409 | -0.30537 | 10.4423
49 | -0.10699 | -0.027098 | 0.10703 | 0.027127 | 4.6611e-05 | 2.8864e-05 | 0.16178 | 0.16178 | 0.16178 | 0.98467 | -0.294 | 0.98514 | -0.28494 | 11.1112
50 | 0.099169 | 0.025118 | -0.099163 | -0.025114 | 6.7214e-06 | 4.1399e-06 | 0.15005 | 0.15005 | 0.15005 | 0.98409 | -0.30537 | 0.98401 | -0.30678 | 10.3054
51 | -0.11098 | -0.028115 | 0.11102 | 0.028143 | 4.5304e-05 | 2.8119e-05 | 0.16774 | 0.16774 | 0.16774 | 0.98514 | -0.28494 | 0.98558 | -0.27644 | 11.5203
52 | 0.0039438 | 0.00098807 | -0.0039436 | -0.00098813 | 2.0296e-07 | -6.43e-08 | 0.0059568 | 0.0059569 | 0.0059569 | 0.98514 | -0.28494 | 0.98509 | -0.28602 | 1.6365
53 | 0.097962 | 0.024814 | -0.097941 | -0.024801 | 2.1003e-05 | 1.2924e-05 | 0.14823 | 0.14823 | 0.14823 | 0.98401 | -0.30678 | 0.98378 | -0.31124 | 10.1807
54 | -0.1232 | -0.031195 | 0.12323 | 0.031217 | 3.5864e-05 | 2.239e-05 | 0.18612 | 0.18611 | 0.18612 | 0.98558 | -0.27644 | 0.9859 | -0.27038 | 12.7826
55 | 0.0039436 | 0.00098813 | -0.0039432 | -0.00098825 | 3.8835e-07 | -1.2296e-07 | 0.0059569 | 0.005957 | 0.005957 | 0.98509 | -0.28602 | 0.98498 | -0.28808 | 1.6365
56 | 0.096165 | 0.024355 | -0.096132 | -0.024335 | 3.2597e-05 | 2.0029e-05 | 0.14554 | 0.14554 | 0.14554 | 0.98378 | -0.31124 | 0.98342 | -0.3183 | 9.9962
57 | -0.13068 | -0.033083 | 0.13071 | 0.033103 | 3.1339e-05 | 1.9619e-05 | 0.19735 | 0.19735 | 0.19735 | 0.9859 | -0.27038 | 0.98615 | -0.26539 | 13.5546
58 | 0.0074468 | 0.0018664 | -0.0074465 | -0.0018663 | 3.408e-07 | 1.2638e-07 | 0.01124 | 0.01124 | 0.01124 | 0.9859 | -0.27038 | 0.98585 | -0.27134 | 3.0878
59 | 0.0074465 | 0.0018663 | -0.0074463 | -0.0018662 | 1.504e-07 | 5.5778e-08 | 0.01124 | 0.01124 | 0.01124 | 0.98585 | -0.27134 | 0.98582 | -0.27176 | 3.0878
60 | 0.0024885 | 0.00062343 | -0.0024884 | -0.00062365 | 1.3251e-07 | -2.2884e-07 | 0.003773 | 0.0037731 | 0.0037731 | 0.98142 | -0.35722 | 0.98137 | -0.35834 | 1.0366
61 | -0.0024885 | -0.00062343 | 0.0024887 | 0.00062323 | 1.1384e-07 | -1.9664e-07 | 0.003773 | 0.0037729 | 0.003773 | 0.98142 | -0.35722 | 0.98147 | -0.35626 | 1.0365
62 | -0.0046277 | -0.0011593 | 0.0046281 | 0.0011593 | 4.3276e-07 | -1.9362e-08 | 0.0070158 | 0.0070157 | 0.0070158 | 0.98147 | -0.35626 | 0.98157 | -0.35429 | 1.9274
63 | 0.094059 | 0.023816 | -0.094043 | -0.023806 | 1.5787e-05 | 9.682e-06 | 0.14241 | 0.14241 | 0.14241 | 0.98342 | -0.3183 | 0.98324 | -0.3218 | 9.7807
64 | -0.14187 | -0.035899 | 0.14195 | 0.035949 | 8.026e-05 | 5.0413e-05 | 0.21419 | 0.21419 | 0.21419 | 0.98615 | -0.26539 | 0.98676 | -0.2536 | 14.7107
65 | -0.0046281 | -0.0011593 | 0.0046287 | 0.0011593 | 6.0657e-07 | -2.7255e-08 | 0.0070157 | 0.0070156 | 0.0070157 | 0.98157 | -0.35429 | 0.98171 | -0.35154 | 1.9274
66 | 0.092614 | 0.023448 | -0.092593 | -0.023435 | 2.1571e-05 | 1.3212e-05 | 0.14025 | 0.14025 | 0.14025 | 0.98324 | -0.3218 | 0.98299 | -0.32665 | 9.6322
67 | -0.021307 | -0.0053418 | 0.021307 | 0.0053421 | 4.2067e-07 | 2.5619e-07 | 0.03264 | 0.03264 | 0.03264 | 0.97138 | -0.55396 | 0.9714 | -0.55354 | 8.9669
68 | 0.017654 | 0.0044264 | -0.01765 | -0.004424 | 4.0124e-06 | 2.3869e-06 | 0.027044 | 0.027044 | 0.027044 | 0.97138 | -0.55396 | 0.97114 | -0.55873 | 7.4297
69 | -0.024604 | -0.0061682 | 0.024606 | 0.0061699 | 2.626e-06 | 1.6196e-06 | 0.037689 | 0.037689 | 0.037689 | 0.9714 | -0.55354 | 0.97152 | -0.5513 | 10.3542
70 | 0.0079703 | 0.0019978 | -0.0079687 | -0.0019971 | 1.6472e-06 | 6.8989e-07 | 0.012212 | 0.012213 | 0.012213 | 0.97114 | -0.55873 | 0.97092 | -0.56307 | 3.3551
71 | 0.0096798 | 0.0024262 | -0.0096785 | -0.0024255 | 1.2821e-06 | 6.2827e-07 | 0.014832 | 0.014832 | 0.014832 | 0.97114 | -0.55873 | 0.971 | -0.56151 | 4.0747
72 | -0.026945 | -0.0067561 | 0.026951 | 0.0067599 | 6.0879e-06 | 3.7782e-06 | 0.041272 | 0.041272 | 0.041272 | 0.97152 | -0.5513 | 0.97176 | -0.54656 | 11.3384
73 | 0.0028386 | 0.0007114 | -0.0028386 | -0.00071142 | 2.0267e-08 | -2.2344e-08 | 0.0043504 | 0.0043504 | 0.0043504 | 0.97092 | -0.56307 | 0.97091 | -0.56322 | 1.1952
74 | 0.0081246 | 0.0020361 | -0.008124 | -0.0020359 | 5.5818e-07 | 2.3847e-07 | 0.012451 | 0.012451 | 0.012451 | 0.971 | -0.56151 | 0.97093 | -0.56295 | 3.4205
75 | -0.028453 | -0.0071362 | 0.028474 | 0.0071494 | 2.1211e-05 | 1.3205e-05 | 0.043571 | 0.043571 | 0.043571 | 0.97176 | -0.54656 | 0.97255 | -0.53094 | 11.9701
76 | 0.0060953 | 0.0015274 | -0.006095 | -0.0015273 | 2.0779e-07 | 5.4454e-08 | 0.0093413 | 0.0093414 | 0.0093414 | 0.97093 | -0.56295 | 0.97089 | -0.56367 | 2.5663
77 | -0.030972 | -0.0077754 | 0.030976 | 0.0077775 | 3.3558e-06 | 2.0982e-06 | 0.047393 | 0.047393 | 0.047393 | 0.97255 | -0.53094 | 0.97266 | -0.52867 | 13.02
78 | 0.002498 | 0.00062599 | -0.002498 | -0.00062605 | 4.1351e-08 | -6.7203e-08 | 0.003822 | 0.003822 | 0.003822 | 0.97255 | -0.53094 | 0.97253 | -0.53128 | 1.05
79 | 0.001558 | 0.00039024 | -0.0015579 | -0.00039045 | 4.0632e-08 | -2.0901e-07 | 0.0023877 | 0.0023878 | 0.0023878 | 0.97089 | -0.56367 | 0.97086 | -0.56421 | 0.65599
80 | -0.03593 | -0.009019 | 0.035961 | 0.0090388 | 3.1351e-05 | 1.9721e-05 | 0.054972 | 0.054971 | 0.054972 | 0.97266 | -0.52867 | 0.97359 | -0.51039 | 15.1021
81 | 0.0078801 | 0.0019746 | -0.00788 | -0.0019745 | 8.649e-08 | 3.4873e-08 | 0.011938 | 0.011938 | 0.011938 | 0.98218 | -0.34343 | 0.98217 | -0.34366 | 3.2798
82 | -0.011783 | -0.0029524 | 0.011784 | 0.0029533 | 1.7464e-06 | 9.3272e-07 | 0.017851 | 0.017851 | 0.017851 | 0.98218 | -0.34343 | 0.98234 | -0.34031 | 4.904
83 | -0.0029651 | -0.00074313 | 0.0029652 | 0.00074306 | 6.9483e-08 | -6.7924e-08 | 0.0045298 | 0.0045298 | 0.0045298 | 0.97402 | -0.50191 | 0.97404 | -0.50142 | 1.2445
84 | 0.039827 | 0.010014 | -0.03981 | -0.010003 | 1.7055e-05 | 1.0762e-05 | 0.060854 | 0.060854 | 0.060854 | 0.97404 | -0.50142 | 0.97359 | -0.51039 | 16.7181
85 | -0.042792 | -0.010757 | 0.042819 | 0.010774 | 2.7358e-05 | 1.7296e-05 | 0.065384 | 0.065384 | 0.065384 | 0.97404 | -0.50142 | 0.97472 | -0.48804 | 17.9626
86 | -0.044747 | -0.011258 | 0.044778 | 0.011277 | 3.1213e-05 | 1.9754e-05 | 0.068326 | 0.068326 | 0.068326 | 0.97472 | -0.48804 | 0.97547 | -0.47345 | 18.771
87 | -0.049382 | -0.012431 | 0.049453 | 0.012476 | 7.0659e-05 | 4.4807e-05 | 0.075349 | 0.075349 | 0.075349 | 0.97547 | -0.47345 | 0.97699 | -0.44356 | 20.7004
88 | -0.052463 | -0.013231 | 0.052493 | 0.013249 | 2.9491e-05 | 1.872e-05 | 0.079935 | 0.079935 | 0.079935 | 0.97699 | -0.44356 | 0.97759 | -0.43182 | 21.9601
89 | -0.055511 | -0.014006 | 0.055532 | 0.014019 | 2.1079e-05 | 1.3392e-05 | 0.084528 | 0.084528 | 0.084528 | 0.97759 | -0.43182 | 0.978 | -0.4239 | 23.2219
90 | 0.1937 | 0.049 | -0.19364 | -0.048964 | 5.7825e-05 | 3.6637e-05 | 0.29189 | 0.29189 | 0.29189 | 0.98798 | -0.23001 | 0.98766 | -0.23624 | 20.0476
91 | 0.19142 | 0.048408 | -0.19129 | -0.048322 | 0.00013543 | 8.5787e-05 | 0.28855 | 0.28855 | 0.28855 | 0.98766 | -0.23624 | 0.9869 | -0.251 | 19.8183
92 | 0.17447 | 0.044107 | -0.17447 | -0.044106 | 2.1542e-06 | 1.3617e-06 | 0.26319 | 0.26319 | 0.26319 | 0.9869 | -0.251 | 0.98688 | -0.25125 | 18.0765
93 | 0.15131 | 0.038302 | -0.15129 | -0.038291 | 1.7084e-05 | 1.0755e-05 | 0.22828 | 0.22828 | 0.22828 | 0.98688 | -0.25125 | 0.98676 | -0.2536 | 15.6783
94 | 0.0050628 | 0.0012685 | -0.0050619 | -0.0012684 | 8.8016e-07 | 5.851e-08 | 0.0076701 | 0.0076703 | 0.0076703 | 0.98217 | -0.34366 | 0.98198 | -0.34731 | 2.1072
95 | -0.017438 | -0.0043703 | 0.017439 | 0.0043707 | 6.5656e-07 | 3.8843e-07 | 0.026415 | 0.026415 | 0.026415 | 0.98234 | -0.34031 | 0.98238 | -0.33952 | 7.2569
96 | 0.0024284 | 0.00060839 | -0.0024284 | -0.00060846 | 4.0813e-08 | -7.556e-08 | 0.0036797 | 0.0036798 | 0.0036798 | 0.98198 | -0.34731 | 0.98196 | -0.34766 | 1.0109
97 | -0.021576 | -0.0054076 | 0.021585 | 0.0054127 | 8.3785e-06 | 5.0973e-06 | 0.032682 | 0.032682 | 0.032682 | 0.98238 | -0.33952 | 0.98279 | -0.33138 | 8.9785
98 | 0.0024284 | 0.00060846 | -0.0024283 | -0.00060859 | 6.8899e-08 | -1.2754e-07 | 0.0036798 | 0.0036798 | 0.0036798 | 0.98196 | -0.34766 | 0.98193 | -0.34826 | 1.0109
99 | -0.070356 | -0.017804 | 0.070382 | 0.01782 | 2.5626e-05 | 1.6325e-05 | 0.10678 | 0.10678 | 0.10678 | 0.98097 | -0.36594 | 0.98136 | -0.35835 | 29.3363
100 | 0.068954 | 0.017453 | -0.068844 | -0.017382 | 0.00011053 | 7.04e-05 | 0.10466 | 0.10466 | 0.10466 | 0.98097 | -0.36594 | 0.97925 | -0.39939 | 28.7521
101 | -0.071967 | -0.018218 | 0.072023 | 0.018254 | 5.6607e-05 | 3.6068e-05 | 0.10919 | 0.10919 | 0.10919 | 0.98136 | -0.35835 | 0.9822 | -0.34198 | 29.9964
102 | 0.059781 | 0.01511 | -0.05975 | -0.015091 | 3.1257e-05 | 1.9877e-05 | 0.090886 | 0.090886 | 0.090886 | 0.97925 | -0.39939 | 0.97869 | -0.4103 | 24.9687
103 | 0.0090629 | 0.0022719 | -0.009062 | -0.0022715 | 9.5099e-07 | 4.4044e-07 | 0.013772 | 0.013772 | 0.013772 | 0.97925 | -0.39939 | 0.97914 | -0.40159 | 3.7835
104 | 0.010501 | 0.0026323 | -0.0105 | -0.002632 | 6.9503e-07 | 3.5215e-07 | 0.015909 | 0.015909 | 0.015909 | 0.9822 | -0.34198 | 0.98213 | -0.34337 | 4.3706
105 | 0.0086623 | 0.0021706 | -0.0086604 | -0.0021698 | 1.8422e-06 | 8.1804e-07 | 0.013123 | 0.013123 | 0.013123 | 0.9822 | -0.34198 | 0.98197 | -0.34644 | 3.6053
106 | -0.091187 | -0.023057 | 0.091254 | 0.023099 | 6.7088e-05 | 4.2462e-05 | 0.13822 | 0.13822 | 0.13822 | 0.9822 | -0.34198 | 0.98299 | -0.32665 | 18.9861
107 | 0.057839 | 0.014612 | -0.057801 | -0.014588 | 3.7675e-05 | 2.3949e-05 | 0.087981 | 0.087981 | 0.087981 | 0.97869 | -0.4103 | 0.978 | -0.4239 | 24.1706
108 | 0.009062 | 0.0022715 | -0.0090604 | -0.0022707 | 1.6333e-06 | 7.5653e-07 | 0.013772 | 0.013772 | 0.013772 | 0.97914 | -0.40159 | 0.97895 | -0.40537 | 3.7835
109 | 0.0090144 | 0.0022595 | -0.0090123 | -0.0022586 | 2.1501e-06 | 9.8722e-07 | 0.013658 | 0.013658 | 0.013658 | 0.98213 | -0.34337 | 0.98187 | -0.34838 | 3.7522
110 | 0.0067261 | 0.001685 | -0.0067244 | -0.0016845 | 1.6323e-06 | 5.1472e-07 | 0.010192 | 0.010192 | 0.010192 | 0.98197 | -0.34644 | 0.98171 | -0.35154 | 2.8
111 | 0.006855 | 0.001718 | -0.006855 | -0.001718 | 6.7319e-08 | 2.2296e-08 | 0.01042 | 0.01042 | 0.01042 | 0.97895 | -0.40537 | 0.97894 | -0.40558 | 2.8626
112 | 0.0045064 | 0.0011293 | -0.0045059 | -0.0011293 | 4.1109e-07 | -3.4157e-08 | 0.0068293 | 0.0068294 | 0.0068294 | 0.98187 | -0.34838 | 0.98178 | -0.35029 | 1.8762
113 | 0.0047028 | 0.0011786 | -0.0047027 | -0.0011786 | 9.7075e-08 | -1.5608e-09 | 0.0071484 | 0.0071484 | 0.0071484 | 0.97894 | -0.40558 | 0.97891 | -0.40601 | 1.9639
114 | -0.0053973 | -0.0013527 | 0.0053974 | 0.0013527 | 1.084e-07 | 1.235e-08 | 0.0080929 | 0.0080929 | 0.0080929 | 0.99239 | -0.14566 | 0.99241 | -0.14524 | 2.2233
115 | -0.010223 | -0.0025621 | 0.010224 | 0.0025625 | 8.3597e-07 | 4.1242e-07 | 0.015328 | 0.015328 | 0.015328 | 0.99241 | -0.14524 | 0.9925 | -0.14353 | 4.2111
116 | 0.0023042 | 0.00057747 | -0.0023042 | -0.00057748 | 3.2098e-09 | -6.7177e-09 | 0.0035025 | 0.0035025 | 0.0035025 | 0.97891 | -0.40601 | 0.97891 | -0.40604 | 0.96223
117 | -0.010224 | -0.0025625 | 0.010226 | 0.0025635 | 1.9609e-06 | 9.6732e-07 | 0.015328 | 0.015328 | 0.015328 | 0.9925 | -0.14353 | 0.99271 | -0.1395 | 4.2111
118 | -0.27066 | -0.068757 | 0.27068 | 0.068768 | 1.6324e-05 | 1.0392e-05 | 0.40576 | 0.40576 | 0.40576 | 0.99338 | -0.12617 | 0.99345 | -0.12492 | 27.868
119 | -0.27312 | -0.06938 | 0.27358 | 0.069675 | 0.00046299 | 0.00029479 | 0.40942 | 0.40942 | 0.40942 | 0.99345 | -0.12492 | 0.99529 | -0.089765 | 28.1195
120 | 0.56039 | 0.14307 | -0.55887 | -0.1421 | 0.001521 | 0.00097221 | 0.8348 | 0.8348 | 0.8348 | 1 | 0 | 0.99704 | -0.056328 | 57.3354
121 | 0.5517 | 0.1403 | -0.55081 | -0.13974 | 0.00088721 | 0.00056709 | 0.8241 | 0.8241 | 0.8241 | 0.99704 | -0.056328 | 0.99529 | -0.089765 | 56.6005
122 | 0.015886 | 0.0039817 | -0.015885 | -0.0039811 | 9.6336e-07 | 5.6045e-07 | 0.02407 | 0.02407 | 0.02407 | 0.98208 | -0.34532 | 0.98202 | -0.3466 | 6.6126
123 | 0.012512 | 0.0031358 | -0.012512 | -0.0031358 | 1.0403e-08 | 5.6812e-09 | 0.018959 | 0.018959 | 0.018959 | 0.98202 | -0.3466 | 0.98202 | -0.34662 | 5.2086
124 | 0.0091321 | 0.0022887 | -0.009132 | -0.0022886 | 9.0173e-08 | 4.1823e-08 | 0.013838 | 0.013838 | 0.013838 | 0.98202 | -0.34662 | 0.982 | -0.34682 | 3.8015
125 | 0.0061377 | 0.0015382 | -0.0061376 | -0.0015382 | 1.8718e-07 | 4.6792e-08 | 0.0093004 | 0.0093004 | 0.0093004 | 0.982 | -0.34682 | 0.98197 | -0.34746 | 2.5551
126 | 0.0031379 | 0.00078637 | -0.0031378 | -0.00078642 | 5.0094e-08 | -4.2682e-08 | 0.0047549 | 0.004755 | 0.004755 | 0.98197 | -0.34746 | 0.98196 | -0.3478 | 1.3063

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56204 | 0.14307

## res_load
| p_mw | q_mvar
0 | 0.0060481 | 0.0015158
1 | 0.0018624 | 0.00046676
2 | 0.0028909 | 0.00072452
3 | 0.0021034 | 0.00052716
4 | 0.022874 | 0.0057326
5 | 0.0068378 | 0.0017137
6 | 0.036029 | 0.0090298
7 | 0.0090266 | 0.0022623
8 | 0.0090452 | 0.0022669
9 | 0.0031061 | 0.00077846
10 | 0.0054976 | 0.0013778
11 | 0.035323 | 0.0088529
12 | 0.0039022 | 0.00097798
13 | 0.0073759 | 0.0018486
14 | 0.0029959 | 0.00075085
15 | 0.0062985 | 0.0015786
16 | 0.0036321 | 0.0009103
17 | 0.0035047 | 0.00087837
18 | 0.0051563 | 0.0012923
19 | 0.0093269 | 0.0023375
20 | 0.0045483 | 0.0011399
21 | 0.0034655 | 0.00086854
22 | 0.0047782 | 0.0011975
23 | 0.0051389 | 0.0012879
24 | 0.004987 | 0.0012499
25 | 0.0072283 | 0.0018116
26 | 0.0072843 | 0.0018256
27 | 0.0025477 | 0.00063852
28 | 0.0038958 | 0.00097639
29 | 0.0013188 | 0.00033051
30 | 0.0012004 | 0.00030084
31 | 0.012174 | 0.0030511
32 | 0.0017765 | 0.00044523
33 | 0.0074463 | 0.0018662
34 | 0.0039432 | 0.00098825
35 | 0.0024884 | 0.00062365
36 | 0.002139 | 0.00053608
37 | 0.0020736 | 0.00051969
38 | 0.011156 | 0.0027959
39 | 0.0014288 | 0.0003581
40 | 0.0036527 | 0.00091546
41 | 0.0032964 | 0.00082617
42 | 0.002339 | 0.00058621
43 | 0.00513 | 0.0012857
44 | 0.0015539 | 0.00038945
45 | 0.0015016 | 0.00037633
46 | 0.0028386 | 0.00071142
47 | 0.0020288 | 0.00050846
48 | 0.0045371 | 0.0011371
49 | 0.0049539 | 0.0012416
50 | 0.002498 | 0.00062605
51 | 0.0015579 | 0.00039045
52 | 0.0029651 | 0.00074313
53 | 0.0038489 | 0.00096462
54 | 0.0019277 | 0.00048313
55 | 0.0046039 | 0.0011539
56 | 0.0030106 | 0.00075454
57 | 0.0030177 | 0.00075631
58 | 0.0064911 | 0.0016268
59 | 0.002217 | 0.00055563
60 | 0.01682 | 0.0042155
61 | 0.023158 | 0.005804
62 | 0.0093428 | 0.0023415
63 | 0.0028172 | 0.00070606
64 | 0.0056539 | 0.001417
65 | 0.0026335 | 0.00066001
66 | 0.0041372 | 0.0010369
67 | 0.0027525 | 0.00068985
68 | 0.0014019 | 0.00035136
69 | 0.0015847 | 0.00039717
70 | 0.0019108 | 0.00047888
71 | 0.0014859 | 0.00037241
72 | 0.0019344 | 0.0004848
73 | 0.0013388 | 0.00033555
74 | 0.0022695 | 0.00056878
75 | 0.0022053 | 0.00055271
76 | 0.0045059 | 0.0011293
77 | 0.0020957 | 0.00052524
78 | 0.0021522 | 0.00053938
79 | 0.0053973 | 0.0013527
80 | 0.0048256 | 0.0012094
81 | 0.0045059 | 0.0011293
82 | 0.0023985 | 0.00060113
83 | 0.0039045 | 0.00097857
84 | 0.0024447 | 0.0006127
85 | 0.00717 | 0.001797
86 | 0.002369 | 0.00059372
87 | 0.059847 | 0.014999
88 | 0.0029959 | 0.00075085
89 | 0.0024283 | 0.00060859
90 | 0.0033727 | 0.00084527
91 | 0.0033801 | 0.00084714
92 | 0.0029943 | 0.00075044
93 | 0.0029997 | 0.00075179
94 | 0.0031378 | 0.00078642
95 | 0.0090509 | 0.0022684
96 | 0.0023042 | 0.00057748

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1