## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2495-10_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2495-10_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2495-10_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2495-10_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2495-10_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2495-10_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2495-10_0_5_node_104 | 0.4 | n |  | TRUE
7 | bus_LV_2495-10_0_5_node_113 | 0.4 | n |  | TRUE
8 | bus_LV_2495-10_0_5_node_103 | 0.4 | n |  | TRUE
9 | bus_LV_2495-10_0_5_node_75 | 0.4 | n |  | TRUE
10 | bus_LV_2495-10_0_5_node_89 | 0.4 | n |  | TRUE
11 | bus_LV_2495-10_0_5_node_124 | 0.4 | n |  | TRUE
12 | bus_LV_2495-10_0_5_node_101 | 0.4 | n |  | TRUE
13 | bus_LV_2495-10_0_5_node_102 | 0.4 | n |  | TRUE
14 | bus_LV_2495-10_0_5_node_88 | 0.4 | n |  | TRUE
15 | bus_LV_2495-10_0_5_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_2495-10_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2495-10_0_5_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_2495-10_0_5_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_2495-10_0_5_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2495-10_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2495-10_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2495-10_0_5_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_2495-10_0_5_node_122 | 0.4 | n |  | TRUE
24 | bus_LV_2495-10_0_5_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_2495-10_0_5_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2495-10_0_5_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_2495-10_0_5_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_2495-10_0_5_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_2495-10_0_5_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2495-10_0_5_node_128 | 0.4 | n |  | TRUE
31 | bus_LV_2495-10_0_5_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_2495-10_0_5_node_127 | 0.4 | n |  | TRUE
33 | bus_LV_2495-10_0_5_node_86 | 0.4 | n |  | TRUE
34 | bus_LV_2495-10_0_5_node_87 | 0.4 | n |  | TRUE
35 | bus_LV_2495-10_0_5_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_2495-10_0_5_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_2495-10_0_5_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_2495-10_0_5_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_2495-10_0_5_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2495-10_0_5_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2495-10_0_5_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2495-10_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2495-10_0_5_node_79 | 0.4 | n |  | TRUE
44 | bus_LV_2495-10_0_5_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_2495-10_0_5_node_70 | 0.4 | n |  | TRUE
46 | bus_LV_2495-10_0_5_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_2495-10_0_5_node_80 | 0.4 | n |  | TRUE
48 | bus_LV_2495-10_0_5_node_108 | 0.4 | n |  | TRUE
49 | bus_LV_2495-10_0_5_node_77 | 0.4 | n |  | TRUE
50 | bus_LV_2495-10_0_5_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_2495-10_0_5_node_69 | 0.4 | n |  | TRUE
52 | bus_LV_2495-10_0_5_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_2495-10_0_5_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_2495-10_0_5_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2495-10_0_5_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_2495-10_0_5_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_2495-10_0_5_node_114 | 0.4 | n |  | TRUE
58 | bus_LV_2495-10_0_5_node_73 | 0.4 | n |  | TRUE
59 | bus_LV_2495-10_0_5_node_91 | 0.4 | n |  | TRUE
60 | bus_LV_2495-10_0_5_node_96 | 0.4 | n |  | TRUE
61 | bus_LV_2495-10_0_5_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_2495-10_0_5_node_33 | 0.4 | n |  | TRUE
63 | bus_LV_2495-10_0_5_node_34 | 0.4 | n |  | TRUE
64 | bus_LV_2495-10_0_5_node_35 | 0.4 | n |  | TRUE
65 | bus_LV_2495-10_0_5_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_2495-10_0_5_node_68 | 0.4 | n |  | TRUE
67 | bus_LV_2495-10_0_5_node_42 | 0.4 | n |  | TRUE
68 | bus_LV_2495-10_0_5_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_2495-10_0_5_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_2495-10_0_5_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_2495-10_0_5_node_37 | 0.4 | n |  | TRUE
72 | bus_LV_2495-10_0_5_node_38 | 0.4 | n |  | TRUE
73 | bus_LV_2495-10_0_5_node_39 | 0.4 | n |  | TRUE
74 | bus_LV_2495-10_0_5_node_40 | 0.4 | n |  | TRUE
75 | bus_LV_2495-10_0_5_node_41 | 0.4 | n |  | TRUE
76 | bus_LV_2495-10_0_5_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_2495-10_0_5_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_2495-10_0_5_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2495-10_0_5_node_115 | 0.4 | n |  | TRUE
80 | bus_LV_2495-10_0_5_node_95 | 0.4 | n |  | TRUE
81 | bus_LV_2495-10_0_5_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_2495-10_0_5_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_2495-10_0_5_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_2495-10_0_5_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_2495-10_0_5_node_94 | 0.4 | n |  | TRUE
86 | bus_LV_2495-10_0_5_node_50 | 0.4 | n |  | TRUE
87 | bus_LV_2495-10_0_5_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_2495-10_0_5_node_52 | 0.4 | n |  | TRUE
89 | bus_LV_2495-10_0_5_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2495-10_0_5_node_117 | 0.4 | n |  | TRUE
91 | bus_LV_2495-10_0_5_node_53 | 0.4 | n |  | TRUE
92 | bus_LV_2495-10_0_5_node_55 | 0.4 | n |  | TRUE
93 | bus_LV_2495-10_0_5_node_57 | 0.4 | n |  | TRUE
94 | bus_LV_2495-10_0_5_node_97 | 0.4 | n |  | TRUE
95 | bus_LV_2495-10_0_5_node_59 | 0.4 | n |  | TRUE
96 | bus_LV_2495-10_0_5_node_60 | 0.4 | n |  | TRUE
97 | bus_LV_2495-10_0_5_node_110 | 0.4 | n |  | TRUE
98 | bus_LV_2495-10_0_5_node_111 | 0.4 | n |  | TRUE
99 | bus_LV_2495-10_0_5_node_61 | 0.4 | n |  | TRUE
100 | bus_LV_2495-10_0_5_node_62 | 0.4 | n |  | TRUE
101 | bus_LV_2495-10_0_5_node_63 | 0.4 | n |  | TRUE
102 | bus_LV_2495-10_0_5_node_64 | 0.4 | n |  | TRUE
103 | bus_LV_2495-10_0_5_node_65 | 0.4 | n |  | TRUE
104 | bus_LV_2495-10_0_5_node_72 | 0.4 | n |  | TRUE
105 | bus_LV_2495-10_0_5_node_105 | 0.4 | n |  | TRUE
106 | bus_LV_2495-10_0_5_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_2495-10_0_5_node_106 | 0.4 | n |  | TRUE
108 | bus_LV_2495-10_0_5_node_118 | 0.4 | n |  | TRUE
109 | bus_LV_2495-10_0_5_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_2495-10_0_5_node_78 | 0.4 | n |  | TRUE
111 | bus_LV_2495-10_0_5_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_2495-10_0_5_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_2495-10_0_5_node_81 | 0.4 | n |  | TRUE
114 | bus_LV_2495-10_0_5_node_82 | 0.4 | n |  | TRUE
115 | bus_LV_2495-10_0_5_node_84 | 0.4 | n |  | TRUE
116 | bus_LV_2495-10_0_5_node_92 | 0.4 | n |  | TRUE
117 | bus_LV_2495-10_0_5_node_93 | 0.4 | n |  | TRUE
118 | bus_LV_2495-10_0_5_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_2495-10_0_5_node_98 | 0.4 | n |  | TRUE
120 | bus_LV_2495-10_0_5_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_2495-10_0_5_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_2495-10_0_5_node_126 | 0.4 | n |  | TRUE
123 | bus_LV_2495-10_0_5_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_2495-10_0_5_node_112 | 0.4 | n |  | TRUE
125 | bus_LV_2495-10_0_5_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_2495-10_0_5_node_125 | 0.4 | n |  | TRUE
127 | bus_MV_291_1_node_76 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2495-10_0_5_load_0 | 0 | 0.0014402 | 0.00036096 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2495-10_0_5_load_3 | 3 | 0.0024735 | 0.00061992 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2495-10_0_5_load_4 | 4 | 0.0011247 | 0.00028188 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2495-10_0_5_load_5 | 5 | 0.0022836 | 0.00057233 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2495-10_0_5_load_113 | 7 | 0.0026588 | 0.00066635 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2495-10_0_5_load_103 | 8 | 0.0037729 | 0.00094558 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2495-10_0_5_load_75 | 9 | 0.0020748 | 0.00052001 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2495-10_0_5_load_89 | 10 | 0.0019163 | 0.00048026 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2495-10_0_5_load_124 | 11 | 0.0026354 | 0.0006605 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2495-10_0_5_load_102 | 13 | 0.0017349 | 0.00043481 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2495-10_0_5_load_88 | 14 | 0.0038494 | 0.00096475 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2495-10_0_5_load_20 | 15 | 0.0056079 | 0.0014055 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2495-10_0_5_load_6 | 17 | 0.0044049 | 0.001104 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2495-10_0_5_load_7 | 18 | 0.0049486 | 0.0012402 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2495-10_0_5_load_9 | 20 | 0.0021051 | 0.00052758 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2495-10_0_5_load_122 | 23 | 0.018264 | 0.0045775 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2495-10_0_5_load_85 | 24 | 0.0012752 | 0.00031959 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2495-10_0_5_load_11 | 26 | 0.0014971 | 0.00037522 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2495-10_0_5_load_12 | 27 | 0.0013639 | 0.00034184 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2495-10_0_5_load_13 | 28 | 0.0018967 | 0.00047537 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2495-10_0_5_load_15 | 29 | 0.0012161 | 0.00030478 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2495-10_0_5_load_128 | 30 | 0.0076733 | 0.0019231 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2495-10_0_5_load_58 | 31 | 0.001216 | 0.00030475 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2495-10_0_5_load_127 | 32 | 0.0010153 | 0.00025446 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2495-10_0_5_load_86 | 33 | 0.0013076 | 0.00032772 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2495-10_0_5_load_87 | 34 | 0.0019342 | 0.00048475 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2495-10_0_5_load_16 | 35 | 0.0015542 | 0.00038951 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2495-10_0_5_load_17 | 36 | 0.0024668 | 0.00061825 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2495-10_0_5_load_18 | 37 | 0.002782 | 0.00069723 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2495-10_0_5_load_19 | 38 | 0.0022499 | 0.00056387 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2495-10_0_5_load_21 | 39 | 0.0024157 | 0.00060544 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2495-10_0_5_load_22 | 40 | 0.002274 | 0.00056991 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2495-10_0_5_load_26 | 41 | 0.001217 | 0.00030501 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2495-10_0_5_load_79 | 43 | 0.0056765 | 0.0014227 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2495-10_0_5_load_76 | 44 | 0.0023279 | 0.00058343 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2495-10_0_5_load_70 | 45 | 0.00091427 | 0.00022914 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2495-10_0_5_load_90 | 46 | 0.0038525 | 0.00096554 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2495-10_0_5_load_80 | 47 | 0.0015206 | 0.00038111 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2495-10_0_5_load_108 | 48 | 0.002159 | 0.0005411 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2495-10_0_5_load_77 | 49 | 0.0014596 | 0.00036582 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2495-10_0_5_load_83 | 50 | 0.00086698 | 0.00021729 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2495-10_0_5_load_69 | 51 | 0.00091458 | 0.00022922 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2495-10_0_5_load_27 | 52 | 0.0032953 | 0.00082589 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2495-10_0_5_load_28 | 53 | 0.0024149 | 0.00060522 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2495-10_0_5_load_29 | 54 | 0.0024541 | 0.00061505 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2495-10_0_5_load_30 | 55 | 0.0026928 | 0.00067488 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2495-10_0_5_load_31 | 56 | 0.0020375 | 0.00051063 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2495-10_0_5_load_114 | 57 | 0.0056672 | 0.0014203 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2495-10_0_5_load_73 | 58 | 0.0043811 | 0.001098 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2495-10_0_5_load_32 | 61 | 0.0028859 | 0.00072327 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2495-10_0_5_load_33 | 62 | 0.0024945 | 0.00062518 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2495-10_0_5_load_34 | 63 | 0.0016524 | 0.00041414 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2495-10_0_5_load_35 | 64 | 0.008346 | 0.0020917 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2495-10_0_5_load_36 | 65 | 0.0058849 | 0.0014749 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2495-10_0_5_load_68 | 66 | 0.0018885 | 0.00047331 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2495-10_0_5_load_67 | 68 | 0.0025761 | 0.00064564 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2495-10_0_5_load_43 | 69 | 0.0044675 | 0.0011197 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2495-10_0_5_load_44 | 70 | 0.0029551 | 0.00074061 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2495-10_0_5_load_37 | 71 | 0.0055718 | 0.0013964 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2495-10_0_5_load_38 | 72 | 0.0075255 | 0.0018861 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2495-10_0_5_load_39 | 73 | 0.0077328 | 0.001938 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2495-10_0_5_load_40 | 74 | 0.0077347 | 0.0019385 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2495-10_0_5_load_66 | 76 | 0.0079103 | 0.0019825 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2495-10_0_5_load_56 | 77 | 0.0022942 | 0.00057497 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2495-10_0_5_load_54 | 78 | 0.0019101 | 0.00047872 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2495-10_0_5_load_115 | 79 | 0.0030746 | 0.00077058 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2495-10_0_5_load_45 | 81 | 0.0023051 | 0.00057772 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2495-10_0_5_load_46 | 82 | 0.0035423 | 0.00088779 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2495-10_0_5_load_47 | 83 | 0.001851 | 0.00046392 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2495-10_0_5_load_48 | 84 | 0.0033786 | 0.00084675 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2495-10_0_5_load_94 | 85 | 0.0026995 | 0.00067656 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2495-10_0_5_load_50 | 86 | 0.0011427 | 0.00028638 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2495-10_0_5_load_51 | 87 | 0.0012188 | 0.00030546 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2495-10_0_5_load_52 | 88 | 0.0015999 | 0.00040096 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2495-10_0_5_load_74 | 89 | 0.0018347 | 0.00045981 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2495-10_0_5_load_117 | 90 | 0.0019696 | 0.00049362 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2495-10_0_5_load_53 | 91 | 0.0023948 | 0.00060018 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2495-10_0_5_load_55 | 92 | 0.011026 | 0.0027635 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2495-10_0_5_load_57 | 93 | 0.0011541 | 0.00028925 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2495-10_0_5_load_97 | 94 | 0.0024436 | 0.00061244 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2495-10_0_5_load_59 | 95 | 0.0017263 | 0.00043264 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2495-10_0_5_load_60 | 96 | 0.0012206 | 0.00030592 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2495-10_0_5_load_110 | 97 | 0.0012054 | 0.00030211 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2495-10_0_5_load_111 | 98 | 0.001738 | 0.00043557 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2495-10_0_5_load_61 | 99 | 0.0012503 | 0.00031336 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2495-10_0_5_load_62 | 100 | 0.0011596 | 0.00029062 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2495-10_0_5_load_63 | 101 | 0.0015459 | 0.00038743 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2495-10_0_5_load_64 | 102 | 0.0037607 | 0.00094253 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2495-10_0_5_load_65 | 103 | 0.0016357 | 0.00040995 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2495-10_0_5_load_105 | 105 | 0.0011679 | 0.00029269 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2495-10_0_5_load_71 | 106 | 0.0012682 | 0.00031784 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2495-10_0_5_load_106 | 107 | 0.0011712 | 0.00029354 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2495-10_0_5_load_118 | 108 | 0.0023882 | 0.00059855 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2495-10_0_5_load_116 | 109 | 0.0032294 | 0.00080936 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2495-10_0_5_load_78 | 110 | 0.0031927 | 0.00080017 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2495-10_0_5_load_109 | 111 | 0.0030668 | 0.00076862 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2495-10_0_5_load_81 | 113 | 0.0033224 | 0.00083267 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2495-10_0_5_load_82 | 114 | 0.0036239 | 0.00090824 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2495-10_0_5_load_84 | 115 | 0.0030588 | 0.00076661 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2495-10_0_5_load_92 | 116 | 0.0036341 | 0.0009108 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2495-10_0_5_load_93 | 117 | 0.0016036 | 0.0004019 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2495-10_0_5_load_100 | 121 | 0.0011204 | 0.0002808 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2495-10_0_5_load_119 | 123 | 0.0017132 | 0.00042936 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2495-10_0_5_load_112 | 124 | 0.0012171 | 0.00030503 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2495-10_0_5_load_121 | 125 | 0.0018959 | 0.00047515 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2495-10_0_5_load_125 | 126 | 0.0019033 | 0.00047702 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2495-10_0_5_line_0 |  | 0 | 1 | 0.017667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2495-10_0_5_line_1 |  | 0 | 2 | 0.026525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2495-10_0_5_line_2 |  | 1 | 3 | 0.036483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2495-10_0_5_line_3 |  | 2 | 4 | 0.0083704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2495-10_0_5_line_4 |  | 2 | 5 | 0.018565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2495-10_0_5_line_5 |  | 4 | 9 | 0.017594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2495-10_0_5_line_6 |  | 5 | 10 | 0.017211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2495-10_0_5_line_7 |  | 5 | 11 | 0.046389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2495-10_0_5_line_8 |  | 6 | 7 | 0.03957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2495-10_0_5_line_9 |  | 6 | 8 | 0.022297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2495-10_0_5_line_10 |  | 8 | 69 | 0.0018698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2495-10_0_5_line_11 |  | 9 | 15 | 0.020602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2495-10_0_5_line_12 |  | 10 | 16 | 0.036555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2495-10_0_5_line_13 |  | 12 | 13 | 0.039923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2495-10_0_5_line_14 |  | 12 | 14 | 0.02706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2495-10_0_5_line_15 |  | 13 | 123 | 0.0074861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2495-10_0_5_line_16 |  | 14 | 34 | 0.010451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2495-10_0_5_line_17 |  | 15 | 37 | 0.0069577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2495-10_0_5_line_18 |  | 16 | 33 | 0.023595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2495-10_0_5_line_19 |  | 16 | 27 | 0.020251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2495-10_0_5_line_20 |  | 17 | 18 | 0.024633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2495-10_0_5_line_21 |  | 17 | 19 | 0.0089568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2495-10_0_5_line_22 |  | 18 | 20 | 0.021298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2495-10_0_5_line_23 |  | 19 | 21 | 0.008009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2495-10_0_5_line_24 |  | 20 | 22 | 0.014767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2495-10_0_5_line_25 |  | 21 | 23 | 0.028909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2495-10_0_5_line_26 |  | 22 | 24 | 0.012617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2495-10_0_5_line_27 |  | 22 | 25 | 0.02365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2495-10_0_5_line_28 |  | 24 | 50 | 0.0102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2495-10_0_5_line_29 |  | 25 | 41 | 0.014092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2495-10_0_5_line_30 |  | 25 | 39 | 0.016898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2495-10_0_5_line_31 |  | 26 | 27 | 0.027487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2495-10_0_5_line_32 |  | 26 | 28 | 0.0015702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2495-10_0_5_line_33 |  | 28 | 29 | 0.0039654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2495-10_0_5_line_34 |  | 30 | 31 | 0.086807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2495-10_0_5_line_35 |  | 30 | 32 | 0.010072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2495-10_0_5_line_36 |  | 31 | 95 | 0.0075033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2495-10_0_5_line_37 |  | 32 | 122 | 0.027694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2495-10_0_5_line_38 |  | 33 | 34 | 0.014851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2495-10_0_5_line_39 |  | 35 | 36 | 0.011602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2495-10_0_5_line_40 |  | 35 | 37 | 0.011429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2495-10_0_5_line_41 |  | 36 | 38 | 0.013787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2495-10_0_5_line_42 |  | 39 | 40 | 0.0024412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2495-10_0_5_line_43 |  | 41 | 45 | 0.013794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2495-10_0_5_line_44 |  | 42 | 43 | 0.020648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2495-10_0_5_line_45 |  | 42 | 44 | 0.016152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2495-10_0_5_line_46 |  | 43 | 46 | 0.028179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2495-10_0_5_line_47 |  | 44 | 49 | 0.016841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2495-10_0_5_line_48 |  | 45 | 51 | 0.0072831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2495-10_0_5_line_49 |  | 46 | 59 | 0.0068461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2495-10_0_5_line_50 |  | 47 | 48 | 0.019465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2495-10_0_5_line_51 |  | 48 | 75 | 0.0045057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2495-10_0_5_line_52 |  | 49 | 110 | 0.0017114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2495-10_0_5_line_53 |  | 50 | 113 | 0.017098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2495-10_0_5_line_54 |  | 51 | 106 | 0.014186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2495-10_0_5_line_55 |  | 52 | 53 | 0.011756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2495-10_0_5_line_56 |  | 52 | 54 | 0.0058747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2495-10_0_5_line_57 |  | 53 | 55 | 0.0086813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2495-10_0_5_line_58 |  | 54 | 56 | 0.0036274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2495-10_0_5_line_59 |  | 55 | 57 | 0.0070579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2495-10_0_5_line_60 |  | 56 | 58 | 0.0086522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2495-10_0_5_line_61 |  | 57 | 59 | 0.028244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2495-10_0_5_line_62 |  | 58 | 60 | 0.014134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2495-10_0_5_line_63 |  | 59 | 90 | 0.013561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2495-10_0_5_line_64 |  | 60 | 108 | 0.017993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2495-10_0_5_line_65 |  | 60 | 109 | 0.026228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2495-10_0_5_line_66 |  | 61 | 62 | 0.010107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2495-10_0_5_line_67 |  | 61 | 63 | 0.0032911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2495-10_0_5_line_68 |  | 62 | 64 | 0.0025487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2495-10_0_5_line_69 |  | 63 | 65 | 0.015193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2495-10_0_5_line_70 |  | 64 | 66 | 0.015865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2495-10_0_5_line_71 |  | 65 | 67 | 0.02589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2495-10_0_5_line_72 |  | 66 | 68 | 0.0094013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2495-10_0_5_line_73 |  | 67 | 69 | 0.010033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2495-10_0_5_line_74 |  | 67 | 70 | 0.014171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_2495-10_0_5_line_75 |  | 68 | 76 | 0.0024478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2495-10_0_5_line_76 |  | 70 | 79 | 0.020285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2495-10_0_5_line_77 |  | 71 | 72 | 0.0026099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2495-10_0_5_line_78 |  | 71 | 73 | 0.01448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2495-10_0_5_line_79 |  | 72 | 74 | 0.017899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2495-10_0_5_line_80 |  | 73 | 75 | 0.023571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2495-10_0_5_line_81 |  | 74 | 76 | 0.016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2495-10_0_5_line_82 |  | 75 | 77 | 0.012103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2495-10_0_5_line_83 |  | 77 | 78 | 0.0021838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2495-10_0_5_line_84 |  | 78 | 91 | 0.019644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2495-10_0_5_line_85 |  | 79 | 80 | 0.0050614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_2495-10_0_5_line_86 |  | 80 | 109 | 0.011649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2495-10_0_5_line_87 |  | 80 | 85 | 0.01455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2495-10_0_5_line_88 |  | 81 | 82 | 0.025766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2495-10_0_5_line_89 |  | 81 | 83 | 0.0014506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2495-10_0_5_line_90 |  | 82 | 84 | 0.0014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2495-10_0_5_line_91 |  | 84 | 85 | 0.026509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2495-10_0_5_line_92 |  | 86 | 87 | 0.0013027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2495-10_0_5_line_93 |  | 87 | 88 | 0.027041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2495-10_0_5_line_94 |  | 88 | 89 | 0.016928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2495-10_0_5_line_95 |  | 89 | 90 | 0.0019114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2495-10_0_5_line_96 |  | 91 | 92 | 0.010988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2495-10_0_5_line_97 |  | 92 | 93 | 0.0031831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2495-10_0_5_line_98 |  | 93 | 94 | 0.001532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2495-10_0_5_line_99 |  | 95 | 96 | 0.010444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2495-10_0_5_line_100 |  | 96 | 97 | 0.0055425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2495-10_0_5_line_101 |  | 97 | 98 | 0.0018473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2495-10_0_5_line_102 |  | 98 | 124 | 0.0056391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2495-10_0_5_line_103 |  | 99 | 100 | 0.025961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2495-10_0_5_line_104 |  | 99 | 101 | 0.0018118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2495-10_0_5_line_105 |  | 100 | 102 | 0.012358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2495-10_0_5_line_106 |  | 101 | 103 | 0.011004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2495-10_0_5_line_107 |  | 103 | 104 | 0.017221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2495-10_0_5_line_108 |  | 104 | 105 | 0.011338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_2495-10_0_5_line_109 |  | 104 | 106 | 0.013153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2495-10_0_5_line_110 |  | 105 | 107 | 0.0077425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2495-10_0_5_line_111 |  | 107 | 112 | 0.016025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2495-10_0_5_line_112 |  | 108 | 120 | 0.0016442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2495-10_0_5_line_113 |  | 110 | 111 | 0.017546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2495-10_0_5_line_114 |  | 111 | 112 | 0.015496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2495-10_0_5_line_115 |  | 113 | 114 | 0.021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2495-10_0_5_line_116 |  | 114 | 115 | 0.019152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2495-10_0_5_line_117 |  | 115 | 116 | 0.021959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2495-10_0_5_line_118 |  | 116 | 117 | 0.022787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2495-10_0_5_line_119 |  | 117 | 118 | 0.012349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2495-10_0_5_line_120 |  | 118 | 119 | 0.030219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2495-10_0_5_line_121 |  | 119 | 121 | 0.023191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2495-10_0_5_line_122 |  | 120 | 125 | 0.015023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2495-10_0_5_line_123 |  | 121 | 122 | 0.017944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_2495-10_0_5_line_124 |  | 123 | 124 | 0.0018531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2495-10_0_5_line_125 |  | 125 | 126 | 0.0074989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2495-10_0_5_trafo_40 | 0.63 MVA 20/0.4 kV | 127 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2641904.0107 | 1246580.276 | 2641905.7984 | 1246571.0047 | 2641907.4999 | 1246562.9579
1 | 2641909.9013 | 1246536.5998 | 2641910.1022 | 1246538.1022 | 2641908.1037 | 1246560.1026 | 2641907.4999 | 1246562.9579
2 | 2641904.0107 | 1246580.276 | 2641871.5989 | 1246563.5283
3 | 2641909.9013 | 1246536.5998 | 2641912.1001 | 1246536.5041 | 2641915.4029 | 1246537.3058 | 2641917.9023 | 1246538.502
4 | 2641900.357 | 1246521.1444 | 2641908.6025 | 1246531.1982 | 2641909.6004 | 1246534.2961 | 2641909.9013 | 1246536.5998
5 | 2641930.4558 | 1246550.8073 | 2641921.101 | 1246541.2041 | 2641917.9023 | 1246538.502
6 | 2641900.357 | 1246521.1444 | 2641889.4397 | 1246507.8397
7 | 2641900.357 | 1246521.1444 | 2641918.2146 | 1246507.139 | 2641936.2164 | 1246491.7331
8 | 2641864.5728 | 1246658.5161 | 2641894.9913 | 1246674.4635 | 2641899.5937 | 1246676.9361
9 | 2641864.5728 | 1246658.5161 | 2641852.4008 | 1246677.1981 | 2641852.4008 | 1246677.1981
10 | 2641851.5555 | 1246678.866 | 2641852.4008 | 1246677.1981
11 | 2641930.4558 | 1246550.8073 | 2641944.8314 | 1246565.5647
12 | 2641867.5043 | 1246478.6067 | 2641878.4034 | 1246493.7047 | 2641888.0972 | 1246506.2036 | 2641889.4397 | 1246507.8397
13 | 2641828.6902 | 1246543.3425 | 2641799.0012 | 1246528.8016 | 2641792.6913 | 1246526.1
14 | 2641828.6902 | 1246543.3425 | 2641833.1034 | 1246534.5011 | 2641841.4394 | 1246519.4808
15 | 2641785.8094 | 1246523.1536 | 2641792.6913 | 1246526.1
16 | 2641841.4394 | 1246519.4808 | 2641846.5106 | 1246510.3431
17 | 2641949.6863 | 1246570.5485 | 2641944.8314 | 1246565.5647
18 | 2641867.5043 | 1246478.6067 | 2641863.9041 | 1246481.4054 | 2641861.4013 | 1246483.9005 | 2641859.7974 | 1246486.402 | 2641853.7172 | 1246497.3576
19 | 2641867.5043 | 1246478.6067 | 2641856.4185 | 1246461.6598
20 | 2641571.9234 | 1246749.0589 | 2641590.0991 | 1246750.6031 | 2641596.4833 | 1246750.919
21 | 2641562.9987 | 1246748.3006 | 2641571.9234 | 1246749.0589
22 | 2641617.755 | 1246751.9718 | 2641596.4833 | 1246750.919
23 | 2641562.9987 | 1246748.3006 | 2641554.9971 | 1246747.5997
24 | 2641632.5039 | 1246752.7017 | 2641617.755 | 1246751.9718
25 | 2641554.9971 | 1246747.5997 | 2641547.1012 | 1246746.8995 | 2641526.2596 | 1246744.4746
26 | 2641632.5039 | 1246752.7017 | 2641632.2366 | 1246740.0878
27 | 2641656.1986 | 1246753.802 | 2641642.5992 | 1246753.2062 | 2641632.5039 | 1246752.7017
28 | 2641632.2366 | 1246740.0878 | 2641632.0204 | 1246729.8902
29 | 2641656.1986 | 1246753.802 | 2641655.9958 | 1246767.8924
30 | 2641656.1986 | 1246753.802 | 2641673.093 | 1246754.1574
31 | 2641841.1446 | 1246438.8082 | 2641850.0994 | 1246451.9998 | 2641856.4185 | 1246461.6598
32 | 2641841.1446 | 1246438.8082 | 2641840.2628 | 1246437.5091
33 | 2641838.0356 | 1246434.2282 | 2641840.2628 | 1246437.5091
34 | 2641706.4369 | 1246582.8307 | 2641755.2926 | 1246511.0769
35 | 2641706.4369 | 1246582.8307 | 2641696.8805 | 1246579.6501
36 | 2641755.2926 | 1246511.0769 | 2641762.3274 | 1246513.6868
37 | 2641670.6035 | 1246570.9045 | 2641696.8805 | 1246579.6501
38 | 2641853.7172 | 1246497.3576 | 2641846.5106 | 1246510.3431
39 | 2641957.7196 | 1246578.6784 | 2641965.8906 | 1246586.9154
40 | 2641949.6863 | 1246570.5485 | 2641951.3977 | 1246572.3054 | 2641957.7196 | 1246578.6784
41 | 2641975.6004 | 1246596.7037 | 2641965.8906 | 1246586.9154
42 | 2641675.5337 | 1246754.2087 | 2641673.093 | 1246754.1574
43 | 2641655.9958 | 1246767.8924 | 2641655.7972 | 1246781.6849
44 | 2641694.2995 | 1246754.6034 | 2641714.922 | 1246755.6392
45 | 2641694.2995 | 1246754.6034 | 2641693.2516 | 1246770.7209
46 | 2641714.922 | 1246755.6392 | 2641743.0652 | 1246757.0527
47 | 2641693.2516 | 1246770.7209 | 2641692.159 | 1246787.526
48 | 2641655.6924 | 1246788.9672 | 2641655.7972 | 1246781.6849
49 | 2641749.9027 | 1246757.3961 | 2641748.0981 | 1246757.3055 | 2641743.0652 | 1246757.0527
50 | 2641691.1337 | 1246709.8666 | 2641688.7839 | 1246690.5438
51 | 2641688.24 | 1246686.0711 | 2641688.7839 | 1246690.5438
52 | 2641692.159 | 1246787.526 | 2641692.048 | 1246789.2337
53 | 2641631.6581 | 1246712.7963 | 2641632.0204 | 1246729.8902
54 | 2641655.6924 | 1246788.9672 | 2641655.4882 | 1246803.152
55 | 2641805.4984 | 1246761.3562 | 2641793.7844 | 1246760.3629
56 | 2641811.3521 | 1246761.8526 | 2641805.4984 | 1246761.3562
57 | 2641785.131 | 1246759.671 | 2641787.1992 | 1246759.8045 | 2641793.7844 | 1246760.3629
58 | 2641811.3521 | 1246761.8526 | 2641814.9665 | 1246762.1591
59 | 2641785.131 | 1246759.671 | 2641778.0878 | 1246759.2162
60 | 2641814.9665 | 1246762.1591 | 2641817.8021 | 1246762.3995 | 2641823.5665 | 1246763.0974
61 | 2641749.9027 | 1246757.3961 | 2641778.0878 | 1246759.2162
62 | 2641837.5976 | 1246764.7962 | 2641823.5665 | 1246763.0974
63 | 2641749.9027 | 1246757.3961 | 2641748.8618 | 1246770.9172
64 | 2641837.5976 | 1246764.7962 | 2641855.5565 | 1246765.9009
65 | 2641837.5976 | 1246764.7962 | 2641838.197 | 1246761.198 | 2641840.8721 | 1246738.7767
66 | 2641803.5284 | 1246686.1612 | 2641793.4222 | 1246686.0113
67 | 2641806.8191 | 1246686.21 | 2641803.5284 | 1246686.1612
68 | 2641790.8738 | 1246685.9735 | 2641793.4222 | 1246686.0113
69 | 2641806.8191 | 1246686.21 | 2641822.0102 | 1246686.4353
70 | 2641775.0123 | 1246686.1581 | 2641786.2015 | 1246685.9042 | 2641790.8738 | 1246685.9735
71 | 2641847.7993 | 1246688.1063 | 2641841.1978 | 1246687.0034 | 2641826.2003 | 1246686.4974 | 2641822.0102 | 1246686.4353
72 | 2641775.0123 | 1246686.1581 | 2641765.6134 | 1246686.3714
73 | 2641847.7993 | 1246688.1063 | 2641848.7009 | 1246684.4991 | 2641851.5555 | 1246678.866
74 | 2641847.7993 | 1246688.1063 | 2641846.9032 | 1246692.0025 | 2641845.4024 | 1246701.2981 | 2641845.3095 | 1246702.0494
75 | 2641763.1662 | 1246686.4269 | 2641765.6134 | 1246686.3714
76 | 2641845.3095 | 1246702.0494 | 2641842.8196 | 1246722.1806
77 | 2641728.7922 | 1246687.2069 | 2641726.1829 | 1246687.2661
78 | 2641711.7065 | 1246687.5946 | 2641726.1829 | 1246687.2661
79 | 2641728.7922 | 1246687.2069 | 2641746.6865 | 1246686.8008
80 | 2641688.24 | 1246686.0711 | 2641702.7984 | 1246687.7967 | 2641711.7065 | 1246687.5946
81 | 2641763.1662 | 1246686.4269 | 2641746.6865 | 1246686.8008
82 | 2641688.24 | 1246686.0711 | 2641685.5164 | 1246674.2788
83 | 2641685.025 | 1246672.151 | 2641685.5164 | 1246674.2788
84 | 2641680.0794 | 1246653.1401 | 2641684.7214 | 1246670.8363 | 2641685.025 | 1246672.151
85 | 2641842.1983 | 1246727.2037 | 2641842.8196 | 1246722.1806
86 | 2641842.1983 | 1246727.2037 | 2641842.0023 | 1246729.3037 | 2641840.8721 | 1246738.7767
87 | 2641842.1983 | 1246727.2037 | 2641846.9041 | 1246727.2036 | 2641853.4014 | 1246727.0048 | 2641856.7278 | 1246726.6664
88 | 2641884.5899 | 1246723.8141 | 2641910.2199 | 1246721.1707
89 | 2641911.6628 | 1246721.0219 | 2641910.2199 | 1246721.1707
90 | 2641883.0986 | 1246723.9679 | 2641884.5899 | 1246723.8141
91 | 2641883.0986 | 1246723.9679 | 2641872.1019 | 1246725.1021 | 2641856.7278 | 1246726.6664
92 | 2641745.2404 | 1246817.9603 | 2641745.3404 | 1246816.6614
93 | 2641745.3404 | 1246816.6614 | 2641747.4159 | 1246789.7005
94 | 2641747.4159 | 1246789.7005 | 2641748.7151 | 1246772.8229
95 | 2641748.8618 | 1246770.9172 | 2641748.7151 | 1246772.8229
96 | 2641680.0794 | 1246653.1401 | 2641677.6445 | 1246643.8577 | 2641677.1311 | 1246642.5642
97 | 2641675.9567 | 1246639.6057 | 2641677.1311 | 1246642.5642
98 | 2641675.3914 | 1246638.1817 | 2641675.9567 | 1246639.6057
99 | 2641762.3274 | 1246513.6868 | 2641772.1192 | 1246517.3196
100 | 2641777.2237 | 1246519.4777 | 2641772.5978 | 1246517.4971 | 2641772.1192 | 1246517.3196
101 | 2641778.9219 | 1246520.2048 | 2641777.2237 | 1246519.4777
102 | 2641778.9219 | 1246520.2048 | 2641784.1059 | 1246522.4242
103 | 2641625.7459 | 1246810.9367 | 2641611.8023 | 1246808.4045 | 2641600.2628 | 1246805.9928
104 | 2641627.5285 | 1246811.2605 | 2641625.7459 | 1246810.9367
105 | 2641600.2628 | 1246805.9928 | 2641588.1666 | 1246803.4647
106 | 2641627.5285 | 1246811.2605 | 2641638.3555 | 1246813.2267
107 | 2641655.2989 | 1246816.3037 | 2641638.3555 | 1246813.2267
108 | 2641655.2989 | 1246816.3037 | 2641659.9008 | 1246817.1032 | 2641666.4733 | 1246818.221
109 | 2641655.2989 | 1246816.3037 | 2641655.4882 | 1246803.152
110 | 2641666.4733 | 1246818.221 | 2641674.1062 | 1246819.5192
111 | 2641689.9042 | 1246822.2061 | 2641674.1062 | 1246819.5192
112 | 2641857.1975 | 1246766.0018 | 2641855.5565 | 1246765.9009
113 | 2641690.9096 | 1246806.7427 | 2641692.048 | 1246789.2337
114 | 2641689.9042 | 1246822.2061 | 2641690.9096 | 1246806.7427
115 | 2641631.6581 | 1246712.7963 | 2641631.2092 | 1246691.6132
116 | 2641629.477 | 1246672.586 | 2641631.0059 | 1246682.0223 | 2641631.2092 | 1246691.6132
117 | 2641629.477 | 1246672.586 | 2641625.965 | 1246650.9093
118 | 2641625.965 | 1246650.9093 | 2641622.9986 | 1246632.6001 | 2641622.012 | 1246628.4776
119 | 2641618.1317 | 1246616.7889 | 2641620.7971 | 1246623.4008 | 2641622.012 | 1246628.4776
120 | 2641618.1317 | 1246616.7889 | 2641626.8683 | 1246613.9594 | 2641634.0099 | 1246610.2403 | 2641639.5577 | 1246606.5101 | 2641643.9484 | 1246601.9046
121 | 2641643.9484 | 1246601.9046 | 2641660.2438 | 1246585.4041
122 | 2641857.1975 | 1246766.0018 | 2641872.1894 | 1246766.9627
123 | 2641670.6035 | 1246570.9045 | 2641666.5028 | 1246578.3028 | 2641664.0021 | 1246581.5985 | 2641660.2438 | 1246585.4041
124 | 2641785.8094 | 1246523.1536 | 2641784.1059 | 1246522.4242
125 | 2641872.1894 | 1246766.9627 | 2641879.6729 | 1246767.4424

## bus_geodata
| x | y | coords
0 | 2641907.4999 | 1246562.9579
1 | 2641904.0107 | 1246580.276
2 | 2641909.9013 | 1246536.5998
3 | 2641871.5989 | 1246563.5283
4 | 2641917.9023 | 1246538.502
5 | 2641900.357 | 1246521.1444
6 | 2641864.5728 | 1246658.5161
7 | 2641899.5937 | 1246676.9361
8 | 2641852.4008 | 1246677.1981
9 | 2641930.4558 | 1246550.8073
10 | 2641889.4397 | 1246507.8397
11 | 2641936.2164 | 1246491.7331
12 | 2641828.6902 | 1246543.3425
13 | 2641792.6913 | 1246526.1
14 | 2641841.4394 | 1246519.4808
15 | 2641944.8314 | 1246565.5647
16 | 2641867.5043 | 1246478.6067
17 | 2641571.9234 | 1246749.0589
18 | 2641596.4833 | 1246750.919
19 | 2641562.9987 | 1246748.3006
20 | 2641617.755 | 1246751.9718
21 | 2641554.9971 | 1246747.5997
22 | 2641632.5039 | 1246752.7017
23 | 2641526.2596 | 1246744.4746
24 | 2641632.2366 | 1246740.0878
25 | 2641656.1986 | 1246753.802
26 | 2641841.1446 | 1246438.8082
27 | 2641856.4185 | 1246461.6598
28 | 2641840.2628 | 1246437.5091
29 | 2641838.0356 | 1246434.2282
30 | 2641706.4369 | 1246582.8307
31 | 2641755.2926 | 1246511.0769
32 | 2641696.8805 | 1246579.6501
33 | 2641853.7172 | 1246497.3576
34 | 2641846.5106 | 1246510.3431
35 | 2641957.7196 | 1246578.6784
36 | 2641965.8905 | 1246586.9154
37 | 2641949.6863 | 1246570.5485
38 | 2641975.6004 | 1246596.7037
39 | 2641673.093 | 1246754.1574
40 | 2641675.5337 | 1246754.2087
41 | 2641655.9958 | 1246767.8924
42 | 2641694.2995 | 1246754.6034
43 | 2641714.922 | 1246755.6392
44 | 2641693.2516 | 1246770.7209
45 | 2641655.7972 | 1246781.6849
46 | 2641743.0652 | 1246757.0527
47 | 2641691.1337 | 1246709.8666
48 | 2641688.7839 | 1246690.5438
49 | 2641692.159 | 1246787.526
50 | 2641632.0204 | 1246729.8902
51 | 2641655.6924 | 1246788.9672
52 | 2641805.4984 | 1246761.3562
53 | 2641793.7844 | 1246760.3629
54 | 2641811.3521 | 1246761.8526
55 | 2641785.131 | 1246759.671
56 | 2641814.9665 | 1246762.1591
57 | 2641778.0878 | 1246759.2162
58 | 2641823.5665 | 1246763.0974
59 | 2641749.9027 | 1246757.3961
60 | 2641837.5976 | 1246764.7962
61 | 2641803.5284 | 1246686.1612
62 | 2641793.4222 | 1246686.0113
63 | 2641806.8191 | 1246686.21
64 | 2641790.8738 | 1246685.9735
65 | 2641822.0102 | 1246686.4353
66 | 2641775.0123 | 1246686.1581
67 | 2641847.7993 | 1246688.1063
68 | 2641765.6134 | 1246686.3714
69 | 2641851.5555 | 1246678.866
70 | 2641845.3095 | 1246702.0494
71 | 2641726.1829 | 1246687.2661
72 | 2641728.7922 | 1246687.2069
73 | 2641711.7065 | 1246687.5946
74 | 2641746.6865 | 1246686.8008
75 | 2641688.24 | 1246686.0711
76 | 2641763.1662 | 1246686.4269
77 | 2641685.5164 | 1246674.2788
78 | 2641685.025 | 1246672.151
79 | 2641842.8196 | 1246722.1806
80 | 2641842.1983 | 1246727.2037
81 | 2641910.2199 | 1246721.1707
82 | 2641884.5899 | 1246723.8141
83 | 2641911.6628 | 1246721.0219
84 | 2641883.0986 | 1246723.9679
85 | 2641856.7278 | 1246726.6664
86 | 2641745.2404 | 1246817.9603
87 | 2641745.3404 | 1246816.6614
88 | 2641747.4159 | 1246789.7005
89 | 2641748.7151 | 1246772.8229
90 | 2641748.8618 | 1246770.9172
91 | 2641680.0794 | 1246653.1401
92 | 2641677.1311 | 1246642.5642
93 | 2641675.9567 | 1246639.6057
94 | 2641675.3914 | 1246638.1817
95 | 2641762.3274 | 1246513.6868
96 | 2641772.1192 | 1246517.3196
97 | 2641777.2237 | 1246519.4777
98 | 2641778.9219 | 1246520.2048
99 | 2641625.7459 | 1246810.9367
100 | 2641600.2628 | 1246805.9928
101 | 2641627.5285 | 1246811.2605
102 | 2641588.1666 | 1246803.4647
103 | 2641638.3555 | 1246813.2267
104 | 2641655.2989 | 1246816.3037
105 | 2641666.4733 | 1246818.221
106 | 2641655.4882 | 1246803.152
107 | 2641674.1062 | 1246819.5192
108 | 2641855.5565 | 1246765.9009
109 | 2641840.8721 | 1246738.7767
110 | 2641692.048 | 1246789.2337
111 | 2641690.9096 | 1246806.7427
112 | 2641689.9042 | 1246822.2061
113 | 2641631.6581 | 1246712.7963
114 | 2641631.2092 | 1246691.6132
115 | 2641629.477 | 1246672.586
116 | 2641625.965 | 1246650.9093
117 | 2641622.012 | 1246628.4776
118 | 2641618.1317 | 1246616.7889
119 | 2641643.9484 | 1246601.9046
120 | 2641857.1975 | 1246766.0018
121 | 2641660.2438 | 1246585.4041
122 | 2641670.6035 | 1246570.9045
123 | 2641785.8094 | 1246523.1536
124 | 2641784.1059 | 1246522.4242
125 | 2641872.1894 | 1246766.9627
126 | 2641879.6729 | 1246767.4424
127 | 2641688.24 | 1246686.0711

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97113 | -0.55836 | 0.0014402 | 0.00036096
1 | 0.97109 | -0.55917 | 0 | 0
2 | 0.97123 | -0.55644 | 0 | 0
3 | 0.971 | -0.56084 | 0.0024735 | 0.00061992
4 | 0.97109 | -0.55921 | 0.0011247 | 0.00028188
5 | 0.9716 | -0.54898 | 0.0022836 | 0.00057233
6 | 0.99433 | -0.10772 | 0 | 0
7 | 0.99423 | -0.10957 | 0.0026588 | 0.00066635
8 | 0.99438 | -0.10667 | 0.0037729 | 0.00094558
9 | 0.97081 | -0.56465 | 0.0020748 | 0.00052001
10 | 0.97203 | -0.5405 | 0.0019163 | 0.00048026
11 | 0.97149 | -0.55123 | 0.0026354 | 0.0006605
12 | 0.97429 | -0.49594 | 0 | 0
13 | 0.97468 | -0.4883 | 0.0017349 | 0.00043481
14 | 0.97403 | -0.50112 | 0.0038494 | 0.00096475
15 | 0.97053 | -0.57024 | 0.0056079 | 0.0014055
16 | 0.97301 | -0.52122 | 0 | 0
17 | 0.97864 | -0.41069 | 0.0044049 | 0.001104
18 | 0.97916 | -0.40053 | 0.0049486 | 0.0012402
19 | 0.97849 | -0.41366 | 0 | 0
20 | 0.97971 | -0.38984 | 0.0021051 | 0.00052758
21 | 0.97836 | -0.41633 | 0 | 0
22 | 0.98011 | -0.38187 | 0 | 0
23 | 0.97787 | -0.42595 | 0.018264 | 0.0045775
24 | 0.97988 | -0.38649 | 0.0012752 | 0.00031959
25 | 0.98072 | -0.37003 | 0 | 0
26 | 0.97278 | -0.52578 | 0.0014971 | 0.00037522
27 | 0.9729 | -0.52345 | 0.0013639 | 0.00034184
28 | 0.97277 | -0.52587 | 0.0018967 | 0.00047537
29 | 0.97277 | -0.52596 | 0.0012161 | 0.00030478
30 | 0.97622 | -0.4581 | 0.0076733 | 0.0019231
31 | 0.97513 | -0.47935 | 0.001216 | 0.00030475
32 | 0.97636 | -0.45529 | 0.0010153 | 0.00025446
33 | 0.97377 | -0.5062 | 0.0013076 | 0.00032772
34 | 0.97394 | -0.50294 | 0.0019342 | 0.00048475
35 | 0.9704 | -0.57273 | 0.0015542 | 0.00038951
36 | 0.97035 | -0.57375 | 0.0024668 | 0.00061825
37 | 0.97047 | -0.57141 | 0.002782 | 0.00069723
38 | 0.97032 | -0.57432 | 0.0022499 | 0.00056387
39 | 0.98065 | -0.37147 | 0.0024157 | 0.00060544
40 | 0.98064 | -0.37157 | 0.002274 | 0.00056991
41 | 0.9811 | -0.36268 | 0.001217 | 0.00030501
42 | 0.98563 | -0.27474 | 0 | 0
43 | 0.9863 | -0.26167 | 0.0056765 | 0.0014227
44 | 0.9851 | -0.28497 | 0.0023279 | 0.00058343
45 | 0.98147 | -0.35542 | 0.00091427 | 0.00022914
46 | 0.98726 | -0.24315 | 0.0038525 | 0.00096554
47 | 0.99816 | -0.035346 | 0.0015206 | 0.00038111
48 | 0.99819 | -0.034828 | 0.002159 | 0.0005411
49 | 0.98455 | -0.29548 | 0.0014596 | 0.00036582
50 | 0.97969 | -0.39017 | 0.00086698 | 0.00021729
51 | 0.98167 | -0.35156 | 0.00091458 | 0.00022922
52 | 0.98961 | -0.19807 | 0.0032953 | 0.00082589
53 | 0.98914 | -0.20693 | 0.0024149 | 0.00060522
54 | 0.98984 | -0.19356 | 0.0024541 | 0.00061505
55 | 0.98881 | -0.21339 | 0.0026928 | 0.00067488
56 | 0.98999 | -0.19074 | 0.0020375 | 0.00051063
57 | 0.98854 | -0.21855 | 0.0056672 | 0.0014203
58 | 0.99034 | -0.18393 | 0.0043811 | 0.001098
59 | 0.9875 | -0.23854 | 0 | 0
60 | 0.99094 | -0.17254 | 0 | 0
61 | 0.99679 | -0.060807 | 0.0028859 | 0.00072327
62 | 0.99733 | -0.050528 | 0.0024945 | 0.00062518
63 | 0.99662 | -0.064115 | 0.0016524 | 0.00041414
64 | 0.99747 | -0.04791 | 0.008346 | 0.0020917
65 | 0.99582 | -0.07929 | 0.0058849 | 0.0014749
66 | 0.99836 | -0.03105 | 0.0018885 | 0.00047331
67 | 0.99449 | -0.10453 | 0 | 0
68 | 0.99889 | -0.020996 | 0.0025761 | 0.00064564
69 | 0.99439 | -0.10646 | 0.0044675 | 0.0011197
70 | 0.9938 | -0.1177 | 0.0029551 | 0.00074061
71 | 0.99917 | -0.01602 | 0.0055718 | 0.0013964
72 | 0.99926 | -0.014279 | 0.0075255 | 0.0018861
73 | 0.99874 | -0.024275 | 0.0077328 | 0.001938
74 | 1 | 0 | -0.30638 | -0.07783
75 | 0.9982 | -0.034538 | 0 | 0
76 | 0.99903 | -0.018352 | 0.0079103 | 0.0019825
77 | 0.99797 | -0.039032 | 0.0022942 | 0.00057497
78 | 0.99793 | -0.039756 | 0.0019101 | 0.00047872
79 | 0.99283 | -0.13631 | 0.0030746 | 0.00077058
80 | 0.99259 | -0.14089 | 0 | 0
81 | 0.99203 | -0.15173 | 0.0023051 | 0.00057772
82 | 0.99213 | -0.14984 | 0.0035423 | 0.00088779
83 | 0.99203 | -0.15178 | 0.001851 | 0.00046392
84 | 0.99214 | -0.14963 | 0.0033786 | 0.00084675
85 | 0.99241 | -0.14443 | 0.0026995 | 0.00067656
86 | 0.98727 | -0.24298 | 0.0011427 | 0.00028638
87 | 0.98728 | -0.24296 | 0.0012188 | 0.00030546
88 | 0.98733 | -0.24182 | 0.0015999 | 0.00040096
89 | 0.9874 | -0.24062 | 0.0018347 | 0.00045981
90 | 0.98741 | -0.24042 | 0.0019696 | 0.00049362
91 | 0.99763 | -0.045609 | 0.0023948 | 0.00060018
92 | 0.99748 | -0.048424 | 0.011026 | 0.0027635
93 | 0.99747 | -0.048624 | 0.0011541 | 0.00028925
94 | 0.99747 | -0.04869 | 0.0024436 | 0.00061244
95 | 0.97504 | -0.48115 | 0.0017263 | 0.00043264
96 | 0.97492 | -0.48357 | 0.0012206 | 0.00030592
97 | 0.97486 | -0.48482 | 0.0012054 | 0.00030211
98 | 0.97484 | -0.48523 | 0.001738 | 0.00043557
99 | 0.98218 | -0.34153 | 0.0012503 | 0.00031336
100 | 0.98207 | -0.34384 | 0.0011596 | 0.00029062
101 | 0.98219 | -0.34133 | 0.0015459 | 0.00038743
102 | 0.98202 | -0.34468 | 0.0037607 | 0.00094253
103 | 0.98227 | -0.3398 | 0.0016357 | 0.00040995
104 | 0.98242 | -0.33689 | 0 | 0
105 | 0.98276 | -0.33029 | 0.0011679 | 0.00029269
106 | 0.98206 | -0.34398 | 0.0012682 | 0.00031784
107 | 0.98299 | -0.32576 | 0.0011712 | 0.00029354
108 | 0.99083 | -0.17452 | 0.0023882 | 0.00059855
109 | 0.99207 | -0.15073 | 0.0032294 | 0.00080936
110 | 0.9845 | -0.29654 | 0.0031927 | 0.00080017
111 | 0.98395 | -0.30713 | 0.0030668 | 0.00076862
112 | 0.98348 | -0.31628 | 0 | 0
113 | 0.97937 | -0.39627 | 0.0033224 | 0.00083267
114 | 0.979 | -0.40351 | 0.0036239 | 0.00090824
115 | 0.97868 | -0.40975 | 0.0030588 | 0.00076661
116 | 0.97833 | -0.4166 | 0.0036341 | 0.0009108
117 | 0.97799 | -0.42334 | 0.0016036 | 0.0004019
118 | 0.97781 | -0.4269 | 0 | 0
119 | 0.97736 | -0.43562 | 0 | 0
120 | 0.99083 | -0.17463 | 0 | 0
121 | 0.97702 | -0.44232 | 0.0011204 | 0.0002808
122 | 0.97676 | -0.44742 | 0 | 0
123 | 0.97476 | -0.48681 | 0.0017132 | 0.00042936
124 | 0.97477 | -0.48643 | 0.0012171 | 0.00030503
125 | 0.99078 | -0.17564 | 0.0018959 | 0.00047515
126 | 0.99076 | -0.1759 | 0.0019033 | 0.00047702
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0024738 | 0.00061944 | -0.0024737 | -0.0006196 | 9.518e-08 | -1.5766e-07 | 0.0037903 | 0.0037904 | 0.0037904 | 0.97113 | -0.55836 | 0.97109 | -0.55917 | 1.0413
1 | -0.0039141 | -0.0009804 | 0.0039144 | 0.0009803 | 3.5774e-07 | -9.9267e-08 | 0.0059971 | 0.005997 | 0.0059971 | 0.97113 | -0.55836 | 0.97123 | -0.55644 | 1.6476
2 | 0.0024737 | 0.0006196 | -0.0024735 | -0.00061992 | 1.9657e-07 | -3.2551e-07 | 0.0037904 | 0.0037905 | 0.0037905 | 0.97109 | -0.55917 | 0.971 | -0.56084 | 1.0414
3 | 0.017872 | 0.0044826 | -0.01787 | -0.0044812 | 2.3537e-06 | 1.4028e-06 | 0.027383 | 0.027383 | 0.027383 | 0.97123 | -0.55644 | 0.97109 | -0.55921 | 7.5228
4 | -0.021787 | -0.0054629 | 0.021794 | 0.0054677 | 7.7571e-06 | 4.7347e-06 | 0.03338 | 0.03338 | 0.03338 | 0.97123 | -0.55644 | 0.9716 | -0.54898 | 9.1704
5 | 0.016745 | 0.0041994 | -0.016741 | -0.0041968 | 4.3441e-06 | 2.5626e-06 | 0.02566 | 0.02566 | 0.02566 | 0.97109 | -0.55921 | 0.97081 | -0.56465 | 7.0494
6 | -0.026714 | -0.0067001 | 0.026724 | 0.0067068 | 1.0804e-05 | 6.701e-06 | 0.040914 | 0.040914 | 0.040914 | 0.9716 | -0.54898 | 0.97203 | -0.5405 | 11.2401
7 | 0.0026357 | 0.00066011 | -0.0026354 | -0.0006605 | 2.8344e-07 | -3.9304e-07 | 0.0040364 | 0.0040366 | 0.0040366 | 0.9716 | -0.54898 | 0.97149 | -0.55123 | 1.109
8 | 0.002659 | 0.00066599 | -0.0026588 | -0.00066635 | 2.3495e-07 | -3.6284e-07 | 0.0039791 | 0.0039792 | 0.0039792 | 0.99433 | -0.10772 | 0.99423 | -0.10957 | 1.0932
9 | -0.002659 | -0.00066599 | 0.0026591 | 0.00066578 | 1.3238e-07 | -2.0451e-07 | 0.0039791 | 0.003979 | 0.0039791 | 0.99433 | -0.10772 | 0.99438 | -0.10667 | 1.0932
10 | -0.006432 | -0.0016114 | 0.0064321 | 0.0016114 | 6.4955e-08 | 1.7315e-08 | 0.0096248 | 0.0096248 | 0.0096248 | 0.99438 | -0.10667 | 0.99439 | -0.10646 | 2.6442
11 | 0.014666 | 0.0036768 | -0.014662 | -0.0036745 | 3.904e-06 | 2.2439e-06 | 0.02248 | 0.02248 | 0.02248 | 0.97081 | -0.56465 | 0.97053 | -0.57024 | 6.1757
12 | -0.028641 | -0.0071871 | 0.028667 | 0.0072035 | 2.6355e-05 | 1.6413e-05 | 0.043847 | 0.043847 | 0.043847 | 0.97203 | -0.5405 | 0.97301 | -0.52122 | 12.046
13 | -0.041777 | -0.010503 | 0.041793 | 0.010511 | 1.5243e-05 | 7.7659e-06 | 0.063818 | 0.063817 | 0.063818 | 0.97429 | -0.49594 | 0.97468 | -0.4883 | 4.3831
14 | 0.041777 | 0.010503 | -0.041767 | -0.010498 | 1.0332e-05 | 5.2649e-06 | 0.063818 | 0.063818 | 0.063818 | 0.97429 | -0.49594 | 0.97403 | -0.50112 | 4.3831
15 | -0.043527 | -0.010946 | 0.043531 | 0.010948 | 3.1004e-06 | 1.611e-06 | 0.066466 | 0.066465 | 0.066466 | 0.97468 | -0.4883 | 0.97476 | -0.48681 | 4.5649
16 | 0.037918 | 0.0095335 | -0.037914 | -0.0095319 | 3.2887e-06 | 1.5845e-06 | 0.057937 | 0.057938 | 0.057938 | 0.97403 | -0.50112 | 0.97394 | -0.50294 | 3.9792
17 | 0.009054 | 0.0022691 | -0.0090535 | -0.0022688 | 5.0278e-07 | 2.3581e-07 | 0.013882 | 0.013882 | 0.013882 | 0.97053 | -0.57024 | 0.97047 | -0.57141 | 3.8136
18 | -0.034642 | -0.0087008 | 0.034667 | 0.0087164 | 2.484e-05 | 1.5605e-05 | 0.052985 | 0.052985 | 0.052985 | 0.97301 | -0.52122 | 0.97377 | -0.5062 | 14.5562
19 | 0.0059751 | 0.0014973 | -0.0059744 | -0.0014971 | 6.3407e-07 | 1.5431e-07 | 0.0091376 | 0.0091377 | 0.0091377 | 0.97301 | -0.52122 | 0.9729 | -0.52345 | 2.5103
20 | -0.022682 | -0.0056894 | 0.022693 | 0.0056961 | 1.0988e-05 | 6.723e-06 | 0.03449 | 0.03449 | 0.03449 | 0.97864 | -0.41069 | 0.97916 | -0.40053 | 9.4753
21 | 0.018278 | 0.0045854 | -0.018275 | -0.0045838 | 2.5944e-06 | 1.5479e-06 | 0.027792 | 0.027793 | 0.027793 | 0.97864 | -0.41069 | 0.97849 | -0.41366 | 7.6353
22 | -0.027642 | -0.0069363 | 0.027656 | 0.0069451 | 1.4095e-05 | 8.753e-06 | 0.04201 | 0.04201 | 0.04201 | 0.97916 | -0.40053 | 0.97971 | -0.38984 | 11.5413
23 | 0.018275 | 0.0045838 | -0.018273 | -0.0045825 | 2.3199e-06 | 1.3841e-06 | 0.027793 | 0.027793 | 0.027793 | 0.97849 | -0.41366 | 0.97836 | -0.41633 | 7.6353
24 | -0.029761 | -0.0074726 | 0.029773 | 0.0074797 | 1.1317e-05 | 7.057e-06 | 0.045207 | 0.045207 | 0.045207 | 0.97971 | -0.38984 | 0.98011 | -0.38187 | 12.4196
25 | 0.018273 | 0.0045825 | -0.018264 | -0.0045775 | 8.3738e-06 | 4.9964e-06 | 0.027793 | 0.027793 | 0.027793 | 0.97836 | -0.41633 | 0.97787 | -0.42595 | 7.6354
26 | 0.081084 | 0.020467 | -0.081066 | -0.020456 | 1.794e-05 | 1.0846e-05 | 0.12315 | 0.12316 | 0.12316 | 0.98011 | -0.38187 | 0.97988 | -0.38649 | 8.4585
27 | -0.11086 | -0.027947 | 0.11092 | 0.027986 | 6.2848e-05 | 3.903e-05 | 0.16836 | 0.16836 | 0.16836 | 0.98011 | -0.38187 | 0.98072 | -0.37003 | 11.5633
28 | 0.079791 | 0.020136 | -0.079777 | -0.020128 | 1.4051e-05 | 8.4788e-06 | 0.12122 | 0.12122 | 0.12122 | 0.97988 | -0.38649 | 0.97969 | -0.39017 | 8.3255
29 | -0.11561 | -0.029161 | 0.11565 | 0.029186 | 4.068e-05 | 2.5324e-05 | 0.17548 | 0.17548 | 0.17548 | 0.98072 | -0.37003 | 0.9811 | -0.36268 | 12.0521
30 | 0.00469 | 0.0011753 | -0.0046897 | -0.0011753 | 3.2089e-07 | -7.8421e-09 | 0.007116 | 0.0071161 | 0.0071161 | 0.98072 | -0.37003 | 0.98065 | -0.37147 | 1.955
31 | -0.00461 | -0.0011553 | 0.0046105 | 0.0011553 | 5.1255e-07 | -1.3254e-08 | 0.0070517 | 0.0070516 | 0.0070517 | 0.97278 | -0.52578 | 0.9729 | -0.52345 | 1.9373
32 | 0.0031129 | 0.00078009 | -0.0031128 | -0.00078011 | 1.335e-08 | -1.0949e-08 | 0.0047616 | 0.0047616 | 0.0047616 | 0.97278 | -0.52578 | 0.97277 | -0.52587 | 1.3081
33 | 0.0012161 | 0.00030474 | -0.0012161 | -0.00030478 | 5.1456e-09 | -4.5935e-08 | 0.0018602 | 0.0018602 | 0.0018602 | 0.97277 | -0.52587 | 0.97277 | -0.52596 | 0.51105
34 | 0.053639 | 0.013503 | -0.053585 | -0.013473 | 5.4432e-05 | 3.05e-05 | 0.081782 | 0.081784 | 0.081784 | 0.97622 | -0.4581 | 0.97513 | -0.47935 | 5.617
35 | -0.061313 | -0.015426 | 0.061321 | 0.015431 | 8.2508e-06 | 4.7768e-06 | 0.093478 | 0.093478 | 0.093478 | 0.97622 | -0.4581 | 0.97636 | -0.45529 | 6.4202
36 | 0.052369 | 0.013168 | -0.052364 | -0.013165 | 4.4939e-06 | 2.5017e-06 | 0.079928 | 0.079928 | 0.079928 | 0.97513 | -0.47935 | 0.97504 | -0.48115 | 5.4896
37 | -0.062336 | -0.015686 | 0.06236 | 0.015699 | 2.3444e-05 | 1.3618e-05 | 0.095026 | 0.095025 | 0.095026 | 0.97636 | -0.45529 | 0.97676 | -0.44742 | 6.5265
38 | -0.035975 | -0.0090441 | 0.03598 | 0.0090471 | 5.6121e-06 | 3.0374e-06 | 0.054983 | 0.054983 | 0.054983 | 0.97377 | -0.5062 | 0.97394 | -0.50294 | 5.035
39 | 0.004717 | 0.001182 | -0.0047168 | -0.001182 | 2.2762e-07 | 2.3474e-09 | 0.007233 | 0.007233 | 0.007233 | 0.9704 | -0.57273 | 0.97035 | -0.57375 | 1.9871
40 | -0.0062711 | -0.0015715 | 0.0062715 | 0.0015716 | 3.9632e-07 | 1.1244e-07 | 0.0096161 | 0.0096161 | 0.0096161 | 0.9704 | -0.57273 | 0.97047 | -0.57141 | 2.6418
41 | 0.0022499 | 0.00056374 | -0.0022499 | -0.00056387 | 6.1546e-08 | -1.3092e-07 | 0.0034501 | 0.0034502 | 0.0034502 | 0.97035 | -0.57375 | 0.97032 | -0.57432 | 0.94786
42 | 0.002274 | 0.00056989 | -0.002274 | -0.00056991 | 1.09e-08 | -2.3824e-08 | 0.0034505 | 0.0034505 | 0.0034505 | 0.98065 | -0.37147 | 0.98064 | -0.37157 | 0.94794
43 | -0.11687 | -0.029491 | 0.11691 | 0.029517 | 4.0662e-05 | 2.5327e-05 | 0.17732 | 0.17732 | 0.17732 | 0.9811 | -0.36268 | 0.98147 | -0.35542 | 12.1788
44 | -0.14226 | -0.036061 | 0.14234 | 0.036117 | 8.9408e-05 | 5.6168e-05 | 0.21491 | 0.21491 | 0.21491 | 0.98563 | -0.27474 | 0.9863 | -0.26167 | 14.7604
45 | 0.14226 | 0.036061 | -0.14219 | -0.036017 | 6.9936e-05 | 4.3936e-05 | 0.21491 | 0.21491 | 0.21491 | 0.98563 | -0.27474 | 0.9851 | -0.28497 | 14.7604
46 | -0.14802 | -0.03754 | 0.14815 | 0.037623 | 0.00013193 | 8.2996e-05 | 0.22347 | 0.22347 | 0.22347 | 0.9863 | -0.26167 | 0.98726 | -0.24315 | 15.3485
47 | 0.13986 | 0.035433 | -0.13979 | -0.035389 | 7.0553e-05 | 4.4297e-05 | 0.21139 | 0.2114 | 0.2114 | 0.9851 | -0.28497 | 0.98455 | -0.29548 | 14.5189
48 | -0.11782 | -0.029746 | 0.11784 | 0.029759 | 2.1806e-05 | 1.3588e-05 | 0.17871 | 0.17871 | 0.17871 | 0.98147 | -0.35542 | 0.98167 | -0.35156 | 12.274
49 | -0.15201 | -0.038588 | 0.15204 | 0.038609 | 3.374e-05 | 2.1244e-05 | 0.22928 | 0.22928 | 0.22928 | 0.98726 | -0.24315 | 0.9875 | -0.23854 | 15.7473
50 | -0.0015206 | -0.00038111 | 0.0015207 | 0.00038088 | 3.751e-08 | -2.3043e-07 | 0.0022669 | 0.0022668 | 0.0022669 | 0.99816 | -0.035346 | 0.99819 | -0.034828 | 0.62278
51 | -0.0036797 | -0.00092198 | 0.0036797 | 0.00092195 | 5.0838e-08 | -2.6362e-08 | 0.0054853 | 0.0054853 | 0.0054853 | 0.99819 | -0.034828 | 0.9982 | -0.034538 | 1.5069
52 | 0.13833 | 0.035023 | -0.13832 | -0.035019 | 7.0209e-06 | 4.4063e-06 | 0.20919 | 0.20919 | 0.20919 | 0.98455 | -0.29548 | 0.9845 | -0.29654 | 14.3674
53 | 0.07891 | 0.019911 | -0.078887 | -0.019897 | 2.3044e-05 | 1.3887e-05 | 0.1199 | 0.1199 | 0.1199 | 0.97969 | -0.39017 | 0.97937 | -0.39627 | 8.2351
54 | -0.11876 | -0.029989 | 0.1188 | 0.030015 | 4.3136e-05 | 2.689e-05 | 0.1801 | 0.1801 | 0.1801 | 0.98167 | -0.35156 | 0.98206 | -0.34398 | 12.3692
55 | 0.1709 | 0.043458 | -0.17083 | -0.043412 | 7.2907e-05 | 4.6056e-05 | 0.2572 | 0.2572 | 0.2572 | 0.98961 | -0.19807 | 0.98914 | -0.20693 | 17.6647
56 | -0.1742 | -0.044284 | 0.17423 | 0.044308 | 3.785e-05 | 2.3922e-05 | 0.26215 | 0.26215 | 0.26215 | 0.98961 | -0.19807 | 0.98984 | -0.19356 | 18.005
57 | 0.16841 | 0.042807 | -0.16836 | -0.042774 | 5.2329e-05 | 3.3045e-05 | 0.25357 | 0.25357 | 0.25357 | 0.98914 | -0.20693 | 0.98881 | -0.21339 | 17.4152
58 | -0.17669 | -0.044923 | 0.17671 | 0.044938 | 2.4033e-05 | 1.5195e-05 | 0.26584 | 0.26584 | 0.26584 | 0.98984 | -0.19356 | 0.98999 | -0.19074 | 18.2584
59 | 0.16567 | 0.042099 | -0.16563 | -0.042073 | 4.1194e-05 | 2.6002e-05 | 0.24951 | 0.24951 | 0.24951 | 0.98881 | -0.21339 | 0.98854 | -0.21855 | 17.1369
60 | -0.17875 | -0.045449 | 0.17881 | 0.045486 | 5.8654e-05 | 3.7093e-05 | 0.2689 | 0.2689 | 0.2689 | 0.98999 | -0.19074 | 0.99034 | -0.18393 | 18.4687
61 | 0.15996 | 0.040652 | -0.15981 | -0.040555 | 0.00015377 | 9.6965e-05 | 0.24098 | 0.24098 | 0.24098 | 0.98854 | -0.21855 | 0.9875 | -0.23854 | 16.5511
62 | -0.18319 | -0.046584 | 0.18329 | 0.046647 | 0.00010056 | 6.3631e-05 | 0.27549 | 0.27549 | 0.27549 | 0.99034 | -0.18393 | 0.99094 | -0.17254 | 18.9208
63 | 0.0077667 | 0.0019462 | -0.007766 | -0.0019459 | 6.9651e-07 | 2.7229e-07 | 0.011703 | 0.011703 | 0.011703 | 0.9875 | -0.23854 | 0.98741 | -0.24042 | 3.2151
64 | 0.0061883 | 0.0015507 | -0.0061877 | -0.0015506 | 5.8262e-07 | 1.4111e-07 | 0.0092924 | 0.0092925 | 0.0092925 | 0.99094 | -0.17254 | 0.99083 | -0.17452 | 2.5529
65 | -0.18948 | -0.048198 | 0.18968 | 0.048324 | 0.00019941 | 0.00012627 | 0.28478 | 0.28478 | 0.28478 | 0.99094 | -0.17254 | 0.99207 | -0.15073 | 19.559
66 | -0.23498 | -0.060041 | 0.2351 | 0.060116 | 0.00011687 | 7.4269e-05 | 0.35119 | 0.35119 | 0.35119 | 0.99679 | -0.060807 | 0.99733 | -0.050528 | 24.1204
67 | 0.2321 | 0.059318 | -0.23206 | -0.059294 | 3.7126e-05 | 2.3589e-05 | 0.34689 | 0.34689 | 0.34689 | 0.99679 | -0.060807 | 0.99662 | -0.064115 | 23.8245
68 | -0.2376 | -0.060741 | 0.23763 | 0.06076 | 3.0098e-05 | 1.913e-05 | 0.35491 | 0.35491 | 0.35491 | 0.99733 | -0.050528 | 0.99747 | -0.04791 | 24.376
69 | 0.23041 | 0.05888 | -0.23024 | -0.058773 | 0.00016896 | 0.00010734 | 0.34442 | 0.34442 | 0.34442 | 0.99662 | -0.064115 | 0.99582 | -0.07929 | 23.6551
70 | -0.24597 | -0.062852 | 0.24617 | 0.062979 | 0.00020073 | 0.00012764 | 0.36737 | 0.36737 | 0.36737 | 0.99747 | -0.04791 | 0.99836 | -0.03105 | 25.2311
71 | 0.22435 | 0.057298 | -0.22408 | -0.057124 | 0.0002734 | 0.00017363 | 0.33563 | 0.33563 | 0.33563 | 0.99582 | -0.07929 | 0.99449 | -0.10453 | 23.0512
72 | -0.24806 | -0.063453 | 0.24818 | 0.063529 | 0.00012078 | 7.6805e-05 | 0.37018 | 0.37018 | 0.37018 | 0.99836 | -0.03105 | 0.99889 | -0.020996 | 25.4244
73 | 0.010901 | 0.0027316 | -0.0109 | -0.002731 | 1.0009e-06 | 5.1039e-07 | 0.01631 | 0.01631 | 0.01631 | 0.99449 | -0.10453 | 0.99439 | -0.10646 | 4.4808
74 | 0.21318 | 0.054393 | -0.21304 | -0.054307 | 0.00013546 | 8.5959e-05 | 0.31932 | 0.31932 | 0.31932 | 0.99449 | -0.10453 | 0.9938 | -0.1177 | 21.931
75 | -0.25076 | -0.064175 | 0.25079 | 0.064195 | 3.2102e-05 | 2.0417e-05 | 0.37402 | 0.37402 | 0.37402 | 0.99889 | -0.020996 | 0.99903 | -0.018352 | 25.688
76 | 0.21009 | 0.053566 | -0.2099 | -0.053447 | 0.00018856 | 0.00011963 | 0.31489 | 0.31489 | 0.31489 | 0.9938 | -0.1177 | 0.99283 | -0.13631 | 21.6272
77 | -0.038245 | -0.009598 | 0.038248 | 0.0096 | 3.1754e-06 | 1.9981e-06 | 0.056961 | 0.056961 | 0.056961 | 0.99917 | -0.01602 | 0.99926 | -0.014279 | 15.6485
78 | 0.032673 | 0.0082015 | -0.03266 | -0.0081935 | 1.2859e-05 | 8.04e-06 | 0.048663 | 0.048663 | 0.048663 | 0.99917 | -0.01602 | 0.99874 | -0.024275 | 13.3689
79 | -0.045773 | -0.011486 | 0.045804 | 0.011506 | 3.1189e-05 | 1.9727e-05 | 0.068167 | 0.068167 | 0.068167 | 0.99926 | -0.014279 | 1 | 0 | 18.7272
80 | 0.024927 | 0.0062555 | -0.024915 | -0.006248 | 1.2194e-05 | 7.4956e-06 | 0.037142 | 0.037142 | 0.037142 | 0.99874 | -0.024275 | 0.9982 | -0.034538 | 10.2038
81 | 0.25893 | 0.066324 | -0.2587 | -0.066178 | 0.00023001 | 0.00014635 | 0.3858 | 0.3858 | 0.3858 | 1 | 0 | 0.99903 | -0.018352 | 26.4972
82 | 0.021235 | 0.005326 | -0.021231 | -0.0053233 | 4.5482e-06 | 2.7527e-06 | 0.031656 | 0.031657 | 0.031657 | 0.9982 | -0.034538 | 0.99797 | -0.039032 | 8.6969
83 | 0.018936 | 0.0047483 | -0.018936 | -0.0047479 | 6.529e-07 | 3.8932e-07 | 0.028236 | 0.028236 | 0.028236 | 0.99797 | -0.039032 | 0.99793 | -0.039756 | 7.7571
84 | 0.017026 | 0.0042692 | -0.017021 | -0.0042664 | 4.748e-06 | 2.7821e-06 | 0.025388 | 0.025388 | 0.025388 | 0.99793 | -0.039756 | 0.99763 | -0.045609 | 6.9747
85 | 0.20683 | 0.052676 | -0.20678 | -0.052647 | 4.5683e-05 | 2.8976e-05 | 0.31028 | 0.31028 | 0.31028 | 0.99283 | -0.13631 | 0.99259 | -0.14089 | 21.3107
86 | 0.193 | 0.049192 | -0.19291 | -0.049134 | 9.1608e-05 | 5.8027e-05 | 0.28962 | 0.28962 | 0.28962 | 0.99259 | -0.14089 | 0.99207 | -0.15073 | 19.8917
87 | 0.013782 | 0.0034554 | -0.01378 | -0.0034541 | 2.3292e-06 | 1.3027e-06 | 0.020662 | 0.020662 | 0.020662 | 0.99259 | -0.14089 | 0.99241 | -0.14443 | 5.6763
88 | -0.0041562 | -0.0010416 | 0.0041566 | 0.0010415 | 3.7551e-07 | -9.2368e-08 | 0.0062342 | 0.0062341 | 0.0062342 | 0.99203 | -0.15173 | 0.99213 | -0.14984 | 1.7127
89 | 0.0018511 | 0.0004639 | -0.001851 | -0.00046392 | 4.1934e-09 | -1.6044e-08 | 0.0027765 | 0.0027765 | 0.0027765 | 0.99203 | -0.15173 | 0.99203 | -0.15178 | 0.76278
90 | -0.0076989 | -0.0019293 | 0.007699 | 0.0019294 | 7.4961e-08 | 2.8614e-08 | 0.011547 | 0.011547 | 0.011547 | 0.99213 | -0.14984 | 0.99214 | -0.14963 | 3.1722
91 | -0.011078 | -0.0027761 | 0.01108 | 0.0027775 | 2.7439e-06 | 1.4137e-06 | 0.016614 | 0.016614 | 0.016614 | 0.99214 | -0.14963 | 0.99241 | -0.14443 | 4.5643
92 | -0.0011427 | -0.00028638 | 0.0011427 | 0.00028636 | 1.4489e-09 | -1.5731e-08 | 0.0017222 | 0.0017222 | 0.0017222 | 0.98727 | -0.24298 | 0.98728 | -0.24296 | 0.47313
93 | -0.0023615 | -0.00059182 | 0.0023616 | 0.00059156 | 1.2845e-07 | -2.636e-07 | 0.0035592 | 0.0035591 | 0.0035592 | 0.98728 | -0.24296 | 0.98733 | -0.24182 | 0.9778
94 | -0.0039615 | -0.00099252 | 0.0039617 | 0.00099245 | 2.2626e-07 | -7.1696e-08 | 0.0059702 | 0.0059702 | 0.0059702 | 0.98733 | -0.24182 | 0.9874 | -0.24062 | 1.6402
95 | -0.0057964 | -0.0014523 | 0.0057964 | 0.0014523 | 5.469e-08 | 1.0553e-08 | 0.008735 | 0.008735 | 0.008735 | 0.9874 | -0.24062 | 0.98741 | -0.24042 | 2.3997
96 | 0.014626 | 0.0036662 | -0.014624 | -0.0036651 | 1.9611e-06 | 1.1116e-06 | 0.021816 | 0.021816 | 0.021816 | 0.99763 | -0.045609 | 0.99748 | -0.048424 | 5.9934
97 | 0.0035978 | 0.00090165 | -0.0035978 | -0.00090167 | 3.4385e-08 | -1.9544e-08 | 0.0053671 | 0.0053671 | 0.0053671 | 0.99748 | -0.048424 | 0.99747 | -0.048624 | 1.4745
98 | 0.0024437 | 0.00061242 | -0.0024436 | -0.00061244 | 7.6348e-09 | -1.5112e-08 | 0.0036454 | 0.0036454 | 0.0036454 | 0.99747 | -0.048624 | 0.99747 | -0.04869 | 1.0015
99 | 0.050638 | 0.012733 | -0.050632 | -0.01273 | 5.8496e-06 | 3.2228e-06 | 0.077294 | 0.077294 | 0.077294 | 0.97504 | -0.48115 | 0.97492 | -0.48357 | 5.3087
100 | 0.049412 | 0.012424 | -0.049409 | -0.012422 | 2.9565e-06 | 1.6157e-06 | 0.075431 | 0.075431 | 0.075431 | 0.97492 | -0.48357 | 0.97486 | -0.48482 | 5.1807
101 | 0.048203 | 0.01212 | -0.048202 | -0.012119 | 9.3792e-07 | 5.0814e-07 | 0.073591 | 0.073591 | 0.073591 | 0.97486 | -0.48482 | 0.97484 | -0.48523 | 5.0543
102 | 0.046464 | 0.011684 | -0.046462 | -0.011682 | 2.6604e-06 | 1.4214e-06 | 0.070938 | 0.070938 | 0.070938 | 0.97484 | -0.48523 | 0.97477 | -0.48643 | 4.8721
103 | 0.004921 | 0.0012331 | -0.0049205 | -0.0012331 | 5.411e-07 | 1.779e-08 | 0.0074553 | 0.0074554 | 0.0074554 | 0.98218 | -0.34153 | 0.98207 | -0.34384 | 2.0482
104 | -0.0061713 | -0.0015465 | 0.0061714 | 0.0015465 | 5.939e-08 | 1.508e-08 | 0.0093495 | 0.0093495 | 0.0093495 | 0.98218 | -0.34153 | 0.98219 | -0.34133 | 2.5685
105 | 0.0037609 | 0.00094247 | -0.0037607 | -0.00094253 | 1.5048e-07 | -6.0046e-08 | 0.0056984 | 0.0056985 | 0.0056985 | 0.98207 | -0.34384 | 0.98202 | -0.34468 | 1.5655
106 | -0.0077172 | -0.0019339 | 0.0077178 | 0.0019341 | 5.6406e-07 | 2.2171e-07 | 0.011691 | 0.011691 | 0.011691 | 0.98219 | -0.34133 | 0.98227 | -0.3398 | 3.2119
107 | -0.0093535 | -0.0023441 | 0.0093548 | 0.0023447 | 1.2965e-06 | 6.1175e-07 | 0.014169 | 0.014169 | 0.014169 | 0.98227 | -0.3398 | 0.98242 | -0.33689 | 3.8927
108 | -0.12947 | -0.032703 | 0.12951 | 0.032729 | 4.091e-05 | 2.5608e-05 | 0.19619 | 0.19619 | 0.19619 | 0.98242 | -0.33689 | 0.98276 | -0.33029 | 13.4743
109 | 0.12011 | 0.030359 | -0.12007 | -0.030333 | 4.0853e-05 | 2.548e-05 | 0.18202 | 0.18202 | 0.18202 | 0.98242 | -0.33689 | 0.98206 | -0.34398 | 12.5012
110 | -0.13067 | -0.033022 | 0.1307 | 0.03304 | 2.8443e-05 | 1.7811e-05 | 0.19795 | 0.19795 | 0.19795 | 0.98276 | -0.33029 | 0.98299 | -0.32576 | 13.5957
111 | -0.13187 | -0.033333 | 0.13193 | 0.033371 | 5.9929e-05 | 3.7542e-05 | 0.19973 | 0.19973 | 0.19973 | 0.98299 | -0.32576 | 0.98348 | -0.31628 | 13.7175
112 | 0.0037994 | 0.000952 | -0.0037994 | -0.00095201 | 2.0073e-08 | -8.3297e-09 | 0.0057058 | 0.0057058 | 0.0057058 | 0.99083 | -0.17452 | 0.99083 | -0.17463 | 1.5675
113 | 0.13513 | 0.034219 | -0.13506 | -0.034176 | 6.87e-05 | 4.3076e-05 | 0.20436 | 0.20436 | 0.20436 | 0.9845 | -0.29654 | 0.98395 | -0.30713 | 14.036
114 | 0.13199 | 0.033407 | -0.13193 | -0.033371 | 5.7951e-05 | 3.6302e-05 | 0.19973 | 0.19973 | 0.19973 | 0.98395 | -0.30713 | 0.98348 | -0.31628 | 13.7175
115 | 0.075564 | 0.019064 | -0.075538 | -0.019048 | 2.6203e-05 | 1.5704e-05 | 0.11485 | 0.11485 | 0.11485 | 0.97937 | -0.39627 | 0.979 | -0.40351 | 7.8884
116 | 0.071914 | 0.01814 | -0.071893 | -0.018127 | 2.1469e-05 | 1.2777e-05 | 0.10935 | 0.10935 | 0.10935 | 0.979 | -0.40351 | 0.97868 | -0.40975 | 7.5101
117 | 0.068834 | 0.017361 | -0.068812 | -0.017347 | 2.2566e-05 | 1.3339e-05 | 0.1047 | 0.1047 | 0.1047 | 0.97868 | -0.40975 | 0.97833 | -0.4166 | 7.1907
118 | 0.065177 | 0.016437 | -0.065156 | -0.016424 | 2.1009e-05 | 1.2302e-05 | 0.099169 | 0.09917 | 0.09917 | 0.97833 | -0.4166 | 0.97799 | -0.42334 | 6.8111
119 | 0.063553 | 0.016022 | -0.063542 | -0.016016 | 1.0832e-05 | 6.3131e-06 | 0.09673 | 0.09673 | 0.09673 | 0.97799 | -0.42334 | 0.97781 | -0.4269 | 6.6436
120 | 0.063542 | 0.016016 | -0.063515 | -0.016001 | 2.6508e-05 | 1.545e-05 | 0.09673 | 0.096731 | 0.096731 | 0.97781 | -0.4269 | 0.97736 | -0.43562 | 6.6436
121 | 0.063515 | 0.016001 | -0.063495 | -0.015989 | 2.0343e-05 | 1.1857e-05 | 0.096731 | 0.096731 | 0.096731 | 0.97736 | -0.43562 | 0.97702 | -0.44232 | 6.6436
122 | 0.0037994 | 0.00095201 | -0.0037992 | -0.00095209 | 1.8341e-07 | -7.6095e-08 | 0.0057058 | 0.0057059 | 0.0057059 | 0.99083 | -0.17463 | 0.99078 | -0.17564 | 1.5676
123 | 0.062375 | 0.015708 | -0.06236 | -0.015699 | 1.5191e-05 | 8.8234e-06 | 0.095025 | 0.095025 | 0.095025 | 0.97702 | -0.44232 | 0.97676 | -0.44742 | 6.5264
124 | -0.045244 | -0.011377 | 0.045245 | 0.011377 | 8.2905e-07 | 4.3819e-07 | 0.069081 | 0.069081 | 0.069081 | 0.97476 | -0.48681 | 0.97477 | -0.48643 | 4.7445
125 | 0.0019034 | 0.00047694 | -0.0019033 | -0.00047702 | 2.2979e-08 | -8.1866e-08 | 0.0028586 | 0.0028586 | 0.0028586 | 0.99078 | -0.17564 | 0.99076 | -0.1759 | 0.78533

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31412 | 0.079769

## res_load
| p_mw | q_mvar
0 | 0.0014402 | 0.00036096
1 | 0.0024735 | 0.00061992
2 | 0.0011247 | 0.00028188
3 | 0.0022836 | 0.00057233
4 | 0.0026588 | 0.00066635
5 | 0.0037729 | 0.00094558
6 | 0.0020748 | 0.00052001
7 | 0.0019163 | 0.00048026
8 | 0.0026354 | 0.0006605
9 | 0.0017349 | 0.00043481
10 | 0.0038494 | 0.00096475
11 | 0.0056079 | 0.0014055
12 | 0.0044049 | 0.001104
13 | 0.0049486 | 0.0012402
14 | 0.0021051 | 0.00052758
15 | 0.018264 | 0.0045775
16 | 0.0012752 | 0.00031959
17 | 0.0014971 | 0.00037522
18 | 0.0013639 | 0.00034184
19 | 0.0018967 | 0.00047537
20 | 0.0012161 | 0.00030478
21 | 0.0076733 | 0.0019231
22 | 0.001216 | 0.00030475
23 | 0.0010153 | 0.00025446
24 | 0.0013076 | 0.00032772
25 | 0.0019342 | 0.00048475
26 | 0.0015542 | 0.00038951
27 | 0.0024668 | 0.00061825
28 | 0.002782 | 0.00069723
29 | 0.0022499 | 0.00056387
30 | 0.0024157 | 0.00060544
31 | 0.002274 | 0.00056991
32 | 0.001217 | 0.00030501
33 | 0.0056765 | 0.0014227
34 | 0.0023279 | 0.00058343
35 | 0.00091427 | 0.00022914
36 | 0.0038525 | 0.00096554
37 | 0.0015206 | 0.00038111
38 | 0.002159 | 0.0005411
39 | 0.0014596 | 0.00036582
40 | 0.00086698 | 0.00021729
41 | 0.00091458 | 0.00022922
42 | 0.0032953 | 0.00082589
43 | 0.0024149 | 0.00060522
44 | 0.0024541 | 0.00061505
45 | 0.0026928 | 0.00067488
46 | 0.0020375 | 0.00051063
47 | 0.0056672 | 0.0014203
48 | 0.0043811 | 0.001098
49 | 0.0028859 | 0.00072327
50 | 0.0024945 | 0.00062518
51 | 0.0016524 | 0.00041414
52 | 0.008346 | 0.0020917
53 | 0.0058849 | 0.0014749
54 | 0.0018885 | 0.00047331
55 | 0.0025761 | 0.00064564
56 | 0.0044675 | 0.0011197
57 | 0.0029551 | 0.00074061
58 | 0.0055718 | 0.0013964
59 | 0.0075255 | 0.0018861
60 | 0.0077328 | 0.001938
61 | 0.0077347 | 0.0019385
62 | 0.0079103 | 0.0019825
63 | 0.0022942 | 0.00057497
64 | 0.0019101 | 0.00047872
65 | 0.0030746 | 0.00077058
66 | 0.0023051 | 0.00057772
67 | 0.0035423 | 0.00088779
68 | 0.001851 | 0.00046392
69 | 0.0033786 | 0.00084675
70 | 0.0026995 | 0.00067656
71 | 0.0011427 | 0.00028638
72 | 0.0012188 | 0.00030546
73 | 0.0015999 | 0.00040096
74 | 0.0018347 | 0.00045981
75 | 0.0019696 | 0.00049362
76 | 0.0023948 | 0.00060018
77 | 0.011026 | 0.0027635
78 | 0.0011541 | 0.00028925
79 | 0.0024436 | 0.00061244
80 | 0.0017263 | 0.00043264
81 | 0.0012206 | 0.00030592
82 | 0.0012054 | 0.00030211
83 | 0.001738 | 0.00043557
84 | 0.0012503 | 0.00031336
85 | 0.0011596 | 0.00029062
86 | 0.0015459 | 0.00038743
87 | 0.0037607 | 0.00094253
88 | 0.0016357 | 0.00040995
89 | 0.0011679 | 0.00029269
90 | 0.0012682 | 0.00031784
91 | 0.0011712 | 0.00029354
92 | 0.0023882 | 0.00059855
93 | 0.0032294 | 0.00080936
94 | 0.0031927 | 0.00080017
95 | 0.0030668 | 0.00076862
96 | 0.0033224 | 0.00083267
97 | 0.0036239 | 0.00090824
98 | 0.0030588 | 0.00076661
99 | 0.0036341 | 0.0009108
100 | 0.0016036 | 0.0004019
101 | 0.0011204 | 0.0002808
102 | 0.0017132 | 0.00042936
103 | 0.0012171 | 0.00030503
104 | 0.0018959 | 0.00047515
105 | 0.0019033 | 0.00047702

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1