## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2495-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2495-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2495-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2495-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2495-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2495-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2495-3_0_4_node_85 | 0.4 | n |  | TRUE
7 | bus_LV_2495-3_0_4_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_2495-3_0_4_node_126 | 0.4 | n |  | TRUE
9 | bus_LV_2495-3_0_4_node_84 | 0.4 | n |  | TRUE
10 | bus_LV_2495-3_0_4_node_81 | 0.4 | n |  | TRUE
11 | bus_LV_2495-3_0_4_node_127 | 0.4 | n |  | TRUE
12 | bus_LV_2495-3_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2495-3_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2495-3_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2495-3_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2495-3_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2495-3_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2495-3_0_4_node_97 | 0.4 | n |  | TRUE
19 | bus_LV_2495-3_0_4_node_132 | 0.4 | n |  | TRUE
20 | bus_LV_2495-3_0_4_node_122 | 0.4 | n |  | TRUE
21 | bus_LV_2495-3_0_4_node_139 | 0.4 | n |  | TRUE
22 | bus_LV_2495-3_0_4_node_137 | 0.4 | n |  | TRUE
23 | bus_LV_2495-3_0_4_node_92 | 0.4 | n |  | TRUE
24 | bus_LV_2495-3_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2495-3_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2495-3_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2495-3_0_4_node_61 | 0.4 | n |  | TRUE
28 | bus_LV_2495-3_0_4_node_58 | 0.4 | n |  | TRUE
29 | bus_LV_2495-3_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2495-3_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2495-3_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2495-3_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2495-3_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2495-3_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2495-3_0_4_node_120 | 0.4 | n |  | TRUE
36 | bus_LV_2495-3_0_4_node_95 | 0.4 | n |  | TRUE
37 | bus_LV_2495-3_0_4_node_121 | 0.4 | n |  | TRUE
38 | bus_LV_2495-3_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2495-3_0_4_node_94 | 0.4 | n |  | TRUE
40 | bus_LV_2495-3_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_2495-3_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2495-3_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2495-3_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2495-3_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2495-3_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_2495-3_0_4_node_54 | 0.4 | n |  | TRUE
47 | bus_LV_2495-3_0_4_node_134 | 0.4 | n |  | TRUE
48 | bus_LV_2495-3_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_2495-3_0_4_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_2495-3_0_4_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_2495-3_0_4_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_2495-3_0_4_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_2495-3_0_4_node_30 | 0.4 | n |  | TRUE
54 | bus_LV_2495-3_0_4_node_125 | 0.4 | n |  | TRUE
55 | bus_LV_2495-3_0_4_node_96 | 0.4 | n |  | TRUE
56 | bus_LV_2495-3_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_2495-3_0_4_node_133 | 0.4 | n |  | TRUE
58 | bus_LV_2495-3_0_4_node_77 | 0.4 | n |  | TRUE
59 | bus_LV_2495-3_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_2495-3_0_4_node_128 | 0.4 | n |  | TRUE
61 | bus_LV_2495-3_0_4_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_2495-3_0_4_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_2495-3_0_4_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_2495-3_0_4_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_2495-3_0_4_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_2495-3_0_4_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_2495-3_0_4_node_138 | 0.4 | n |  | TRUE
68 | bus_LV_2495-3_0_4_node_90 | 0.4 | n |  | TRUE
69 | bus_LV_2495-3_0_4_node_91 | 0.4 | n |  | TRUE
70 | bus_LV_2495-3_0_4_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_2495-3_0_4_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_2495-3_0_4_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_2495-3_0_4_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_2495-3_0_4_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_2495-3_0_4_node_102 | 0.4 | n |  | TRUE
76 | bus_LV_2495-3_0_4_node_117 | 0.4 | n |  | TRUE
77 | bus_LV_2495-3_0_4_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_2495-3_0_4_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_2495-3_0_4_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_2495-3_0_4_node_109 | 0.4 | n |  | TRUE
81 | bus_LV_2495-3_0_4_node_110 | 0.4 | n |  | TRUE
82 | bus_LV_2495-3_0_4_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_2495-3_0_4_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_2495-3_0_4_node_50 | 0.4 | n |  | TRUE
85 | bus_LV_2495-3_0_4_node_51 | 0.4 | n |  | TRUE
86 | bus_LV_2495-3_0_4_node_52 | 0.4 | n |  | TRUE
87 | bus_LV_2495-3_0_4_node_53 | 0.4 | n |  | TRUE
88 | bus_LV_2495-3_0_4_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_2495-3_0_4_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2495-3_0_4_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_2495-3_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_2495-3_0_4_node_56 | 0.4 | n |  | TRUE
93 | bus_LV_2495-3_0_4_node_57 | 0.4 | n |  | TRUE
94 | bus_LV_2495-3_0_4_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_2495-3_0_4_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_2495-3_0_4_node_104 | 0.4 | n |  | TRUE
97 | bus_LV_2495-3_0_4_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_2495-3_0_4_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_2495-3_0_4_node_103 | 0.4 | n |  | TRUE
100 | bus_LV_2495-3_0_4_node_98 | 0.4 | n |  | TRUE
101 | bus_LV_2495-3_0_4_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_2495-3_0_4_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_2495-3_0_4_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_2495-3_0_4_node_131 | 0.4 | n |  | TRUE
105 | bus_LV_2495-3_0_4_node_124 | 0.4 | n |  | TRUE
106 | bus_LV_2495-3_0_4_node_135 | 0.4 | n |  | TRUE
107 | bus_LV_2495-3_0_4_node_123 | 0.4 | n |  | TRUE
108 | bus_LV_2495-3_0_4_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_2495-3_0_4_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_2495-3_0_4_node_73 | 0.4 | n |  | TRUE
111 | bus_LV_2495-3_0_4_node_74 | 0.4 | n |  | TRUE
112 | bus_LV_2495-3_0_4_node_75 | 0.4 | n |  | TRUE
113 | bus_LV_2495-3_0_4_node_76 | 0.4 | n |  | TRUE
114 | bus_LV_2495-3_0_4_node_83 | 0.4 | n |  | TRUE
115 | bus_LV_2495-3_0_4_node_82 | 0.4 | n |  | TRUE
116 | bus_LV_2495-3_0_4_node_79 | 0.4 | n |  | TRUE
117 | bus_LV_2495-3_0_4_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_2495-3_0_4_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_2495-3_0_4_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_2495-3_0_4_node_88 | 0.4 | n |  | TRUE
121 | bus_LV_2495-3_0_4_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_2495-3_0_4_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_2495-3_0_4_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_2495-3_0_4_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_2495-3_0_4_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_2495-3_0_4_node_111 | 0.4 | n |  | TRUE
127 | bus_LV_2495-3_0_4_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_2495-3_0_4_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_2495-3_0_4_node_114 | 0.4 | n |  | TRUE
130 | bus_LV_2495-3_0_4_node_115 | 0.4 | n |  | TRUE
131 | bus_LV_2495-3_0_4_node_116 | 0.4 | n |  | TRUE
132 | bus_LV_2495-3_0_4_node_136 | 0.4 | n |  | TRUE
133 | bus_MV_291_1_node_85 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2495-3_0_4_load_0 | 0 | 0.0013595 | 0.00034071 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2495-3_0_4_load_1 | 1 | 0.001935 | 0.00048495 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2495-3_0_4_load_3 | 3 | 0.0013621 | 0.00034138 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2495-3_0_4_load_4 | 4 | 0.0016635 | 0.0004169 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2495-3_0_4_load_5 | 5 | 0.0014926 | 0.00037407 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2495-3_0_4_load_85 | 6 | 0.0020186 | 0.00050592 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2495-3_0_4_load_80 | 7 | 0.0016774 | 0.0004204 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2495-3_0_4_load_126 | 8 | 0.0049621 | 0.0012436 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2495-3_0_4_load_84 | 9 | 0.0015387 | 0.00038563 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2495-3_0_4_load_81 | 10 | 0.0044471 | 0.0011146 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2495-3_0_4_load_127 | 11 | 0.0016448 | 0.00041224 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2495-3_0_4_load_6 | 12 | 0.019157 | 0.0048013 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2495-3_0_4_load_7 | 13 | 0.0035731 | 0.00089551 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2495-3_0_4_load_9 | 15 | 0.00419 | 0.0010501 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2495-3_0_4_load_11 | 17 | 0.00768 | 0.0019248 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2495-3_0_4_load_97 | 18 | 0.0035821 | 0.00089777 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2495-3_0_4_load_132 | 19 | 0.0033045 | 0.00082819 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2495-3_0_4_load_122 | 20 | 0.002536 | 0.00063557 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2495-3_0_4_load_139 | 21 | 0.0041996 | 0.0010525 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2495-3_0_4_load_137 | 22 | 0.0033626 | 0.00084275 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2495-3_0_4_load_12 | 24 | 0.0015232 | 0.00038174 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2495-3_0_4_load_14 | 26 | 0.00085553 | 0.00021442 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2495-3_0_4_load_61 | 27 | 0.00089795 | 0.00022505 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2495-3_0_4_load_15 | 29 | 0.0082489 | 0.0020674 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2495-3_0_4_load_16 | 30 | 0.002609 | 0.00065389 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2495-3_0_4_load_18 | 32 | 0.002199 | 0.00055113 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2495-3_0_4_load_19 | 33 | 0.034567 | 0.0086634 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2495-3_0_4_load_20 | 34 | 0.0092971 | 0.0023301 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2495-3_0_4_load_95 | 36 | 0.0021107 | 0.00052898 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2495-3_0_4_load_121 | 37 | 0.0021897 | 0.00054878 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2495-3_0_4_load_32 | 38 | 0.0067747 | 0.0016979 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2495-3_0_4_load_21 | 40 | 0.0014357 | 0.00035983 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2495-3_0_4_load_22 | 41 | 0.0067947 | 0.0017029 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2495-3_0_4_load_23 | 42 | 0.029834 | 0.0074771 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2495-3_0_4_load_24 | 43 | 0.0038631 | 0.00096818 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2495-3_0_4_load_25 | 44 | 0.00079609 | 0.00019952 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2495-3_0_4_load_54 | 46 | 0.0012061 | 0.00030227 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2495-3_0_4_load_134 | 47 | 0.0005761 | 0.00014439 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2495-3_0_4_load_33 | 48 | 0.0018556 | 0.00046506 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2495-3_0_4_load_26 | 49 | 0.0022387 | 0.00056107 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2495-3_0_4_load_27 | 50 | 0.001691 | 0.00042381 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2495-3_0_4_load_28 | 51 | 0.0011043 | 0.00027678 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2495-3_0_4_load_30 | 53 | 0.0022646 | 0.00056756 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2495-3_0_4_load_125 | 54 | 0.0011065 | 0.00027732 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2495-3_0_4_load_96 | 55 | 0.0016479 | 0.000413 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2495-3_0_4_load_133 | 57 | 0.0038412 | 0.00096269 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2495-3_0_4_load_77 | 58 | 0.00071605 | 0.00017946 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2495-3_0_4_load_46 | 59 | 0.0019694 | 0.00049358 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2495-3_0_4_load_128 | 60 | 0.0027274 | 0.00068356 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2495-3_0_4_load_34 | 61 | 0.0022585 | 0.00056604 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2495-3_0_4_load_35 | 62 | 0.0014101 | 0.0003534 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2495-3_0_4_load_37 | 63 | 0.0022427 | 0.00056206 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2495-3_0_4_load_70 | 64 | 0.0010439 | 0.00026162 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2495-3_0_4_load_71 | 65 | 0.0023551 | 0.00059025 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2495-3_0_4_load_93 | 66 | 0.0025293 | 0.00063391 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2495-3_0_4_load_138 | 67 | 0.0031306 | 0.00078461 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2495-3_0_4_load_90 | 68 | 0.0033014 | 0.0008274 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2495-3_0_4_load_91 | 69 | 0.003555 | 0.00089097 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2495-3_0_4_load_39 | 70 | 0.0017201 | 0.0004311 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2495-3_0_4_load_40 | 71 | 0.0011124 | 0.00027878 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2495-3_0_4_load_41 | 72 | 0.0015221 | 0.00038147 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2495-3_0_4_load_42 | 73 | 0.0062926 | 0.0015771 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2495-3_0_4_load_43 | 74 | 0.0014639 | 0.00036688 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2495-3_0_4_load_102 | 75 | 0.0017117 | 0.000429 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2495-3_0_4_load_117 | 76 | 0.0020463 | 0.00051285 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2495-3_0_4_load_44 | 77 | 0.0013754 | 0.0003447 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2495-3_0_4_load_45 | 78 | 0.0013777 | 0.00034528 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2495-3_0_4_load_47 | 79 | 0.0022287 | 0.00055855 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2495-3_0_4_load_109 | 80 | 0.0021403 | 0.00053641 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2495-3_0_4_load_110 | 81 | 0.0019013 | 0.0004765 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2495-3_0_4_load_78 | 82 | 0.0010197 | 0.00025555 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2495-3_0_4_load_49 | 83 | 0.0031495 | 0.00078933 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2495-3_0_4_load_50 | 84 | 0.0041008 | 0.0010278 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2495-3_0_4_load_51 | 85 | 0.0030302 | 0.00075943 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2495-3_0_4_load_53 | 87 | 0.0036023 | 0.00090282 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2495-3_0_4_load_65 | 88 | 0.0019194 | 0.00048104 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2495-3_0_4_load_68 | 89 | 0.0066456 | 0.0016655 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2495-3_0_4_load_63 | 90 | 0.0016832 | 0.00042185 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2495-3_0_4_load_69 | 91 | 0.0056109 | 0.0014062 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2495-3_0_4_load_56 | 92 | 0.00068292 | 0.00017116 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2495-3_0_4_load_57 | 93 | 0.0012771 | 0.00032008 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2495-3_0_4_load_59 | 94 | 0.0014159 | 0.00035487 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2495-3_0_4_load_104 | 96 | 0.001088 | 0.00027268 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2495-3_0_4_load_89 | 97 | 0.0019033 | 0.00047702 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2495-3_0_4_load_86 | 98 | 0.0029948 | 0.00075057 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2495-3_0_4_load_103 | 99 | 0.00058917 | 0.00014766 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2495-3_0_4_load_98 | 100 | 0.0023832 | 0.00059728 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2495-3_0_4_load_87 | 101 | 0.0035194 | 0.00088204 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2495-3_0_4_load_62 | 102 | 0.0022384 | 0.00056101 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2495-3_0_4_load_131 | 104 | 0.0027539 | 0.00069019 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2495-3_0_4_load_124 | 105 | 0.011202 | 0.0028075 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2495-3_0_4_load_135 | 106 | 0.0027488 | 0.00068892 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2495-3_0_4_load_123 | 107 | 0.0066776 | 0.0016736 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2495-3_0_4_load_99 | 108 | 0.0011916 | 0.00029865 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2495-3_0_4_load_72 | 109 | 0.0029783 | 0.00074644 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2495-3_0_4_load_73 | 110 | 0.0022322 | 0.00055944 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2495-3_0_4_load_76 | 113 | 0.0011463 | 0.0002873 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2495-3_0_4_load_83 | 114 | 0.0014558 | 0.00036485 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2495-3_0_4_load_82 | 115 | 0.0015369 | 0.00038519 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2495-3_0_4_load_101 | 117 | 0.0022886 | 0.00057359 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2495-3_0_4_load_100 | 118 | 0.0004622 | 0.00011584 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2495-3_0_4_load_88 | 120 | 0.00048201 | 0.0001208 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2495-3_0_4_load_119 | 121 | 0.0017077 | 0.00042799 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2495-3_0_4_load_106 | 122 | 0.0050326 | 0.0012613 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2495-3_0_4_load_107 | 123 | 0.0023373 | 0.00058578 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2495-3_0_4_load_108 | 125 | 0.0015699 | 0.00039345 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2495-3_0_4_load_111 | 126 | 0.0014451 | 0.00036217 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2495-3_0_4_load_112 | 127 | 0.0039942 | 0.001001 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2495-3_0_4_load_113 | 128 | 0.0047914 | 0.0012008 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2495-3_0_4_load_114 | 129 | 0.00098686 | 0.00024733 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2495-3_0_4_load_115 | 130 | 0.0030893 | 0.00077425 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2495-3_0_4_load_116 | 131 | 0.002652 | 0.00066464 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2495-3_0_4_load_136 | 132 | 0.011007 | 0.0027586 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 55 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2495-3_0_4_line_0 |  | 0 | 1 | 0.0017413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2495-3_0_4_line_1 |  | 0 | 2 | 0.014851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2495-3_0_4_line_2 |  | 1 | 3 | 0.0061693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2495-3_0_4_line_3 |  | 2 | 4 | 0.011785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2495-3_0_4_line_4 |  | 2 | 5 | 0.0040814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2495-3_0_4_line_5 |  | 3 | 6 | 0.016155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2495-3_0_4_line_6 |  | 4 | 7 | 0.0011711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2495-3_0_4_line_7 |  | 5 | 8 | 0.011046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2495-3_0_4_line_8 |  | 6 | 9 | 0.0036452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2495-3_0_4_line_9 |  | 7 | 10 | 0.014452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2495-3_0_4_line_10 |  | 8 | 11 | 0.015034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2495-3_0_4_line_11 |  | 9 | 115 | 0.01942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2495-3_0_4_line_12 |  | 11 | 106 | 0.00092396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2495-3_0_4_line_13 |  | 12 | 13 | 0.0033537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2495-3_0_4_line_14 |  | 12 | 14 | 0.017688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2495-3_0_4_line_15 |  | 13 | 15 | 0.010421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2495-3_0_4_line_16 |  | 14 | 16 | 0.009491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2495-3_0_4_line_17 |  | 14 | 17 | 0.0341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2495-3_0_4_line_18 |  | 15 | 18 | 0.0019569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2495-3_0_4_line_19 |  | 16 | 19 | 0.0029775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2495-3_0_4_line_20 |  | 16 | 20 | 0.021891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2495-3_0_4_line_21 |  | 18 | 21 | 0.0052327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2495-3_0_4_line_22 |  | 19 | 22 | 0.028313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2495-3_0_4_line_23 |  | 20 | 23 | 0.014424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2495-3_0_4_line_24 |  | 22 | 132 | 0.0061784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2495-3_0_4_line_25 |  | 23 | 69 | 0.0097081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2495-3_0_4_line_26 |  | 24 | 25 | 0.0037535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2495-3_0_4_line_27 |  | 25 | 26 | 0.017532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2495-3_0_4_line_28 |  | 26 | 27 | 0.0073422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2495-3_0_4_line_29 |  | 27 | 28 | 0.01661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2495-3_0_4_line_30 |  | 28 | 95 | 0.003017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2495-3_0_4_line_31 |  | 28 | 92 | 0.019074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2495-3_0_4_line_32 |  | 29 | 30 | 0.0091293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2495-3_0_4_line_33 |  | 29 | 31 | 0.01944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2495-3_0_4_line_34 |  | 30 | 32 | 0.0021348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2495-3_0_4_line_35 |  | 31 | 33 | 0.025512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2495-3_0_4_line_36 |  | 31 | 34 | 0.0017532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2495-3_0_4_line_37 |  | 32 | 35 | 0.014999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2495-3_0_4_line_38 |  | 33 | 36 | 0.029495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2495-3_0_4_line_39 |  | 35 | 37 | 0.0090029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2495-3_0_4_line_40 |  | 35 | 38 | 0.038905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2495-3_0_4_line_41 |  | 36 | 39 | 0.0024095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2495-3_0_4_line_42 |  | 37 | 132 | 0.011709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2495-3_0_4_line_43 |  | 38 | 45 | 0.013006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2495-3_0_4_line_44 |  | 39 | 55 | 0.033802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2495-3_0_4_line_45 |  | 39 | 91 | 0.014857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2495-3_0_4_line_46 |  | 40 | 41 | 0.021017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2495-3_0_4_line_47 |  | 40 | 42 | 0.0069205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2495-3_0_4_line_48 |  | 41 | 43 | 0.0042447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2495-3_0_4_line_49 |  | 42 | 44 | 0.014118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2495-3_0_4_line_50 |  | 43 | 45 | 0.011587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2495-3_0_4_line_51 |  | 44 | 46 | 0.016885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2495-3_0_4_line_52 |  | 44 | 47 | 0.057544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2495-3_0_4_line_53 |  | 45 | 48 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2495-3_0_4_line_54 |  | 48 | 60 | 0.0083395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2495-3_0_4_line_55 |  | 49 | 50 | 0.0016603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_2495-3_0_4_line_56 |  | 49 | 51 | 0.0037449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_2495-3_0_4_line_57 |  | 50 | 52 | 0.014833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_2495-3_0_4_line_58 |  | 51 | 53 | 0.014925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_2495-3_0_4_line_59 |  | 52 | 54 | 0.012234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2495-3_0_4_line_60 |  | 52 | 55 | 0.0075258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_2495-3_0_4_line_61 |  | 53 | 56 | 0.01146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_2495-3_0_4_line_62 |  | 54 | 57 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2495-3_0_4_line_63 |  | 56 | 58 | 0.018472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2495-3_0_4_line_64 |  | 56 | 59 | 0.011016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2495-3_0_4_line_65 |  | 58 | 82 | 0.022574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_2495-3_0_4_line_66 |  | 59 | 77 | 0.02693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2495-3_0_4_line_67 |  | 61 | 62 | 0.014477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2495-3_0_4_line_68 |  | 62 | 63 | 0.001884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2495-3_0_4_line_69 |  | 63 | 64 | 0.013387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2495-3_0_4_line_70 |  | 64 | 65 | 0.0035516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2495-3_0_4_line_71 |  | 65 | 108 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2495-3_0_4_line_72 |  | 66 | 67 | 0.0056385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2495-3_0_4_line_73 |  | 67 | 121 | 0.012958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2495-3_0_4_line_74 |  | 68 | 69 | 0.01741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2495-3_0_4_line_75 |  | 70 | 71 | 0.0059368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2495-3_0_4_line_76 |  | 70 | 72 | 0.0067911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2495-3_0_4_line_77 |  | 71 | 73 | 0.0056929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2495-3_0_4_line_78 |  | 72 | 74 | 0.0011303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2495-3_0_4_line_79 |  | 74 | 75 | 0.0019883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2495-3_0_4_line_80 |  | 75 | 76 | 0.01497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2495-3_0_4_line_81 |  | 76 | 124 | 0.013816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2495-3_0_4_line_82 |  | 77 | 78 | 0.0020135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2495-3_0_4_line_83 |  | 78 | 79 | 0.0047527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2495-3_0_4_line_84 |  | 79 | 80 | 0.0012172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2495-3_0_4_line_85 |  | 80 | 81 | 0.018346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2495-3_0_4_line_86 |  | 81 | 126 | 0.014413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2495-3_0_4_line_87 |  | 82 | 116 | 0.010766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_2495-3_0_4_line_88 |  | 83 | 84 | 0.026542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2495-3_0_4_line_89 |  | 83 | 85 | 0.0018989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2495-3_0_4_line_90 |  | 84 | 86 | 0.024307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2495-3_0_4_line_91 |  | 85 | 87 | 0.0241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2495-3_0_4_line_92 |  | 86 | 88 | 0.02772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2495-3_0_4_line_93 |  | 87 | 89 | 0.037651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2495-3_0_4_line_94 |  | 88 | 90 | 0.011657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2495-3_0_4_line_95 |  | 89 | 91 | 0.018285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2495-3_0_4_line_96 |  | 90 | 102 | 0.011417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2495-3_0_4_line_97 |  | 92 | 93 | 0.010112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2495-3_0_4_line_98 |  | 93 | 94 | 0.017848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2495-3_0_4_line_99 |  | 94 | 96 | 0.034645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2495-3_0_4_line_100 |  | 95 | 97 | 0.014868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2495-3_0_4_line_101 |  | 95 | 98 | 0.01895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_2495-3_0_4_line_102 |  | 96 | 99 | 0.019942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2495-3_0_4_line_103 |  | 97 | 100 | 0.014554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2495-3_0_4_line_104 |  | 98 | 101 | 0.01753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_2495-3_0_4_line_105 |  | 99 | 112 | 0.021175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2495-3_0_4_line_106 |  | 100 | 108 | 0.0038011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2495-3_0_4_line_107 |  | 101 | 120 | 0.0035089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_2495-3_0_4_line_108 |  | 103 | 104 | 0.043429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2495-3_0_4_line_109 |  | 103 | 105 | 0.018613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2495-3_0_4_line_110 |  | 104 | 106 | 0.017613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2495-3_0_4_line_111 |  | 105 | 107 | 0.02505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2495-3_0_4_line_112 |  | 107 | 131 | 0.012814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2495-3_0_4_line_113 |  | 109 | 110 | 0.058976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2495-3_0_4_line_114 |  | 109 | 111 | 0.011975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2495-3_0_4_line_115 |  | 110 | 112 | 0.036137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2495-3_0_4_line_116 |  | 111 | 113 | 0.019648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2495-3_0_4_line_117 |  | 112 | 114 | 0.018997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2495-3_0_4_line_118 |  | 114 | 115 | 0.022843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2495-3_0_4_line_119 |  | 116 | 117 | 0.022452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2495-3_0_4_line_120 |  | 116 | 118 | 0.01483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_2495-3_0_4_line_121 |  | 117 | 119 | 0.004209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2495-3_0_4_line_122 |  | 118 | 120 | 0.00028044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_2495-3_0_4_line_123 |  | 119 | 122 | 0.023509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2495-3_0_4_line_124 |  | 119 | 123 | 0.023437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2495-3_0_4_line_125 |  | 121 | 124 | 0.010723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2495-3_0_4_line_126 |  | 122 | 125 | 0.013669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2495-3_0_4_line_127 |  | 123 | 124 | 0.001284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2495-3_0_4_line_128 |  | 127 | 128 | 0.0035629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2495-3_0_4_line_129 |  | 127 | 129 | 0.015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2495-3_0_4_line_130 |  | 128 | 130 | 0.0088272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2495-3_0_4_line_131 |  | 129 | 131 | 0.005843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2495-3_0_4_trafo_96 | 0.63 MVA 20/0.4 kV | 133 | 55 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2641952.6943 | 1246781.2138 | 2641954.3466 | 1246780.6642
1 | 2641938.6025 | 1246785.9007 | 2641952.6943 | 1246781.2138
2 | 2641954.3466 | 1246780.6642 | 2641960.2006 | 1246778.7172
3 | 2641938.6025 | 1246785.9007 | 2641939.6041 | 1246787.3976 | 2641943.2028 | 1246791.2034 | 2641946.4642 | 1246794.6513
4 | 2641938.6025 | 1246785.9007 | 2641938.2003 | 1246785.0973 | 2641937.2604 | 1246782.0563
5 | 2641960.2006 | 1246778.7172 | 2641975.5303 | 1246773.6185
6 | 2641946.4642 | 1246794.6513 | 2641947.269 | 1246795.502
7 | 2641933.9986 | 1246771.5031 | 2641937.2604 | 1246782.0563
8 | 2641975.5303 | 1246773.6185 | 2641978.9892 | 1246772.4681
9 | 2641957.2001 | 1246806.001 | 2641947.269 | 1246795.502
10 | 2641919.0129 | 1246770.2926 | 2641933.9986 | 1246771.5031 | 2641933.9986 | 1246771.5031
11 | 2641996.0068 | 1246774.7831 | 2641989.8002 | 1246769.6964 | 2641988.9042 | 1246769.3009 | 2641987.8981 | 1246769.505 | 2641978.9892 | 1246772.4681
12 | 2641919.0129 | 1246770.2926 | 2641918.092 | 1246770.2183
13 | 2641952.8904 | 1247032.0185 | 2641952.4591 | 1247033.1289 | 2641951.2386 | 1247034.9141
14 | 2641960.8155 | 1247017.7889 | 2641957.5832 | 1247018.8001 | 2641955.2864 | 1247022.0972 | 2641954.5824 | 1247027.6625 | 2641952.8904 | 1247032.0185
15 | 2641944.2248 | 1247042.4463 | 2641948.1547 | 1247039.4249 | 2641951.2386 | 1247034.9141
16 | 2641960.8155 | 1247017.7889 | 2641961.9697 | 1247008.3686
17 | 2641980.8358 | 1247041.6463 | 2641981.4351 | 1247037.0141 | 2641978.5352 | 1247031.6123 | 2641970.0785 | 1247021.6348 | 2641965.5456 | 1247018.5785 | 2641960.8155 | 1247017.7889
18 | 2641944.2248 | 1247042.4463 | 2641942.6735 | 1247043.639
19 | 2641961.9697 | 1247008.3686 | 2641959.0341 | 1247007.8712
20 | 2641961.9697 | 1247008.3686 | 2641980.9127 | 1247011.5714 | 2641983.5537 | 1247012.0202
21 | 2641938.5252 | 1247046.8284 | 2641942.6735 | 1247043.639
22 | 2641959.0341 | 1247007.8712 | 2641931.1193 | 1247003.141
23 | 2641997.7734 | 1247014.437 | 2641983.5537 | 1247012.0202
24 | 2641925.0277 | 1247002.1088 | 2641931.1193 | 1247003.141
25 | 2641997.7734 | 1247014.437 | 2642007.3435 | 1247016.0679
26 | 2642133.3475 | 1246902.0678 | 2642136.2127 | 1246904.4926
27 | 2642133.3475 | 1246902.0678 | 2642126.8007 | 1246896.5066 | 2642122.1027 | 1246893.3044 | 2642119.1838 | 1246891.8608
28 | 2642119.1838 | 1246891.8608 | 2642113.8007 | 1246889.1984 | 2642112.506 | 1246888.8662
29 | 2642096.1038 | 1246888.1054 | 2642106.8041 | 1246887.4031 | 2642112.506 | 1246888.8662
30 | 2642096.1038 | 1246888.1054 | 2642093.1097 | 1246888.5401
31 | 2642096.1038 | 1246888.1054 | 2642092.7988 | 1246873.8059 | 2642091.3353 | 1246869.6588
32 | 2641884.4567 | 1246981.9971 | 2641890.349 | 1246988.4829 | 2641890.6172 | 1246988.7329
33 | 2641868.7495 | 1246971.0412 | 2641873.7194 | 1246973.1888 | 2641876.9848 | 1246974.9797 | 2641880.2235 | 1246977.3374 | 2641884.4567 | 1246981.9971
34 | 2641892.179 | 1246990.1883 | 2641890.6172 | 1246988.7329
35 | 2641868.7495 | 1246971.0412 | 2641874.1316 | 1246964.019 | 2641876.5795 | 1246961.7681 | 2641882.6938 | 1246958.0198 | 2641888.4703 | 1246955.8581
36 | 2641868.7495 | 1246971.0412 | 2641867.0924 | 1246970.4688
37 | 2641904.6916 | 1246998.1906 | 2641901.3852 | 1246996.8664 | 2641898.6006 | 1246995.4458 | 2641894.6411 | 1246992.4825 | 2641892.179 | 1246990.1883
38 | 2641888.4703 | 1246955.8581 | 2641890.8879 | 1246954.9534 | 2641916.2752 | 1246946.0198
39 | 2641904.6916 | 1246998.1906 | 2641913.5216 | 1246999.9465
40 | 2641904.6916 | 1246998.1906 | 2641901.6117 | 1247010.7772 | 2641893.9106 | 1247035.5552
41 | 2641918.5481 | 1246945.22 | 2641916.2752 | 1246946.0198
42 | 2641913.5216 | 1246999.9465 | 2641920.7494 | 1247001.3839 | 2641925.0277 | 1247002.1088
43 | 2641890.3361 | 1247048.0556 | 2641891.6881 | 1247042.7061 | 2641893.9106 | 1247035.5552
44 | 2641918.5481 | 1246945.22 | 2641921.3872 | 1246944.2728 | 2641926.4685 | 1246942.4074 | 2641932.0023 | 1246939.5669 | 2641938.46 | 1246934.2645 | 2641944.4025 | 1246928.1024 | 2641946.0146 | 1246926.5197
45 | 2641918.5481 | 1246945.22 | 2641916.2036 | 1246940.3002 | 2641913.2973 | 1246935.7989 | 2641910.2593 | 1246933.122
46 | 2641894.6294 | 1247062.8832 | 2641906.7856 | 1247080.0281
47 | 2641911.0202 | 1247085.4989 | 2641907.9014 | 1247081.6018 | 2641906.7856 | 1247080.0281
48 | 2641894.6294 | 1247062.8832 | 2641892.1743 | 1247059.4206
49 | 2641911.0202 | 1247085.4989 | 2641919.8412 | 1247096.5214
50 | 2641890.3361 | 1247048.0556 | 2641890.4607 | 1247052.8708 | 2641892.1743 | 1247059.4206
51 | 2641930.3915 | 1247109.7046 | 2641919.8412 | 1247096.5214
52 | 2641919.8412 | 1247096.5214 | 2641872.9238 | 1247129.8395
53 | 2641890.3361 | 1247048.0556 | 2641878.9978 | 1247046.0965 | 2641878.8972 | 1247046.0803
54 | 2641878.8972 | 1247046.0803 | 2641872.8039 | 1247045.0966 | 2641870.7549 | 1247044.3904
55 | 2641963.152 | 1246909.6907 | 2641961.9674 | 1246910.8541
56 | 2641965.8238 | 1246907.0667 | 2641963.152 | 1246909.6907
57 | 2641951.3848 | 1246921.2472 | 2641961.9674 | 1246910.8541
58 | 2641976.6979 | 1246896.85 | 2641971.8981 | 1246901.1012 | 2641965.8238 | 1246907.0667
59 | 2641951.3848 | 1246921.2472 | 2641957.5279 | 1246931.8273
60 | 2641951.3848 | 1246921.2472 | 2641946.0146 | 1246926.5197
61 | 2641986.9987 | 1246892.3021 | 2641986.7042 | 1246892.3 | 2641981.9983 | 1246893.4008 | 2641977.2035 | 1246896.4022 | 2641976.6979 | 1246896.85
62 | 2641964.8802 | 1246944.4899 | 2641957.5279 | 1246931.8273
63 | 2641986.9987 | 1246892.3021 | 2641991.9982 | 1246892.4042 | 2642005.3003 | 1246894.3997 | 2642005.3205 | 1246894.4028
64 | 2641986.9987 | 1246892.3021 | 2641986.7039 | 1246890.1986 | 2641986.9022 | 1246887.7985 | 2641988.1977 | 1246885.1058 | 2641990.2227 | 1246882.2563
65 | 2642005.3205 | 1246894.4028 | 2642015.5008 | 1246896.0063 | 2642022.703 | 1246896.502 | 2642027.7481 | 1246896.3072
66 | 2641984.8384 | 1246858.7409 | 2641991.9007 | 1246869.8997 | 2641993.2006 | 1246872.9999 | 2641993.7996 | 1246874.8053 | 2641993.5973 | 1246876.7051 | 2641993.1033 | 1246878.2026 | 2641990.2227 | 1246882.2563
67 | 2642096.0581 | 1246952.2123 | 2642096.1981 | 1246955.7064 | 2642096.7193 | 1246966.6741
68 | 2642095.9827 | 1246950.3298 | 2642096.0581 | 1246952.2123
69 | 2642095.9827 | 1246950.3298 | 2642095.4467 | 1246936.9535
70 | 2642095.3045 | 1246933.4048 | 2642095.4467 | 1246936.9535
71 | 2642094.8359 | 1246921.7095 | 2642095.3045 | 1246933.4048
72 | 2642046.2622 | 1246970.459 | 2642046.6816 | 1246976.0819
73 | 2642046.2622 | 1246970.459 | 2642045.8999 | 1246965.6009 | 2642045.0477 | 1246957.56
74 | 2642024.5063 | 1247018.9928 | 2642007.3435 | 1247016.0679
75 | 2641999.2855 | 1246946.7383 | 2642005.2223 | 1246946.7594
76 | 2642012.0133 | 1246946.7835 | 2642005.2223 | 1246946.7594
77 | 2641993.5926 | 1246946.7181 | 2641999.2855 | 1246946.7383
78 | 2642012.0133 | 1246946.7835 | 2642013.1436 | 1246946.7875
79 | 2642013.1436 | 1246946.7875 | 2642015.1319 | 1246946.7946
80 | 2642030.1013 | 1246946.8477 | 2642015.1319 | 1246946.7946
81 | 2642043.9176 | 1246946.8967 | 2642030.1013 | 1246946.8477
82 | 2641984.8384 | 1246858.7409 | 2641983.7616 | 1246857.0395
83 | 2641981.22 | 1246853.0235 | 2641983.7616 | 1246857.0395
84 | 2641981.22 | 1246853.0235 | 2641980.569 | 1246851.995
85 | 2641980.569 | 1246851.995 | 2641976.9016 | 1246846.2002 | 2641976.2015 | 1246844.8054 | 2641976.1991 | 1246843.0042 | 2641977.1999 | 1246841.3991 | 2641982.0804 | 1246837.5187
86 | 2641993.6034 | 1246828.8958 | 2641988.7014 | 1246832.0965 | 2641985.5023 | 1246834.7979 | 2641982.0804 | 1246837.5187
87 | 2642038.5016 | 1246895.8023 | 2642035.5998 | 1246896.0041 | 2642027.7481 | 1246896.3072
88 | 2641843.5381 | 1246885.7628 | 2641821.3359 | 1246871.2192
89 | 2641843.5381 | 1246885.7628 | 2641845.1266 | 1246886.8033
90 | 2641801.0028 | 1246857.8999 | 2641821.3359 | 1246871.2192
91 | 2641865.2867 | 1246900.0093 | 2641845.1266 | 1246886.8033
92 | 2641801.0028 | 1246857.8999 | 2641806.7993 | 1246847.8008 | 2641813.3998 | 1246834.0048 | 2641813.6686 | 1246833.2702
93 | 2641865.2867 | 1246900.0093 | 2641866.8042 | 1246901.0033 | 2641872.5995 | 1246905.0024 | 2641896.3832 | 1246921.2354
94 | 2641817.6735 | 1246822.3224 | 2641813.6686 | 1246833.2702
95 | 2641910.2593 | 1246933.122 | 2641898.0968 | 1246922.405 | 2641896.3832 | 1246921.2354
96 | 2641821.596 | 1246811.6001 | 2641817.6735 | 1246822.3224
97 | 2642091.3353 | 1246869.6588 | 2642089.9037 | 1246865.6021 | 2642087.0771 | 1246860.5255
98 | 2642087.0771 | 1246860.5255 | 2642086.3984 | 1246859.3064 | 2642082.798 | 1246854.7001 | 2642075.5046 | 1246846.9998
99 | 2642051.6804 | 1246821.8463 | 2642075.5046 | 1246846.9998
100 | 2642093.1097 | 1246888.5401 | 2642093.7854 | 1246895.4939 | 2642094.101 | 1246903.369
101 | 2642093.1097 | 1246888.5401 | 2642082.599 | 1246890.2 | 2642074.3657 | 1246891.319
102 | 2642051.6804 | 1246821.8463 | 2642043.4006 | 1246813.1045 | 2642038.3856 | 1246806.9989
103 | 2642094.6837 | 1246917.9115 | 2642094.101 | 1246903.369
104 | 2642074.3657 | 1246891.319 | 2642056.9958 | 1246893.6799
105 | 2642029.9998 | 1246787.7039 | 2642034.299 | 1246800.2982 | 2642037.4022 | 1246805.8016 | 2642038.3856 | 1246806.9989
106 | 2642094.6837 | 1246917.9115 | 2642094.8359 | 1246921.7095
107 | 2642053.5189 | 1246894.1525 | 2642056.9958 | 1246893.6799
108 | 2641857.1975 | 1246766.0018 | 2641899.3033 | 1246768.7007 | 2641900.5364 | 1246768.8003
109 | 2641857.1975 | 1246766.0018 | 2641868.9075 | 1246780.47
110 | 2641900.5364 | 1246768.8003 | 2641918.092 | 1246770.2183
111 | 2641884.667 | 1246799.9416 | 2641868.9075 | 1246780.47
112 | 2641884.667 | 1246799.9416 | 2641892.7287 | 1246809.9021
113 | 2641965.1151 | 1246721.0108 | 2641975.4987 | 1246728.5013 | 2642011.6092 | 1246757.2747
114 | 2641955.4035 | 1246714.0052 | 2641965.1151 | 1246721.0108
115 | 2642029.9998 | 1246787.7039 | 2642027.1992 | 1246780.0012 | 2642023.3983 | 1246771.7021 | 2642020.2984 | 1246766.7991 | 2642017.9007 | 1246763.0019 | 2642014.3981 | 1246759.497 | 2642011.6092 | 1246757.2747
116 | 2641955.4035 | 1246714.0052 | 2641954.1042 | 1246715.0967 | 2641952.2004 | 1246716.2062 | 2641949.7029 | 1246716.9001 | 2641936.6303 | 1246718.3702
117 | 2642029.9998 | 1246787.7039 | 2642024.101 | 1246789.7968 | 2642021.0973 | 1246790.4983 | 2642018.3987 | 1246790.8016 | 2642015.3032 | 1246790.6018 | 2642011.6017 | 1246789.5971 | 2642011.6017 | 1246789.5971
118 | 2641996.0068 | 1246774.7831 | 2642002.4992 | 1246780.1042 | 2642003.1033 | 1246781.1981 | 2642003.0974 | 1246783.0993 | 2642003.2989 | 1246784.5017 | 2642004.1001 | 1246785.4969 | 2642004.9026 | 1246786.3031 | 2642007.4011 | 1246787.5994 | 2642011.6017 | 1246789.5971
119 | 2642038.5016 | 1246895.8023 | 2642040.6776 | 1246918.149
120 | 2642038.5016 | 1246895.8023 | 2642048.0023 | 1246894.9023 | 2642053.241 | 1246894.1903
121 | 2642041.0856 | 1246922.3382 | 2642040.6776 | 1246918.149
122 | 2642053.5189 | 1246894.1525 | 2642053.241 | 1246894.1903
123 | 2642041.0856 | 1246922.3382 | 2642017.5768 | 1246922.4669
124 | 2642041.0856 | 1246922.3382 | 2642043.7705 | 1246945.6212
125 | 2642043.9176 | 1246946.8967 | 2642045.0477 | 1246957.56
126 | 2642003.9076 | 1246922.5418 | 2642017.5768 | 1246922.4669
127 | 2642043.9176 | 1246946.8967 | 2642043.7705 | 1246945.6212
128 | 2641906.3036 | 1246826.6744 | 2641908.5451 | 1246829.444
129 | 2641896.4046 | 1246814.4439 | 2641906.3036 | 1246826.6744
130 | 2641914.0985 | 1246836.3054 | 2641908.5451 | 1246829.444
131 | 2641896.4046 | 1246814.4439 | 2641892.7287 | 1246809.9021

## bus_geodata
| x | y | coords
0 | 2641952.6943 | 1246781.2138
1 | 2641954.3466 | 1246780.6642
2 | 2641938.6025 | 1246785.9007
3 | 2641960.2006 | 1246778.7172
4 | 2641946.4642 | 1246794.6513
5 | 2641937.2604 | 1246782.0563
6 | 2641975.5303 | 1246773.6185
7 | 2641947.269 | 1246795.502
8 | 2641933.9986 | 1246771.5031
9 | 2641978.9892 | 1246772.4681
10 | 2641957.2001 | 1246806.001
11 | 2641919.0129 | 1246770.2926
12 | 2641952.8904 | 1247032.0185
13 | 2641951.2386 | 1247034.9141
14 | 2641960.8155 | 1247017.7889
15 | 2641944.2248 | 1247042.4463
16 | 2641961.9697 | 1247008.3686
17 | 2641980.8358 | 1247041.6463
18 | 2641942.6735 | 1247043.639
19 | 2641959.0341 | 1247007.8712
20 | 2641983.5537 | 1247012.0202
21 | 2641938.5252 | 1247046.8284
22 | 2641931.1193 | 1247003.141
23 | 2641997.7734 | 1247014.437
24 | 2642136.2127 | 1246904.4926
25 | 2642133.3475 | 1246902.0678
26 | 2642119.1838 | 1246891.8608
27 | 2642112.506 | 1246888.8662
28 | 2642096.1038 | 1246888.1054
29 | 2641884.4567 | 1246981.9971
30 | 2641890.6172 | 1246988.7329
31 | 2641868.7495 | 1246971.0412
32 | 2641892.179 | 1246990.1883
33 | 2641888.4703 | 1246955.8581
34 | 2641867.0924 | 1246970.4688
35 | 2641904.6916 | 1246998.1906
36 | 2641916.2752 | 1246946.0198
37 | 2641913.5216 | 1246999.9465
38 | 2641893.9106 | 1247035.5552
39 | 2641918.5481 | 1246945.22
40 | 2641906.7856 | 1247080.0281
41 | 2641894.6294 | 1247062.8832
42 | 2641911.0202 | 1247085.4989
43 | 2641892.1743 | 1247059.4206
44 | 2641919.8412 | 1247096.5214
45 | 2641890.3361 | 1247048.0556
46 | 2641930.3915 | 1247109.7046
47 | 2641872.9238 | 1247129.8395
48 | 2641878.8972 | 1247046.0803
49 | 2641963.152 | 1246909.6907
50 | 2641961.9674 | 1246910.8541
51 | 2641965.8238 | 1246907.0667
52 | 2641951.3848 | 1246921.2472
53 | 2641976.6979 | 1246896.85
54 | 2641957.5279 | 1246931.8273
55 | 2641946.0146 | 1246926.5197
56 | 2641986.9987 | 1246892.3021
57 | 2641964.8802 | 1246944.4899
58 | 2642005.3205 | 1246894.4028
59 | 2641990.2227 | 1246882.2563
60 | 2641870.7549 | 1247044.3904
61 | 2642096.7193 | 1246966.6741
62 | 2642096.0581 | 1246952.2123
63 | 2642095.9827 | 1246950.3298
64 | 2642095.4467 | 1246936.9535
65 | 2642095.3045 | 1246933.4048
66 | 2642046.6816 | 1246976.0819
67 | 2642046.2622 | 1246970.459
68 | 2642024.5063 | 1247018.9928
69 | 2642007.3435 | 1247016.0679
70 | 2642005.2223 | 1246946.7594
71 | 2641999.2855 | 1246946.7383
72 | 2642012.0133 | 1246946.7835
73 | 2641993.5926 | 1246946.7181
74 | 2642013.1436 | 1246946.7875
75 | 2642015.1319 | 1246946.7946
76 | 2642030.1013 | 1246946.8477
77 | 2641984.8384 | 1246858.7409
78 | 2641983.7616 | 1246857.0395
79 | 2641981.22 | 1246853.0235
80 | 2641980.569 | 1246851.995
81 | 2641982.0804 | 1246837.5187
82 | 2642027.7481 | 1246896.3072
83 | 2641843.5381 | 1246885.7628
84 | 2641821.3359 | 1246871.2192
85 | 2641845.1266 | 1246886.8033
86 | 2641801.0028 | 1246857.8999
87 | 2641865.2867 | 1246900.0093
88 | 2641813.6686 | 1246833.2702
89 | 2641896.3832 | 1246921.2354
90 | 2641817.6735 | 1246822.3224
91 | 2641910.2593 | 1246933.122
92 | 2642091.3353 | 1246869.6588
93 | 2642087.0771 | 1246860.5255
94 | 2642075.5046 | 1246846.9998
95 | 2642093.1097 | 1246888.5401
96 | 2642051.6804 | 1246821.8463
97 | 2642094.101 | 1246903.369
98 | 2642074.3658 | 1246891.319
99 | 2642038.3856 | 1246806.9989
100 | 2642094.6837 | 1246917.9115
101 | 2642056.9958 | 1246893.6799
102 | 2641821.596 | 1246811.6001
103 | 2641857.1975 | 1246766.0018
104 | 2641900.5364 | 1246768.8003
105 | 2641868.9075 | 1246780.47
106 | 2641918.092 | 1246770.2183
107 | 2641884.667 | 1246799.9416
108 | 2642094.8359 | 1246921.7095
109 | 2641965.1151 | 1246721.0108
110 | 2642011.6092 | 1246757.2747
111 | 2641955.4035 | 1246714.0052
112 | 2642029.9998 | 1246787.7039
113 | 2641936.6303 | 1246718.3702
114 | 2642011.6017 | 1246789.5971
115 | 2641996.0068 | 1246774.7831
116 | 2642038.5016 | 1246895.8023
117 | 2642040.6776 | 1246918.1489
118 | 2642053.241 | 1246894.1903
119 | 2642041.0856 | 1246922.3382
120 | 2642053.5189 | 1246894.1525
121 | 2642045.0477 | 1246957.56
122 | 2642017.5768 | 1246922.4669
123 | 2642043.7705 | 1246945.6212
124 | 2642043.9176 | 1246946.8967
125 | 2642003.9076 | 1246922.5418
126 | 2641993.6034 | 1246828.8958
127 | 2641906.3036 | 1246826.6744
128 | 2641908.5451 | 1246829.444
129 | 2641896.4046 | 1246814.4439
130 | 2641914.0985 | 1246836.3054
131 | 2641892.7287 | 1246809.9021
132 | 2641925.0277 | 1247002.1088
133 | 2641951.3848 | 1246921.2472

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97629 | -0.4558 | 0.0013595 | 0.00034071
1 | 0.97638 | -0.45401 | 0.001935 | 0.00048495
2 | 0.97553 | -0.47069 | 0 | 0
3 | 0.97671 | -0.44746 | 0.0013621 | 0.00034138
4 | 0.97544 | -0.47237 | 0.0016635 | 0.0004169
5 | 0.97535 | -0.4742 | 0.0014926 | 0.00037407
6 | 0.97761 | -0.42993 | 0.0020186 | 0.00050592
7 | 0.97544 | -0.4725 | 0.0016774 | 0.0004204
8 | 0.97488 | -0.48341 | 0.0049621 | 0.0012436
9 | 0.97782 | -0.42584 | 0.0015387 | 0.00038563
10 | 0.97538 | -0.47368 | 0.0044471 | 0.0011146
11 | 0.97431 | -0.4946 | 0.0016448 | 0.00041224
12 | 0.98356 | -0.31654 | 0.019157 | 0.0048013
13 | 0.98351 | -0.31748 | 0.0035731 | 0.00089551
14 | 0.98413 | -0.30549 | 0 | 0
15 | 0.9834 | -0.31973 | 0.00419 | 0.0010501
16 | 0.9845 | -0.29825 | 0 | 0
17 | 0.98388 | -0.31021 | 0.00768 | 0.0019248
18 | 0.98338 | -0.32001 | 0.0035821 | 0.00089777
19 | 0.98464 | -0.29548 | 0.0033045 | 0.00082819
20 | 0.98431 | -0.30195 | 0.002536 | 0.00063557
21 | 0.98336 | -0.3204 | 0.0041996 | 0.0010525
22 | 0.98608 | -0.26749 | 0.0033626 | 0.00084275
23 | 0.98422 | -0.30373 | 0 | 0
24 | 0.98993 | -0.19178 | 0.0015232 | 0.00038174
25 | 0.98993 | -0.19168 | 0 | 0
26 | 0.98996 | -0.19121 | 0.00085553 | 0.00021442
27 | 0.98997 | -0.19089 | 0.00089795 | 0.00022505
28 | 0.99002 | -0.18993 | 0 | 0
29 | 0.99088 | -0.17443 | 0.0082489 | 0.0020674
30 | 0.98977 | -0.1959 | 0.002609 | 0.00065389
31 | 0.99214 | -0.1502 | 0 | 0
32 | 0.98951 | -0.20082 | 0.002199 | 0.00055113
33 | 0.9939 | -0.11641 | 0.034567 | 0.0086634
34 | 0.99213 | -0.15049 | 0.0092971 | 0.0023301
35 | 0.98775 | -0.23493 | 0 | 0
36 | 0.9964 | -0.06854 | 0.0021107 | 0.00052898
37 | 0.98716 | -0.24646 | 0.0021897 | 0.00054878
38 | 0.98575 | -0.27384 | 0.0067747 | 0.0016979
39 | 0.99661 | -0.064595 | 0 | 0
40 | 0.98387 | -0.31047 | 0.0014357 | 0.00035983
41 | 0.98453 | -0.29767 | 0.0067947 | 0.0017029
42 | 0.98366 | -0.31451 | 0.029834 | 0.0074771
43 | 0.98469 | -0.29456 | 0.0038631 | 0.00096818
44 | 0.98363 | -0.31516 | 0.00079609 | 0.00019952
45 | 0.98516 | -0.2853 | 0 | 0
46 | 0.98361 | -0.31553 | 0.0012061 | 0.00030227
47 | 0.9836 | -0.31576 | 0.0005761 | 0.00014439
48 | 0.98511 | -0.28625 | 0.0018556 | 0.00046506
49 | 0.99822 | -0.033621 | 0.0022387 | 0.00056107
50 | 0.99834 | -0.031338 | 0.001691 | 0.00042381
51 | 0.99796 | -0.038698 | 0.0011043 | 0.00027678
52 | 0.99943 | -0.010752 | 0 | 0
53 | 0.9969 | -0.058814 | 0.0022646 | 0.00056756
54 | 0.99938 | -0.011809 | 0.0011065 | 0.00027732
55 | 1 | 0 | -0.38877 | -0.09886
56 | 0.99609 | -0.074061 | 0 | 0
57 | 0.99933 | -0.01279 | 0.0038412 | 0.00096269
58 | 0.99491 | -0.096665 | 0.00071605 | 0.00017946
59 | 0.99597 | -0.076469 | 0.0019694 | 0.00049358
60 | 0.98509 | -0.28666 | 0.0027274 | 0.00068356
61 | 0.98961 | -0.19805 | 0.0022585 | 0.00056604
62 | 0.98964 | -0.19746 | 0.0014101 | 0.0003534
63 | 0.98964 | -0.19734 | 0.0022427 | 0.00056206
64 | 0.98972 | -0.19593 | 0.0010439 | 0.00026162
65 | 0.98974 | -0.19549 | 0.0023551 | 0.00059025
66 | 0.99122 | -0.1675 | 0.0025293 | 0.00063391
67 | 0.99123 | -0.16724 | 0.0031306 | 0.00078461
68 | 0.9841 | -0.30596 | 0.0033014 | 0.0008274
69 | 0.98415 | -0.30493 | 0.003555 | 0.00089097
70 | 0.99089 | -0.17384 | 0.0017201 | 0.0004311
71 | 0.99085 | -0.17462 | 0.0011124 | 0.00027878
72 | 0.99095 | -0.17274 | 0.0015221 | 0.00038147
73 | 0.99082 | -0.17526 | 0.0062926 | 0.0015771
74 | 0.99096 | -0.17253 | 0.0014639 | 0.00036688
75 | 0.99098 | -0.1721 | 0.0017117 | 0.000429
76 | 0.99117 | -0.16843 | 0.0020463 | 0.00051285
77 | 0.99571 | -0.081424 | 0.0013754 | 0.0003447
78 | 0.9957 | -0.081746 | 0.0013777 | 0.00034528
79 | 0.99566 | -0.082391 | 0.0022287 | 0.00055855
80 | 0.99566 | -0.082508 | 0.0021403 | 0.00053641
81 | 0.9956 | -0.083588 | 0.0019013 | 0.0004765
82 | 0.99346 | -0.12422 | 0.0010197 | 0.00025555
83 | 0.99468 | -0.10176 | 0.0031495 | 0.00078933
84 | 0.99444 | -0.10641 | 0.0041008 | 0.0010278
85 | 0.9947 | -0.10132 | 0.0030302 | 0.00075943
86 | 0.99431 | -0.10891 | 0 | 0
87 | 0.99506 | -0.094478 | 0.0036023 | 0.00090282
88 | 0.99416 | -0.11177 | 0.0019194 | 0.00048104
89 | 0.99574 | -0.081412 | 0.0066456 | 0.0016655
90 | 0.99412 | -0.11258 | 0.0016832 | 0.00042185
91 | 0.99618 | -0.072938 | 0.0056109 | 0.0014062
92 | 0.98865 | -0.21622 | 0.00068292 | 0.00017116
93 | 0.98793 | -0.23007 | 0.0012771 | 0.00032008
94 | 0.98667 | -0.25415 | 0.0014159 | 0.00035487
95 | 0.99025 | -0.1856 | 0 | 0
96 | 0.98428 | -0.30019 | 0.001088 | 0.00027268
97 | 0.99005 | -0.18951 | 0.0019033 | 0.00047702
98 | 0.99109 | -0.16953 | 0.0029948 | 0.00075057
99 | 0.98293 | -0.32639 | 0.00058917 | 0.00014766
100 | 0.98988 | -0.19284 | 0.0023832 | 0.00059728
101 | 0.99189 | -0.15423 | 0.0035194 | 0.00088204
102 | 0.9941 | -0.11303 | 0.0022384 | 0.00056101
103 | 0.97233 | -0.53366 | 0 | 0
104 | 0.97369 | -0.50696 | 0.0027539 | 0.00069019
105 | 0.97175 | -0.54513 | 0.011202 | 0.0028075
106 | 0.97428 | -0.49526 | 0.0027488 | 0.00068892
107 | 0.97123 | -0.55539 | 0.0066776 | 0.0016736
108 | 0.98984 | -0.19355 | 0.0011916 | 0.00029865
109 | 0.98106 | -0.36264 | 0.0029783 | 0.00074644
110 | 0.98129 | -0.35824 | 0.0022322 | 0.00055944
111 | 0.98105 | -0.36289 | 0 | 0
112 | 0.9815 | -0.35408 | 0 | 0
113 | 0.98103 | -0.3633 | 0.0011463 | 0.0002873
114 | 0.98033 | -0.37679 | 0.0014558 | 0.00036485
115 | 0.97896 | -0.40356 | 0.0015369 | 0.00038519
116 | 0.99278 | -0.13729 | 0 | 0
117 | 0.99207 | -0.15099 | 0.0022886 | 0.00057359
118 | 0.99207 | -0.1508 | 0.0004622 | 0.00011584
119 | 0.99195 | -0.15339 | 0 | 0
120 | 0.99206 | -0.15106 | 0.00048201 | 0.0001208
121 | 0.9913 | -0.16594 | 0.0017077 | 0.00042799
122 | 0.9918 | -0.15614 | 0.0050326 | 0.0012613
123 | 0.9914 | -0.16401 | 0.0023373 | 0.00058578
124 | 0.99137 | -0.16454 | 0 | 0
125 | 0.99178 | -0.15652 | 0.0015699 | 0.00039345
126 | 0.99558 | -0.083954 | 0.0014451 | 0.00036217
127 | 0.9708 | -0.56391 | 0.0039942 | 0.001001
128 | 0.97078 | -0.56443 | 0.0047914 | 0.0012008
129 | 0.97098 | -0.56046 | 0.00098686 | 0.00024733
130 | 0.97075 | -0.56494 | 0.0030893 | 0.00077425
131 | 0.97105 | -0.55907 | 0.002652 | 0.00066464
132 | 0.98641 | -0.26101 | 0.011007 | 0.0027586
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.056332 | -0.014189 | 0.056337 | 0.014192 | 4.8165e-06 | 3.0608e-06 | 0.085884 | 0.085884 | 0.085884 | 0.97629 | -0.4558 | 0.97638 | -0.45401 | 23.5945
1 | 0.054972 | 0.013848 | -0.054933 | -0.013823 | 3.9119e-05 | 2.4851e-05 | 0.083812 | 0.083812 | 0.083812 | 0.97629 | -0.4558 | 0.97553 | -0.47069 | 23.0253
2 | -0.058272 | -0.014677 | 0.05829 | 0.014688 | 1.8256e-05 | 1.1607e-05 | 0.088833 | 0.088833 | 0.088833 | 0.97638 | -0.45401 | 0.97671 | -0.44746 | 24.4046
3 | 0.0077889 | 0.0019521 | -0.0077883 | -0.0019518 | 6.238e-07 | 2.5211e-07 | 0.011881 | 0.011881 | 0.011881 | 0.97553 | -0.47069 | 0.97544 | -0.47237 | 3.264
4 | 0.047144 | 0.011871 | -0.047136 | -0.011866 | 7.9191e-06 | 5.0173e-06 | 0.071931 | 0.071931 | 0.071931 | 0.97553 | -0.47069 | 0.97535 | -0.4742 | 19.7613
5 | -0.059652 | -0.01503 | 0.059702 | 0.015062 | 5.0067e-05 | 3.1841e-05 | 0.090908 | 0.090908 | 0.090908 | 0.97671 | -0.44746 | 0.97761 | -0.42993 | 24.9747
6 | 0.0061248 | 0.0015349 | -0.0061248 | -0.0015349 | 3.8336e-08 | 9.917e-09 | 0.0093432 | 0.0093432 | 0.0093432 | 0.97544 | -0.47237 | 0.97544 | -0.4725 | 2.5668
7 | 0.045644 | 0.011492 | -0.045624 | -0.011479 | 2.0097e-05 | 1.2724e-05 | 0.069654 | 0.069654 | 0.069654 | 0.97535 | -0.4742 | 0.97488 | -0.48341 | 19.1358
8 | -0.061721 | -0.015568 | 0.061733 | 0.015575 | 1.2073e-05 | 7.6813e-06 | 0.09398 | 0.09398 | 0.09398 | 0.97761 | -0.42993 | 0.97782 | -0.42584 | 25.8188
9 | 0.0044474 | 0.0011145 | -0.0044471 | -0.0011146 | 2.4945e-07 | -2.074e-08 | 0.0067844 | 0.0067845 | 0.0067845 | 0.97544 | -0.4725 | 0.97538 | -0.47368 | 1.8639
10 | 0.040662 | 0.010236 | -0.04064 | -0.010222 | 2.1728e-05 | 1.3719e-05 | 0.06208 | 0.06208 | 0.06208 | 0.97488 | -0.48341 | 0.97431 | -0.4946 | 17.055
11 | -0.063271 | -0.015961 | 0.063339 | 0.016004 | 6.7565e-05 | 4.2998e-05 | 0.096322 | 0.096322 | 0.096322 | 0.97782 | -0.42584 | 0.97896 | -0.40356 | 26.4621
12 | 0.038995 | 0.0098097 | -0.038994 | -0.009809 | 1.2295e-06 | 7.7534e-07 | 0.059568 | 0.059568 | 0.059568 | 0.97431 | -0.4946 | 0.97428 | -0.49526 | 16.3649
13 | 0.015547 | 0.003897 | -0.015546 | -0.0038966 | 6.9579e-07 | 4.0274e-07 | 0.023521 | 0.023521 | 0.023521 | 0.98356 | -0.31654 | 0.98351 | -0.31748 | 6.4619
14 | -0.034704 | -0.0086983 | 0.034723 | 0.0087098 | 1.8285e-05 | 1.1478e-05 | 0.052504 | 0.052504 | 0.052504 | 0.98356 | -0.31654 | 0.98413 | -0.30549 | 14.4242
15 | 0.011973 | 0.0030011 | -0.011972 | -0.0030004 | 1.2824e-06 | 6.8853e-07 | 0.018115 | 0.018115 | 0.018115 | 0.98351 | -0.31748 | 0.9834 | -0.31973 | 4.9767
16 | -0.042404 | -0.010635 | 0.042419 | 0.010644 | 1.4632e-05 | 9.2441e-06 | 0.064119 | 0.064119 | 0.064119 | 0.98413 | -0.30549 | 0.9845 | -0.29825 | 17.6151
17 | 0.0076817 | 0.0019255 | -0.00768 | -0.0019248 | 1.7252e-06 | 6.7093e-07 | 0.011615 | 0.011615 | 0.011615 | 0.98413 | -0.30549 | 0.98388 | -0.31021 | 3.191
18 | 0.0077819 | 0.0019503 | -0.0077818 | -0.0019503 | 1.0175e-07 | 4.0292e-08 | 0.011775 | 0.011775 | 0.011775 | 0.9834 | -0.31973 | 0.98338 | -0.32001 | 3.2349
19 | -0.051814 | -0.012999 | 0.051821 | 0.013004 | 6.8489e-06 | 4.3454e-06 | 0.078319 | 0.078319 | 0.078319 | 0.9845 | -0.29825 | 0.98464 | -0.29548 | 21.5163
20 | 0.0093952 | 0.0023549 | -0.0093935 | -0.0023541 | 1.6554e-06 | 7.8114e-07 | 0.0142 | 0.014201 | 0.014201 | 0.9845 | -0.29825 | 0.98431 | -0.30195 | 3.9012
21 | 0.0041997 | 0.0010525 | -0.0041996 | -0.0010525 | 7.9243e-08 | -1.567e-08 | 0.0063548 | 0.0063548 | 0.0063548 | 0.98338 | -0.32001 | 0.98336 | -0.3204 | 1.7458
22 | -0.055126 | -0.013832 | 0.055199 | 0.013879 | 7.3695e-05 | 4.6804e-05 | 0.083313 | 0.083313 | 0.083313 | 0.98464 | -0.29548 | 0.98608 | -0.26749 | 22.8882
23 | 0.0068575 | 0.0017186 | -0.006857 | -0.0017184 | 5.8129e-07 | 1.8871e-07 | 0.010367 | 0.010367 | 0.010367 | 0.98431 | -0.30195 | 0.98422 | -0.30373 | 2.848
24 | -0.058562 | -0.014721 | 0.05858 | 0.014733 | 1.81e-05 | 1.1505e-05 | 0.088387 | 0.088387 | 0.088387 | 0.98608 | -0.26749 | 0.98641 | -0.26101 | 24.2822
25 | 0.006857 | 0.0017184 | -0.0068566 | -0.0017183 | 3.9126e-07 | 1.2704e-07 | 0.010367 | 0.010367 | 0.010367 | 0.98422 | -0.30373 | 0.98415 | -0.30493 | 2.848
26 | -0.0015232 | -0.00038174 | 0.0015232 | 0.0003817 | 7.3784e-09 | -4.3534e-08 | 0.0022895 | 0.0022895 | 0.0022895 | 0.98993 | -0.19178 | 0.98993 | -0.19168 | 0.629
27 | -0.0015232 | -0.0003817 | 0.0015232 | 0.00038149 | 3.4462e-08 | -2.0335e-07 | 0.0022895 | 0.0022895 | 0.0022895 | 0.98993 | -0.19168 | 0.98996 | -0.19121 | 0.62899
28 | -0.0023787 | -0.00059591 | 0.0023788 | 0.00059584 | 3.5197e-08 | -7.1875e-08 | 0.0035754 | 0.0035754 | 0.0035754 | 0.98996 | -0.19121 | 0.98997 | -0.19089 | 0.98226
29 | -0.0032767 | -0.00082089 | 0.0032769 | 0.00082077 | 1.5108e-07 | -1.1688e-07 | 0.0049251 | 0.004925 | 0.0049251 | 0.98997 | -0.19089 | 0.99002 | -0.18993 | 1.353
30 | -0.081773 | -0.020913 | 0.08179 | 0.020924 | 1.7132e-05 | 1.0926e-05 | 0.12306 | 0.12306 | 0.12306 | 0.99002 | -0.18993 | 0.99025 | -0.1856 | 33.8065
31 | 0.078496 | 0.020093 | -0.078396 | -0.020029 | 9.9818e-05 | 6.3638e-05 | 0.11813 | 0.11813 | 0.11813 | 0.99002 | -0.18993 | 0.98865 | -0.21622 | 32.4535
32 | 0.1331 | 0.033658 | -0.13296 | -0.03357 | 0.00013691 | 8.7506e-05 | 0.19998 | 0.19998 | 0.19998 | 0.99088 | -0.17443 | 0.98977 | -0.1959 | 54.9393
33 | -0.14135 | -0.035725 | 0.14151 | 0.03583 | 0.00016439 | 0.00010471 | 0.21237 | 0.21237 | 0.21237 | 0.99088 | -0.17443 | 0.99214 | -0.1502 | 29.1712
34 | 0.13035 | 0.032917 | -0.13032 | -0.032897 | 3.0772e-05 | 1.9667e-05 | 0.19606 | 0.19606 | 0.19606 | 0.98977 | -0.1959 | 0.98951 | -0.20082 | 53.8618
35 | -0.15081 | -0.03816 | 0.15105 | 0.038316 | 0.000245 | 0.00015614 | 0.22631 | 0.22631 | 0.22631 | 0.99214 | -0.1502 | 0.9939 | -0.11641 | 31.0866
36 | 0.0092972 | 0.0023301 | -0.0092971 | -0.0023301 | 1.2783e-07 | 5.9172e-08 | 0.013944 | 0.013944 | 0.013944 | 0.99214 | -0.1502 | 0.99213 | -0.15049 | 3.8308
37 | 0.12812 | 0.032346 | -0.12791 | -0.032212 | 0.00020896 | 0.00013354 | 0.19275 | 0.19275 | 0.19275 | 0.98951 | -0.20082 | 0.98775 | -0.23493 | 52.9533
38 | -0.18562 | -0.04698 | 0.18605 | 0.047253 | 0.00042759 | 0.00027289 | 0.27806 | 0.27806 | 0.27806 | 0.9939 | -0.11641 | 0.9964 | -0.06854 | 38.1953
39 | 0.071864 | 0.018096 | -0.071825 | -0.018071 | 3.9592e-05 | 2.5223e-05 | 0.10829 | 0.10829 | 0.10829 | 0.98775 | -0.23493 | 0.98716 | -0.24646 | 29.7505
40 | 0.056047 | 0.014116 | -0.055943 | -0.01405 | 0.00010407 | 6.6107e-05 | 0.084458 | 0.084458 | 0.084458 | 0.98775 | -0.23493 | 0.98575 | -0.27384 | 23.2029
41 | -0.18816 | -0.047782 | 0.18819 | 0.047804 | 3.5727e-05 | 2.2803e-05 | 0.28121 | 0.28121 | 0.28121 | 0.9964 | -0.06854 | 0.99661 | -0.064595 | 38.6283
42 | 0.069635 | 0.017522 | -0.069587 | -0.017492 | 4.84e-05 | 3.0826e-05 | 0.10499 | 0.10499 | 0.10499 | 0.98716 | -0.24646 | 0.98641 | -0.26101 | 28.8438
43 | 0.049169 | 0.012352 | -0.049142 | -0.012335 | 2.6875e-05 | 1.7035e-05 | 0.074232 | 0.074232 | 0.074232 | 0.98575 | -0.27384 | 0.98516 | -0.2853 | 20.3934
44 | -0.22022 | -0.055846 | 0.2209 | 0.056284 | 0.00068616 | 0.00043826 | 0.32904 | 0.32904 | 0.32904 | 0.99661 | -0.064595 | 1 | 0 | 45.1972
45 | 0.032025 | 0.0080413 | -0.032013 | -0.0080333 | 1.2741e-05 | 7.9609e-06 | 0.047822 | 0.047822 | 0.047822 | 0.99661 | -0.064595 | 0.99618 | -0.072938 | 13.1379
46 | -0.033854 | -0.008486 | 0.033875 | 0.0084989 | 2.0662e-05 | 1.2957e-05 | 0.051202 | 0.051202 | 0.051202 | 0.98387 | -0.31047 | 0.98453 | -0.29767 | 14.0665
47 | 0.032419 | 0.0081261 | -0.032412 | -0.0081222 | 6.2389e-06 | 3.905e-06 | 0.049031 | 0.049031 | 0.049031 | 0.98387 | -0.31047 | 0.98366 | -0.31451 | 13.47
48 | -0.04067 | -0.010202 | 0.040676 | 0.010206 | 6.0149e-06 | 3.7955e-06 | 0.061471 | 0.061471 | 0.061471 | 0.98453 | -0.29767 | 0.98469 | -0.29456 | 16.8878
49 | 0.0025784 | 0.00064512 | -0.0025783 | -0.00064525 | 8.0524e-08 | -1.2767e-07 | 0.0039 | 0.0039001 | 0.0039001 | 0.98366 | -0.31451 | 0.98363 | -0.31516 | 1.0714
50 | -0.044539 | -0.011174 | 0.044558 | 0.011186 | 1.9686e-05 | 1.2451e-05 | 0.067309 | 0.067309 | 0.067309 | 0.98469 | -0.29456 | 0.98516 | -0.2853 | 18.4915
51 | 0.0012061 | 0.00030207 | -0.0012061 | -0.00030227 | 2.1078e-08 | -2.0083e-07 | 0.0018245 | 0.0018245 | 0.0018245 | 0.98363 | -0.31516 | 0.98361 | -0.31553 | 0.50125
52 | 0.00057612 | 0.00014367 | -0.0005761 | -0.00014439 | 1.6386e-08 | -7.1992e-07 | 0.00087128 | 0.00087154 | 0.00087154 | 0.98363 | -0.31516 | 0.9836 | -0.31576 | 0.23944
53 | 0.0045833 | 0.0011485 | -0.0045831 | -0.0011485 | 2.0862e-07 | -1.4283e-08 | 0.0069227 | 0.0069228 | 0.0069228 | 0.98516 | -0.2853 | 0.98511 | -0.28625 | 1.9019
54 | 0.0027275 | 0.00068348 | -0.0027274 | -0.00068356 | 5.308e-08 | -7.2201e-08 | 0.0041198 | 0.0041199 | 0.0041199 | 0.98511 | -0.28625 | 0.98509 | -0.28666 | 1.1318
55 | -0.15931 | -0.040743 | 0.15933 | 0.040754 | 1.7599e-05 | 1.122e-05 | 0.23776 | 0.23776 | 0.23776 | 0.99822 | -0.033621 | 0.99834 | -0.031338 | 32.6599
56 | 0.15707 | 0.040182 | -0.15703 | -0.040157 | 3.8588e-05 | 2.4599e-05 | 0.23443 | 0.23443 | 0.23443 | 0.99822 | -0.033621 | 0.99796 | -0.038698 | 32.2015
57 | -0.16102 | -0.041178 | 0.16118 | 0.04128 | 0.00016057 | 0.00010238 | 0.24028 | 0.24028 | 0.24028 | 0.99834 | -0.031338 | 0.99943 | -0.010752 | 33.0061
58 | 0.15593 | 0.039881 | -0.15577 | -0.039784 | 0.00015164 | 9.6662e-05 | 0.23278 | 0.23278 | 0.23278 | 0.99796 | -0.038698 | 0.9969 | -0.058814 | 31.9753
59 | 0.0049481 | 0.0012399 | -0.0049479 | -0.0012399 | 2.49e-07 | -9.5384e-10 | 0.007367 | 0.0073671 | 0.0073671 | 0.99943 | -0.010752 | 0.99938 | -0.011809 | 2.0239
60 | -0.16612 | -0.04252 | 0.16621 | 0.042576 | 8.6543e-05 | 5.519e-05 | 0.24765 | 0.24765 | 0.24765 | 0.99943 | -0.010752 | 1 | 0 | 34.018
61 | 0.15351 | 0.039216 | -0.1534 | -0.039144 | 0.00011307 | 7.2068e-05 | 0.2294 | 0.2294 | 0.2294 | 0.9969 | -0.058814 | 0.99609 | -0.074061 | 31.511
62 | 0.0038414 | 0.00096262 | -0.0038412 | -0.00096269 | 1.7963e-07 | -7.6888e-08 | 0.0057195 | 0.0057196 | 0.0057196 | 0.99938 | -0.011809 | 0.99933 | -0.01279 | 1.5713
63 | 0.14095 | 0.036025 | -0.1408 | -0.035927 | 0.00015392 | 9.8031e-05 | 0.21081 | 0.21081 | 0.21081 | 0.99609 | -0.074061 | 0.99491 | -0.096665 | 28.9579
64 | 0.012442 | 0.0031191 | -0.012441 | -0.0031183 | 1.4272e-06 | 7.7005e-07 | 0.018587 | 0.018587 | 0.018587 | 0.99609 | -0.074061 | 0.99597 | -0.076469 | 5.1064
65 | 0.14008 | 0.035748 | -0.1399 | -0.035629 | 0.0001862 | 0.00011858 | 0.20974 | 0.20974 | 0.20974 | 0.99491 | -0.096665 | 0.99346 | -0.12422 | 28.8108
66 | 0.010471 | 0.0026247 | -0.010469 | -0.0026235 | 2.4718e-06 | 1.2316e-06 | 0.015645 | 0.015645 | 0.015645 | 0.99597 | -0.076469 | 0.99571 | -0.081424 | 4.2981
67 | -0.0022585 | -0.00056604 | 0.0022586 | 0.00056589 | 6.2609e-08 | -1.4594e-07 | 0.003396 | 0.0033959 | 0.003396 | 0.98961 | -0.19805 | 0.98964 | -0.19746 | 0.93296
68 | -0.0036687 | -0.00091929 | 0.0036687 | 0.00091928 | 2.1497e-08 | -1.0449e-08 | 0.0055161 | 0.0055161 | 0.0055161 | 0.98964 | -0.19746 | 0.98964 | -0.19734 | 1.5154
69 | -0.0059113 | -0.0014813 | 0.0059117 | 0.0014814 | 3.9658e-07 | 8.179e-08 | 0.0088881 | 0.0088881 | 0.0088881 | 0.98964 | -0.19734 | 0.98972 | -0.19593 | 2.4418
70 | -0.0069556 | -0.001743 | 0.0069557 | 0.0017431 | 1.4565e-07 | 4.7574e-08 | 0.010457 | 0.010457 | 0.010457 | 0.98972 | -0.19593 | 0.98974 | -0.19549 | 2.8729
71 | -0.0093109 | -0.0023333 | 0.0093117 | 0.0023337 | 8.6008e-07 | 4.0001e-07 | 0.013998 | 0.013998 | 0.013998 | 0.98974 | -0.19549 | 0.98984 | -0.19355 | 3.8457
72 | -0.0025293 | -0.00063391 | 0.0025293 | 0.00063385 | 3.0484e-08 | -5.317e-08 | 0.003797 | 0.003797 | 0.003797 | 0.99122 | -0.1675 | 0.99123 | -0.16724 | 1.0431
73 | -0.00566 | -0.0014185 | 0.0056603 | 0.0014185 | 3.5079e-07 | 5.7468e-08 | 0.0084966 | 0.0084966 | 0.0084966 | 0.99123 | -0.16724 | 0.9913 | -0.16594 | 2.3342
74 | -0.0033014 | -0.0008274 | 0.0033015 | 0.00082728 | 1.6269e-07 | -1.171e-07 | 0.0049919 | 0.0049918 | 0.0049919 | 0.9841 | -0.30596 | 0.98415 | -0.30493 | 1.3714
75 | 0.0074054 | 0.001856 | -0.0074051 | -0.0018559 | 2.7533e-07 | 9.9738e-08 | 0.011121 | 0.011121 | 0.011121 | 0.99089 | -0.17384 | 0.99085 | -0.17462 | 3.0551
76 | -0.0091255 | -0.0022871 | 0.009126 | 0.0022873 | 4.7824e-07 | 2.1859e-07 | 0.013704 | 0.013704 | 0.013704 | 0.99089 | -0.17384 | 0.99095 | -0.17274 | 3.7648
77 | 0.0062928 | 0.0015771 | -0.0062926 | -0.0015771 | 1.9065e-07 | 4.8695e-08 | 0.0094502 | 0.0094502 | 0.0094502 | 0.99085 | -0.17462 | 0.99082 | -0.17526 | 2.5962
78 | -0.010648 | -0.0026688 | 0.010648 | 0.0026688 | 1.0836e-07 | 5.4789e-08 | 0.015989 | 0.015989 | 0.015989 | 0.99095 | -0.17274 | 0.99096 | -0.17253 | 4.3927
79 | -0.012112 | -0.0030357 | 0.012112 | 0.0030359 | 2.4663e-07 | 1.3223e-07 | 0.018187 | 0.018187 | 0.018187 | 0.99096 | -0.17253 | 0.99098 | -0.1721 | 4.9965
80 | -0.013824 | -0.0034649 | 0.013826 | 0.0034662 | 2.4188e-06 | 1.3551e-06 | 0.020758 | 0.020758 | 0.020758 | 0.99098 | -0.1721 | 0.99117 | -0.16843 | 5.7027
81 | -0.015873 | -0.0039791 | 0.015876 | 0.0039808 | 2.9421e-06 | 1.7048e-06 | 0.02383 | 0.02383 | 0.02383 | 0.99117 | -0.16843 | 0.99137 | -0.16454 | 6.5466
82 | 0.0090936 | 0.0022788 | -0.0090935 | -0.0022787 | 1.3944e-07 | 6.3054e-08 | 0.01359 | 0.01359 | 0.01359 | 0.99571 | -0.081424 | 0.9957 | -0.081746 | 3.7334
83 | 0.0077158 | 0.0019334 | -0.0077156 | -0.0019333 | 2.3697e-07 | 8.9844e-08 | 0.011531 | 0.011531 | 0.011531 | 0.9957 | -0.081746 | 0.99566 | -0.082391 | 3.1678
84 | 0.0054869 | 0.0013748 | -0.0054869 | -0.0013748 | 3.0693e-08 | 3.8125e-09 | 0.0082 | 0.0082 | 0.0082 | 0.99566 | -0.082391 | 0.99566 | -0.082508 | 2.2528
85 | 0.0033466 | 0.00083838 | -0.0033464 | -0.0008385 | 1.7209e-07 | -1.2845e-07 | 0.0050013 | 0.0050014 | 0.0050014 | 0.99566 | -0.082508 | 0.9956 | -0.083588 | 1.374
86 | 0.0014451 | 0.000362 | -0.0014451 | -0.00036217 | 2.5213e-08 | -1.7129e-07 | 0.0021598 | 0.0021598 | 0.0021598 | 0.9956 | -0.083588 | 0.99558 | -0.083954 | 0.59337
87 | 0.13888 | 0.035374 | -0.13879 | -0.035318 | 8.7518e-05 | 5.5733e-05 | 0.20822 | 0.20822 | 0.20822 | 0.99346 | -0.12422 | 0.99278 | -0.13729 | 28.601
88 | 0.0099458 | 0.0024928 | -0.0099436 | -0.0024918 | 2.2034e-06 | 1.0657e-06 | 0.014879 | 0.014879 | 0.014879 | 0.99468 | -0.10176 | 0.99444 | -0.10641 | 4.0876
89 | -0.013095 | -0.0032822 | 0.013095 | 0.0032823 | 2.7328e-07 | 1.5025e-07 | 0.01959 | 0.01959 | 0.01959 | 0.99468 | -0.10176 | 0.9947 | -0.10132 | 5.3819
90 | 0.0058427 | 0.001464 | -0.005842 | -0.0014639 | 6.967e-07 | 1.3057e-07 | 0.0087425 | 0.0087426 | 0.0087426 | 0.99444 | -0.10641 | 0.99431 | -0.10891 | 2.4018
91 | -0.016126 | -0.0040418 | 0.016131 | 0.0040448 | 5.2592e-06 | 3.0529e-06 | 0.024123 | 0.024123 | 0.024123 | 0.9947 | -0.10132 | 0.99506 | -0.094478 | 6.6272
92 | 0.005842 | 0.0014639 | -0.0058412 | -0.0014637 | 7.9455e-07 | 1.4902e-07 | 0.0087426 | 0.0087428 | 0.0087428 | 0.99431 | -0.10891 | 0.99416 | -0.11177 | 2.4019
93 | -0.019733 | -0.0049476 | 0.019746 | 0.004955 | 1.2295e-05 | 7.3795e-06 | 0.02951 | 0.02951 | 0.02951 | 0.99506 | -0.094478 | 0.99574 | -0.081412 | 8.1071
94 | 0.0039218 | 0.00098268 | -0.0039217 | -0.00098274 | 1.5063e-07 | -5.4749e-08 | 0.0058699 | 0.00587 | 0.00587 | 0.99416 | -0.11177 | 0.99412 | -0.11258 | 1.6126
95 | -0.026391 | -0.0066205 | 0.026402 | 0.0066271 | 1.0666e-05 | 6.5886e-06 | 0.039441 | 0.039441 | 0.039441 | 0.99574 | -0.081412 | 0.99618 | -0.072938 | 10.8354
96 | 0.0022385 | 0.00056089 | -0.0022384 | -0.00056101 | 4.8065e-08 | -1.1727e-07 | 0.0033506 | 0.0033506 | 0.0033506 | 0.99412 | -0.11258 | 0.9941 | -0.11303 | 0.9205
97 | 0.077713 | 0.019858 | -0.077661 | -0.019825 | 5.2002e-05 | 3.3152e-05 | 0.1171 | 0.1171 | 0.1171 | 0.98865 | -0.21622 | 0.98793 | -0.23007 | 32.1712
98 | 0.076384 | 0.019505 | -0.076295 | -0.019448 | 8.879e-05 | 5.6597e-05 | 0.11518 | 0.11518 | 0.11518 | 0.98793 | -0.23007 | 0.98667 | -0.25415 | 31.6427
99 | 0.074879 | 0.019093 | -0.074713 | -0.018987 | 0.00016602 | 0.00010581 | 0.11304 | 0.11304 | 0.11304 | 0.98667 | -0.25415 | 0.98428 | -0.30019 | 31.0561
100 | 0.014795 | 0.0037096 | -0.014792 | -0.003708 | 2.7559e-06 | 1.5725e-06 | 0.022233 | 0.022233 | 0.022233 | 0.99025 | -0.1856 | 0.99005 | -0.18951 | 6.1079
101 | -0.096585 | -0.024634 | 0.09666 | 0.024681 | 7.5001e-05 | 4.7513e-05 | 0.14529 | 0.14529 | 0.14529 | 0.99025 | -0.1856 | 0.99109 | -0.16953 | 19.9572
102 | 0.073625 | 0.018715 | -0.073533 | -0.018656 | 9.2803e-05 | 5.9141e-05 | 0.1114 | 0.1114 | 0.1114 | 0.98428 | -0.30019 | 0.98293 | -0.32639 | 30.6043
103 | 0.012889 | 0.003231 | -0.012887 | -0.0032298 | 2.0482e-06 | 1.1237e-06 | 0.019372 | 0.019372 | 0.019372 | 0.99005 | -0.18951 | 0.98988 | -0.19284 | 5.322
104 | -0.099655 | -0.025432 | 0.099729 | 0.025479 | 7.3741e-05 | 4.6742e-05 | 0.14978 | 0.14978 | 0.14978 | 0.99109 | -0.16953 | 0.99189 | -0.15423 | 20.5748
105 | 0.072943 | 0.018508 | -0.072847 | -0.018446 | 9.6972e-05 | 6.1794e-05 | 0.11051 | 0.11051 | 0.11051 | 0.98293 | -0.32639 | 0.9815 | -0.35408 | 30.3593
106 | 0.010504 | 0.0026326 | -0.010503 | -0.0026324 | 3.5537e-07 | 1.7857e-07 | 0.01579 | 0.01579 | 0.01579 | 0.98988 | -0.19284 | 0.98984 | -0.19355 | 4.3378
107 | -0.10325 | -0.026361 | 0.10326 | 0.026371 | 1.5819e-05 | 1.0034e-05 | 0.15506 | 0.15506 | 0.15506 | 0.99189 | -0.15423 | 0.99206 | -0.15106 | 21.3
108 | -0.033428 | -0.0083904 | 0.033471 | 0.0084171 | 4.2629e-05 | 2.6743e-05 | 0.051162 | 0.051161 | 0.051162 | 0.97233 | -0.53366 | 0.97369 | -0.50696 | 14.0554
109 | 0.033428 | 0.0083904 | -0.03341 | -0.0083789 | 1.827e-05 | 1.1462e-05 | 0.051162 | 0.051162 | 0.051162 | 0.97233 | -0.53366 | 0.97175 | -0.54513 | 14.0554
110 | -0.036225 | -0.0091073 | 0.036245 | 0.00912 | 2.0249e-05 | 1.274e-05 | 0.05537 | 0.05537 | 0.05537 | 0.97369 | -0.50696 | 0.97428 | -0.49526 | 15.2115
111 | 0.022208 | 0.0055714 | -0.022197 | -0.0055648 | 1.0865e-05 | 6.6431e-06 | 0.034008 | 0.034008 | 0.034008 | 0.97175 | -0.54513 | 0.97123 | -0.55539 | 9.343
112 | 0.015519 | 0.0038912 | -0.015517 | -0.0038896 | 2.7168e-06 | 1.5802e-06 | 0.023778 | 0.023778 | 0.023778 | 0.97123 | -0.55539 | 0.97105 | -0.55907 | 6.5324
113 | -0.0041247 | -0.0010334 | 0.0041256 | 0.0010332 | 8.6551e-07 | -1.9094e-07 | 0.0062559 | 0.0062557 | 0.0062559 | 0.98106 | -0.36264 | 0.98129 | -0.35824 | 1.7187
114 | 0.0011464 | 0.00028692 | -0.0011464 | -0.00028706 | 1.3574e-08 | -1.4252e-07 | 0.0017386 | 0.0017387 | 0.0017387 | 0.98106 | -0.36264 | 0.98105 | -0.36289 | 0.47765
115 | -0.0063577 | -0.0015926 | 0.006359 | 0.001593 | 1.2594e-06 | 3.4943e-07 | 0.0096405 | 0.0096404 | 0.0096405 | 0.98129 | -0.35824 | 0.9815 | -0.35408 | 2.6485
116 | 0.0011464 | 0.00028706 | -0.0011463 | -0.0002873 | 2.2273e-08 | -2.3382e-07 | 0.0017387 | 0.0017387 | 0.0017387 | 0.98105 | -0.36289 | 0.98103 | -0.3633 | 0.47768
117 | 0.066488 | 0.016853 | -0.066415 | -0.016807 | 7.2479e-05 | 4.6146e-05 | 0.10087 | 0.10087 | 0.10087 | 0.9815 | -0.35408 | 0.98033 | -0.37679 | 27.7109
118 | 0.064959 | 0.016442 | -0.064876 | -0.016389 | 8.3378e-05 | 5.3075e-05 | 0.098658 | 0.098658 | 0.098658 | 0.98033 | -0.37679 | 0.97896 | -0.40356 | 27.1038
119 | 0.034513 | 0.0086665 | -0.034491 | -0.0086523 | 2.2536e-05 | 1.4133e-05 | 0.051736 | 0.051736 | 0.051736 | 0.99278 | -0.13729 | 0.99207 | -0.15099 | 14.2132
120 | 0.10428 | 0.026651 | -0.10421 | -0.026608 | 6.8087e-05 | 4.3192e-05 | 0.15648 | 0.15648 | 0.15648 | 0.99278 | -0.13729 | 0.99207 | -0.1508 | 21.4945
121 | 0.032202 | 0.0080787 | -0.032198 | -0.0080764 | 3.6827e-06 | 2.3026e-06 | 0.048303 | 0.048303 | 0.048303 | 0.99207 | -0.15099 | 0.99195 | -0.15339 | 13.2701
122 | 0.10375 | 0.026492 | -0.10375 | -0.026492 | 1.2762e-06 | 8.095e-07 | 0.15579 | 0.15579 | 0.15579 | 0.99207 | -0.1508 | 0.99206 | -0.15106 | 21.3993
123 | 0.0066034 | 0.0016548 | -0.0066026 | -0.0016546 | 8.6506e-07 | 2.5021e-07 | 0.0099057 | 0.0099059 | 0.0099059 | 0.99195 | -0.15339 | 0.9918 | -0.15614 | 2.7214
124 | 0.025595 | 0.0064216 | -0.025582 | -0.0064136 | 1.2958e-05 | 7.9909e-06 | 0.038398 | 0.038398 | 0.038398 | 0.99195 | -0.15339 | 0.9914 | -0.16401 | 10.5488
125 | -0.007368 | -0.0018465 | 0.0073685 | 0.0018467 | 4.9187e-07 | 1.7655e-07 | 0.01106 | 0.01106 | 0.01106 | 0.9913 | -0.16594 | 0.99137 | -0.16454 | 3.0385
126 | 0.0015699 | 0.0003933 | -0.0015699 | -0.00039345 | 2.8438e-08 | -1.582e-07 | 0.0023553 | 0.0023554 | 0.0023554 | 0.9918 | -0.15614 | 0.99178 | -0.15652 | 0.64709
127 | 0.023245 | 0.0058278 | -0.023244 | -0.0058275 | 5.8613e-07 | 3.5857e-07 | 0.03489 | 0.03489 | 0.03489 | 0.9914 | -0.16401 | 0.99137 | -0.16454 | 9.585
128 | 0.0078809 | 0.0019751 | -0.0078807 | -0.001975 | 1.9496e-07 | 8.0722e-08 | 0.01208 | 0.01208 | 0.01208 | 0.9708 | -0.56391 | 0.97078 | -0.56443 | 3.3186
129 | -0.011875 | -0.0029761 | 0.011877 | 0.0029772 | 1.9548e-06 | 1.0565e-06 | 0.018202 | 0.018202 | 0.018202 | 0.9708 | -0.56391 | 0.97098 | -0.56046 | 5.0005
130 | 0.0030894 | 0.00077419 | -0.0030893 | -0.00077425 | 7.4228e-08 | -6.1628e-08 | 0.0047354 | 0.0047354 | 0.0047354 | 0.97078 | -0.56443 | 0.97075 | -0.56494 | 1.3009
131 | -0.012864 | -0.0032245 | 0.012865 | 0.003225 | 8.5157e-07 | 4.7273e-07 | 0.019714 | 0.019714 | 0.019714 | 0.97098 | -0.56046 | 0.97105 | -0.55907 | 5.4159

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39041 | 0.099273

## res_load
| p_mw | q_mvar
0 | 0.0013595 | 0.00034071
1 | 0.001935 | 0.00048495
2 | 0.0013621 | 0.00034138
3 | 0.0016635 | 0.0004169
4 | 0.0014926 | 0.00037407
5 | 0.0020186 | 0.00050592
6 | 0.0016774 | 0.0004204
7 | 0.0049621 | 0.0012436
8 | 0.0015387 | 0.00038563
9 | 0.0044471 | 0.0011146
10 | 0.0016448 | 0.00041224
11 | 0.019157 | 0.0048013
12 | 0.0035731 | 0.00089551
13 | 0.00419 | 0.0010501
14 | 0.00768 | 0.0019248
15 | 0.0035821 | 0.00089777
16 | 0.0033045 | 0.00082819
17 | 0.002536 | 0.00063557
18 | 0.0041996 | 0.0010525
19 | 0.0033626 | 0.00084275
20 | 0.0015232 | 0.00038174
21 | 0.00085553 | 0.00021442
22 | 0.00089795 | 0.00022505
23 | 0.0082489 | 0.0020674
24 | 0.002609 | 0.00065389
25 | 0.002199 | 0.00055113
26 | 0.034567 | 0.0086634
27 | 0.0092971 | 0.0023301
28 | 0.0021107 | 0.00052898
29 | 0.0021897 | 0.00054878
30 | 0.0067747 | 0.0016979
31 | 0.0014357 | 0.00035983
32 | 0.0067947 | 0.0017029
33 | 0.029834 | 0.0074771
34 | 0.0038631 | 0.00096818
35 | 0.00079609 | 0.00019952
36 | 0.0012061 | 0.00030227
37 | 0.0005761 | 0.00014439
38 | 0.0018556 | 0.00046506
39 | 0.0022387 | 0.00056107
40 | 0.001691 | 0.00042381
41 | 0.0011043 | 0.00027678
42 | 0.0022646 | 0.00056756
43 | 0.0011065 | 0.00027732
44 | 0.0016479 | 0.000413
45 | 0.0038412 | 0.00096269
46 | 0.00071605 | 0.00017946
47 | 0.0019694 | 0.00049358
48 | 0.0027274 | 0.00068356
49 | 0.0022585 | 0.00056604
50 | 0.0014101 | 0.0003534
51 | 0.0022427 | 0.00056206
52 | 0.0010439 | 0.00026162
53 | 0.0023551 | 0.00059025
54 | 0.0025293 | 0.00063391
55 | 0.0031306 | 0.00078461
56 | 0.0033014 | 0.0008274
57 | 0.003555 | 0.00089097
58 | 0.0017201 | 0.0004311
59 | 0.0011124 | 0.00027878
60 | 0.0015221 | 0.00038147
61 | 0.0062926 | 0.0015771
62 | 0.0014639 | 0.00036688
63 | 0.0017117 | 0.000429
64 | 0.0020463 | 0.00051285
65 | 0.0013754 | 0.0003447
66 | 0.0013777 | 0.00034528
67 | 0.0022287 | 0.00055855
68 | 0.0021403 | 0.00053641
69 | 0.0019013 | 0.0004765
70 | 0.0010197 | 0.00025555
71 | 0.0031495 | 0.00078933
72 | 0.0041008 | 0.0010278
73 | 0.0030302 | 0.00075943
74 | 0.0036023 | 0.00090282
75 | 0.0019194 | 0.00048104
76 | 0.0066456 | 0.0016655
77 | 0.0016832 | 0.00042185
78 | 0.0056109 | 0.0014062
79 | 0.00068292 | 0.00017116
80 | 0.0012771 | 0.00032008
81 | 0.0014159 | 0.00035487
82 | 0.001088 | 0.00027268
83 | 0.0019033 | 0.00047702
84 | 0.0029948 | 0.00075057
85 | 0.00058917 | 0.00014766
86 | 0.0023832 | 0.00059728
87 | 0.0035194 | 0.00088204
88 | 0.0022384 | 0.00056101
89 | 0.0027539 | 0.00069019
90 | 0.011202 | 0.0028075
91 | 0.0027488 | 0.00068892
92 | 0.0066776 | 0.0016736
93 | 0.0011916 | 0.00029865
94 | 0.0029783 | 0.00074644
95 | 0.0022322 | 0.00055944
96 | 0.0011463 | 0.0002873
97 | 0.0014558 | 0.00036485
98 | 0.0015369 | 0.00038519
99 | 0.0022886 | 0.00057359
100 | 0.0004622 | 0.00011584
101 | 0.00048201 | 0.0001208
102 | 0.0017077 | 0.00042799
103 | 0.0050326 | 0.0012613
104 | 0.0023373 | 0.00058578
105 | 0.0015699 | 0.00039345
106 | 0.0014451 | 0.00036217
107 | 0.0039942 | 0.001001
108 | 0.0047914 | 0.0012008
109 | 0.00098686 | 0.00024733
110 | 0.0030893 | 0.00077425
111 | 0.002652 | 0.00066464
112 | 0.011007 | 0.0027586

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1